## Cover
Bill of Quantities
Project : Construction of N. Fohdhoo Health Center
CLIENT
Ministry Of Health
Republic of Maldives

## Summary of Building
Project : Construction of N. Fohdhoo Health Center
SUMMARY OF BILL OF QUANTITIES
Bl.no | Item Description | Amount
Note | PREAMBLE TO BILL OF QUANTITY
1 | PRELIMINARIES
2 | GROUND WORKS
3 | CONCRETE WORKS
4 | MASONRY & PLASTERING
5 | FLOORING & TILING
6 | DOORS & WINDOWS
7 | WOOD WORK & CEILING
8 | PAINTING
9 | METAL WORK
10 | HYDRAULICS & DRAINAGE
11 | ELECTRICAL INSTALLATIONS
12 | FIRE FIGHTING SYSTEM
13 | AIR-CONDITIONING SYSTEM
14 | INTER LOCK PAVING BLOCK
15 | ADDITIONS
16 | OMISSIONS
TOTAL Mvr
8% GST Mvr
GRAND TOTAL Mvr

## BoQ of Building
Project : Construction of N. Fohdhoo Health Center
Item | Description | Unit | Qty | Material Rate | Labour Rate | Total
PREAMBLE TO BILL OF QUANTITY
Note | 1. General
a) The nature of this contract is measured unit price contract and the Bill of Quantity (BOQ) shall reflect this fact.
b) BOQ shall be read and construed in conjunction with other Contract Documents
c) The Tenderer is obliged to check the number of the pages of the Bill of Quantity and should any be found missing or duplicated or the figures or writing indistinct, the Tenderer must notify the Employer/Engineer at once and have the matter rectified before the Tender is submitted. No liability whatsoever will be accepted in respect of any claim for errors in the Tenderer’s offer resulting from failure to comply with the foregoing.
d) The Tenderer is deemed to have visited the site/s and fully acquainted himself as to the location of each of the items and works to be carried out and to all conditions which may affect the performance of the works, including but not limited to: -Access to each of the roads where solid waste transfer process will be carried out, and Access for the dump site. -Restrictions applicable to working in Male City area. -All safety regulations and employer site safety procedures. -All Safety regulations.
e) The Tenderer is also deemed to have surveyed the actual condition of the site and buildings and made his own assessment of the type and extent of the works prior to submitting his offer
2. Quantities
Even though that practical care was exercised in preparing the BOQ, but all quantities given herein shall be deemed to be estimated quantities of the work to be done but they are not to be taken as actual and correct quantities of the work to be executed and they are not to absolve the contractor of his obligations under the Contract. They are not to be taken as guarantee that the actual quantities increase or decrease, and any claim whatsoever submitted for cost or extra expenses incurred from such increase or decrease will not be accepted by Employer/Engineer except where else stipulated in the Contract.
3. Materials
All materials used are to be of the best new available and subject to the Employer/Engineer approval, and of durable nature, guaranteed, not liable to any base exchange and manufactured according to applicable BS, ASTM or DIN Standards. Execution also is subject to approval of Employer/Engineer and shall be the best available common practice in engineering codes at the time of execution.
4. Unit Price and Currency
The Unit Prices entered against the various items in the following Bill of Quantities include all operations for execution, completion and maintenance of the various items of the works finished completely in every respect till the final acceptance as specified or described in the Tender Documents, with or without modifications, either by way of additions or deductions, or alterations as may be offered in writing during the progress of the works, and include, without being limited to, all matters and things particularly referred to in the Tender Documents.
The Unit Price shall cover all costs of every kind whatsoever including, without being limited to, all charges for additional site installations, relocation, supervision, labor, transportation and supply of materials; the provision, maintenance, use and efficient repair of all plant, equipment and appliance of every kind, the construction and maintenance of all temporary works, the performance of all services and the fulfillment of all obligations and responsibilities herein defined.
The Tenderer shall be deemed to have fully considered all the conditions, obligations, and requirements of the Tender Documents before entering the respective unit price against the various items of the Bill of Quantities.
The Unit Prices given hereunder the BOQ shall also include erection, installation, fixing, and re-fixing of all elements. These prices shall also include taxes, visa for labor, gate passes, accommodations for the Contractor’s staff and labors, all required insurance and work permits, guarantees, bonds, traffic plan requirements, safety procedures, etc. and all requirements necessary to have the work maintained until its final handing over.
The Unit Prices given hereunder in the Bill of Quantity for this work shall also include overheads, risks, profit etc. and all other financial matters to have all these civil works completed.
PREAMBLE TO BILL OF QUANTITY
BILL No: 01
PRELIMINARIES
1.1.0 | General Notes
1 ) | Abbreviations
m - metre
no - numbers
m³ - cubic metre
m² - square metre
m - metre
t - tonnes
incl - including
mm - millimetre
dia - diameter
SS - Stainless Steel
GI - Galvanised Iron
1.2.0 | Site Management Costs
1 ) | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings, fences, Crane/Concrete pump, Machinaries and similar items | Item | 1
1.3.0 | Sign Board
1 ) | Allow for sign board. | item | 1
1.4.0 | Safety
1 ) | Safety - Providing and fixing scaffolding with G.I. pipes and clamps and pvc netting alaround building during construction | Item | 1
1.5.0 | Clean-up
1 ) | Allow for clean-up of completed works and site upon completion. | Item | 1
1.6.0 | Insurance, Bonds, Guarantees and Warranties
1 ) | Insurance as stated in the General Consditions. | Item | 1
1.7.0 | As-Built Drawings
1 ) | Preparation and submission of "as-built" Drawings. | Item | 1
1.8.0 | Dewatering
1 ) | Environment Impact Assessment that has to be done prior to dewatering works as required by government authorities. | Item | 1
2 ) | Dewatering Works ,Rates shall include all pipe and fitting , pumps road trenching ,all complete. | Item | 1
1.9.0 | INSPECTION TRIPS
1 ) | Arrange inspection trip to PMU team. Each inspection trip takes 2 days. Contractor has to arrange following for trips; (a) Air tickets for 2 person: Male'/N. Maafaru/Male' by air (normal fair), (b) Speed boat transfer from N. Maafaru/N. Fohdhoo/N. Maafaru. (C) Accommodations (2 Air-condition room) per trip. | Item | 5
BILL No: 01 PRELIMINARIES
TOTAL OF BILL No: 01 - Carried over to summary
BILL NO : 02
GROUND WORK
2.1.0 | General
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating, additional working space and disposing surplus soil.
2.2.0 | Site clearance
| Clearing site - Demolition of Existing building and dispatch all debris, clearing and dispose all unwanted materials away from site and prepare site ready for proposed construction. The contractor has visited the site and checked the ground condition as well as the number of trees to be removed and the size of the building to be demolished, and clean debris from the site as per the site plan before bidding. Rates must include EIA to remove or reallocate trees. | m² | 1500
2.3.0 | Shoring
| Charges for construction of 150mm thick solid block Masonry wall complete including plastering, below existing adjacent building to protect side buildings. | m² | 386.4
2.4.0 | Excavation
(a) Excavation quantities are measured to the faces of concrete members. Rates shall include for all additional excavation required to place the formwork , back fill , dewatering and others
2.4.1 | Excavation
1 | F1, 1600 x 1600 x 350 | m³ | 9.22
2 | F2, 1550 x 1550 x 300 | m³ | 23.07
3 | F3, 1375 x 1375 x 300 | m³ | 13.62
4 | F4, 1350 x 1350 x 300 | m³ | 15.31
5 | F5, 1225 x 1225 x 300 | m³ | 19.81
6 | F6, 1150 x 1150 x 300 | m³ | 30.16
7 | F7, 1450 x 1100 x 300 | m³ | 1.92
8 | F8, 1250 x 1000 x 300 | m³ | 12
9 | TB, 200 x 400 | m³ | 96.72
2.4.2 | Back filling
(a) Rates shall include for: leveling, grading, trimming and compacting.
(b) Ground need to be compacted to the density required by the consultant
1 ) | Back Fill all the Footing and tie beams | m² | 184.84
2 | Back Fill the Ground floor to Finishing level (150mm) | m² | 688.7
2.4.3 | Damp Proof Membrane
(a) Rates shall include for: dressing around and sealing to all penetrations, laps and turnups.
2.4.3.1 | Foundation & Beams Below ground
1 ) | Polythene damp proof membrane (2000 gauge) laid on blinding layer. | m² | 184.84
BILL No: 02 GROUND WORKS
TOTAL OF BILL No: 02 - Carried over to summary
BILL NO : 03
3.0.0 | CONCRETE
(a) Rates shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
(b) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6 by volume.
(c) Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
3.0.1 | FORM WORK
(a) Exposed surface shall have fair finish while remaining may have rough finish.
(b) Timber used for unexposed concrete surface shall sound dressed and seasoned good quality common timber while for exposed concrete surfaces dressedand matched boards uniformly thick and not more than 251mm wide.
c) Plywood used for forms shall be of commercial standard, moisture resistane conrete form plywoodnot lessthan 6mm thick and atleast 12mm thick.
(d) Rates shall include for; all necessary boarding,supports, erecting, framing, temporary cambering cutting, perforations for reinforcing bars, bolts,straps,ties, hangers, pipes and removal of formwork.
3.0.2 | REINFORCEMENT WORK
(a) Main reinforcement steel shall be high tensile steel hot rolled deformed bars complying with BS 1119 or BS 1172 Characteristic strength not less than 160N/mm2.
(b) Stirrups shall be hot rolled mildsteel round bars complying with BS 1119, Characteristic strength not less than 250N/mm2
(c ) Rates shall include for; distribution steel, cleaning, fabrication, placing, the provision for all necessary temporary fixings, and supports including chairs and tie wire , laps and wastage.
3.1.0 | LEAN CONCRETE
3.1.1 | 50mm thick lean concrete below Foundation
1 ) | Foundation Footings & Tie beams | m² | 184.84
3.2.0 | REINFORCED CONCRETE
3.2.1 | FOUNDATIONS
1 ) | F1, 1600 x 1600 x 350 | m³ | 2.69
| Formwork | m2 | 6.72
| 12 | kg | 113.67
2 | F2, 1550 x 1550 x 300 | m³ | 5.77
| Formwork | m2 | 14.88
| 12 | kg | 284.46
3 | F3, 1375 x 1375 x 300 | m³ | 3.41
| Formwork | m2 | 9.9
| 10 | kg | 139.76
4 | F4, 1350 x 1350 x 300 | m³ | 3.83
| Formwork | m2 | 11.34
| 10 | kg | 130.98
5 | F5, 1225 x 1225 x 300 | m³ | 4.96
| Formwork | m2 | 16.17
| 10 | kg | 145.27
6 | F6, 1150 x 1150 x 300 | m³ | 7.54
| Formwork | m2 | 26.22
| 10 | kg | 206.39
7 | F7, 1450 x 1100 x 300 | m³ | 0.48
| Formwork | m2 | 1.53
| 12 | kg | 28.33
8 | F8, 1250 x 1000 x 300 | m³ | 3
| Formwork | m2 | 10.8
| 10 | kg | 123.2
9 | TB, 200 x 400 | m³ | 32.24
| Formwork | m2 | 322.4
| 16 | kg | 6363.37
| 6 | kg | 1431.46
10 | Boundary Wall Beam, 250 x 200 | m³ | 1
| Formwork | m2 | 8
| 12 | kg | 71
| 6 | kg | 30.74
11 | Boundary Wall caping Beam, 125 x 100 | m³ | 0.25
| Formwork | m2 | 5
| 12 | kg | 35.52
| 6 | kg | 13.32
3.2.2 | Column
1 ) | C1, 250 x 300 | m3 | 2.61
| Formwork | m2 | 38.28
| 16 | kg | 329.7
| 6 | kg | 113.31
2 | C2, 250 x 300 | m3 | 2.7
| Formwork | m2 | 39.6
| 12 | kg | 191.81
| 6 | kg | 117.22
3 | C3, Dia 300mm | m3 | 0.11
| Formwork | m2 | 3.56
| 12 | kg | 25.58
| 6 | kg | 5.26
4 | BC, Boundary wall Column, 200 x 200 | m3 | 0.38
| Formwork | m2 | 7.56
| 12 | kg | 33.57
| 6 | kg | 11.19
3.2.4 | Staircase (2 numbers)
1 ) | R.c.c. Staircase | m3 | 2.58
| Formwork | m2 | 57
| 10 | kg | 141.27
3.3.0 | GROUND FLOOR
3.3.1 | Rc Ground Floor Slab
1 ) | 100 | m3 | 72.38
| Formwork, slab including Entrance Steps | m2 | 28.3
| 6 | kg | 1397.19
3.3.2 | Column
1 ) | C1, 250 x 300 | m3 | 5.77
| Formwork | m2 | 84.54
| 16 | kg | 728.08
| 6 | kg | 250.23
2 | C2, 250 x 300 | m3 | 5.97
| Formwork | m2 | 87.45
| 12 | kg | 423.58
| 10 | kg | 718.26
3 | C3, Dia 300mm | m3 | 0.23
| Formwork | m2 | 7.85
| 12 | kg | 56.48
| 6 | kg | 11.61
3.3.3 | Staircase (2 numbers)
1 ) | R.c.c. Staircase | m3 | 2.58
| Formwork | m2 | 57
| 10 | kg | 141.27
3.4.0 | FIRST FLOOR BEAM LEVEL
3.4.1 | Slab Beams
1 ) | B1, 250 x 550 | m3 | 15.11
| Formwork | m2 | 120.86
| 20 | kg | 4415.13
| 6 | kg | 757.09
2 | B2, 200 x 550 | m3 | 12.41
| Formwork | m2 | 124.1
| 16 | kg | 2902.84
| 6 | kg | 728.8
3 | B3, 200 x 450 | m3 | 8.12
| Formwork | m2 | 81.13
| 16 | kg | 1680.06
| 6 | kg | 274.17
3.4.2 | Slab - 1st.FL
1 | 145 | m3 | 106.72
| Formwork | m2 | 735.95
| 10 | kg | 10908.38
3.4.3 | Column
1 ) | C1, 250 x 300 | m3 | 5.77
| Formwork | m2 | 84.54
| 16 | kg | 728.08
| 6 | kg | 250.23
2 | C2, 250 x 300 | m3 | 5.97
| Formwork | m2 | 87.45
| 12 | kg | 423.58
| 6 | kg | 258.86
3.4.5 | RC wall 1.2m
1 ) | RC wall 1.2m | m3 | 4.14
| Formwork | m2 | 82.8
| 10 | kg | 21.26
| 10 | kg | 21.26
3.5.0 | ROOF BEAM LEVEL
3.5.1 | Slab Beams
1 ) | B1, 250 x 550 | m3 | 48.33
| Formwork | m2 | 386.6
| 20 | kg | 10400.11
| 6 | kg | 1783.36
2 | B2, 200 x 550 | m3 | 15.92
| Formwork | m2 | 159.14
| 16 | kg | 2844.67
| 6 | kg | 714.19
3 | B3, 200 x 450 | m3 | 9.16
| Formwork | m2 | 91.58
| 16 | kg | 1285.31
| 6 | kg | 209.76
3.5.2 | Slab - Roof Level
1 | 150 | m3 | 7.5
| Formwork | m2 | 50
| 10 | kg | 850.08
3.6.0 | OTHER CONCRETE WORKS
3.6.1 | Window Sill & Lintels
1 | Charges for construction of R.c.c. Sills and Lintels for the windows and doors as per details. Rate shall include for shuttering and Reinforcement works complete. | item | 1
2 | Design and Fabrication of sink cupboard at Treatment Room, 900mm length and 750mm width as per Floor plan, Rates shall include, concrete works tiling of all surfaces, installation of ceramic laboratory sink 620x480x255mm, (Cotto or equivalent) with an wall mount elbow operated faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. | Item | 1
3 | Design and Fabrication of sink cupboard at Pantry Area, 1900mm length and 750mm width as per Floor plan, Rates shall include, concrete works tiling of all surfaces, installation of ceramic laboratory sink 620x480x255mm, (Cotto or equivalent) with an wall mount elbow operated faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. | Item | 2
4 | Design and Fabrication of sink cupboard at labour Room, 2500mm length and 750mm width as per Floor plam, Rates shall include, concrete works tiling of all surfaces, installation of ceramic laboratory sink 620x480x255mm, (Cotto or equivalent) with an wall mount elbow operated faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. | Item | 1
5 | Design and Fabrication of sink cupboard at Behind the Nurse stations, 2500mm length and 750mm width as per floor plan, Rates shall include, concrete works tiling of all surfaces, installation of ceramic laboratory sink 620x480x255mm, (Cotto or equivalent) with an wall mount elbow operated faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. | Item | 2
6 | Design and Fabrication of sink cupboard at Traiage, 2000mm length and 750mm width as per Floor plan, Rates shall include, concrete works tiling of all surfaces, installation of ceramic laboratory sink 620x480x255mm, (Cotto or equivalent) with an wall mount elbow operated faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. | Item | 1
7 | Design and Fabrication of sink cupboard at Dirty utility, 900mm length and 750mm width as per Floor plan, Rates shall include, concrete works tiling of all surfaces, installation of ceramic laboratory sink 620x480x255mm, (Cotto or equivalent) with an wall mount elbow operated faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. | Item | 1
8 | Design and Fabrication of sink cupboard at Dirty utility, 4400mm length and 750mm width as per floor plan, Rates shall include, concrete works tiling of all surfaces, installation of two ceramic laboratory sink 620x480x255mm, (Cotto or equivalent) with an wall mount elbow operated faucet. And Rates shall also include all hydraulic works related to this item. Also rates shall include fixing of timber door panel and shelves. | Item | 1
9 | Design and fabrication of kichen cupboard with over head cupbord at accomodation area as per floor plan. Rates includes to sink and hood, stove 3 burner, length of kitchen cupboard is 2.6 meter. | Item | 2
3.6.2 | Rc Ground Water Well (1200mm dia)
(a) | Design and Fabrication of Construction of 1200mm Diameter R.c.c. Well as per drawing details. Rate shall include for; form work, reinforcement etc complete. | item | 1
3.6.3 | Absorption Trench 700mm dia 1400 Depth
(a) | Design and Fabrication of Concrete Grate Drain Trench. Charges for Construction of 700mm Diameter R.c.c. Well as per drawing details. Rate shall include for; form work, reinforcement etc complete. | item | 2
3.6.4 | Rc Grease Trap ( with cover)
(a) | Design and Fabrication of 1200mm x 900mm. Rate shall include for; form work, reinforcement etc complete. | item | 1
3.6.5 | Waterproofing & Admixtures
(a) | Apply Rubberised bitumin water proofing paint, 2 coats to all exposed concrete and masonry surface below ground level. Consultant to approve | item | 1
(b) | Add approved water proofing admixture as per specification to all concrete below ground level. | item | 1
(c) | Add Plasticiser admixture as per specification to all concrete Substreucture and Super structure. | item | 1
3.7.0 | Boundary wall, 1.2Meter Height, from Ground level.
(a) | 150mm thick Solid block single wall 2m Height of boundary wall surrounded by the land area with oil based paint system with textured finish Footing: 600 x 600mm (T10 @150 BW) for every 3 meter distance. Foundation Beam: 300 x 200mm (4T12, R6@150) Columns (at 3.5M span): 200 x 200mm (4T12, R6@150) for every 3 meter distance. Foundation Depth: 750mm Capping Beam: 150 x 150mm (4T10, R6@150) with capping. | m | 183
BILL No: 03 - CONCRETE WORKS
TOTAL OF BILL No: 03 - Carried over to summary
BILL No: 04
MASONRY AND PLASTERING
4.1.0 | General
a )Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good. Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:4 i.e. cement: sand) shall be of OPC & Local sand free form salt.
b )Cutting or leaving holes and openings as recesses for and building in pipes, conduits , sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joints.
c ) All external wall and all inetrenal walls shall be 150mm thick Solid cement blocks and for masonry mix ratio 1:5 (cement and river sand)
c ) Plastering should be used manufactures sand with Rio fiber and Feb mix chemicals, (mixing ratio 1:4 i.e. cement: sand) shall be of OPC &Manufactured sand.
MASONRY
4.1.1 | BELOW GROUND LEVEL
1 | Interior walls
a ) | 150mm thick Solid block single wall | m2 | 201.79
4.1.2 | GROUND FLOOR LEVEL
1 ) | External walls Boundary
a ) | 150mm thick Solid block single wall | m2 | 36.5
1 ) | External walls
a ) | 150mm thick Solid block single wall | m2 | 370.21
1 | Interior walls
a ) | 150mm thick Solid block single wall | m2 | 644.85
4.1.3 | FIRST FLOOR LEVEL
1 ) | External walls
a ) | 150mm thick Solid block single wall | m2 | 222.69
1 | Interior walls
a ) | 150mm thick Solid block single wall | m2 | 461.18
4.1.4 | ABOVE ROOF BEAM LEVEL
1 ) | External walls
a ) | 150mm thick Solid block single wall | m2 | 45
2 ) | Interior walls
a ) | 150mm thick Solid block single wall | m2 | 45
4.2.1 | PLASTERING
(a) 25mm thick Cement plastering on Exterior surface of External masonry walls and concrete surfaces and 16mm thick plastering on interior walls and concrete surface as specified incl. wire mesh shall be fixed at the joints of concrete surfaces and walls before plastering. Quantity is measured including concrete surfaces - Parapetwalls, Liftwalls, columns & beams.
(b)Rates shall include for External plastering shall 25mm thick (13+12mm) 2 coats in 1:4 cement and river sand mix ratio
c) Rates shall include for approved brand water proofing compound shall be mixed with cement mortar for external wall plastering as per manufacturers specifications.
4.2.2 | BELOW GROUND LEVEL
1 ) | Both Surface Plastering
a ) | Both surface | m2 | 201.79
4.2.3 | GROUND FLOOR LEVEL
1 ) | External Plastering
a ) | External surface of exeterior wall | m2 | 370.21
b ) | External surface of boundary wall | m2 | 73
2 ) | Internal Plastering
a ) | Internal surface of external wall and both surface of Interior walls | m2 | 1659.91
4.2.4 | FIRST FLOOR LEVEL
1 ) | External Plastering
a ) | External surface of exeterior wall | m2 | 222.69
2 ) | Internal Plastering
a ) | Internal surface of external wall and both surface of Interior walls | m2 | 1145.04
d ) | Both surface of RC wall 1.2m | m2 | 82.56
4.2.4 | ABOVE ROOF BEAM LEVEL
1 ) | External Plastering
a ) | External surface of exeterior wall | m2 | 45
2 ) | Internal Plastering
a ) | Internal surface of external wall and both surface of Interior walls | m2 | 135
BILL No: 04 - MASONRY AND PLASTERING
TOTAL OF BILL No: 04 - Carried over to summary
BILL N0: 05
FLOORING & TILING
5.1.0 | General
(a) Rates shall include for laying 50mm thick cement mortar in 1 : 5 mix ratio,cleaning down to reveals where necessary and water proofing of Toilet and Balcony floors & Terrace.
5.1.1 | FLOORING
50mm thick Floor Screeding
1 | Ground floor Screed | m2 | 688
2 | First floor Screed | m2 | 735.95
5.2.1.0 | FLOOR FINISHES
(a) Rates shall include for: Fixing, bedding, grouting, and pointing materials, making good around pipes, sanitary fixtures, and similar; cleaning & Polishing.
(b) All Tiling work in accordance with specifications and finishes schedule.
(c) Tiles rate shall be given as specified in the drawing.
5.2.2.0 | GROUND FLOOR
A) | FLOOR TILING
1 | Ground Floor 600x600mm homogenous floor tiles | m2 | 642.04
2 | Toilets 300x300mm homogenous floor tiles | m2 | 46.66
B) | WALL TILING
1 ) | Toilet walls 300x600mm Homogenous wall tile up to ceiling level | m2 | 252.7
5.2.3.0 | FIRST FLOOR
A ) | FLOOR TILING
1 ) | Ground Floor 600x600mm homogenous floor tiles | m2 | 483.95
2 | Toilets 300x300mm homogenous floor tiles | m2 | 17.05
B ) | WALL TILING
1 ) | Toilet walls 300x600mm Homogenous wall tile up to ceiling level | m2 | 118.72
5.3.1.0 | WATER PROOFING
Apply 2 coats of Water proofing Compound, on wet surfaces - Toilets, Balcony, Roof slabs
1 | Portico Slab | m2 | 26.5
2 | Toilet | m2 | 63.71
3 | Terrace | m2 | 207
4 | Roof slab | m2 | 50
5.4.1.0 | TILE ADHESIVE
1 ) | Charges for supplying special tiles grout for fixing tiles to all floors. With Toilet wall tiles | m2 | 1322.35
BILL No: 05 -FLOORING AND TILING
TOTAL OF BILL No: 05 - Carried over to summary
BILL N0: 06
DOORS AND WINDOWS
6.1.0 | General
Aluminum Doors and windows, Fabricate and fix in position the aluminum doors and window frame - aluminum doors and window (white powder coated, 60-80 micron, 1.5mm profile thickness) using recommended material with specified fixtures as shown in approved working drawings and installation should be as per technical specifications. Rates shall include for locks, latches, closures, push plates, pull handles, bolts, kick plates hinges, screws, washer and all door and window hardware and these materials should be of ss steel according to drawing and of superior quality.
(a) Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
(b) Rates shall include for door frames and window frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings and installation.
(c) All Timber door frames shall be treated timber. Rate shall include for Paint/Varnish finish.
(d) All louvres, windows and sliding doors shall be 30 micron powder coated aluminium as per details given in Door/Window schedule.
(e) All doors and windows shall be accordance with door/window drawing details.
(Profiles to be chosen by client, Thickess of aluminium profile must be minimum 2mm thick).
6.2.0 | GROUND FLOOR
DOOR UNITS
External
1 | D1, 2400 x 1400, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 4
2 | D2, 2500 x 1700, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, GRP (Glass reinforced polyester) door frame Panel/Leaf, Clear Glass | no | 1
3 | D4, 2500 x 900, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, GRP hermetically hygenic sealed door panel Panel/Leaf, (No Glazing) | no | 4
4 | DW1, 2400 x 2900, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
5 | SD1, 1200 x 1600, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
6 | SD2, 1200 x 2100, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 6
7 | SD3, 1200 x 3700, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
8 | SD4, 1200 x 4100, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
9 | W1, 600 x 800, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 12
10 | W2, 1400 x 800, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
11 | W13, 1200 x 2750, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 2
12 | W15, 2100 x 1532, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
13 | W17, 2100 x 1388, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
14 | W18, 2100 x 2066, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
15 | W19, 2100 x 1721, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
16 | W5, 1200 x 1816, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 2
17 | W6, 1400 x 1756, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
18 | Roller Shutter, 2800 x 3500, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (minimum 60 microns) Aluminum panel of selected colour Roller Shutter | no | 1
Internal
1 | D2, 2500 x 1700, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, GRP (Glass reinforced polyester) door frame Panel/Leaf, Clear Glass | no | 9
2 | D3, 2500 x 900, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, GRP (Glass reinforced polyester) door frame Panel/Leaf, Clear Glass | no | 9
3 | D4, 2500 x 900, 50x100x2mm Thick powder coated (minimum 60microns) Aluminum frame of selected colour Frame, GRP hermetically hygenic sealed door panel Panel/Leaf, (No Glazing) | no | 16
6.3.0 | FIRST FLOOR
DOOR UNITS
External
1 | D4, 2500 x 900, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, GRP hermetically hygenic sealed door panel Panel/Leaf, (No Glazing) | no | 2
2 | D5, 2500 x 900, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
3 | SD2, 1200 x 2100, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
4 | W1, 600 x 800, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 6
5 | W13, 1200 x 2750, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
6 | W14, 2100 x 625, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 2
7 | W15, 2100 x 1532, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
8 | W16, 2100 x 2400, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
9 | W17, 2100 x 1388, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 6
10 | W18, 2100 x 2066, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
11 | W2, 1400 x 800, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
12 | W20, 2100 x 1062, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
13 | W5, 1200 x 1816, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
14 | W6, 1400 x 1756, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
15 | W7, 1200 x 2925, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 4
16 | W8, 1200 x 3700, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 5
17 | W9, 1200 x 1816, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
Internal
1 | D3, 2500 x 900, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, GRP (Glass reinforced polyester) door frame Panel/Leaf, Clear Glass | no | 9
2 | D4, 2500 x 900, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, GRP hermetically hygenic sealed door panel Panel/Leaf, (No Glazing) | no | 9
3 | D6, 2500 x 750, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, GRP hermetically hygenic sealed door panel Panel/Leaf, (No Glazing) | no | 7
4 | W1, 600 x 800, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
5 | W10, 1400 x 1100, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 2
6 | W11, 1400 x 2000, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 1
7 | W12, 1400 x 2925, 50x100x2mm Thick powder coated (60microns) Aluminum frame of selected colour Frame, 50x100x2mm Thick powder coated (60 microns) Aluminum panel of selected colour Panel/Leaf, Clear Glass | no | 3
8 | Supply and complete instalation of roller shutter of Garage area, 6540X2700mm,colour and quality of aluminium is same as doors and windows. | no | 1
6.3.0 | Vertical Blinds
1 | Supply and installation of Vertical Blinds for all windows, quality of vertical blinds should be high quality sun protected , Rates should be complete installation of Vertical blinds with railing and ect.. | Item | 1
6.7.0 | BED SIDE CURTAINS
Supply and complete installation of top quality Hospital grade bed side curtain including railing/Track. Length of rail/track is 6870mm, and height of curtain would be 2.4 meter.
1 | Triage | Item | 2
2 | Consultation rooms | Item | 3
3 | Gynee ward | Item | 1
4 | Female ward | Item | 2
5 | Pediatric ward | Item | 2
6 | Labour room | Item | 2
7 | Male ward | Item | 4
8 | Private room | Item | 1
9 | Treatment room | Item | 2
BILL N0: 06 - DOORS AND WINDOWS
TOTAL OF BILL No: 06 - Carried over to summary
BILL No: 07
WOOD WORK & CEILING
7.1.0 | General
(a) Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails,bolts & screws.
(b) Rates shall include for applying approved quality wood preservators as per manufactures instructions for all Timber structures.
(c) Rates shall include for 6mm thick Cement board fixed on 35 x 50mm Timber frame,trimming, nails, screws,hooks, hangers, clips and similar.
(d) Rates shall include for 9mm thick Plaster board fixed on 35 x 50mm Timber frame,trimming, nails, screws,hooks, hangers, clips and similar.
7.2.0 | CEILING WORKS
7.2.1 | GROUND FLOOR
Ceiling
1 | Aluminium framed ceiling panels 600x600 | m2 | 1978
2 | Cement Board False Ceiling 6mm thick | m2 | 110
7.3.0 | FIRST FLOOR LEVEL
Ceiling
1 | Aluminium framed ceiling panels 600x600 | m2 | 2096
2 | Cement Board False Ceiling 6mm thick | m2 | 50
7.4.0 | ROOFING WORKS
7.4.1 | ROOF LEVEL-1
1 | Lysaght Roofing Sheet, with other accesorries, flashing and other necessary items. Roofin sheets, flashing must be Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick - Aqua marine or equivalent. | m2 | 487
2 | 200x50mmTimber Ridge /Hip | m | 36.5
3 | 150mm x 50mm Timber Rafters @800c/c | m | 600.84
4 | 50x50mm Timber Purlins @600c/c | m | 798.28
5 | 150mm x 65mm Wall plate | m | 72
6 | 200mm x 25mm Timber Facia | m | 72
7 | Standard Gutter, Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick - Aqua marine or equivalent | m | 72
7.5.0 | COUNTERS
Design and Fabrication of Registration counter as per floor plan, Fabrication of counter to be timber and appropriate thick plywood with PVC fomica.
1 | Reception Counter | Item | 1
2 | Nurse Station Counters | Item | 2
7.6.0 | SHELVES
1 | Design and Fabrication of Wooden shelves at Medical Store room, length of Shelf is 1.2M, Width is 0.4m and heigh is 2M, 18mm thick Plywood with both side paint to be used. Frame with 4 shelf, | Item | 15
7.6.0 | SUPPLY AND INSTALLATION OF FURNITURES.
Supply and Complete installation of Furniture's.
1 | Office Table with drawer, 1200mm ( table should be solid wood) | No | 15
2 | Office Table with drawer 1500mm ( table should be solid wood). | No | 2
3 | Secretary chair , high back. | No | 6
4 | Secretary chair , Medium back. | No | 25
5 | Meeting room chair Material: Iron/Aluminum Surface treatment: Spray painting finished. Seat and back: Hight-density sponge, minimum 2.5" thick seat cushion | No | 30
6 | Folding Meeting Table, 1400X600mm, Specifications: Lockable castorsm Aluminum components Feature: Chrome with polished aluminum feet, Easy tilt mechanism for compact storage, Table surface: Scratch resistant, Natural Ash. | No | 6
7 | Supply and installation of 4 seater Airport Bench set, Armrest/Leg/bracket: Die-casting molding of high strength aluminum alloy. Seat: Numerical control hydraulic molding of high quality cold rolling steel plate. Sponge: Cold consolidation and foam-forming of high density and super soft PU. Beam: metal tube with a diamond shape. Coating: Electrostatic coating after Rust-proof treatment, electroplated polishing. | No | 6
8 | Double bed, | Item | 2
9 | Single bed, | Item | 4
10 | Wordrobe 2 door panel, | Item | 4
11 | Dressing table, | Item | 4
12 | Double bed mattress, 6 inch thick. High quality. | Item | 2
13 | Single bed mattress, 6 inch thick. High quality. | Item | 4
14 | Dining table, for 4 people with chairs | Item | 3
15 | Sofa set, 1 sofa for 2 person and 1 sofa for 1 person with coffee table. | Item | 3
BILL No: 07 - WOOD WORK & CEILING
TOTAL OF BILL No: 07 - Carried over to summary
BILL No: 08
PAINTING
8.1.0 | General
Exterior wall shall be of 1 coat of oil based textured paint and 2 coats of Kansani weather bond paint ( oil based ) over 1 coat of oil based sealer ( white) or equivalent (according to technical specifications or approved drawings). Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Interior wall shall be of 2-3 coats over 1 coat of water based sealer. Rates includes Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint, Kansani or equivalent as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
All painting work shall be carried in accordance with the Specifications
Rate shall include for weather proof paint finish for exterior surfaces of the wall complete including application of two coats of oil based wall sealer and two coats of weather bond paint
Rate shall include for putty and paint finish for interior surfaces of the wall and ceilings complete including application of two coats of wall sealer, two coats of putty finish and two coats of emulsion paint finish on top for Interior painting.
8.1.0 | GROUND FLOOR
1 ) | Painting exterior surfaces of External Wall, Columns & beams. | m2 | 370.21
2 ) | Painting interior surfaces Wall, Columns & beams) | m2 | 1659.91
3 ) | Painting Soffit of slab (Ceiling) | m2 | 688
4 ) | Painting exterior 2 sides of boundary wall | m2 | 73
8.2.0 | FIRST FLOOR
1 ) | Painting exterior surfaces of External Wall, Columns & beams. | m2 | 305.25
2 ) | Painting interior surfaces Wall, Columns & beams) | m2 | 1145.04
3 ) | Painting Soffit of slab (Ceiling) | m2 | 735.95
8.4.0 | ABOVE ROOF BEAM FLOOR
1 ) | Painting exterior surfaces of External Wall, Columns & beams. | m2 | 45
2 ) | Painting interior surfaces Wall, Columns & beams) | m2 | 135
BILL No: 08 - PAINTING
TOTAL OF BILL No: 08 - Carried over to summary
BILL No: 09
METAL WORK
9.1.0 | General
(a) Rates shall include for ; all labour in framing, cutting, welding, cleats, baseplates, flanges,screws, nails, bends, and similar complete with grinding, surface smoothening and polish finishes.
9.2.0 | RAILING STAIR
Supply, Fabrication and Fixing SS Railing as per details
1 | SS. Railing - Staircase (G-1st) | item | 2
9.3.0 | BALCONY RAILING
Supply, Fabrication and Fixing SS Railing as per details. 5mm thk 30x35mm flat bar bracket eq. distr. with max. spacing of 1200mm
1 | SS. Railing Balcony (1st Floor) | m | 30
9.4.0 | FLAG POST
(a) | Supply and Complete installation of 75mm dia Flag post, length of flag post is minimum 5.9 Meter, Flag post must install minimum 10mm thick SS flang with SS bolts. Flag post to be fabricated in Marine grade SS pipe with 350X350X600mm concrete footings. | Item | 1
BILL No: 09 - METAL WORK
TOTAL OF BILL No: 09 - Carried over to summary
BILL No: 10
HYDRAULICS & DRAINAGE
10.1.0 | General
(a) Design provide and install plumbing network for the entire building complete in accordance to standard set by the local governing body MWSC
(b) The following items and description and the plumbing drawings are given as guidance as to the nature of the information to be returned by the contractor.
(c) Ground water connection shall be made as specified in the drawings.
(d) The cost shall include for; sockets, running joints, connectors, elbows, junctions, reducers, expansion joints, back nuts and similar, incidental fittings, clips, saddles, brackets, straps, hangers, screws, nails , pvc glues, threadseals and fixing complete, including cutting and forming holes, excavating, laying pipes , backfilling trenches.
(e) All pipes shall be High Pressure uPVC "Mutha" or equivalent brand.
10.2.0 | GROUND FLOOR
10.2.1 | Hydraulics
a ) | Charges for Piping for fresh water Pipe work | item | 1
b ) | Charges for Piping for Ground water supply pipe work. | item | 1
c ) | Charges for Providing and Fixing Heavy duty water pump Davey brand for Ground water supply to all floors | no | 1
10.2.2 | Drains / Traps & other fixtures
1 | MWSC Meter | no | 1
2 | 40Ø Stub For Washing Machine Or Tub | no | 2
3 | Floor Drain | no | 15
4 | Floor Gully | no | 15
5 | Gully Trap | no | 15
6 | Manhole | no | 1
7 | Bottle Trap | no | 15
8 | Bottle Trap For Sink | no | 5
10.2.3 | Sanitary Fixures & Accessories
1 ) | Basin Faucet ( Cotto) or equivalent | no | 15
2 ) | Bib Tap ( Cotto) or equivalent | no | 13
3 ) | Bidet Shower with Stop valve, ( Cotto) or equivalent | no | 13
4 ) | Sink Tap ( Cotto) or equivalent | no | 5
5 ) | Wash Basin with half pedastal. ( Cotto) or equivalent | no | 15
6 ) | Water closet (American standard, Neo Modern, Anti bacterial type) or equivalent, (dual top flush) with Stop valve, ( Cotto) or equivalent | no | 13
7 ) | Washing Machine Tap | no | 2
8 ) | Gate Valve ( Cotto) or equivalent | no | 25
10.2.3 | Drainage
10.2.4 | Sewerage & Drainage: Charges for piping for all discharge pipes, sewerage and drainage pipes including connection to Main Sewer network from the Fixtures. | item | 1
10.3.0 | FIRST FLOOR
10.3.1 | Hydraulics
a ) | Charges for Piping for fresh water Pipe work | item | 1
b ) | Charges for Piping for Ground water supply pipe work. | item | 1
10.3.2 | Drains / Traps & other fixtures
1 ) | Floor Drain | no | 6
2 | Floor Gully | no | 6
3 | Bottle Trap | no | 6
4 | Bottle Trap For Sink | no | 6
10.3.3 | Sanitary Fixures & Accessories
1 ) | Basin Faucet | no | 6
2 ) | Bidet Shower with Stop valve, ( Cotto) or equivalent | no | 6
3 ) | Hot Water Mixer Basin Faucet ( Cotto) or equivalent | no | 6
4 ) | Sink Tap ( Cotto) or equivalent | no | 6
5 ) | Wash Basin with half pedastal. | no | 6
6 ) | Water closet (American standard, Neo Modern, Anti bacterial type) or equivalent, (dual top flush) with Stop valve, ( Cotto) or equivalent | no | 10
7 ) | Hand shower with hand sgower valve, ( Cotto) or equivalent, ( Private room and apartment toilets) | no | 4
8 | Head shower with hand sgower valve, ( Cotto) or equivalent, ( Private room and apartment toilets) | no | 4
9 | Gate Valve ( Cotto) or equivalent | no | 6
10 | Water tap for Gardening with 10 Meter high quality pipe 12.5mm dia, ( Cotto) or equivalent, ( 2 taps for ground floor ann 1 tap for terace area). | no | 3
10.3.3 | Drainage
10.3.4 | Sewerage & Drainage: Charges for piping for all discharge pipes, sewerage and drainage pipes including connection to Main Sewer network from the Fixtures. | item | 1
10.7.0 | ROOF LEVEL
10.7.1 | Hydraulics
a ) | Charges for Piping for fresh water Pipe work | item | 1
b ) | Charges for Piping for Ground water supply pipe work. | item | 1
10.7.2 | Drains / Traps & other fixtures
1 ) | 110Ø Rainwater Outlet | no | 5
10.7.4 | Drainage
10.7.5 | Sewerage & Drainage: Charges for piping for all discharge pipes, sewerage and drainage pipes including connection to Main Sewer network from the Fixtures. | item | 1
BILL No: 10 - HYDRAULICS AND DRAINAGE
TOTAL OF BILL No: 10 - Carried over to summary
BILL No: 11
ELECTRICAL INSTALLATIONS
11.1.0 | General
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil
(c) Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces and also all elecetrical work shall be carried out according to the Utility Regulation Authority standards and specifications.
(d) Each Light/ light fixture and its switch is measured as one one point; similarly each fan or each socket outlet is measured as one point;
(e) Rates shall include for supply and complete installation of fittings and fixtures.
(f) Rate for all electrical panels shall include for supply and installation of all necessary MCCBs, MCBS, EFRs, ELCBs, auxiliary contacts, Voltmeters, ammeters, Digital analyser,kWh meters, indicator lamps, selector switches, copper bus bars, inter locks, aligning and grounding of the panel, inter connectors, internal wiring connections to switch gear,steel channels and necessary hardware fixing insulating materials,all in fully enclosed metal clad panels and distribution boards completed as shown in drawing. They shall comply with the specifications andI.E.E.regulations and be complete to working order to the approval of local authorities.
(g) Rate shall include for supply, installation, maintaining, testing and commissioning of the system for power and lighting according to drawings and specifications to working order.
(h) All materials, equipment wiring shall confirm to local codes, specifications, standards/latest I.E.E. regulations ( BS 7671 ).
11.2.0 | GROUND FLOOR
11.2.1 | Electric Boards
1 ) | Supply and Complete Installation of Utility Regulatory Authority approved Panel Board with kWh Meter | item | 1
2 ) | Wiring connection to Main Panel Board from Islan Main Distribution Panel network. | item | 1
3 ) | Supply and Complete Installation of 'Main Sub Distribution Board | nos | 3
4 ) | DB, Supply and Installation of Utility Regulation Authority approved brand Distribution board | nos | 1
5 ) | 16mm2 Cabling to DBs Wiring | nos | 4
11.2.2 | Lights/ Switches-Fixtures
1 | Ceiling diffusing embedded down light 200mm dia with 21W LED bulb, (Philips), Cool day light, (not crystal light or not Stellar bright) Total lumen 2300 or equivalent, | nos | 155
2 | Wall Mount Light | nos | 13
3 | Outdoor Terrace Light,light with 13W LED bulb, (Philips) E27, warm white, Total lumen 1400, for Portico area | nos | 29
4 | Light Switch (1 Gang ) "Legrand" or equivalent. | nos | 16
5 | Light Switch (2 Gang ) "Legrand" or equivalent. | nos | 59
6 | Light Switch (3 Gang ) "Legrand" or equivalent. | nos | 21
7 | Two Way Light Switch (1 Gang ) "Legrand" or equivalent. | nos | 2
8 | Two Way Light Switches (2 Gang ) "Legrand" or equivalent. | nos | 2
11.2.3 | Wiring - Lights/ Switches
1 | 2.5mm2 Wiring to Light Points | points | 297
11.2.4 | Fixtures do not Required Wiring (Plug Top)
1 | Emergency Light | nos | 9
11.2.5 | Power Points-Fixtures
1 ) | Single Socket (13 Amp) "Legrand" or equivalent. | points | 2
2 ) | Single Socket (15 Amp) "Legrand" or equivalent. | nos | 101
3 ) | Double Socket (13 Amp) "Legrand" or equivalent. | nos | 129
4 ) | Double Floor Socket (13 Amp) "Legrand" or equivalent. | nos | 9
11.2.6 | Wiring -Power Points
1 ) | 2.5mm2 Wiring to Power Points | points | 241
11.2.6 | Telecommunications
a) Provide & install Network and Telephone fittings, wiring equipment inclusive of all necessary connection as per local regulations as described
b) All network ,TV and Telephone socket outlets shall be 'Legrand' brand or equivalent, and PABX Gigabit switch shall be Cisco or equivalent
1 | Computer Network Outlet | nos | 10
2 | Twin Computer Network Outlet | nos | 10
3 | Twin Computer Network Outlet In Floor Mount Pop-up Box | nos | 5
4 | Security Monitor | nos | 1
5 | Internet Switchboard | nos | 1
6 | Telephone Line Outlet | nos | 38
11.2.7 | Wiring - Telecommunications
a) Wiring connections to main telecommunication switch boards from main telecommunication network
1 | Cabling - Computer Network Outlet | points | 10
2 | Cabling - Twin Computer Network Outlet | points | 10
3 | Cabling - Twin Computer Network Outlet In Floor Mount Pop-up Box | points | 5
4 | Cabling - Security Monitor | points | 1
5 | Cabling - Internet Switchboard | points | 1
6 | Cabling - Telephone Line Outlet | points | 38
11.2.8 | CCTV Security Systems
Supply and installation of access control and CCTV security system as per specifications (Refer to the ICT specification) including all Wiring connection, equipment inclusive of all necessary connection
1 | Angular Camera | nos | 4
2 | Digital or network Video Recorder, minimum 7 days backup. | item | 1
3 | Cabling & Connection to all CCTV | item | 1
11.2.9 | Mains connection
1 | Three PhaseMain connection: Rates shall include for screws, nails, bolts ,nuts, standard cable, fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories. Rates shall including for electrical conduits, fittings, equipment and similar items. Three - PHASE CABLE WIRING TO D-BOARD: All necessary work in trench shall include for excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers warning tape and disposal of surplus soil supply and laying of the cable in according to Maldives electricity bureau. ( 16mm2 4-Core Cable, Approved by respective Authorities, GI pipe, warning tape), contractor has to measure cable length from site. ( Health center Building) | Item | 1
2 | Three PhaseMain connection: Rates shall include for screws, nails, bolts ,nuts, standard cable, fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories. Rates shall including for electrical conduits, fittings, equipment and similar items. Three - PHASE CABLE WIRING TO D-BOARD: All necessary work in trench shall include for excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers warning tape and disposal of surplus soil supply and laying of the cable in according to Maldives electricity bureau. ( 16mm2 4-Core Cable, Approved by respective Authorities, GI pipe, warning tape), contractor has to measure cable length from site. ( Pharmacy area) | Item | 1
11.3.0 | FIRST FLOOR
11.3.1 | Electric Boards
1 | Main Sub Distribution Board | nos | 2
2 | DB, Supply and Installation of Utility Regulation Authority approved brand Distribution board | nos | 1
3 | 16mm2 Cabling to DBs Wiring | nos | 3
11.3.2 | Lights/ Switches-Fixtures
1 | Ceiling diffusing embedded down light 200mm dia with 21W LED bulb, (Philips), Cool day light, (not crystal light or not Stellar bright) Total lumen 2300 or equivalent, | nos | 101
2 | Wall Mount Light | nos | 7
3 | Light Switch (1 Gang ) "Legrand" or equivalent. | nos | 8
4 | Light Switch (2 Gang ) "Legrand" or equivalent. | nos | 40
5 | Light Switch (3 Gang ) "Legrand" or equivalent. | nos | 6
6 | Two Way Light Switches (1 Gang ) "Legrand" or equivalent. | nos | 1
7 | Two Way Light Switches (2 Gang ) "Legrand" or equivalent. | nos | 1
11.3.3 | Wiring - Lights/ Switches
1 | 2.5mm2 Wiring to Light Points | points | 164
11.3.4 | Fixtures do not Required Wiring (Plug Top)
1 | Emergency Light | nos | 5
11.3.5 | Power Points-Fixtures
(a) All socket outlets shall be "Legrand" or equivalent.
1 ) | Single Socket (15 Amp) "Legrand" or equivalent. | points | 31
2 ) | Double Socket (13 Amp) "Legrand" or equivalent. | nos | 74
3 ) | Double Floor Socket (13 Amp) "Legrand" or equivalent. | points | 29
11.3.6 | Wiring -Power Points
1 ) | 2.5mm2 Wiring to Power Points | points | 134
11.3.7 | Telecommunications
Provide & install Network and Telephone fittings, wiring equipment inclusive of all necessary connection as per local regulations as described
All network ,TV and Telephone socket outlets shall be 'Legrand' brand or equivalent, and PABX Gigabit switch shall be Cisco or equivalent
1 | Computer Network Outlet | nos | 6
2 | Twin Computer Network Outlet | nos | 2
3 | Twin Computer Network Outlet In Floor Mount Pop-up Box | nos | 2
4 | Supply and complete installation of IP PABX, minimum 30 Extensoon and 4 lines, including console. | Item | 1
5 | Supply and complete installation of IP Telephone, | Item | 25
11.3.8 | Wiring - Telecommunications
a) Wiring connections to main telecommunication switch boards from main telecommunication network, Cat6 cable to be used for laying telephone network.
1 | Cabling - Computer Network Outlet | points | 6
2 | Cabling - Twin Computer Network Outlet | points | 2
3 | Cabling - Twin Computer Network Outlet In Floor Mount Pop-up Box | points | 2
4 | Cabling - Telephone Line Outlet | points | 25
11.3.9 | CCTV Security Systems
Supply and installation of access control and CCTV security system as per specifications (Refer to the ICT specification) including all Wiring connection, equipment inclusive of all necessary connection
1 | Angular Camera | nos | 3
2 | Cabling & Connection to all CCTV | item | 1
11.3.10 | Water pump
1 | Supply and complete installation of DEAVY or equivalent pump for ground water | item | 1
11.3.11 | Supply and installation of following IT equipments
1 | Supply and complete installation of 24 port, Double layer VoiP Manageable network switch. | item | 2
2 | Supply and complete installation of Computer system as per specifications | item | 8
3 | Supply and complete installation of 75" QLED TV, LG or Equivalent at meting room. Any cast or chrome cast must support. | item | 1
4 | Supply and complete installation of 65" QLED TV, LG or Equivalent at waiting area. | item | 1
5 | Supply and complete installation of 65" QLED TV, LG or Equivalent at Nurse station area. | item | 1
6 | Supply and complete installation of 65" QLED TV, LG or Equivalent at accomodation area. | item | 2
7 | Supplying of Canon Monochrome Multi-Functional Device, image RUNNER 2725/ 2725i, (A4 & A3 sze) 3 in 1 printer or equivalent. | item | 1
11.3.12 | Lightening Protection System
1 | Design, supply, and Complete installation of Erco, Eritech or equivalent lightening Protection System to cover the whole building as per local regulations (Rate shall include for all fixing of the system and down conductor to earthing) Coverage of lightning protection should be minimum 50 Meter Radius. Price also include to install GI pipe post. GI pipe must be 75mm dia and minimum thickness is 2mm thick. | Item | 1
11.3.13 | Solar PV System
1 | Design supply and complete installation on 20KW Solar PV grid system. Rates includes to Design, complete the system and connect to the grid with net metering as per specification. ( junction box specs, Solar AC&DC cable specs, solar bracket specs, inverter specs & solar panel specs). | Item | 1
BILL No: 11 - ELECTRICAL INSTALLATIONS
TOTAL OF BILL No: 11 - Carried over to summary
BILL No: 12
FIRE FIGHTING SYSTEM
12.1.0 | GENERAL
a )Rates shall include for: sockets, running joints, connectors, elbows, junctions, reducers, expansion joints, back nuts, and similar incidental fittings, clips, saddles, brackets, straps, hangers screws nails and fixing complete including cutting and forming holes.
b ) Rate shall include for pipe works and inner and outer surface of all pipe work shall be galvanized steel.
c )All wiring and pipe work shall be done as specified in the drawing.
d )Shop drawings of the system shall be prepared to the standard of the government's relevant authority and submitted to the Consultant for approval.
e )Heat Resistant cable shall be laid for connecting the detectors.
12.2.0 | Fire Alarm System
Heat Resistant cable shall be laid for connecting the detectors.
12.3.0 | GROUND FLOOR
1 | Exit Sign | no | 7
2 | H2O Extinguisher (load 9L) In Polycarbonate Enclosure | no | 1
3 | DCP Extinguisher (load 6kg) In Polycarbonate Enclosure | no | 1
4 | CO2 Extinguisher (load 2kg) In Polycarbonate Enclosure | no | 1
12.3.0 | FIRST FLOOR
1 | Exit Sign | no | 2
2 | H2O Extinguisher (load 9L) In Polycarbonate Enclosure | no | 2
3 | CO2 Extinguisher (load 2kg) In Polycarbonate Enclosure | no | 2
4 | DCP Extinguisher (load 6kg) In Polycarbonate Enclosure | no | 2
BILL No: 12 - FIRE FIGHTING SYSTEM
TOTAL OF BILL No: 12 - Carried over to summary
BILL No: 13
AIR-CONDITIONING SYSTEM
13.1.0 | General
(a) Rates shall include for detail design, supply and complete installation of A/C units pipework, insulation, fixings, electrical wiring, drain pipes etc.
(b) The Contractor shall provide detailed and complete set of shop drawings
13.2.0 | Air Condition
13.2.1 | Design, supply and complete installation of indoor and out door unit, All AC unit is DAIKIN or equivalent (INVERTER TYPE).
The whole of the liquid and suction refrigerant lines including all fittings, valves etc. shall be insulated with 25mm thick insulation for all copper sizes. Insulation shall be closed cell elastomeric nitrile rubber.
Protection of exposed Refrigerant Pipe Insulation: To protect nitrile rubber of exposed piping from degrading due ultra violet rays & atmospheric conditions, it shall be covered polychelid coating with at least two coats of resin and hardener (Make-Polybond /Paramount Polytreat). Fiberglass tape shall be helically wound & painted with two coats of resin with hardener to give smooth & plain finish.
The brand of AC Equipment proposed should have an outdoor or outdoor sets with a maximum Energy Efficiency Ratio of (EER) kw/kw 4.5.
The Outdoor Unit Shall be Factory assembled with Weather Proof casing, constructed from Heavy Gauge Mild Steel Panels and coated with Anti Corrosive Epoxy resin finish. The unit should be completely factory wired and tested and shall be fitted with all necessary controls and switch gear.
All outdoor units needs to have aluminum fins with 105+2 μm thickness, with special Anti corrosive coating of 1.3 ± 0. 35 μm thickness and an outside Hydrophilic layer coating of 0.35 ± 0. 07 μm thickness.
All outdoor units shall be equipped with high efficiency optimized heat exchangers with variable heat exchanger circuits
Following rooms should be installed AC,
13.3.0 | GROUND FLOOR
13.3.1 | Air Conditioning Systems
Supply and install Hitachi brand Inverter or equivalent Split Air conditioning system as decribed
1 | Air Handling Unit with duct system as per manufacture's requirements | nos | 1
2 | 24,000BTU Split type Airconditioner with duct system as per manufacturer's requirements | nos | 54
13.4.0 | FIRST FLOOR
13.4.1 | Air Conditioning Systems
Supply and install Hitachi brand Inverter or equivalent Split Air conditioning system as decribed
1 | Air Handling Unit with duct system as per manufacture's requirements | nos | 1
2 | 24,000BTU Split type Airconditioner with duct system as per manufacturer's requirements | nos | 29
13.4.1 | Air Curtains
Supply and Complete installation of Air curtain.
1 | Supply and Complete installation on KDK (10ESK ) air curtain, 900mm length at Exit door. Rates also includes to electric connection. | Iten | 6
BILL No: 13 - AIR-CONDITIONING SYSTEM
TOTAL OF BILL No: 13 - Carried over to summary
BILL No: 14
INTER LOCK PAVING BLOCK
14.1.0 | GENERAL
(a) Surface dressing of the ground including removing vegetation and inequalities and disposal of unwanted materials.
(b) Providing and laying 60 mm thick factory made cement concrete interlocking paver block of approved size, design & shape, laid in required colour and pattern over and including 20 mm thick compacted bed of coarse sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge
14.2.0 | INTER LOCK PAVING BLOCK
1 ) | Interlock Paving block (100mm x 50mm) | m2 | 222
BILL No: 14 - INTER LOCK PAVING BLOCK
TOTAL OF BILL No: 14 - Carried over to summary
BILL No: 15
ADDITIONS
15.1.0 | General
Provision to include quantities as per the drawing which is missed in the bill of quantities.
1 | PRELIMINARIES
2 | GROUND WORKS
3 | CONCRETE WORKS
4 | MASONRY & PLASTERING
5 | FLOORING & TILING
6 | DOORS & WINDOWS
7 | WOOD WORK & CEILING
8 | PAINTING
9 | METAL WORK
10 | HYDRAULICS & DRAINAGE
11 | ELECTRICAL INSTALLATIONS
12 | FIRE FIGHTING SYSTEM
13 | AIR-CONDITIONING SYSTEM
14 | INTER LOCK PAVING BLOCK
15 | ADDITIONS
16 | OMISSIONS
BILL No: 15 - ADDITIONS
TOTAL OF BILL No: 15 - Carried over to summary
BILL No: 16
OMISSIONS
16.1.0 | General
Any adjustments that the contractor may consider necessary should be written below and on similar continuation sheets if required, and the net amount of the adjustments is to be carried to the summary.
(a) If there are discrepancies between BOQ and Drawings, the Contractor must include them in the Addition/Ommision Bill. If the contractor does not include the Addition/Ommision bill, the contractor must proceed with the works without any cost.
Provision to remove the excess quantity given in the bill quantities if any as per the drawing details
1 | PRELIMINARIES
2 | GROUND WORKS
3 | CONCRETE WORKS
4 | MASONRY & PLASTERING
5 | FLOORING & TILING
6 | DOORS & WINDOWS
7 | WOOD WORK & CEILING
8 | PAINTING
9 | METAL WORK
10 | HYDRAULICS & DRAINAGE
11 | ELECTRICAL INSTALLATIONS
12 | FIRE FIGHTING SYSTEM
13 | AIR-CONDITIONING SYSTEM
14 | INTER LOCK PAVING BLOCK
15 | ADDITIONS
16 | OMISSIONS
BILL No: 16 - OMISSIONS
TOTAL OF BILL No: 16 - Carried over to summary