PART 2 – Employer’s Requirements

Section VII - Technical Requirements

Contents

Part A -	Overview	7

Part B -	Specifications	14

Part C -	General Site Descriptions	32

Part D -	Solar Farm Connection Requirements	87

Part E -	Array Structure Requirements	121

Part F -	Environmental, Social, Health and Safety Requirements	147

ABBREVIATIONS

ARISE			Accelerate Renewable Energy Integration and Sustainable Energy project

ASPIRE		Accelerating Sustainable Private Investments in Renewable Energy project

AVSL			Aviation Obstacle Surface Limit guidelines

BESS			Battery Energy Storage System

BMS			Battery Management System

COD			Commercial Operation Date

CUF			Capacity Utilization Factor

DBFOOT		Design Build Finance Own Operate and Transfer

EIA			Environmental Impact Assessment

EMS			Energy Management System

ESIA                           Environmental and Social Impact Assessment

ESMP                         Environmental and Social Management Plan

FAA			Federal Aviation Authority (of USA)

FENAKA		FENAKA Corporation Ltd.

GoM			Government of the Republic of Maldives

IA			Implementation Agreement

IDA			International Development Association (World Bank Group)

IFC			International Finance Corporation (World Bank Group)

IPP			Independent Power Producer

LA			License Agreement

LV			Low voltage (400Vac of 230Vac)

MCAA		Maldives Civil Aviation Authority

MEA			Maldives Energy Authority

MCCEE		Ministry of Climate Change, Environment and Energy

MIGA			Multilateral Investment Guarantee Agency

MMS			Maldives Meteorological Service

MV			Medium voltage (11kV)

MW			Mega-watt

MWp			Mega-watt peak

MWSC 		Male’ Water and Sewerage Company Pvt. Ltd.

PPA			Power Purchase Agreement

PPP			Public-Private Partnership

PR			Performance Ratio

PV			Solar Photovoltaic

RLA			Roof Lease Agreement

RMU			Ring Main Unit (of MV network)

SGHAT		Solar Glare Hazard Analysis Tool

SREP			Scaling-up Renewable Energy Program

STELCO 		State Electric Company Limited

URA			Utility Regulatory Authority

Contents - Parts A to F (detailed)

A.1. BACKGROUND	7

A.2. PROJECT INVESTMENTS AND ARRANGEMENTS	9

A.3. DOING BUSINESS IN MALDIVES	13

B.1. SCOPE OF WORK	14

B.1.1.	General Scope	14

B.1.2.	Project Design Documents	15

B.1.3.	Implementation and Conditions on Site	16

B.2. COMPLETING THE TENDER DOCUMENTATION	17

B.2.1.	Data provided: Data Room structure	17

B.2.2.	Design basis	18

B.2.3.	Technical Information to be submitted	18

B.2.4.	Work Teams	19

B.3. SYSTEM DESIGN	20

B.3.1.	Solar Radiation Data	20

B.3.2.	Capacity Utilization Factor and Performance Ratio	21

B.3.3.	Environmental conditions	22

B.4. INSTALLATION QUALITY AND SAFETY	23

B.5. COMPATIBILITY WITH THE UTILITY INTERFACE	23

B.5.1.	Technical Requirements for Grid Connection	23

B.5.2.	Network ownership and responsibility	24

B.5.3.	Solar plant interconnection requirements	24

B.6. ARRAY LOCATIONS AND STRUCTURAL REQUIREMENTS	24

B.7. TECHNICAL SPECIFICATIONS FOR KEY PV PLANT COMPONENTS	25

B.7.1.	Applicable Codes and Standards	25

B.7.2.	Photovoltaic Modules	26

B.7.3.	PV inverters	26

B.7.4.	MV switchgear, transformers and protection	28

B.7.5.	Communications interface	28

B.7.6.	Weather station	28

B.7.7.	Earthing	28

B.7.8.	Labelling, Safety Signs and Notices	29

C.1. DESCRIPTION OF THE SELECTED SITES IN THE BID	32

C.2. SPECIAL SITE CONSIDERATIONS	42

C.2.1.	Material Site Clearance and Preparatory works	42

C.2.2.	Vegetation Clearances	42

C.2.3.	Road based PV installations	42

C.2.4.	Considerations for aesthetics	43

C.2.5.	Airport restrictions & glare mitigation	43

C.2.6.	Interconnection cabling installations	43

C.2.7.	Safety Measures	44

C.2.8.	Restrictive access	44

C.3. SPECIAL SITE CONSIDERATIONS	44

C.3.1.	Specific Requirements	44

D.1. INTRODUCTION	87

D.2. SOLAR FARM CONNECTION CONFIGURATION	87

D.2.1.	Connection voltage	87

D.3. 11KV CONNECTIONS	88

D.3.1.	Physical limits	88

D.3.2.	Environmental conditions	90

D.3.3.	Switchgear	91

D.3.4.	Metering	93

D.3.5.	Step-up Transformer	95

D.3.6.	Protection	97

D.3.7.	Control / Communications interface	98

D.3.8.	Harmonic Emissions	98

D.3.9.	Earthing	98

D.3.10.	Engineering studies	99

D.4. LV CONNECTIONS	99

D.4.1.	LV grid connection	101

D.4.2.	LV metering	101

D.4.3.	Engineering studies	101

D.5. GRID SUPPORT	102

D.5.1.	Automatic grid support functionality	102

D.5.2.	Dispatch control	104

D.6. COMMUNICATIONS INTERFACE	105

D.7. WEATHER STATION	106

D.8. STANDARDS	107

D.9. TYPICAL SCADA IO LIST	107

D.10. NETWORK EXTENSIONS	113

D.10.1.	Electrical cables	113

D.10.2.	Low voltage Distribution Box	114

D.10.3.	Low voltage Busbar on Transformer Substation	114

D.10.4.	Distribution transforners	115

D.10.5.	RMU switchgear	115

D.10.6.	Earthing of network extension works	116

D.10.7.	Final cable routes	116

D.10.8.	Engineering studies	117

D.10.9.	Compact substations and substation buildings	117

D.11. DESCRIPTION OF THE INTERCONNECTION AND NETWORK EXTENSION WORKS	119

E.1. GENERAL REQUIREMENTS FOR PV ARRAY STRUCTURES	121

E.1.1.	Introduction	121

E.1.2.	General requirements	121

E.2. ARRAY STRUCTURE SPECIFIC REQUIREMENTS	125

E.2.1.	Site summary	125

E.3. DIAGRAMS OF TYPICAL ARRAY STRUCTURES AND REPRESENTATIVE CONCEPTUAL DESIGNS		126

E.4. CIVIL WORKS CONSTRUCTION SPECIFICATION	137

E.4.1.	Standard and Codes	138

E.4.2.	Drawings and Specifications	138

E.4.3.	Loading Specifications	138

E.4.4.	Site Clearance	139

E.4.5.	Metal works and Corrosion resistance	140

E.4.6.	Concrete Works	140

E.4.7.	Concrete Formwork and Falsework	144

E.4.8.	Steel Reinforcement	145

F.4. ENVIRONMENT, SOCIAL, HEALTH AND SAFETY REQUIREMENTS	147

F.4.1.	Information Provided in Data Room	147

F.4.2.	Specific Requirements	148

F.4.3.	General Safegaurds Requirements	150

F.4.4.	Grievance Redress Mechanism for contracted Work Force	160

F.4.5.	Grievance Redress Mechanism for the Public	162

F.4.6.	Applicable Laws and Policies	170

F.4.7.	Procedure for Management of Physical Cultural Resources- Protection and Chane Find Procedure	187

- Overview

  - Background

The Republic of Maldives is a South Asian Island country, located southwest of Sri Lanka and India. It is comprised of 1,192 coral islands grouped into 26 geographical atolls, spreading over an area of 115,300 sq. km and occupying a total land area of 224 sq. km. Maldives is recognized as an upper middle-income economy by the World Bank, with a GDP growth rate of 7% in 2019

Out of the total 1192 islands, 187 are inhabited, 123 are self-contained tourist resorts and 128 are used for other industrial and commercial activities. The total population of Maldives is 530,953. The dispersed nature of the islands requires each island to have a separate power generation and distribution system. The powerhouses are operated mainly by three utility companies namely, State Electric Company Limited (STELCO), FENAKA Corporation Ltd. (FENAKA) and Male’ Water and Sewerage Company Pvt. Ltd. (MWSC). Maldives has achieved provision of 24 hours electricity service throughout the country in 2008.

By the end of 2018, the total installed capacity in Maldives stood as below:

- Diesel based installed capacity: Diesel based installed capacity in inhabited islands stood at 319 MW, and around 210 MW across resort islands, therefore, making a total of ~530 MW.

- Renewable based installed capacity: Total installed capacity of Renewable Energy Systems stood at 16.5 MW.

To ensure energy security, the Government of Republic of Maldives (GoM) has embarked on a plan to transform the electricity sector and the enabling policies and programs of the GoM makes the country an attractive destination for private sector investments in renewable energy. Furthermore, Maldives is located at the Equator and receives abundant solar energy. It has on average 280 – 300 sunny days per annum. The Daily Average Global Irradiation in Maldives is around 4.5-6 kWh/m2/day.

The National Strategic Action Plan (2019-2023) (SAP) sets targets to increase the share of renewable energy by 20% compared to 2018 level. Further GoM is working towards an ambitious goal of carbon neutrality by 2030 given extensive international support.

There are several solar PV projects that have already been installed/awarded in the country through various modes under different programs. By the end of 2019, the total installed capacity of renewable energy systems in the Maldives reached 20.5 MW. This represents 4% of the national energy mix. Growth of Solar PV installations in Maldives over the past decade is shown below.

Figure 1: Renewable energy installations in Maldives

Some of the selected solar projects with installation size are provided in the table below:

Table 1: Selected solar projects in Maldives

| Description | Project size (kWp) | Project status |
| --- | --- | --- |
| Solar PV installation at the MCCEE Building, Male’ | 25 kWp | Installed |
| Solar PV grid connected system in R. Ungoofaaru and Dh. Kudahuvadhoo | 324 kWp | Installed |
| Solar PV hybrid system in Vaavu atoll Rakeedhoo Island | 29 kWp | Installed |
| Solar PV installation at Billabong School, Male’ | 70 kWp | Installed |
| Solar rooftop PV in 3 public buildings in GDh. Thinadhoo | 558 kWp | Installed |
| Rooftop installations in 12 public buildings, Male’ and Hulhumale’ | 740 kWp | Installed |
| Installation of Solar PV system in 05 islands (Addu city, GA. Villingili, Th. Buruni, Lh. Kurendhoo, B. Goidhoo) under POISED Project at various public buildings rooftops | 2,500 kWp | Installed |
| Installation of Solar PV systems in islands of HA, Sh and Noonu atolls under POISED Project | 6,631 kWp | Installed |
| Solar PV installation at Hulhumale’ under ASPIRE project on rooftops of 33 blocks. | 1,500 kWp | Installed |
| Hulhumale’ - Hulhule’ Link Road under ASPIRE project | 5,000 kWp | Installed |
| Installation of 11 MW Solar PV system in Addu city, Fuvahmulah city, Kulhudhuffushi city, Gdh. Thinadhoo, B. Eydhafushi and Lh. Hinnavaru | 11,000 kWp | Commissioning - Dec 2024 |
| Installation of 10 MW Floating Solar PV system in Addu City | 10,000 kWp | Tendering Stage |

  - Project investments and arrangements

Under a first of its kind Public Private Partnership (PPP) contract in the country, a 1.5 MWp solar photovoltaic rooftop system have been installed across housing units in Hulhumale’ island under DBFOOT model. The project was commissioned on February 2018. The investors have signed a Roof Lease Agreement (RLA) with the Housing Development Corporation Ltd., and a long-term Power Purchase Agreement (PPA) with the State Electricity Company Limited (STELCO) for offtake of the energy generated.

Further, another 5 MWp DC nominal electrical capacity project covering the Hulhumale’ - Hulhule’ Link Road and an 11 MWp DC nominal electrical capacity project for Addu City, Fuvahmulah City, Kulhudhuffushi City, and on the islands of Gaafu Dhaalu Thinadhoo, Baa Eydhafushi, Lhaviyani Hinnavaru has been procured and contracted under similar contractual structure and DBFOOT model. The World Bank is supporting these projects through a SREP (Scaling-up Renewable Energy Program) grant and a guarantee partially covering termination payment. Under this, The World Bank and the GoM approved the Accelerating Sustainable Private Investments in Renewable Energy (ASPIRE) project in May 2014. ASPIRE project kick-started the growth of private sector investments in large-scale solar projects in the Maldives. The risk mitigation measures established under the ASPIRE projects have set favourable platform for renewable Independent Power Producers (IPP’s) in Maldives and substantial reduction in PPA tariffs.

Building on the success of the ASPIRE project, the WB and the GoM approved a new project titled Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) in December 2020. ARISE project aims at building resilience to climate change, natural hazards, and other exogenous shock by increasing electricity generation from renewable energy and improve climate resilience by diversifying the energy mix and strengthening fiscal sustainability.

The GoM, under the ARISE project, encourages and facilitates private investments in the sector by addressing key barriers to private investment through provision of appropriate risk mitigation instruments. Under the ARISE project, the GoM is now seeking for a total 15 MWp Electric Capacity from generation facilities distributed across multiple islands.

The islands considered for installation and the existing profile is provided below:

- L. Hithadhoo: The total population of Hithadhoo is around 1,197 with a projected annual power consumption of around 1.9 million kWh by 2024. Currently the installed generation capacity in operation includes 780 kW of diesel generators.

- L. Kunahandhoo: The total population of Kunahandhoo is around 874 with a projected annual power consumption of around 0.9 million kWh by 2024. Currently the installed generation capacity in operation includes 550 kW of diesel generators.

- L. Maabaidhoo: The total population of Maabaidhoo is around 1,113 with a projected annual power consumption of around 1.1 million kWh by 2024. Currently the installed generation capacity in operation includes 830 kW of diesel generators.

- L. Maamendhoo: The total population of Maamendhoo is around 1,303 with a projected annual power consumption of around 1.7 million kWh by 2024. Currently the installed generation capacity in operation includes 820 kW of diesel generators.

- L. Maavah: The total population of Maavah is around 2,030 with a projected annual power consumption of around 3.2 million kWh by 2024. Currently the installed generation capacity in operation includes 1.15 MW of diesel generators.

- L. Isdhoo: The total population of Isdhoo is around 1,387 with a projected annual power consumption of around 2 million kWh by 2024. Currently the installed generation capacity in operation includes 800 kW of diesel generators.

- L. Kalaidhoo: The total population of Kalaidhoo is around 1,026 with annual power consumption of around 1.3 million kWh. Currently the installed generation capacity in operation includes 460 kW of diesel generators.

- L. Dhanbidhoo: The total population of Dhanbidhoo is around 1,041 with a projected annual power consumption of around 1.4 million kWh by 2024. Currently the installed generation capacity in operation includes 560 kW of diesel generators.

- L. Fonadhoo: The total population of Fonadhoo is around 2,810 with a projected annual power consumption of around 8 million kWh by 2024. Currently the installed generation capacity in operation includes 2.6 MW of diesel generators.

- L. Gan: The total population of Gan is around 4,829 with annual power consumption of around 9.4 million kWh by 2024. Currently the installed generation capacity in operation includes 2.6 MW of diesel generators.

- Lh. Naifaru: The total population of Naifaru is around 5,488 with a projected annual power consumption of around 10.6 million kWh by 2024. Currently the installed generation capacity in operation includes 3.168 MW of diesel generators.

- GA. Villingili: The total population of Villingili is around 3,606 with a projected annual power consumption of around 7.9 million kWh by 2024. Currently the installed generation capacity in operation includes 3.77 MW of diesel generators.

- Sh. Funadhoo: The total population of Funadhoo is around 2,553 with a projected annual power consumption of around 7.9 million kWh by 2024. The installed capacity includes around 3.3 MW of diesel generators.

With this RFP document, the GoM invites applicants to submit Bids for installation of grid-tied solar photovoltaic system(s) across these islands on design, build, finance, own, operate, and transfer basis in two lots (contracts). Selected Bidder will be responsible for design, build, finance, own, operate and transfer of all facets of the project and for generating the required minimum generation output as described in the bidding document.

The scope of services requested shall include, but is not be limited to Site assessment, providing all labour, services and equipment necessary to develop, permit, design, engineer, procure, install, construct, test, commission, monitor, operate, and maintain fully operational generating facilities, including overhaul of the plant, equipment, works, switch yard and transmission lines and equipment up to the Interconnection Point of the project in accordance with the PPA.

Detailed technical information has been provided for each Site in the form of a Virtual Data-Room. The Data-Room includes detailed Site information including drone images of proposed Sites with marked areas/dimensions available on Google Maps files, sources for solar resource data, Helioscope assessment results, civil and electrical design requirements, etc.

GoM would be setting up Battery Energy Storage Systems (BESS) which would accommodate Solar PV power, over and above the peak load. Along with this GoM is working on upgrading the existing infrastructure of electricity grids across Maldives. The developers would be assured 100% off-take under a Power Purchase Agreement (PPA) with the utility. The BESSs would facilitate grid stability at all times to enable high levels of renewable energy penetration, as well as function as a substitute against diesel-based power during non-solar hours. The procurement for setting up BESSs is being carried out in parallel as a separate procurement.

The selected Bidder would be required to sign a standard PPA for a period of 20 years, with the electricity Service Provider for the island, under US Dollar dominated tariff payable in Maldivian Rufiyaa. The Service Provider for all the islands included in this RFP is FENAKA Corporation Limited. The Sites would be made available through separate space lease agreements and/or license agreements (Site Agreements) facilitated by GoM between the Site owners and the selected Bidder as per the terms and conditions specified in the relevant Site Agreement.

The selected Bidder will be required to enter into the following Project Agreements:

- Power Purchase Agreement (PPA) with electricity service provider (FENAKA) for offtake of energy generated. Key features of PPA:

- Full tariff payment up to contracted energy

- Deemed generation charges payable for supply curtailment beyond threshold level.

- Monthly bills payable within a fixed timeframe of invoicing, which is backed by Payment Security Mechanism (PSM) to include an escrow with a balance of 6 months of tariff payment on contracted energy.

- PPA indemnifies project against force majeure

- Multilateral Investment Guarantee Agency (MIGA) guarantee partially backing GoM termination payment

- Site Agreements with the owners of sites utilized for the project. Site Agreements consists of either Roof Lease Agreements for the sites comprising of rooftops and License Agreements for sites comprising of land areas. Site Agreements will define the rights and obligation of the selected Bidder and the site owners. Key features of Site Agreements:

- The Sites would be made available through a lease or license mechanism facilitated by the GoM between the site owners and selected Bidder as per the terms and conditions specified in the respective Roof Lease Agreement or License Agreement.

- Right of way for project construction provided

- Non-availability of space will require the Off-taker/GoM to identify an alternate site

- Lease/License commencing and co-terminus with PPA

- Lessee/Licensee to insure facility and maintain general liability insurance.

- Lessor/Licensor to either maintain insurance for the buildings or sites and the Facilities or carry out all major repairs at its cost

- Implementation Agreement (IA) with Maldives: The IA will define obligations between the selected Bidder and the Government. Key features of IA:

- Government to procure execution of Roof Lease Agreement and License Agreements for all the Sites.

- Arrangement of alternate Sites in case of unavailability of site due to Political Force Majeure event and Government to pay for cost of relocation of the facility.

- Government to set up and maintain escrow account with the commercial bank. Escrow to provide payment security cover.

- Payment guarantee for termination events.

Bidders are required to go through the draft Agreements described above to understand the full scope of the agreements which will be provided as part of this bidding document.

The Agreements mentioned above may be amended following Bidders’ queries. Once amended, they should be considered final and no substantial amendment shall occur after submission of Bids and award. These documents would be shared with the shortlisted Bidders at the bidding stage.

The Bidder, if selected, will be required to commission the project by the Scheduled COD, i.e. within tweleve (12) months of the Contract Date (as defined in the PPA), unless otherwise determined during the PPA & IA negotiations stage.

The overall ARISE investment program structure is represented below:

Figure 2: ARISE project structure and modalities

The following are the major security packages built in for the program:

    - Escrow Account

In order to provide security to the selected Bidder against payment defaults by FENAKA on its monthly invoices under the PPA, an escrow account will be established by GoM and FENAKA. GoM will provide advance funding to the escrow account to create standing payment security of six months’ worth of invoice payments. In the event of a payment default by FENAKA on its monthly invoices, the selected Bidder will be entitled to draw down on the escrow account for the unpaid amount (to the extent it is not disputed by FENAKA) of the relevant invoice(s). FENAKA will thereafter be obliged to replenish the escrow account, failing which GoM will be responsible for ensuring the replenishment of the escrow account.

    - World Bank support

The World Bank is committed to support the ARISE program. The Multilateral Investment Guarantee Agency (MIGA) under the World Bank Group has agreed to propose its guarantee products to the IPP subprojects as a further layer of project risk mitigation. MIGA guarantees would be proposed to Bidders to cover non-commercial risks such as: (a) termination risk through its breach of contract coverage, (b) transfer restriction and currency inconvertibility, (c) expropriation, and (d) war and civil disturbance risk. The Bidders have the option to decide if they opt for MIGA guarantees. MIGA would also conduct its own due diligence for decision-making. Further, the final guarantee amount under MIGA will be fixed after MIGA’s due diligence and internal approvals.

Further, the Bidders will also have option to opt for IFC debt financing.

  - DOING BUSINESS IN MALDIVES

The Ministry of Economic Development, Government of Maldives has set up an agency, called “Invest Maldives” for promoting and facilitating foreign investments into the Maldives and is responsible for investment promotion, facilitation and registration.

Invest Maldives offers a one-stop shop that takes investors through the A-Z of investing in the Maldives. It is a process that has been streamlined through changes in laws and regulations, and well-defined procedures, designed to offer clarity, security, convenience and speed for investors looking at investing in the Maldives.

Key incentives for Foreign Investment include:

- The right to incorporate businesses with 100% foreign ownership

- Freedom to use foreign managerial, technical and unskilled workers

- No foreign exchange restrictions

- No restrictions on repatriation of profits and capital proceeds

- Provision of a legally backed investment guarantees

- Allows for the availability of international arbitration in dispute settlement

For details, Bidders may log in to Home Page - Invest Maldives

- Specifications

  - SCOPE OF WORK

    - General Scope

Details of the Sites identified for installation and operation of 15 MWp land-based solar PV plant across Maldives in 13 islands, namely; L. Hithadhoo, L. Kunahandhoo, L. Maabaidhoo, L. Maamendhoo, L. Isdhoo, L. Kalaidhoo, L. Fonadhoo, L. Gan, L. Dhanbidhoo, Lh. Naifaru, GA. Villingili and Sh. Funadhoo are given in Part C.

The scope of project includes the design, build, commissioning, operation, and handover or removal of land-based solar PV systems to specification, comprising of 138 individual sites. Each system shall be interconnected to the island grid network as specified.

The required interconnection methods vary on case-by-case basis and include: LV connection to distribution box or transformer, LV connection with feeder upgrade, LV connection with feeder and/or transformer upgrade and/or MV cable extensions, and solar MV RMU with MV interconnection by others.  The interconnection requirements are defined in Part C for each system.

Key items of work for the successful Bidder include, but not limited to:

- Site assessment surveys: Demarcation in coordination with site owners and assessment of existing site conditions along with all necessary detailed surveys and studies for each site prior to the start of the detailed design works. Detailed surveys may include geotechnical investigations, setting out surveys, underground mapping for identification of any service lines or obstructions, or others necessary for optimal structural and electrical design of each system

- Detailed design: The proposed concept design submitted by the successful Bidder at the time of bidding shall be subject to approval of project stakeholders (Government, Site owners), and confirmation and minor adjustments by a detailed design from the Seller (as defined in the PPA) based on their assessment of the project sites and the design criteria, including studies and preliminary reports that they have taken into consideration.

- Site clearing, ground levelling and other preparatory works for the installation of PV systems and establishing electrical interconnections to the grid.

- Fulfil the requirements in the EIA regulations, 2007.

- Procure, transport, clearances and duties, and install the System as per the approved design at the site, and respective electrical interconnections to the grid.

- Works for the interconnection of the System as specified, to the grid maintained by the respective utility in accordance with the regulations of Utility Regulatory Authority (URA).

- Obtaining all necessary permits in accordance to the relevant laws and regulations

- Appropriate measures to prevent any operational malfunction or physical damage on the existing distribution system, diesel engine generators and/or every other distribution network.

- Pre-commissioning and commissioning tests of the PV systems under the witness of Employer or an independent third party approved by the Employer.

- Operation and Maintenance of all facets of the project and for generating the required electricity as described in the bidding documents and Project Agreements.

- Scope of works includes removal/demolition, transportation and disposal of any waste materials and temporary structures installed for the purposes of carrying out the works.

    - Project Design Documents

The following documents shall be submitted (both in soft and hard copies) to the Employer by the selected Bidder as indicated below:

Timeline Summary Table

|  | Task, milestone or deliverable |  | Document reference | Delivery schedule, within |  |
| --- | --- | --- | --- | --- | --- |
|  | Contract Effectiveness achieved |  | Article 2.1 of the PPA | Upon signing of the PPA |  |
| Main Agreements | Implementation Agreement (IA) signing |  | ITB 48.2 | 60 | Days of Receipt of Agreements for negotiation |
|  | Power Purchase Agreement (PPA) signing |  | ITB 48.2 | 60 | Days of Receipt of Agreements for negotiation |
|  | Project Company formation |  | ITB 48.2 | 30 | days of execution of the Project Agreements, at the latest |
|  | Site Agreements (Roof Lease Agreement and License Agreement) signing |  | RFP ITB 48.2, PPA Article 3.5 IA Article 5.1 | 60 | Days of Receipt of Agreements for negotiation, and/or no later than 30 days from Effective Date of IA and PPA |
|  | Escrow Agreement signing |  | RFP ITB 48.2 | 60 | Days of Receipt of Agreements for negotiation |
| Security | Performance / Construction Security |  | RFP ITB 49 IA Article 4.1 | 60 | Days of receipt of Letter of Acceptance and/or on or within 30 days from Effective Date of IA |
|  | E&S Security |  | RFP ITB 49 IA Article 4.3 | 60 | Days of receipt of Letter of Acceptance and/or on or within 30 days from Effective Date of IA |
|  | TBD Security |  | RFP ITB 14.5 IA 5.2(b) | 90 | Days from the Effective Date of IA |
| Technical studies and design documents | Schedule and PV installation concepts |  | IA, Article 3.3(a), PPA, Article 3.2 (d), RFP Section VII, Part B | 30 | days of Contract Effectiveness |
|  | Design documents |  | IA, Article 3.3 | 90 | days of Contract Effectiveness |
|  | Method Statement |  | IA Article 3.3(g) | 150 | days of Contract Effectiveness |
|  |  | Surveys, calculations | RFP Section VII, Part B IA Article 3.3 (c) | 90 | days of Contract Effectiveness |
|  |  | Structural assessments, glare assessments | RFP Section VII, Part E | 90 | days of Contract Effectiveness |
|  |  | Engineering studies: Power systems, protection, earthing, cable sizing | RFP Section VII, Part D, (D.2.10 & D.4.3) | 90 | days of Contract Effectiveness |
|  | Detailed drawings |  | RFP Section VII, Part B IA, Article 3.3 (e) | 120 | days of Contract Effectiveness |
|  |  | Array structures etc | IA, Article 3.3 RFP Section VII, Part B | 120 | days of Contract Effectiveness |
|  |  | Electrical SLD's |  | 120 | days of Contract Effectiveness |
|  | Certified yield analysis |  | RFP Section VII, Part B IA Article 3.3 (d) | 90 | days of Contract Effectiveness |
|  | Environmental site report |  | RFP Section VII, Part F |  |  |
|  |  | ESIA/ESMP | IA, Article 3.3 (h) | 90 | days of Contract Effectiveness |
|  |  | ESMS | IA, Article 3.3 (f) | 30 | days of Contract Effectiveness |
| Financing | Evidence of Financing for Construction |  | PPA, Article 3.6 (d) | 30 | days of Contract Effectiveness |
|  | Financial Closure |  | PPA, Article 3.6 (d) | 180 | days of Contract Effectiveness |
| Other | Exit management plan |  | PPA Article 2.2 IA, Article 3.3 (I) |  | Upon COD |
|  | Community Engagement Plan |  | IA, Article 3.3 (j) (iii) RFP Section VII, Part F, 4.2 | 90 | days of Contract Effectiveness, or at the bidding stage. |
| Operations | Commercial operation date (COD) |  | PPA Article 3.3 (a) | 12 | months of Contract Effectiveness |
|  | Reporting and invoicing |  | PPA Article 5.3 (a) | Monthly |  |
|  | End PPA term or Contract Term |  | PPA Article 2.1 | 20 | years after COD |

    - Implementation and Conditions on Site

            - It is the selected Bidders’ (herein referred to as “Seller” as the term is defined in the PPA)  responsibility to obtain all the permits required (from regulatory authorities, service providers etc.) for the designs, and for construction.

            - The Seller shall not be allowed to undertake any physical activities until the relevant clearances are obtained by the Environment Protection Agency as per the Environment Impact Assessment Regulation (2012) of Maldives

            - The Seller shall implement any gaps identified in the Contractor’s ESMS to the satisfaction of the employer.

            - Ground water shall not be used for any construction. Coral sand shall not be used for any concrete works and shall not be taken from the island or the island lagoon.

            - Quality of construction and materials shall be as specified in the technical specifications. Seller shall submit manufacturers and / or supplier specifications for any materials or works not covered in the technical specifications.

            - The Seller shall have its quality control measures in place and submit quality reports regularly. Apart from this the Employer may at any time without notice carry out independent quality assurance tests to verify the quality of materials and works. If the quality of materials or works is below the specified standard the Seller shall rectify the situation to the satisfaction of the Employer at its own expense

            - The confirmation of the ground and roof conditions is the responsibility of the Seller.

            - The Seller shall provide the testing results provided by an independent third party.

            - Electricity and water required for the project shall be supplied to the Seller at their expense.

            - The metric system of units shall be used throughout.

  - COMPLETING THE TENDER DOCUMENTATION

    - Data provided: Data Room structure

In addition to this bid document, Bidders are referred to the online Data Room containing more precise Site maps, locations and solar studies. Note that the Data Room may be updated as necessary during bidders Q&A. The Data Room can be accessed via the following link.

ONLINE DATA ROOM

Data Room is structured approximately as below:

- Root directory: - Google Earth kmz file (15 MWp PV Installation Locations), - Site Master list file (with all key site details summarised, including network upgrades) - Site Requirements summary file - Site maps, model concepts, Helioscope assessments - Individual island directory, site number sub-directory - Site maps - Aviation Obstacle Surface Limit guidelines (AVOSL) (for applicable islands), - Site capacity and solar yield assessments (Helioscope) - Single line diagrams and network for each island - Array structure concepts - Glare analysis for flight path – Sh. Funadhoo (SGHAT) - Structural assessments - Sub-station building design - (FENAKA CAD) and compact substation housing pictures - Ground level Photos of some of the PV installation sites - Solar Resource data - MCCEE Solar Resource Handbook, (http://www.environment.gov.mv/v2/en/types/publications)) - ESMAP Solar Irradiation Data - Environmental and Social Framework related Documents - Environmental and Social Screening Reports - Individual island directory, site number sub-directory - Laws, Regulations, Guidelines - URA Installation Standards - MIRA Taxation Law

    - Design basis

Site specific data is in Part C General Site Descriptions, and Part E. Array Structure Requirements.

Bidders are to offer solar PV plant at each site to meet the Fixed Energy for First Year (kWh) in Part C (specified in kWh), with a design life of 20 years. Bidders may not propose lower capacity than 2 MWp for Lot 1, 13 MWp for Lot 2 and 15 MWp in total. The Employer shall not be responsible for ensuring space for array capacity beyond that stated in the RFP Part C. After contract award, selected Bidder may be requested to expand capacity to fill remaining sites beyond 15 MWp, from any spare sites or any spare space, given there are no constraints in the grid for absorption of excess energy.

The PPA shall be based on the Fixed Energy (kWh).  The DC Capacity and CUF may be proposed by the bidder, however Bidders are required to ensure compliance to Part C as well as conditions stated in Section III – Evaluation and Qualification Criteria for Fixed Energy, DC Capacity and CUF.

    - Technical Information to be submitted

The Bidder shall submit the following technical information with its Bid, which shall be provided as per Volume 1, Section IV, Bid Forms, Technical Proposal, Form Tech-2 to 6:

- Preliminary yield design calculations.

  - DC kWp capacity proposed per site, meeting the requirement stated in this RFP.

  - Maximum rated AC output capacity of the plant (to meet grid limits)

  - CUF (Year 1), PR (Year 1),

  - kWh/year expected (Y1-20) meeting the requirement stated in this RFP, expected annual degradation of capacity.

- PV system description, preliminary design of one of each PV plant of the type (i) LV connection box connected plant, (ii) LV transformer connected plant, and (iii) solar RMU connected plant, along with the single-line diagrams (showing PV modules, DC cabling, array junction boxes, inverters, DB’s and LV switchgear, AC cabling, (weather station if relevant), communications links, up to LV outgoer of PV plant).

- Interconnection single-line diagram for LV/MV networks, showing transformers, switchgear, cabling, earthing, metering, communications, (weather station if relevant) up to point of connection, and clearly showing for one of each site connection type comprising of (i) LV to connection box, (ii) LV feeder to existing transformer, (iii) LV feeder to new transformer including LV/MV Switchgear, and (iv) Solar RMU connection including LV/MV Switchgear each labelled with site name AND Declaration of 100% Compliance with requirements for compatibility with FENAKA LV/MV network.

- Brochures and certificates for proposed major equipment (PV modules, PV inverters, transformers, switch-gear and cabling, AND declaration of 100% compliance with requirements for these components).

- Array structure proposal in draft confirming compliance PV carrying capacity, with orientation and tilt of the PV arrays for all critical sites and tilt adjustability (AND declaration of 100% compliance with requirements as may be determined for specific sites).

- Brochures for minor equipment (module roof-mounting proposal, metering, etc.) (or declaration of 100% compliance with requirements).

Detailed designs are not required at time of bidding. Bidders are required to show preliminary concept of design and understanding of the design constraints, and to declare that they will resolve these.  Beyond that, Bidders need only to proceed to design in sufficient detail for their own costing for tariff calculation.  Detailed design and engineer certifications will only be required from the selected Bidder.

    - Work Teams

The Bidder shall demonstrate a technical team capable of carrying out the tasks in addition to a construction team with relevant experience required. The structure of this team for planning and installation, and for operation during the full PPA term, shall be presented in the bid submission with a proposed organizational structure.

For the project design and construction phase the team shall comprise key personnel from the below prescribed expertise areas and at a minimum shall meet the stated qualification and experience requirements. In case of replacement of any of the team members during any stage of contract implementation, the replacement shall also satisfy the minimum requirements prescribed below and shall be subject to approval from the Employer.

| Item No | Position/Specialization | Relevant academic qualifications | Minimum years of relevant work experience |
| --- | --- | --- | --- |
| 1 | Sellers’ Representative/Project Manager | Engineering or Project Management Degree or Diploma | 10 years |
| 2 | Design Engineers (Electrical / Renewable power systems) | Electrical/Renewable Energy Engineering Degree | 05 years |
| 3 | Design Engineers (Civil & Structural | Electrical/Renewable Energy Engineering Degree | 10 years |
| 4 | Site supervisors (Civil/Constructions) | Relevant certificate in civil engineering related works | 07 years |
| 5 | Site supervisors (Electrical) | Relevant trainings and certifications | 10 years |
| 6 | PV system commissioning engineer | Electrical/Renewable Energy/ Communications or other relevant Engineering Degree | 10 years Worked specifically in commissioning & grid connection of renewable power projects |
| 7 | Environment Specialist | Degree or Diploma in relevant field | 05 year’s experience |
| 8 | Social Specialist | Degree or Diploma in relevant field | 05 years’ experience |

  - SYSTEM DESIGN

The selected Bidder is entirely responsible for entire system design.

    - Solar Radiation Data

For the purposes of comparison of bids, (for bid evaluation), solar resource data to be used for yield analysis shall be the ESMAP Solar Irradiation Dataset provided in the Data Room.

The Bidder, at its own discretion, may additionally use alternative solar resource information for Maldives as available from various sources, for the purpose of validation/verification. Such resources may include:

- NASA Atmospheric Science Data Centre is most comprehensive from.

- Renewable Energy Resource Mapping for the Republic of Maldives implemented by the World Bank, and published by GoM, provides accurate data on solar radiation and resource overview in Maldives. The project mapped solar measurements at four locations (Hanimaadhoo, Hulhule, Kahdhoo and Gan), and the ground measurements at these sites were used to site adapt satellite derived solar data for the period 1999-2016.  For details, Bidders may refer to the report “SOLAR resource overview of Maldives, 2017” (Source: http://www.environment.gov.mv/v2/en/types/publications)

Commercially available historical and TMY data for global sites. For example, Solcast is a leading provider of solar irradiance data and forecasting technology, delivering data to over 350 customers that manage more than 300GW of assets globally. Solcast produces this data by tracking clouds and aerosols at 1-2km resolution globally, using satellite imagery, global weather data and proprietary AI/ML algorithms to produce over 600 million forecasts every hour. Since 2016 the Solcast API has been bringing accurate data to the market and helping enable the energy industry to deliver the resilient power grids it will take to build a solar-powered future.

- Maldives Meteorological Service (MMS) is the host of solar measuring stations in Maldives.

  - Typical Meteorological Year (TMY) containing hourly data derived from time series covering complete 18 years (1999 to 2016). TMY time series includes all important parameters such as Global Horizontal Irradiance (GHI), Direct Normal Irradiance (DNI), Diffuse Horizontal Irradiance (DHI), Air Temperature (TEMP) and others.

  - P50 TMY dataset represents, for each month, the average climate conditions and most representative cumulative distribution function, therefore extreme situations (e.g. extremely cloudy weather) are not represented in this dataset. The long-term annual summary of GHI and DNI are considered as the most critical parameters to consider.

The solar radiance data from Renewable Energy Resource Mapping for the Republic of Maldives is shown below for one selected site.

Figure 3: GHI solar radiance [GWh/m2/day] derived from time series and TMY P50 and P90 for Hulhulé site (Source: “SOLAR resource overview of Maldives, 2017)

Figure 4: GHI solar radiance [kWh/m2/day] monthly averages for Hulhulé site (Source: “SOLAR resource overview of Maldives, 2017)

    - Capacity Utilization Factor and Performance Ratio

In the PPA, solar PV plant performance is defined by Capacity Utilization Factor (CUF).

While CUF is generally defined in the following IEC standards:

- IEC 61724-1:  Photovoltaic system performance – Part 1: Monitoring.

- IEC TS 61724-2:  Photovoltaic system performance – Part 2: Capacity evaluation method.

- IEC TS 61724-3:  Photovoltaic system performance – Part 3: Energy evaluation method.

for the purposes of this particular project the following definitions in the table below shall hold.

Table 2: Definition of CUF and PR for this project

Capacity Utilisation Factor (CUF) is defined as: CUF = (Eout (kWh/year) / PVdc ) / (24x 365) Where Eout = Electricity Energy delivered in year one (AC kWh/year) PVdc = nameplate kWp of PV arrays. Performance Ratio (PR) is defined as: PR = (Eout / PVdc) / (Hi / GSTCref) Where Eout = Electric Energy (AC kWh) PVdc = Electric Capacity (kWp dc) Hi = plane-of-array solar irradiation (kWh/m2) in time period Gi, ref = irradiance of PVdc rating, usually 1 kW/m2 GHI = Global horizontal solar irradiation (kWh/m2) in time period Please refer to PPA Schedule 5 for more nuanced and detailed formulae to account for grid downtimes and/or limiting of PV plant output.

CUF calculated as above from Helioscope simulations for  each project site in Part C, for year 1.

Table 3: Not used.

    - Environmental conditions

The Solar power station, including all supporting infrastructure, shall be designed and constructed to operate normally under the environmental conditions summarised in table below.

Table 4: Environmental conditions

| Criteria | Condition |
| --- | --- |
| Minimum Ambient Temperature (oC) | 17.2 oC |
| Maximum Ambient Temperature (oC) | 40 oC |
| Humidity (%) | 79% |
| Wind Speed (m/s) | Up to 33m/s / 120km/hr |
| Pollution Level (AS/NZS 2312) | Category D |
| Altitude (m) | 1.5 mADH |
| Corrosion | Compliance with ISO-12944, C5M |

  - INSTALLATION QUALITY AND SAFETY

The entire contract must be carried out in accordance with the latest revisions and amendments of relevant IEC standards as in force in Maldives. Furthermore, the installations much comply with the technical requirements prescribe by the URA, as well as any other laws or regulations of Maldives.

All drawings and electrical designs and engineering studies shall be approved by a URA licenced engineer, and signed by FENAKA and URA prior to works commencing.

URA Installation Standards shall be followed as a general guideline, unless this project specification specifically over-rules those standards.  Each installation shall be certified to meet or exceed the Utility Regulatory Authority (URA) Installation Standards (Part G – Supplementary Information).

AC side of the facility installation (LV and MV):

- Utility Regulatory Authority:  Installation Standards (Part G- Supplementary Information)

- Part D: Solar Farm Connection Requirements describing MV and LV interconnections

DC side of PV installation:

- IEC 62548 Ed.1: Installation and safety requirements for photovoltaic (PV) generators

- IEC 60364-7-712 Electrical installations of buildings – Part 7-712: Requirements for special installations or locations – Solar photovoltaic (PV) power supply systems

- IEC 60364-9-1: Low-voltage electrical installations - Part 9-1: installation, design and safety requirements for photovoltaic systems (PV).

- IEC 62446: Grid connected PV systems - Minimum requirements for system documentation, commissioning tests and inspection

- Once published IEC 60364-9-1 Ed.1.0 will cancel and replace IEC 60364-7-712 Ed.1.0. and IEC 62548 Ed.1.0).

  - COMPATIBILITY WITH THE UTILITY INTERFACE

    - Technical Requirements for Grid Connection

URA has provided guidance on technical requirements for photovoltaic grid connection that needs to be complied by the Bidders with respect to grid connection. The key aspects covered by the guidance are provided below:

- Classification of Interconnection: Solar plant point of connection voltage is dictated by a) availability of point of connection and b) proposed plant size.  Electrical systems of the Maldives Islands consist of 11kV loop distribution backbone networks and 400V radial feeders to customers, limiting the connection options. Interconnection classification shall be selected in accordance with the following table.

Table 5: Classification of Interconnection

| Based Output of PV System (kW) | Breaker Capacity (A) | Interconnection Voltage |
| --- | --- | --- |
| <7 | 40A | LV (1P, 230V) |
| 7-35 | 63A | LV (3P, 400V) |
| 35-175 | 315A | LV (3P, 400V) |
| 175> | - | MV (3P, 11kV) |

    - Network ownership and responsibility

All new cables and equipment required for interconnection of the PV systems to the utility network shall be installed as part of the project cost-to-developer, as described, to URA standards or to FENAKA standards (safety, switchgear), and performance specifically at point of connection.

The interconnection network shall be owned by the Seller (as defined in the PPA) and operated and maintained by the Seller until end of the Contract Term of PPA.

    - Solar plant interconnection requirements

The interconnection classification for each solar plant is summarised in Part C: General Site Descriptions.

The interconnection and performance requirements are detailed in Part D: Solar Farm Connection Requirements which includes LV and MV interconnection configurations, MV protection component specification, grid support functions, control and communications in one functional performance document for ease of reading.

- D.1. Introduction

- D.2. Solar Farm configurations

- D.3. 11kV connections

- D.4. LV connections

- D.5. Grid support (PV inverters)

- D.6. Communication interface

- D.7. Weather station

- D.8. Standards

- D.9.Typcial SCADA IO list

- D.10. Network extensions

- D.11 Description of the interconnection and network extension works

Some specific requirements of Part D shall apply to individual component specification under Section B.7, for example PV inverters, MV switchgear, etc.).

  - Array locations and structural requirements

15 MWp of ground and roof mounted solar PV plant is planned, in locations designated for varying functions which include public open spaces such as community parks, vehicle parking and farm land areas, pedestrian walkways, median strips along island link roads, secure airport locations in close proximity to runways and coastal areas near island harbours subjected to regular loading/unloading activities.

Array structure types include functional elevated arrays providing shading for vehicle-parks, shading for pedestrians’ walkways or harbour areas, and accessible shading of public open spaces. Therefore, retained functionality and access to spaces under the elevated arrays is critical, as well as aesthetic considerations.  The PV plant are referred to in Part C.

The structures for solar arrays are required to meet multiple criteria in order to be acceptable for installation along these routes.  These criteria include:

- Minimum array capacity (kWp);

- Compatibility with existing roof structure and roof space for roof mount structures;

- Array structure clearances for pedestrians, leisure and vehicular traffic;

- Sub-array span foot-print limitations and heights;

- Sub-array foundation constraints caused by new or existing underground cabling, other foundations, etc;

- Sub-array tilt and orientation to avoid airport glare as per Maldives Civil Aviation Authority requirements, or road glare, at specified sites; and

- Sub-array height limitations as a function of distance from runways, as per Aviation Obstacle Surface Limit guidelines, at specified sites.

The requirements for each solar plant have been assessed on a case-by-case basis, and is stated in the Part C: General Site Descriptions.

The specific requirements for array structures are described in Part E: Array Structure Requirements.

- E.1: General requirements for PV array structures (narrative)

- E.2: Array structure specific requirements

- E.3: Diagrams of typical array structures and representative conceptual designs

- E.4. Civil works construction specification

  - TECHNICAL SPECIFICATIONS FOR KEY PV PLANT COMPONENTS

In general, the specification is a performance specification for 20 years. However, there are certain minimum requirements with respect to the quality of installations on roofs, safety concerns, earthing, grid compatibility, and the degradation

of performance of any of the former; as well as the fact that systems shall be handed over after 20 years to the utility and should have at least a further 5-year useful life.

    - Applicable Codes and Standards

Equipment and Installation shall be certified according to equivalent and comparable standards of the following acceptable standard and code organisations to show compliance with the specifications:

- NEC: National Electrical Code

- IEC: International Electro-technical Commission

- UL: Underwriters’ Laboratories

- CSA: Canadian Standard’s Association

- JEC: Japan Electro-technical Commission

- JEM: Standards of Japan Electrical

- CE: Communaute’ Europe’ene

- JEAC: Japan Electro-technical Standards and Codes Committee

- BS: British standard

- DIN: German Institute for Standardization’s Standards

- IEEE: Institute for Electrical and Electronics Engineers’ Standards

Key specifications of the main products and supplemental information.

For some key components, this cross-refers to Part D:  Solar Farm Connection Requirements, to avoid redundancy of text.

    - Photovoltaic Modules

- Photovoltaic Modules shall provide more than 90% of the rated minimum output for 10 years and provide more than 80% of the rated minimum output for 20 years under STC conditions.

- Modules shall be certified to the following standards (or equivalent accepted international standard), and valid certificates shall be included with the tender (Form T5):  Mono and poly-crystalline modules are acceptable but note that thin film modules are not acceptable. The compliance must be certified by at least one recognized laboratory or institution. The certification shall be submitted at the Tender with technical documents of PV Modules.

- IEC 61215: “Crystalline silicon terrestrial photovoltaic (PV) modules – Design qualification and type approval”

- IEC 61730-1:2016: Photovoltaic (PV) module safety qualification - Part 1: Requirements for construction and related test method in Part 2.

- IEC 61701 Ed.2 or 2020: Salt mist corrosion testing of photovoltaic (PV) modules

All modules must be similar and interchangeable. Each module shall have identical characteristics within a tolerance of +5% on the power peak (max) value. Note that negative power tolerances are not allowed.

- Modules with open junction boxes are not acceptable. Modules shall be equipped with fly-leads and approved quick-connectors to standard.  There are a multitude of professional PV array quick connectors available for array fly-leads cables in the 2-4mm2 range, for example Multi-Contact™, Tyco™, SunClix™.

  - IEC 62852: “Connectors for DC application in photovoltaic systems – Safety requirement and tests”

- Modules and frames shall be compatible with the earthing requirements specified in Section B.7.7.

    - PV inverters

PV inverters shall meet the requirements of section B.5. Utility Interface, and Part D: Solar Farm Connection Requirements, including:

  - Automatic cut off in case of the grid failure

  - To avoid islanding operation, Power conditioners shall be equipped with proper detect functions by both active and passive protections to detect any power outages or failures on the grid.

  - Synchronization with the grid frequency

Autonomous and automatic grid support

PV inverters shall also provide autonomous and automatic grid support functionality for frequency and voltage control and fault ride through events for the purpose of maintaining the plant within grid-compliant limits.  It is also required to respond to dispatch instructions (external command) to vary the operating grid support mode or settings, and to curtail active power output

PV inverters shall meet the specific requirements of Part D: Solar Farm Connection Requirements, section D.5. Grid Support (PV inverters)

Specifically:

- DC power regulation: the inverter shall not switch off under overload-conditions arising from high DC power inputs (high irradiance or high temperatures), but shall regulate array power to continue operating at nominal power.

- Dynamic grid support – fault ride through to prevent immediate disconnection in the case of voltage/frequency dips on the mains supply (VDE-AR-N 4105, BDEW Medium Voltage Directive, etc)

- Frequency – dependent active power supply/reduction for under/over-frequency conditions (VDE-AR-N 4105, BDEW Medium Voltage Directive, etc).

- Supply/absorb reactive power on voltage (Q(U)control) during fault ride through and otherwise to counter mains voltage rises/dips (VDE-AR-N 4105, BDEW Medium Voltage Directive, etc).

Ride-through setting ranges as given under: of Part D: Solar Farm Connection Requirements, section D.5.Grid support (PV inverters)

- Frequency withstand:  as per section D.5.1.1

- Voltage with stand capability: as per section D.5.1.2

- Voltage support:  as per section D.5.1.3

- Active power control: as per section D.5.1.4

Dispatch control and response

- Standard Modbus interface for active control of set-points via command of remote dispatch from centralized plant control is a requirement, adjustable parameters including: shutdown, power limiting curtailment capability, ride-through, dynamic voltage control, etc of all of the above. Ideally using standard open source-communication protocols such as certified interfaces SunSpec Alliance’s SunSpec Modbus, SunSpec Rapid Shutdown, SunSpec IEEE2020.5/CSIP.

- Response:  as per section D.5.2

Certifications: as per section D.5.1.5, reprinted below:

The inverter shall conform with advanced feature functionalities which enable integration of higher RE fractions into the grid, (i.e. autonomous and automatic grid support, dispatch control and response) via at least the following recent grrd support certifications:

- DIN VDE 0126-1-1 (2013) Automatic disconnection device between grid parallel power generating system and the public low voltage grid (for frequency and voltage disconnection limits), and

- VDE-AR-N 4105 (2019): Power generating plant in low voltage grid

or similar such as

- G83/1-1, EA Engineering Recommendation G83/1-1: Amendment 1-June 2008, Recommendation for the connection of small-scale embedded generators (up to 16 A per phase) in parallel with the public low-voltage distribution networks.

- AS 4777.2 (2015): Grid connection of energy systems via inverters – inverter requirements

- EN 50438, Requirements for the connection of micro-generators in parallel with public low-voltage distribution networks

- UL1741, Inverters, Converters, Controllers and Interconnection System Equipment for Use with Distributed Energy Resources

- IEEE 1547 (2018): Standard for interconnecting distributed resources with electric power systems

    - MV switchgear, transformers and protection

All MV switchgear shall meet the specific requirements of Part D: Solar Farm Connection Requirements, section D.3. 11kV connections, and all sub-sections, specifically noting

- MV Switchgear 			Section D.3.3

- Ring main units (RMU)		Section D 3.3

- MV metering 			Section D.3.4

- Step-up transformer		Section D.3.5

- RMU protection:			Section D.3.6

- RMU communications		Section D.3.7

- Network extensions		Section D.10

    - Communications interface

Each solar site, comprising Modbus communication links between PV inverters, switchgear, weather station, and metering shall meet the specific requirements of Part D: Solar Farm Connection Requirements, section D.6. Communications Interface.

    - Weather station

Weather station at each solar site shall meet the specific requirements of Part D: Solar Farm Connection Requirements, section D.7. Weather station.

    - Earthing

Majority of PV plant are in publicly accessible areas, unfenced, and public will interact with the array structures, for example public shaded walkways and carport structures. Safety is paramount, so appropriate earthing and protection is essential.

Meet the specific requirements of Part D: Solar Farm Connection Requirements, section D.3.9 MV Earthing.  restated:

The solar site earthing shall ensure the safety of all personnel and equipment under all normal and abnormal operating conditions and all fault conditions.

General earthing shall be according to the Utility Regulatory Authority (URA) Installation Standards and IEC standards as listed in D: Solar Farm Connection Requirements, section D.8. Standards, and shall include the following:

- PV Module to structure frame;

- PV arrays;

- Array structures

- DC electrical system;

- PCU earthing;

- LV distribution side earthing as necessary

- Transformers and Neutral points;

- Fencing;

- Platforms and handrails and

- Buildings/enclosures.

Particular attention shall be given to:

- Achieving low-resistance connections that are resistant to degradation at all locations where grounding conductors or rods are bonded together

- Achieving the best possible contact with earth

- Verifications through tests that all electrical bonding within the grounding system has been properly affected

The design calculations shall include any area of the PV array exposed to step, touch and transfer potentials induced by earth potential rise, low frequency induction as well as electromagnetic and electric fields for the installation.

    - Labelling, Safety Signs and Notices

Majority of array’s are in publicly accessible areas, unfenced, and public will interact with the array structures, or example public shaded walkways and carport structures. Safety is paramount, so appropriate signages located in sufficient locations is essential.

- All labelling and signage must be in English and Dhivehi. All notices, labels or signs shall be durable and not removable except by determined and deliberate action.  The inscriptions shall be legible and indelible.  All custom signage to be ABS plastic silk-screened quality, indelible and easily noticeable.

- Where possible, standard approved symbolic safety signage is to be used.

- All DB labels to be professional quality signage.

Technical labelling

- The Contractor shall procure cabling and wiring materials, such as name tags, stickers, destination signs, board, stakes etc., to indicate destinations of wiring and cabling for future maintenance. The materials shall be insulated on wires and cables near the terminals and in every manhole if necessary.

Signage conventions

- All signage to be to conventions of from ISO 3864-2: 2004: Graphical symbols –safety colours and safety signs. Refer to examples below.

Suggested signage

In addition to the standard electrical labels required in terms of British DTI standards regarding electrical installations, the following signs are required:

| Locations | Sign number | Example sign |
| --- | --- | --- |
| - Main DB - Main display | 1 | SOLAR ARRAY LOCATED: Open circuit voltage: _____VDC Short circuit current: _____DC amps System DC power:___________kWp System AC Voltage:___________VAC 3 phase |
| - FENAKA transformer - Transformer LV breaker cubicle - Main DB - Inverter DB | 2 | WARNING Dual supply Isolate BOTH mains and SOLAR supplies before working on this equipment ISOLATE SOLAR at_____________________ Isolate mains supply at______________ |

| Locations | Sign number | Example sign |  |
| --- | --- | --- | --- |
| - Main DB | 3 | SHUTDOWN PROCEDURE: TURN OFF PV array isolator TURN OFF inverter AC main isolator DO NOT OPEN DC plug and socket connectors or PV string isolator under load |  |
| - Inverter DB - Main DB - Transformer LV breaker cubicle | 4 | P PV SYSTEM – MAIN AC ISOLATOR |  |
| - PV Array Combiner - PV Inverter | 6 | DANGER CONTAINS LIVE PARTS DURING DAYLIGHT |  |
| - MV Transformer enclosure (warning) | 7 |  |  |
| - MV Transformer enclosure (Danger) | 8 |  |  |

- General Site Descriptions

  - Description of the selected sites in the Bid

For each island, bidders shall supply the Fixed Energy for 1st year (kWh) for the two lots (contracts) as stated in table 6 below. For the subsequent years, the Fixed Energy shall be adjusted based on the relevant Degradation Factors. Further, the total capacity of Lot 1 shall not be lesser than 2 MWp and Lot 2 shall not be lesser than 13 MWp. The limit for Fixed Energy for 1st year (kWh) is set based on electricity consumption limit for the island. For each island and the project as a whole, Bidders can propose the capacity and CUF such that the Fixed Energy for 1st year (kWh) for each island are within the limits as stated in Table 6 below. Bidders have the option to ensure optimal DC/AC ratio, CUF levels and optimal utilization of space on each site, subject to the Fixed Energy for 1st year (kWh) limits. In case the Bidder’s proposed combination of DC capacity and CUF results in Energy (in kWh) greater than the Fixed Energy for first year, the Fixed Energy for first year shall be considered. In such a case, the Fixed Energy for first year shall be used, along with the Bidder’s proposed DC capacity to determine the CUF. In such an event, the proposed Degradation Factor may also be adjusted accordingly (revised Degradation Factor), as long as the Energy (in kWh) output for the subsequent years (Year 2 onwards) remains within the prescribed threshold of Fixed Energy for first year.

Table 6: Description of Selected Sites in the bid

Lot 1

| # | Island | Site Ref. | Location | Area (m2) | Helioscope Y1 results |  |  | RFP Indicated Fixed Energy for 1st year (kWh) | Array Structure Type (ref. Part E) | Grid Connection (ref. Part C) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | CUF (Y1) calculated | PR (Y1) (stated) | Capacity (kWp) based on available space |  |  |  |
| 1 | L. Hithadhoo | 1.1 | Harbour west | 450 | 16.90% | 82.5 | 85.8 | 426,524 | Elevated Arrays - medium span | LV (Feeder E- DB-E4) |
|  |  | 1.2 | Hithadhoo school | 325 | 16.10% | 78.5 | 27.5 |  | Road canopy PV | LV (Feeder C- DB-C5, |
|  |  | 1.3 | Park boundary | 700 | 15.90% | 77.3 | 85.8 |  | Road canopy PV | LV (Direct to powerhouse) |
|  |  | 1.4 | Cemetery | 200 | 16.90% | 82.7 | 37.4 |  | Elevated Arrays - medium span | LV (Feeder B- DB-B5) |
|  |  | 1.5 | Harbour south plot border | 900 | 16.00% | 77.9 | 119.9 |  | Elevated Arrays - medium span | LV(Feeder I - DB-I5) & to LV(Feeder H - DB- H5) |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 356.4 | 426,524 |  |  |
| 2 | L. Kunahandhoo | 2.1 | Kunahandhoo school west road | 1537 | 16.90% | 82.7 | 207.9 | 374,697 | Road canopy PV | LV (Feeder D - DB-D4) |
|  |  | 2.2 | Hukuru miski south | 697 | 16.80% | 82.8 | 88 |  | Elevated Array | LV (Feeder E - DB-E1) |
|  |  | 2.3 | Hukuru miski west | 449 | 16.70% | 81.79 | 66 |  | Road canopy PV | LV (Feeder D - DB-D3) |
|  |  | 2.4 | Island office north | 334 | 16.40% | 79.99 | 55 |  | Elevated Array | LV (Feeder E - DB-E2) |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 416.9 | 374,697 |  |  |
| 3 | L. Maabaidhoo | 3.1 | Near Public water tanks | 2972 | 15.90% | 77.1 | 388 | 529,279 | Elevated Array | Distribute to 3 LV connection points: (Feeder C-DB-A8), (Feeder D-DB-New 20), (Feeder F -DB-New 21) |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 388.0 | 529,279 |  |  |
| 4 | L. Maamendhoo | 4.1 | Maamendhoo mosque boundary | 1384 | 16.80% | 82.3 | 182.6 | 890,097 | Elevated Array | LV (Feeder B - DB-B3) 171 kW, LV (Feeder B - DB-B4) 11 kW |
|  |  | 4.2 | Boundary of mortuary | 795 | 17.00% | 82.7 | 125.4 |  | Road canopy | LV (Feeder E- DB-E3) |
|  |  | 4.4 | Park (near harbour) | 390 | 17.40% | 81.7 | 59.4 |  | Carport | LV DB- B2 |
|  |  | 4.5 | Commercial plots area (near harbour) | 680 | 16.70% | 81.6 | 129.8 |  | Elevated Array | LV DB- A3 |
|  |  | 4.6 | Road (Near FENAKA power house) | 460 | 16.40% | 80.2 | 54.5 |  | Elevated Array | LV DB- A1 |
|  |  | 4.7 | Road (Near Maamendhoo school) | 528 | 14.60% | 71.1 | 58.3 |  | Road Canopy | LV DB- A5 |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 610.0 | 890,097 |  |  |
| 5 | L. Maavah | 5.1 | Near harbour | 1012.4 | 17.10% | 83 | 148.5 | 659,441 | Elevated Array | LV-DB -C9 |
|  |  | 5.2 | Volley court | 409.5 | 16.90% | 81.9 | 59.4 |  | Elevated Array | Combined and LV connection to power house |
|  |  | 5.3 | Futsal ground | 300 | 16.70% | 81 | 60 |  | Elevated Array |  |
|  |  | 5.4 | Netball court | 312 | 17.20% | 83.1 | 24.2 |  | Elevated Array |  |
|  |  | 5.5 | Near cemetery | 620 | 16.70% | 80.6 | 104 |  | Carport | Combined and LV-DB-I1 |
|  |  | 5.6 | Near cemetery/ Maavashu school | 395 | 16.80% | 81.7 | 75 |  | Road canopy |  |
|  |  | 5.7 | Zuvaanunge Hiya | 800 | 17.10% | 83 | 161 |  | Elevated Array | LV-DB-D3 |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 632.1 | 659,441 |  |  |
| 6 | L. Dhanbidhoo | 6.1 | Farm lands | 1898 | 16.30% | 79 | 259.6 | 369,821 | Elevated array | MV connection with Solar RMU |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 259.6 | 369,821 |  |  |
| Total (MW / MWp) |  |  |  |  |  |  | 2.66 | 3,249,860 |  |  |

Lot 2

| # | Island | Site Ref. | Location | Area (m2) | Helioscope Y1 results |  |  | RFP Indicated Fixed Energy for 1st year (kWh) | Array Structure Type (ref. Part E) | Grid Connection (ref. Part C) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | CUF (Y1) calculated | PR (Y1) (stated) | Capacity (kWp) based on available space |  |  |  |
| 1 | L. Isdhoo | 1.1 | Outdoor gym area | 2435 | 16.80% | 81.2 | 356.4 | 1,0233.4,895 | Carport | MV (with new Solar RMU/SS) |
|  |  | 1.2 | Plot in island South (Near Havihtha) | 1858 | 16.40% | 79.5 | 308 |  | Elevated Array | MV (SS05) |
|  |  | 1.3 | Isdhoo harbour area | 253 | 17.30% | 83.1 | 39.6 |  | Elevated walkways | LV-DB-S5B3 |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 704.0 | 1,023,895 |  |  |
| 2 | L. Kalaidhoo | 2.1 | Near football ground | 3680 | 16.60% | 80.4 | 569.3 | 827,417 | Elevated Array | MV (with new Solar RMU/SS) |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 569.3 | 827,417 |  |  |
| 3 | L. Fonadhoo | 3.1 | Plot Near Barasil Mosque | 1126 | 16.90% | 82.5 | 158.4 | 4,484,156 | Carport | LV- DB-S5B6 or S5C6 |
|  |  | 3.2 | Barasil Stadium towards rowhouse mosque | 1306 | 16.00% | 78.5 | 155.1 |  | Elevated Array | LV- DB-S5A5 |
|  |  | 3.3 | Barasil Stadium | 977 | 14.90% | 72.5 | 192.5 |  | Elevated Array | Combined at LV-SS01 |
|  |  | 3.4 | B143 Dhandu (Section1) | 1159 | 16.70% | 81.7 | 176 |  | Elevated Array |  |
|  |  | 3.5 | B143 Dhandu (Barasil Childrens park) (Section 2) | 1047 | 17% | 83 | 167.2 |  | Elevated Array | LV- DB-S1B1 with Feeder B upgrade |
|  |  | 3.6 | B143 Dhan(Barasil Childrens Park) (Section3) | 458 | 17.10% | 82.99 | 72.6 |  | Elevated walkway | LV- DB-S1B2x3 with Feeder B upgrade |
|  |  | 3.7 | Infront of LAEC school | 1020 | 17.00% | 83 | 167.3 |  | Elevated Array | LV-DB-PHE2 |
|  |  | 3.8 | Roadside pavement (Westwards) (I) | 400 | 15.40% | 74.5 | 63.8 |  | Elevated walkway | Combined & LV connection to PH |
|  |  | 3.9 | Road median (I) | 499 | 16.90% | 83.1 | 82.5 |  | Elevated Array |  |
|  |  | 3.10 | Roadside pavement (Westwards) (II) | 608 | 16.80% | 81.5 | 93.5 |  | Elevated walkway | Combined & LV connection to PH |
|  |  | 3.11 | Road median (II) | 499 | 16.90% | 82.1 | 89.1 |  | Road median |  |
|  |  | 3.12 | Road median (III) | 159 | 17.10% | 82.91 | 26.4 |  | Road median |  |
|  |  | 3.13 | Road median (IV) | 321 | 16.60% | 80.5 | 52.8 |  | Road median |  |
|  |  | 3.14 | Road median (V) | 727 | 16.70% | 81 | 128.7 |  | Road median | LV to SS04 |
|  |  | 3.15 | Roadside pavement (Westwards) (III) | 518 | 14.90% | 72 | 79.2 |  | Elevated walkway | LV-DB-PHA7 |
|  |  | 3.16 | Kurigamu football ground (Section1) | 1092 | 17.00% | 83.1 | 158.4 |  | Elevated walkway | LV-DB-PHA7 |
|  |  |  |  |  |  |  |  |  |  | With feeder upgrade |
|  |  | 3.17 | Kurigamu foorball ground (Section 2) | 164 | 16.90% | 82.7 | 25.3 |  | Elevated array | Combined & LV-DB-S4A5 |
|  |  | 3.18 | Kurigamu football ground (Section 3) | 163 | 16.90% | 82.7 | 30.8 |  | Elevated array |  |
|  |  | 3.19 | Road median (VI) | 984 | 16.20% | 79.4 | 173.3 |  | Road median | Combined & LV-SS04 |
|  |  | 3.20 | Roadside pavement (Westwards) (IV) | 185 | 14.30% | 69.1 | 28.6 |  | Elevated walkway |  |
|  |  | 3.21 | Road median (VII) | 327 | 15.90% | 76.9 | 57.8 |  | Road median | Combined & LV-SS02 |
|  |  | 3.22 | Roadside pavement (Westwards) (V) | 101 | 15.00% | 72.9 | 15.4 |  | Elevated array |  |
|  |  | 3.23 | Roadside pavement (Westwards) (VI) | 95 | 15.10% | 73.2 | 14.3 |  | Elevated walkway |  |
|  |  | 3.24 | Road median (VIII) | 252 | 16.20% | 78.3 | 44.6 |  | Road median | Combined & LV- SS02 |
|  |  | 3.25 | Road median (IX) | 250 | 17.00% | 82.6 | 42.9 |  | Road median |  |
|  |  | 3.26 | Roadside pavement (Westwards) (VII) | 489 | 15.50% | 74.9 | 78.1 |  | Elevated walkway |  |
|  |  | 3.27 | Roadside pavement (Westwards)(VIII) | 1274 | 14.20% | 68.8 | 203.5 |  | Elevated walkway |  |
|  |  | 3.28 | Boundary of outdoor gym | 635 | 17.00% | 82.9 | 93.5 |  | Elevated array | LV to PH |
|  |  | 3.29 | Harbour area I | 1725 | No Helioscope rep |  | 343.8 |  | Elevated array | LV to PH |
|  |  | 3.30 | Link Road Median (Area I) | 1352 | No Helioscope rep |  | 225 |  | Road median | LV-SS05 |
|  |  | 3.31 | Link Road Median (Area II) | 1441 | No Helioscope rep |  | 240 |  | Road median | LV-SS05 |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 3,480.4 | 4,484,156 |  |  |
| 4 | L. Gan | 4.1 | LR Area 1 (Link1.png) | 693 | 15.60% | 76.1 | 123.8 | 5,962,012 | Road median | LV Connection to SS1 transformer with upgrade to 1000 kVA capacity |
|  |  | 4.2 | LR Area 2 (Link 2.png) | 904 | 15.60% | 76.1 | 161.7 |  | Road median |  |
|  |  | 4.3 | LR Area 3 (Link 3.png) | 872 | 14.90% | 72.9 | 155.1 |  | Road median |  |
|  |  | 4.4 | LR Area 4 (Link 4.png) | 171 | 14.50% | 70.7 | 31.4 |  | Road median |  |
|  |  | 4.5 | LR Area 5 (Link 4.png) | 395 | 16.00% | 78.7 | 66 |  | Road median |  |
|  |  | 4.6 | LR Area 6 (Link 5.png) | 806 | 16.10% | 78.7 | 140.3 |  | Road median |  |
|  |  | 4.7 | LR Area 7 (Link 6.png) | 454 | 15.90% | 77.5 | 74.3 |  | Road median |  |
|  |  | 4.8 | LR Area 8 (Link 7.png) | 1004 | 15.80% | 77 | 173.3 |  | Road median |  |
|  |  | 4.9 | LR Area 9 (Link 8.png) | 502 | 15.10% | 73.8 | 97.4 |  | Road median |  |
|  |  | 4.10 | LR Area 10 (Link8.png) | 754 | 17.00% | 82.8 | 133.7 |  | Road median | LV Connection to SS2 with transformer upgrade to 800 kVA capacity |
|  |  | 4.11 | LR Area 11 (Link9.png) | 706 | 16.80% | 82 | 127.1 |  | Road median |  |
|  |  | 4.12 | LR Area 12 (Link 10.png) | 761 | 16.40% | 80 | 135.3 |  | Road median |  |
|  |  | 4.13 | LR Area 13 (Link 10.png) | 161 | 15.30% | 74.6 | 26.4 |  | Road median |  |
|  |  | 4.14 | LR Area 14 (Link 11.png) | 275 | 15.10% | 73.5 | 41.3 |  | Road median |  |
|  |  | 4.15 | LR Area 15 (Link 12.png) | 711 | 16.00% | 78.2 | 120.5 |  | Road median |  |
|  |  | 4.16 | LR Area 16 (Link 13.png) | 653 | 17.00% | 83.1 | 115.5 |  | Road median |  |
|  |  | 4.17 | LR Area 17 (Link 14.png) | 836 | 17.00% | 82.9 | 146.9 |  | Road median |  |
|  |  | 4.18 | LR Area 18 (Link 15.png) | 731 | 16.90% | 82.7 | 128.7 |  | Road median | LV connection to SS4 existing transformer |
|  |  | 4.19 | LR Area 19 (Link 16.png) | 776 | 16.00% | 78.1 | 138.6 |  | Road median |  |
|  |  | 4.20 | LR Area 20 (Link 17.png) | 704 | 15.20% | 74.2 | 125.4 |  | Road median |  |
|  |  | 4.21 | LR Area 21 (Link 18.png) | 1338 | 15.30% | 74.8 | 239.3 |  | Road median | LV Connection to SS5 with transformer upgrade to 1n 800 kVA |
|  |  | 4.22 | LR Area 22 (Link 19.png) | 1268 | 15.20% | 74.2 | 222.8 |  | Road median |  |
|  |  | 4.23 | LR Area 23 (Link 20.png) | 3230 | 15.10% | 73.8 | 289.9 |  | Road median |  |
|  |  | 4.24 | LR Area 24 (Link 22.png) | 1538 | 15.70% | 76.5 | 584.1 |  | Road median | LV Connection to new SS6 (SS6 has an existing 500 kVA Tx) |
|  |  | 4.25 | LR Area 25 (Link 24.png) | 2917 | 15.50% | 75.7 | 275.6 |  | Road median | LV Connection to new SS7 (SS7 to be constructed but can use Tx from SS2) |
|  |  | 4.26 | LR Area 26 (Link 23.png) | 1538 | 15.00% | 73.1 | 515.9 |  | Road median | LV Connection to new SS8 (SS8 to be constructed but can use Tx from SS5) |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 4,390.3 | 5,962,012 |  |  |
| 5 | Lh. Naifaru | 5.1 | License track boundary | 1136 | 16.90% | 82.5 | 216 | 3,576,443 | Elevated array | LV Connection to SS11 |
|  |  | 5.2 | Common Parking area for Housing units | 208 | 16.90% | 82.7 | 40 |  | Elevated walkway | LV connection to SS11 |
|  |  | 5.3 | 100 Housing units – Block A roof | 881.5 | 17.10% | 82.9 | 140.8 |  | Rooftop | LV-DB-11/2-1 With feeder upgrade |
|  |  | 5.4 | 100 Housing units – Block A Parking (I&II) | 270 | 16.70% | 81.6 | 51 |  | Elevated walkway |  |
|  |  | 5.5 | 100 Housing units – Block B roof | 881.5 | 17.10% | 82.9 | 140.8 |  | Rooftop | LV-DB-11/5-1 |
|  |  | 5.6 | 100 Housing units – Block B Parking (I&II) | 270 | 16.90% | 82.7 | 51 |  | Elevated walkway |  |
|  |  | 5.7 | 100 Housing units - Block C roof | 881.5 | 17.10% | 82.9 | 140.8 |  | Rooftop | LV-DB-11/4-2x1 With feeder upgrade |
|  |  | 5.8 | 100 Housing units – Block C Parking (I& II) | 270 | 17.00% | 83 | 51 |  | Elevated walkway |  |
|  |  | 5.9 | Near fire Building Road Median 40.15 | 246 | 17.00% | 83 | 36.3 |  | Elevated array | LV-DB-11/4-3 |
|  |  | 5.10 | 100 Housing units – Block D Roof | 881.5 | 17.10% | 82.9 | 140.8 |  | Rooftop | LVDB 11/1-1x2 |
|  |  | 5.11 | 100 Housing units – Block D Parking (I&II) | 270 | 17.00% | 82.9 | 51 |  | Elevated walkway |  |
|  |  | 5.12 | Parking Space (Jalaludin Magu) (Plot 40.24) | 168 | No helioscope reports |  | 21 |  | Elevated walkway | LV-DB-11/3/7 With feeder upgrades |
|  |  | 5.13 | Road between school and multipurpose building | 693 | 16.70% | 81.2 | 116.6 |  | Elevated Arrays | LV-DB-11/3/7 With feeder upgrades |
|  |  | 5.14 | Parking Space (40.26) (Jalaaluddin Magu) | 168 | No helioscope reports |  | 21 |  | Elevated walkway | LV-DB-11/3/5 With feeder upgrades |
|  |  | 5.15 | Madhrasatul Ifthithaah | 2823 | 17.00% | 82.6 | 410.9 |  | Rooftop | LV Connection to SS10 |
|  |  | 5.16 | Parking Space (Ifthithaahee Magu) Plot( 40.27 -a) | 252 | 17.00% | 83.1 | 36.3 |  | Elevated Arrays | LV-DB-10/1-3 With feeder upgrades |
|  |  | 5.17 | Parking Space (Ifthithaahee Magu) 40.27 -b | 252 | 17.00% | 83.1 | 116.6 |  | Elevated Arrays | LV-DB-10/1-3 With feeder upgrades |
|  |  | 5.18 | Multipurpose building | 800 | 16.90% | 82.6 |  |  | Rooftop | LV-DB-10/1-4 With feeder upgrades |
|  |  | 5.19 | Prking Space (Nursery EcoYouth) (40.38D) | 209 | 17.00% | 83.2 | 33 |  | Elevated Arrays | LV-DB-PH/2-1 |
|  |  | 5.20 | Go-green Park Boundary | 559 | 16.90% | 82.4 | 71 |  | Elevated Arrays | LV-DB-PH/1-1 |
|  |  | 5.21 | Dhanaal | 758 | 17.20% | 82.7 | 80.9 |  | Rooftop | Building LV Panel |
|  |  | 5.22 | Tiny Park | 411 | 17.00% | 82.9 | 145.8 |  | Elevated walkway | LV Side of SS-12 |
|  |  | 5.23 | Rahvehige (Residential house for visistors) | 132 | 17.10% | 82.7 | 15 |  | Rooftop | LV-DB-13/4-2 as per map label or LV-DB-13/6-2 as per SLD naming |
|  |  | 5.24 | Community centre | 160 | 17.10% | 82.3 | 17.6 |  | Rooftop | LV side SS13 |
|  |  | 5.25 | Harbour Area | 1397 | No helioscope reports |  | 349 |  | Elevated array | LV Side SS13 |
|  |  | 5.26 | Atoll council building | 330 | No helioscope reports |  | 40 |  | Rooftop | LV DB - 13/3-9 |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 2,534 | 3,576,443 |  |  |
| 6 | Ga. Villingili | 6.1 | Infront of Wamco | 440 | 16.90% | 82.9 | 70 | 2,473,868 | Elevated Array | LV-DB- S3A4 |
|  |  | 6.2 | Inside plot for planned football stadium | 2197 | 16.70% | 82.2 | 374 |  | Elevated Array | LV – SS3 with existing transformer upgrade from 315 kVA unit to 800 kVA |
|  |  | 6.3 | Paking for housing units | 359 | 16.40% | 80.6 | 66 |  | Elevated Array | LV-DB- S3B1x1 |
|  |  | 6.4 | Northern housing Block West side | 325.5 | 16.90% | 82.6 | 79 |  | Elevated walkway | LV-DB- S3B1 |
|  |  | 6.5 | Northern housing Block East side | 217 | 16.40% | 80.4 | 69 |  | Elevated walkway | LV-DB- S3B1x1 |
|  |  | 6.6 | Southern Housing Block West | 279 | No helioscope reports |  | 67.7 |  | Elevated walkway | LV-SS03 |
|  |  | 6.7 | Southern Housing Block East | 186 | No helioscope reports |  | 59.1 |  | Elevated walkway | LV-S3C2x2 |
|  |  | 6.8 | Near Hospital (Parking) | 854 | No helioscope reports |  | 132 |  | Carport | LV-SS06 |
|  |  | 6.9 | Mini green zone | 52.8 | 16.90% | 83 | 8 |  | Elevated Array | LV-DB- S3D5 |
|  |  | 6.10 | Green zone between residential blocks | 803 | 17.00% | 83.1 | 132 |  | Elevated Array | LV-SS2 |
|  |  | 6.11 | Parking Zone | 644 | 16.70% | 81.9 | 92 |  | Elevated Array | LV-SS4 with transformer upgrade to 800 kVA |
|  |  | 6.12 | Designated greenzones (I) | 803 | 16.70% | 82.1 | 132 |  | Elevated Array | LV ( SS4- DB - C4) |
|  |  | 6.13 | Designated green zones (II) | 1124 | 17.00% | 83.1 | 158 |  | Elevated Array | LV-SS4 |
|  |  | 6.14 | Designated green zones (III) | 968 | 16.90% | 82.9 | 149 |  | Elevated Array | LV-SS4 |
|  |  | 6.15 | Villingili gate (I) | 520 | 16.20% | 79.4 | 84 |  | Elevated Array | LV-SS4 |
|  |  | 6.16 | Villingili gate (II) | 520 | 15.40% | 75.7 | 76 |  | Elevated Array | LV-SS4 |
|  |  | 6.17 | Parking zone | 859 | 16.30% | 79.9 | 132 |  | Elevated Array | LV (SS4- DB-D5) |
|  |  | 6.18 | Entrance of Wetland Park | 228 | 17.00% | 82.7 | 36 |  | Elevated Array | LV (SS1- DB-A3x2) |
|  |  | 6.19 | Southern side of Wet lands | 1400 | No helioscope reports |  | 220 |  | Elevated Array | LV- Connect to New Powerhouse |
|  |  | 6.20 | Near Harbour | 659 | No helioscope reports |  | 109 |  | Elevated walkway | LV-DB-S2A5 |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 2,244.8 | 2,473,868 |  |  |
| 7 | Sh. Funadhoo | 7.1 | Area 1 – Airport North | 3621 | 17.40% | 82.5 | 561 | 1,862,274 | Elevated Array | MV-Solar RMU |
|  |  | 7.2 | Area 2 – Airport South | 3591 | 17.30% | 82 | 531.3 |  | Elevated Array | MV-Solar RMU |
|  |  | 7.3 | Area 3 – Airport East | 278 | 17.40% | 82.3 | 42.9 |  | Elevated Array | MV-Solar RMU |
|  |  | 7.4 | Area 4 – Harbour section 1 | 185 | 17.20% | 81.5 | 28.6 |  | Elevated Array | F6: LV DB-23 |
|  |  | 7.5 | Area 5 – Harbour section 2 | 185 | 17.20% | 81.5 | 28.6 |  | Elevated Array | F6: LV DB-29 |
|  |  | 7.6 | Area 6 – Harbur section 3 | 185 | 17.20% | 81.5 | 28.6 |  | Elevated Array | F6: LV DB-31 |
|  |  | 7.7 | Area 7 – Harbur section 4 | 185 | 17.20% | 81.5 | 28.6 |  | Elevated Array | F1: LV DB-38 |
|  |  | Total Estimated (kWp) & capacity of connection point & feeders |  |  |  |  | 1,249.6 | 1,862,274 |  |  |
| Total (MW / MWp) LOT -2 |  |  |  |  |  |  | 15.17 | 20,210,065 |  |  |

Detailed site-specific data is available in the online Data Room, see section B.2.1,

III

Disclaimer: Although care has been taken to ensure the accuracy, completeness and reliability of the information provided above, GoM assumes no responsibility thereof. The user of the information agrees that the information is subject to change without notice. MEE assumes no responsibility for the consequences of use of such information, nor for any infringement of third-party intellectual property rights which may result from its use. In no event shall GoM be liable for any direct, indirect, special or incidental damage resulting from, arising out of or in connection with the use of the information. Therefore, each bidder is requested to conduct individual assessment of sites separately. All of the above sites have also been mapped on Google Earth and the same has been provided as additional information. Please note the mapping is only for illustrative purposes and not for measurement of area. Bidders are requested to undertake their own assessment.

  - Special Site considerations

The level of preparatory and construction works is site specific, and the winning Bidder will be required to carry out all the required activities in accordance to the standards and guidelines as prescribed. This section following gives a summary of some special consideration that have to be considered based on nature of some sites.

In general, it is the Bidders’ responsibility, prior to bidding, to assess and verify the level of effort that will be required for each site in order to construct the plants in the respective sites prior to bidding, based on the provided information, and any site visits that the Bidder may arrange themselves at their own cost. Furthermore, for the winning Bidder, prior to construction, any detailed designs will need to be done based on their own assessments prior to finalization of any designs.

Following are some of the key considerations depending on the nature of the available sites.

    - Material Site Clearance and Preparatory works

While general site clearance preparatory works are prescribed in in E.4.4. Site Clearance, the level of effort is anticipated to be minimal. Majority of the installations are in levelled areas with settled soil. However, surveys and investigations should be done for all sites and level of site clearing, grubbing, levelling and compaction works specific to each site determined to make the site ready to support the PV superstructure and other intended functionalities of the site prescribed by site owners (vehicle parking, conversions to parks boulevard spaces etc). Bidders can refer to the Environmental and Social screening reports for further details on existing conditions of sites in terms of vegetation and any other obstructions.

    - Vegetation Clearances

Significant vegetation clearances may be required on some of the sites and should be done in accordance with the environmental requirements. Any neighbouring trees that are to be retained and not interfering with the PV array structures shall be protected from damage. Preference should be given to translocate the trees to an alternative location where it is practical. If any of the removed/translocated trees are owned by an individual, monetary compensation is to be provided for the owners. Publicly owned vegetation is found in sites of L. Maabaidhoo, L. Isdhoo, L. Kalaidhoo, L. Dhanbidhoo and L. Fonadhoo. Bidders can refer to the Environmental Screening reports provided in the data room for more details on environment condition of these sites and indicative comp Data sensation values.

    - Road based PV installations

PV installation on roads, specially the Laamu link road covering L. Fonadhoo and L. Gan will require special considerations in design and management of construction works as this is based on a link road subjected to continuous traffic, with support structures restricted to the 2m width road median. Cables for the existing street lighting is likely routed within this zone and precautionary measures shall be followed in doing any excavation works. Routing of the interconnection cables for the PV arrays need to be planned to utilize the existing cable crossings for the asphalt road. Addition to the link road there are a number of PV installation sites on other islands as well that require PV installations along full width of road sections. Sufficient clearance height for the vehicles as detailed in E.2. Array structure specific requirements shall be maintained and the road way widths need to be clear from the support columns, i.e. all support columns are to be restricted to the sides of the road. Also, when fixing support columns adjacent to existing boundary walls precautionary measures are to be taken to prevent damage to third party property. If any damages are caused project developer shall undertake the repair works at their own cost.

    - Considerations for aesthetics

Depending on the location of the PV array structure, aesthetics should be considered for design. Varied designs to cater for end uses such as vehicle parking, public assembly areas, tourism attraction points such as beach areas, wet land areas etc is expected.  Reference concepts of array structures are proposed in E.3. Diagrams of typical array structures and representative conceptual designs and E.2. Array structure specific requirements.  Further consultations with space owners should be undertaken by winning contractors prior to detailed structural designs to fine tune the concepts to cater for specific end uses, but within the design constraints set in the initial specification (such as the structure height, column spacing etc). Also, if required by site owners' developer shall allow low growing vegetations to be accommodated beneath the PV structures and other retro fitments needed to enhance the usability of the site.

It is also recommended for the solar PV developer to take in to consideration these sorts of value-added amenities and upgrades for the sites and deliver such as part of the CSR activities under the community engagement plan required for the project. This can include providing benches and bike locking facilities for areas such as parks, harbours and school proximity sites, paving the PV installation areas specially areas designated for parking etc.

    - Airport restrictions & glare mitigation

In general, there are more restrictions in design in airport areas or nearby areas due to obstacle height restrictions in flight paths and also due to risks of glare, such as the PV sites in Sh. Funadhoo. The orientations of tilts in these cases will be restricted as per Array structure specific requirements are specified in E.2 Array structure specific requirements and glare analysis reports are shared for reference. It will be the responsibility of the winning bidder to do their own analysis and demonstrate the requirement during the construction stages.

At a minimal, specifics of sites are detailed out in Section E.2 Array structure specific requirements and E.3. Diagrams of typical array structures and representative conceptual designs, along with the Data Room would need to be read together.

    - Interconnection cabling installations

All sites will require underground cabling. Interconnection cables from solar PV site to the grid connection point must be routed along roadside ways. There can be other existing concealed and underground services (water, sewer, electricity and communication lines) along the routes and all measures should be taken to prevent any damages to such infrastructure lines. Consultations with relevant stakeholders and site mapping exercises should be taken prior to any excavations. Where available, duct system can be used, but in restricted cases such as in airports, boring machines can be used to install cables.

    - Safety Measures

In public areas, safety considerations must be a priority. All measures should be taken to prevent any injury or harm to the public, without compromising the normal or intended use of the area and should be compliant with all required regulations, standards and guidelines.

    - Restrictive access

All installations, particularly in areas with where solar PV canopy areas are access open to the public, should ensure restricted access measures to restrict public access to owners’ equipment such as transformers and inverters and protect from vandalism.

  - Special Site considerations

    - Specific Requirements

      - L. Hithadhoo

- The sites for PV installation from L. Hithadhoo include land areas from the west of the Harbour, walkway between cemetery area and cemetery mosque, boundary of parks near Harbour area and road in front of Hithadhoo school. These are all public open spaces and with elevated solar PV arrays the usability of the sites is expected to be enhanced.

- In general, the island community will be utilizing the structures for value added activities of the site, which include various economic, social and recreational activities such as operation of market stalls, vehicle parking, assembly space for community functions etc.

- Specific anticipated uses of the sites include vehicle parking and operation of mini market stalls and food trucks for the harbour west area, recreational activities for harbour facing south plot and community park, shade providing road canopy for pedestrians and visitors to the school for the school front arrays and shaded walkway and vehicle parking for the cemetery strip.

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design to ensure desired end uses specific to each site are met.

- Overall below specified requirements and constraints shall be ensured:

- Constraints to array structure

  - 6m clearance buffer zone from harbour quay wall to structure footings for the Harbour west arrays.

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite.

  - In general, the following applies.

    - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of roadways.

    - Clear height of minimum 3.5 m for elevated array sites that require clear views such as harbour areas, beaches and tourism area arrays.

    - Clear height of minimum 3m for all other elevated arrays, walkways and carports.

    - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list))

    - PV support columns to be restricted to the sides of the road for full width roadway arrays or that extending to parts of the road.

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under array.

  - Park benches to be provided for the park location and Hithadhoo School walkway area. During design stage PV developer can consult with the site owner to work out the details such as quantity and type of benching optimal for individual sites.

- Interconnection route constraints:

  - Feeder upgrades will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - L. Kunahandhoo

- There are 4 different PV installation sites from L. Kunahandhoo which include land areas located north of the island office, in front of the Kunahandhoo school and west and south boundaries of Kunahandhoo Hukuru Miski (Friday Mosque).

- The area near Kunahandhoo school spans laterally across full road width and extends to non-developed areas along its length. Hukuru Miski west area also covers the full span of road. Hukuru Miski south area and island office north area are empty pockets of land spaces.

- The area North to the island office is in the coastal zone of the island at about 30m from shoreline at closest point.

- All these sites are accessible and open to public and installation of shade providing elevated arrays will enhance the usability of these land spaces.

- The area near Kunahandhoo school is anticipated to be used as an assembly space during school pick up’s and drop off’s hours and is also an open road and PV arrays shall be designed with no constraint for continuous vehicle flow.

- Hukuru Miski south and west bound areas extend to roadways and PV arrays can serve as shade providing canopies for pedestrians and can also be used as a space for congregational prayers such as Friday prayer or Eid prayers and to hold such other community mass events.

- The space north to island office is likely to be adopted for parking of large vehicles such as cars and lorries.

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Constraints to array structure

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite.

  - In general, the following applies.

    - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of roadways.

    - Clear height of minimum 3.5 m for sites that require clear views such as harbour areas, beaches and tourism area arrays.

    - Clear height of minimum 3m for all other elevated arrays, walkways and carports.

    - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list))

    - PV support columns to be restricted to the sides of the road for full width roadway arrays or that extending to parts of the road.

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Park benches to be provided in one or two locations. During design stage PV developer can consult with the site owner to work out the details such as quantity, location and type of benching optimal for individual sites.

- Interconnection route constraints:

  - Feeder upgrades will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

        - L.Maabaidhoo

- The PV installation site for Maabaidhoo is South of the island Harbour area and also borders the costal side of the island with about 25m from the island shoreline. The area is also in front of Maabaidhoo school.

- The location is open and accessible to the public and elevated shades from PV installation is expected to enhance this public open space. Island community will be using the site for various economic, social and recreational purposes such as vehicle parking, assembly space for community functions, school children and parents will use the area for shade and is also an ideal beach viewpoint.

- This site has publicly owned coconut palms and compensation should be paid. Site owner will facilitate the process.

- Since this is in an idyllic beach area sufficient clear height is to be accommodated to avoid view obstructions. Also, the landowners have the option of enhancing the site by planting low growing coastal vegetation and other such retrofits needed to have a blended landscape.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken into consideration in detailed design as to ensure desired end uses specific to each site are met.

- Overall, below specified requirements and constraints shall be ensured:

- Constraints to array structure

  - Minimum clear height of 3.5m throughout.

  - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list))

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under array.

  - Park benches to be provided. During design stage PV developer can consult with the site owner to work out the details such as quantity and type of benching optimal for individual sites.

  - If required developer shall allow site owners to do planting of low growing vegetation and landscaping of the area

- Interconnection route constraints:

  - Feeder upgrades will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection points along the sides of the existing roads and should not cross to any public or private lands.

      - L. Maamendhoo

- The PV installation locations for L. Maamendhoo include perimetric areas of L. Maamendhoo mosque and extending to road, area in front of the island harbour and bordering the children's park, area surrounding the boundary of mortuary, area covering road near Maamendhoo School and extending about 3m into the school boundaries and an area near the industrial zone for the island.

- In general, all these spaces are public open areas and the shade providing elevated arrays is expected to enhance the usability of the sites.

- The PV shades are expected to fulfil multiple functions such as vehicle parking, shaded walkways and can also be used as a space for congregational prayers such as Friday prayer or Eid prayers and to hold such other community mass events.

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Constraints to array structure

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite.

  - In general, the following applies:

    - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of road ways.

    - Clear height of minimum 3.5 m for sites that require clear views such as harbour areas, beaches and tourism area arrays.

    - Clear height of minimum 3m for all other elevated arrays, elevated walkways and carports.

  - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list))

    - PV support columns to be restricted to the sides of the road for full width road way arrays or that extending to parts of the road.

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Park benches to be provided for school area and the park area. During design stage PV developer can consult with the site owner to work out the details such as quantity and type of benching optimal for individual sites.

  - For the installations in the cemetery ensure that the footings of the PV are on the road side and outside the burial area.

- Interconnection route constraints:

  - Feeder upgrades will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - L. Maavah

- The PV installation areas designated from Maavah is distributed broadly in to three regions of the island. This includes the island Harbour area, Sports complex area and that surrounding the school and cemetery.

- All these land areas are open and accessible to the general public and similar to other islands it is expected that the setup of shade providing elevated structures will enhance the usability of these land spaces.

- The area on the sides of harbour will be used as a vehicle parking area and also for commercial activities such as operation of road side food stalls. The PV arrays near the sports field namely volley court and netball court areas and futsal ground areas will act as shade providing walk ways and also can be used by spectators during sports events.

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design to ensure desired end uses specific to each site are met.

- Constraints to array structure

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite.

  - In general, the following applies:

    - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of road ways.

    - Clear height of minimum 3.5 m for sites that require clear views such as harbour areas, beaches and tourism area arrays.

    - Clear height of minimum 3m for all other elevated arrays, elevated walkways and carports.

    - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list)).

    - PV support columns to be restricted to the sides of the road for full width road way arrays or that extending to parts of the road.

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Benches to be provided for the Maavah school location. During design stage PV developer can consult with the site owner to work out the details such as quantity and type of benching optimal for individual sites.

- Interconnection route constraints:

  - Feeder upgrades will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - L. Isdhoo

- There are three locations for PV installation from L. Isdhoo which include an area near the island harbour and two other areas located to the West and the East of the island as shown in the below maps.

- All these locations are open and accessible to the public and the elevated arrays is expected to enhance the usability of the sites.

- The PV arrays near the island harbour will be used for commercial activities such as operation of road side food stalls and parking of two-wheeler vehicles.

- The outdoor gym area is an area near the agricultural zone of the island and adjacent to the futsal ground. The PV arrays for the site is expected to be used for vehicle parking and recreational activities.

- The other location is a close to an agricultural zone and also near a historic site for the island known as Havihtha which is a pre-Islamic Buddhist temple complex. The elevated arrays for this location can also be used for various recreational and economic purposes including food/market stalls.

- This second site has publicly owned coconut palms and compensation should be paid. Site owner will facilitate the process

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Constraints to array structure

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite.

  - In general, the following applies:

    - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of road ways.

    - Clear height of minimum 3.5 m for elevated array sites that require clear views such as harbour areas, beaches and tourism area arrays.

    - Clear height of minimum 3m for all other elevated arrays, elevated walkways and carports.

    - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list)).

    - PV support columns to be restricted to the sides of the road for full width road way arrays or that extending to parts of the road

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Park benches to be provided in one or two locations. During design stage PV developer can consult with the site owner to work out the details such as quantity, location and type of benching optimal for individual sites.

- Transformer and interconnection route constraints:

  - Solar RMU’s and transformers for MV connection to be located beneath solar arrays or within allowed foot print. MV interconnection cables and fibre comms cables will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - L. Kalaidhoo

- The PV installation area identified from L. Kalaidhoo is in front of Kalaidhoo pre-school and next to the football ground.

- This is also an open and accessible area to the island public. The elevated and shade providing PV arrays will be used as an assembly area for visitors to the school and will also be used for other recreational activities and vehicle parking.

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- As this site has few publicly owned coconut palms, compensation should be paid to the coconut palms present in this site. Site owner will facilitate the process.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design to ensure desired end uses specific to each site are met.

- Overall, below specified requirements and constraints shall be ensured:

  - Minimum clearance height of 3m throughout.

  - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list)).

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Park benches to be provided. During design stage PV developer can consult with the site owner to work out the details such as quantity and type of benching optimal for individual sites.

- Transformer and interconnection route constraints:

  - Solar RMU’s and transformers for MV connection to be located beneath solar arrays or within allowed foot print. MV interconnection cables and fibre comms cables will be by others. LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - L. Dhanbidhoo

- The PV installation area for Dhanbidhoo is located in the agricultural zone of the island though this designated plot is not anymore used for farming activities.

- This is also a public open space and with the installation of shade providing PV canopies, the area will be used by the island community for different economic, social and recreational activities. Specific examples of such functional usages include operation of farmers market stalls, laydown areas for farming community, vehicle parking etc.

- This site has publicly owned coconut palms and compensation should be paid. Site owner will facilitate the process.

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Overall, below specified requirements and constraints shall be ensured:

- Constraints to array structure

  - Minimum clear height of 3m throughout.

  - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list)).

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under array.

  - Park benches to be provided. During design stage PV developer can consult with the site owner to work out the details such as quantity and type of benching optimal for individual sites.

- Transformer and interconnection route constraints:

  - Solar RMU and transformer for MV connection to be located beneath solar arrays or within allowed footprint. MV interconnection cables and fibre comms cables will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - L. Fonadhoo

- The areas identified for PV installation from L. Fonadhoo can be seen as three clusters of sites based on site proximities. The first cluster is sites in and around the northern most village (Barasil) of the island, and the second and third group respectively are areas in the harbour region and on sides and median of Laamu link road.

- From the PV locations in Barasil shown in the below map, the area behind Barasil mosque is currently an open and empty land. The elevated PV installation structures is aimed to enhance the utilization of the site as a shade for public gatherings, vehicle parking etc and is to be designed to minimize view obstruction. The rest of the installations will serve as shades alongside the sports ground where spectators gather to cheer on during sports events and other recreational events of the sort.

- The harbour area arrays include installations in three locations as shown in the below map.

- The first set of sites is directly to the front and facing the harbour and this area shall also be designed to minimize view obstructions. Similar to other harbour facing sites the desired uses of elevated PV structures for the site include vehicle parking and running mini market stalls and food trucks. Support columns shall be planned in a manner not to obstruct vehicles approaching from the inner roads to the harbour area.

- The second set of sites is southwest of the harbour and in front of the Laamu Atoll Education centre which is the assembly point for school pickup’s and drop offs.

- The third set of sites border the perimeter of the outdoor gym and here also the PV structures will serve as shades which the site owner can enhance with provision of benches and other amenities fit to the site.

- The third group of PV sites are located on the sidewalks as well as median of Laamu link road and is shown in maps below. Site 27 (third map) is towards the South West end of the island and is currently an unpaved sand road.

- The side walk arrays will serve as canopied walkways for pedestrians and site owners can enhance the visibility of the road by planting vines and others low growing plants beneath the PV array structures. The structure design shall be aesthetically pleasing.

- The road median arrays extend about one meter to the road area from both sides and thus the structure heights are required to give sufficient height clearance for vehicles. The design is expected to be duo pitch or T-frame double type carport structures to allow maximum height to the road overlapping areas.

- There is a distinct group of arrays within the below proximal group of arrays categorized from link road. These arrays are located around the Kurigamu football ground. Similar to other PV structures near playground areas the PV canopies will serve as shades alongside the sports ground where spectators gather to cheer on during sports events and other recreational events of the sort and the 6m wide span area parallel to the link road can also be used for other purposes such as parking.

- Site owners always have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Constraints to array structure

  - 6m clearance buffer zone from harbour quay wall to structure footings for the Harbour west arrays.

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite.

  - In general, the following applies.

    - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of road ways.

    - Clear height of minimum 3.5 m for elevated array sites that require clear views such as harbour areas, beaches and tourism area arrays.

    - Clear height of minimum 3m for all other elevated arrays, elevated walkways and carports.

    - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list)).

    - PV support columns to be restricted to the sides of the road for full width road way arrays or that extending to parts of the road.

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Benches to be provided for the area in front of Laamu Atoll Education Centre. During design stage PV developer can consult with the site owner to work out the details such as quantity and type of benching optimal for individual sites.

- Interconnection route constraints:

  - LV feeder upgrades to follow existing routes. LV Interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - L. Gan

- PV installation for L. Gan will be along about 6.7 km of the link road starting from the Northern tip of L. Gan and crossing through the residential districts and extending to agricultural areas. PV arrays are planned for the median section of the road which is about 1.5m in width. The arrays will cover a span of 4m thus having an overhang of about 1.25m to the road from each side. The layout map of installation route and detailed close-up views are illustrated in below maps. For details of individual sections refer the site maps in data room.

- The median area is the green verge for the road and site owners will plant low growing vegetation in the area.

- Further there are existing street lighting cables in this verge and developer shall take all precautionary measures to avoid damages to such.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Constraints to array structure

  - Minimum height of 4.5m at the elevated edge (road side)

  - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list))

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Roadway median array locations coincide with existing streetlighting (2 x 75W LED per pole), and any new array structures may obstruct illumination which is unacceptable. PV developer may consider several alternatives to entirely mitigate this, for example: (a) spacing arrays to entirely avoid affecting streetlights, (b) elevating arrays to entirely avoid affecting streetlights, c) supplying and installing new compliant streetlights of at least equal illumination intensity and angle beneath array structure.  All designs to be approved prior to installation.

- Transformer and interconnection route constraints:

Any existing distribution transformer substation marked for upgrading shall be installed on same footprint and existing substation building shall be re-used. Transformer which has been replaced due to upgrade may be re-used in new substation. Where completely new transformer substation is required, the form shall be either fenced compact substation, or else conventional transformer with RMU’s within new standard substation building, within the allowed array foot print.  MV interconnection cables shall be by contractor, no fibre communication required back to powerhouse.  LV feeder upgrades to follow existing routes. LV Interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - Lh. Naifaru

- There are multiple and dispersed locations in Naifaru identified for PV installation. In contrast to sites from other islands there are multiple roof top sites too. The roof top PV installation includes the buildings; Four blocks of 100 housing units, Madhrasathul Ifthithaah, Multipurpose building, Dhanaal, Atoll Council and Rahvehige (Community home used by council for guest accommodations).

- Land based PV locations are mainly designated parking locations which include areas near island harbour, sections of Ifthithaahee Magu (road), Jalalludin Magu (road) and areas to the east and west sides of the social housing flat areas. The elevated arrays on these sites will serve as shaded walkways as well as spaces for parking of two wheelers and four wheelers depending on site area.

- Also, there is one location that covers the full span of the road which is the road section between the multipurpose building and Ifthithaah school. The shade providing arrays will be used as a gathering point for visitors to the school during school pickup and drop off hours and during other times the road will be open to vehicular traffic.

- Additionally, there are perimetric areas from children’s parks, outdoor gym areas and license parks namely go green park, tiny park and license track area. The shade providing space will be used by people accessing the sites/parks and can be retrofitted to serve recreational functions.

- Location maps of the multiple sites are shown below:

- Site owners have the option of retro fitting and developing the area licensed for PV installation as they desire but, in a manner, not to obstruct the operation and maintenance of the facility. Examples of such developments include adding park benches and other recreational amenities appropriate to the location, setting up of market stalls, paving of the area footprint / planting of low growing vegetation etc.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Constraints to array structure

  - 6m clearance buffer zone from harbour quay wall to structure footings for the Harbour area arrays.

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite. In general, the following applies:

  - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of road ways (includes the road median arrays).

  - Clear height of minimum 3.5 m for sites that require clear views such as harbour areas, beaches and tourism area arrays.

  - Clear height of minimum 3m for all other elevated arrays, elevated walkways and carports.

  - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list)).

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Park benches to be provided in one or two locations. During design stage PV developer can consult with the site owner to work out the details such as quantity, location and type of benching optimal for individual sites.

- Interconnection route constraints:

  - LV feeder upgrades to follow existing routes. LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - GA. Villingili

- There are multiple PV installation locations identified from GA. Villingili mostly located in the reclaimed and undeveloped lands. The allocated areas are finalized in consideration of future land uses and land use development plan.

- One of the largest areas is located close to Integrated Waste Management Centre of the island and is also close to the coastal area with about 35m at the closest point from the island shore-line. The elevated shed can be used for parking of large vehicles and also can be used to support other recreational and social functions hosted by the island community.

- There is also a group of sites around the social housing unit areas. The PV arrays can serve as elevated walkways and parking sheds for the housing tenants as well as the general public.

- There are also sections located near the outer periphery of the island notably known as the eye of Villingili. In addition, there are other multiple areas from the reclaimed land areas located mostly in the central and northern sides of the island. The elevated arrays can be used for vehicle parking and hosting social functions and recreational activities.

- Another notable site is from the area near the wetlands of the islands. This is expected to be a tourism spot and the PV arrays can be used in a manner to enhance recreational and tourism related activities in the area. Visitors to the area can use the shade providing arrays as a waiting area to observe and enjoy the surrounding scenery.

- There is also an area located from the island harbour area and PV structure will serve as a shade providing canopy.

- Constraints to array structure

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite. In general, the following applies. In general, the following applies:

  - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of road ways (includes the road median arrays).

  - Clear height of minimum 3.5 m for sites that require clear views such as harbour areas, beaches and tourism area arrays.

  - Clear height of minimum 3m for all other elevated arrays, elevated walkways and carports.

  - Column spacing between 3-6m (6m requirement to be met for sites where specified (in data room site list)).

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under each array.

  - Park benches to be provided in one or two locations. During design stage PV developer can consult with the site owner to work out the details such as quantity, location and type of benching optimal for individual sites.

- Transformer and interconnection route constraints:

  - Any existing distribution transformer substation marked for upgrading shall be installed on same footprint and existing substation building shall be re-used. Transformer which has been replaced due to upgrade may be re-used in new substation. Where completely new transformer substation is required, the form shall be either fenced compact substation, or else conventional transformer with RMU’s within new standard substation building, located within the allowed array foot print.

  - LV feeder upgrades to follow existing routes. LV Interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

      - Sh. Funadhoo

- PV installations in Sh. Funadhoo is planned for the island harbour area and outside the boundary fence of airport.

- All PV arrays proximate to Funadhoo Airport shall be oriented to comply with glare mitigation affecting aircraft operations.

- PV arrays near airport boundary fence is expected to be used for vehicle parking.

- PV arrays near the harbour is about 9m from the Harbour wall. The elevated arrays will serve as shade providing walkways and also the space can be used be for vehicle parking and other commercial uses such as operation of mini-market stalls.

- Prior to detailed design the winning contractor is required to submit the PV installation concepts for the approval of site owners. Comments for minor design changes from site owners shall be taken in to consideration in detailed design as to ensure desired end uses specific to each site are met.

- Overall, below specified requirements and constraints shall be ensured:

- Constraints to array structure

  - Refer to Data room - Site Requirements table for design constraints and specific requirement for particular subsite. In general, the following applies. In general, the following applies:

  - In general, the following applies:

    - Clear height of minimum 4.5 m for arrays covering full width or extending to parts of road ways (includes the road median arrays).

    - Clear height of minimum 3.5 m for sites that require clear views such as harbour areas, beaches and tourism area arrays.

    - Clear height of minimum 3m for all other elevated arrays, elevated walkways and carports.

    - Column spacing of minimum 6m for all sites.

  - Refer section E.3. Diagrams of typical array structures and representative conceptual designs, for model concepts

- Other

  - Night time lighting to be provided under array.

  - Park benches to be provided in one or two locations. During design stage PV developer can consult with the site owner to work out the details such as quantity, location and type of benching optimal for individual sites.

- Transformer and interconnection route constraints:

  - Solar RMU and transformer for MV connections to be located beneath solar arrays or within allowed foot print. MV interconnection cables and fibre comms cables will be by others.  LV interconnection cables shall be routed from the solar farm areas to the grid connection point along the sides of the existing roads and should not cross to any public or private lands.

END

- Solar Farm Connection Requirements

Part D comprises of guidance document titled Maldives: Solar Farm Connection Requirements.

- D.1. Introduction

- D.2. Solar Farm configurations

- D.3. 11kV connections

- D.4. LV connections

- D.5. Grid support requirements (PV inverters)

- D.6. Communication interface

- D.7. Weather station

- D.8. Standards

- D.9.Typcial SCADA IO list

- D.10. Network extensions

- D.11 Description of the interconnection and network extension works

It is the responsibility of the successful Bidder (herein referred to as the “Seller” as the term is defined in the PPA) to ensure power quality at the point of connection remains within the specified ranges, and that the PV system provides active network support to maintain these ranges.   The due diligence into the quality of the inter-connection, in order that the PV power can be evacuated without encountering out-of-range power quality conditions, is the responsibility of the Seller. The Seller is responsible for ensuring the installation quality and performance of inter-connection.

  - Introduction

Currently the network points of connection, and associated fault levels and voltage constraints have not been finalised. This specification is intended to provide for likely ranges and possible contingency options in respect of these matters, which can be finalised during detailed design by the Seller. This document is limited in scope to specifying the minimum technical requirements from the electrical and communications interface between the solar farm LV inverter outputs up to the 11kV connection point/s within the new system.

This document does not address connection requirements between the solar farm and the final chosen network point of connection. This document does not address requirements for the DC side of the solar farm, nor does it address civil, structural, installation, existing grid reinforcements, environmental or related requirements.

  - Solar Farm connection configuration

    - Connection voltage

Solar Farm point of connection voltage will be dictated by:

  - availability of point of connection, and

  - proposed load size.

As noted in Section Error! Reference source not found. the available points of connection are yet to be finalised, however it should be noted the electrical systems of the Maldives Islands consist of 11 kV loop distribution backbone networks and 400 V radial feeders to customers, limiting the connection options.

The capacity of the 400 V systems requires that Solar Plant loads can only be applied as indicated in the table below.

Table 7: Solar PV connection capacity limits

| Based Output of PV System (kW) | Breaker Capacity (A) | Interconnection Voltage |
| --- | --- | --- |
| <7 | 40A | LV (1P, 230V) |
| 7-35 | 63A | LV (3P, 400V) |
| 35-175 | 315A | LV (3P, 400V) |
| 175> | - | MV (3P, 11kV) |

In addition, reliability of supply requirements will apply to each site on a case by case basis.

  - 11kV connections

Each 11-kV connection will be provided with a ground based outdoor ring main unit (RMU) consisting of two isolators, feeder circuit breaker earth switch, metering, protection and control interfaces.

Solar PV generation will be converted from DC to LV AC, at voltage selectable by the Seller appropriate to the selected inverter type (but not more than 1,000 V). As Maldives commonly operates at 400 V for LV systems, 400 V should be used where it is an option without cost impact. LV feeders will feed to a single step up transformer sized to accommodate maximum generation output, and any harmonic loads.

Refer to Figure 5 below for required arrangement of equipment.

    - Physical limits

The scope of work of the Seller ends at the terminals of the network size switches of the RMU.

      - Connection to the grid

Connection to the grid will be the responsibility of the Employer. The Seller is expected to cooperate with others to enable completion of the electrical and communications connections. Two arrangements, loop feeders and radial feeders, are considered, refer Figure 6:

Power plant controller

Figure 5: Required 11kV connection (solar PV plant scope)

PV plant as per Figure 5

Existing 11kV feeder

Upgraded distribution substation

Existing 11kV feeder

PV plant as per Figure 5                    (1 spare isolator)

CB

Figure 6: Two options for connection to the grid (to be performed by others)

    - Environmental conditions

The Solar power station, including all supporting infrastructure, shall be designed and constructed to operate normally under the environmental conditions summarised in table below.

.

Table 8: Environmental conditions

| Criteria | Condition |
| --- | --- |
| Minimum Ambient Temperature (oC) | 17.2 oC |
| Maximum Ambient Temperature (oC) | 40 oC |
| Humidity (%) | 79% |
| Wind Speed (m/s) | Up to 35m/s or 120km/h |
| Pollution Level (AS/NZS 2312) | Category D |
| Altitude (m) | 1.5 mADH |
| Corrosion | Compliance with ISO-12944, C5M |

    - Switchgear

All switchgear must be selected to ensure it is reliable, compatible with subsystems and equivalent products, readily serviced, and that spare parts are readily available. To this end, all components must be selected from suppliers continuously servicing utilities in major international markets for a minimum of 10 years. Specific products or their product chains must have been offered for at least 5 years, and manufacturers must offer a commitment to support the product for a minimum of 10 years.

In regard to all switchgear the requirements of Section VII. Employer’s Requirements, Part B, Section B.7.4 shall apply unless otherwise stated.

      - Nominal system values

|  | Parameter | Value |
| --- | --- | --- |
| 1 | Nominal System Voltage | 11kV |
| 2 | Maximum Continuous System Voltage | 12kV |
| 3 | Circuit Breaker Nominal Current (Ir) | 200A |
| 4 | Lighting Impulse Withstand Voltage (Up) | 95 kV |
| 5 | Power Frequency Voltage Withstand (Ud) | 38 kV |
| 6 | System Frequency | 50 Hz |
| 7 | Rated Short Circuit Current | 21 kA |
| 8 | Duration of Short Circuit | 3s |
| 9 | Peak making current (Ip) | 53 kA |
| 10 | Time constant | > 45ms |
| 11 | Bus bar and Isolators Nominal current (Ir) | 630A |

      - RMU Configuration

The solar farm RMU shall have the following general configuration:

| - Ring switches | 2 |
| --- | --- |
| - Circuit breakers | 1 |

Enclosure

| - IP Rating | IP65 |
| --- | --- |
| - Rain shield | Yes |
| - Lifting rings | minimum2, OEM to confirm suitability |
| - Colour | to be specified |
| - Paint | ISO C5 Marine Grade Paint coated enclosures |
| - Height above ground | Base must be mounted a minimum of 500 mm above the local ground surface to reduce potential for inundation. |

Circuit Breakers

| - Type | Vacuum |
| --- | --- |
| - Rated current | 200A |
| - Closing (Motor driven charging) | Yes |
| - Spring recharge after closing | Yes |

Ring Switches

| - Remote operation capability | Yes |
| --- | --- |
| Safe operating procedures for closure to be established between the Seller and Grid Operator. Grid Operator shall have authority for remote disconnect if required for system safety or stability (dispatch control to be used preferentially). |  |

Earth Switches

| - Type | Fault making |
| --- | --- |
| - Making capacity | 40 kA peak |
| - Circuit earth switch interlock | Yes, with associated circuit breaker |
| - Remote operation capability | Yes |

Feeder CTs & VTs

- Contractor to specify

Feeder Protection Relay

- Required

- Functions – as detailed in section ‎D.3.6 below.

Communications interfaces 	Modbus

SCADA interface	 	Modbus

Capacitive Voltage Indication

| - Required | Yes |
| --- | --- |
| - Electrical interlock | Contractor to specify |

Surge Arrestor

| - Required | Contractor to specify |
| --- | --- |

Auxiliary Power

| - Required | Yes |
| --- | --- |
| - Auxiliary equipment AC voltage | 400/230 V AC |
| - Tripping and closing supply voltage | 110 V DC |
| - Indication supply voltage | 110 V DC |
| - Spring charge motor voltage | 110 V DC |
| - Alarm supply voltage | 110 V DC |
| - Redundant trip coils | Yes |
| - Redundant trip supplies | Yes |
| - Load | To be calculated by Contractor |
| - UPS power | Yes, to comprise of rectifier and battery bank |
| - Backup duration | Minimum 12 hours without AC supply |
| - Redundant DC supplies | required |

Metering

| - Required | Yes, as per section ‎D.3.4 below |
| --- | --- |

    - Metering

All MV sites shall have installed a revenue meter and Power Quality Meter on each feeder at the point of connection to the network.

Revenue Meters and Power Quality Meters shall be fed from separate CT cores.

Revenue Meters and Power Quality Meters may share VT secondary supplies.

All MV metering shall comply strictly with requirements specified below.

      - Revenue Meters

- Revenue meter: Class 0.5

- Voltage input

57.7 to 240V

Burden IEC 62053-61 compliant

- Current input

CT range 1/10A, 5/10A, 5/20A

CT limit 20 x Imax for 0.5 sec

Burden <0.5VA/phase

- Frequency 45 to 65Hz

- Four quadrant metering – 3 elements

Import/Export/Absolute Wh, varh and VAh

Fundamental Wh

Per quadrant Wh, varh and VAh

Phase A, B, C and Total - W, var, VA, Vrms, Irms

Power factor, frequency, phasor angles

- Communications

Optical ports and RS485 multi drop (2 or 4 wire RJ45 or screw terminals)

DLMS

MODBUS

- PQM - Total Harmonic distortion THD

- PQM – Unbalance (sequence components)

- PQM – programmable sag and swell

recording to 5 cycle resolution

record time/date/phase/duration/average and worst excursion

- Load profiling over 5000 days

- Time of use records

- Tamper detection and alarms

- Conforms to IEC 62052-11, 62053-21, 62052-31, 62053-22, 62053-23, 62053-24

      - Power Quality Meters

- Power Quantities:

All 3-phase configurations.

Active power [kW], Reactive power [kVAr], Apparent power [kVA], Power Factor and cos phi displacement factor, Active Energy [kWh], Reactive energy [kVArh], Apparent energy [kVAh]

Energy accuracy class 0.2S (IEC 62053-22)

- Frequency nominal 50Hz system

- Harmonics data:

100 individual harmonics of voltage

100 individual harmonics of current

- Power harmonics - Harmonic power with direction

- Flicker – Calculate IFL, Pst and Plt to IEC 61000-4-30 Class A

- Voltage channels

minimum 4

resolution 24 bit

accuracy 0.1%

- High speed voltage channels

+/-2.8kV peak level

Detection rate up to 31 000 p/c @50Hz

- Current inputs

minimum 4 isolated inputs

resolution 24 bit

accuracy 0.1%

- User configurable Analogue inputs

minimum 6

voltage or current

- Communication and remote read:

Modbus compatible

Modbus TCP/IP preferred

- Tamper detection and alarm: Yes

- Data logging: Minimum 1-year storage at 30-minute intervals

- Battery backup: Yes

- Display: Configurable

- Complies with:

EMC: EN 50081-1,2, EN 50082-1,2

Voltage characteristics: EN 50160, EN 61000-2-2, EN 61000-2-12

Harmonics: IEC 61000-4-7

Flicker: IEC 61000-4-15

Power quality measurement methods: IEC 61000-4-30, Class A,

IEC 62052-11, IEC 62053-21, IEC 62052-22, IEC 62053-23 compliant

    - Step-up Transformer

Step-up transformers must be selected to ensure they are reliable, compatible with subsystems and equivalent products, readily serviced, and that spare parts are readily available. To this end, step-up transformers must be selected from suppliers continuously servicing utilities in major international markets including Europe for a minimum of 10 years. Specific products or their product chains must have been offered for at least 5 years, and manufacturers must offer a commitment to support the product for a minimum of 10 years.

Step-up transformers shall be rated for inverter source operation and the environment in which each system will operate and shall be provided with protection and monitoring devices such as, but not limited to, pressure relay, oil and winding temperature and oil level.

Transformers are to be enclosed in self bunding Kiosks. Where Kiosk enclosure is not practicable due to transformer size and/or cooling requirements a suitable switchyard and security fence shall be provided.

Transformers will be sized by the tenderer to accommodate the solar plant full load capacity over the full design output, active and reactive power range. An allowance of a 5% capacity shall be added to the final transformer calculation.

Transformers will be provided with off load tap changers. The number and range of taps shall be determined by the tendered during detail design of the site. Tap position indications will be incorporated with site control system for remote monitoring.

It is recommended that the Contractor consider and specify the transformer with a capacitive shield to reduce high frequency harmonics injected into the HV side of the transformer and connected cables.

Note: Throughout the specification two winding transformers have been referred to as indicative of the requirements for the sites. This specification does not prohibit the use of three winding transformers. Three winding transformers will be considered where load size and or harmonic constraints would suggest a three winding transformer is the cost-effective solution.

Construction Characteristics

| - Type | Oil immersed transformer of sealed type construction |  |
| --- | --- | --- |
| - Oil type | Mineral oil |  |
| - Primary insulation level | 12 kV |  |
| - Primary voltage | 11 kV |  |
| - Secondary voltage (no load) | TBA |  |
| - Impedance | Contractor to specify |  |
| - Winding configuration | Dyn# (#=contractor to specify) |  |
| - Impulse withstand | 95 kVpeak |  |
| - Harmonic K factor | 1 – refer to section ‎D.3.8 below |  |
| - Power frequency withstand | 38 kVrms |  |
| - Frequency | 50 Hz |  |
| - Rating | Contractor to specify |  |
| - Cooling | ONAN |  |
| - HV connection | Bottom (conduit) |  |
| - LV connection | Bottom (conduit) |  |
| - IP Rating (Enclosure) | 56 |  |
| - Operating temperature | -4°… + 45 °C without de-ratings |  |
| - Altitude | < 1000 m |  |
| - Environmental class | E2 |  |
| - Climate class | C1 |  |
| - Fire class | F1 |  |
| - Accessories |  |  |
| - Oil and winding temperature monitoring; |  |  |
| - Oil level indicator; |  |  |
| - Oil drain valve and filler cap; |  |  |
| - Ratings plate in English |  |  |
| - 4 flat bi-directional rollers |  |  |
| - 2 earthing points |  |  |
| - Anti-vibration pads |  |  |

    - Protection

RMU’s shall be provided with multifunction protection relays. The Back-protection functions will be provided by the next upstream protection device to the POC. An inter-tripping scheme between the POC point of isolation and the Solar PV incomer CB will be implemented. As a minimum the inter-tripping scheme shall provide:

- CB fail back up tripping and

- anti-island protection tripping

Inter-tripping will be via a dedicated fibre optic link using Modbus TCP/IP protocols.

Each solar RMU shall have the following protection functions:

- 27 – Under voltage;

- 46 – Negative sequence;

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

The solar inverters shall be connected to the solar step up transformer. Each RMU shall have the following transformer protection functions:

- 49 – Thermal; and

- 69 – Buchholz (only if oil type transformers are used);

Step-up transformers. The solar inverters shall be connected to the solar step up transformer. Each RMU shall have the following transformer protection functions:

- 49 – Thermal; and

- 69 – Buchholz (only if oil type transformers are used);

    - Control / Communications interface

The RMU shall interface with the PV station control system for local and remote monitoring and control. Refer to Section ‎D.6 for system communication details.

A locally mounted HMI shall be provided to allow full local control of the RMU and its auxiliaries. The HMI shall be mounted in a suitably weather-proof enclosure, remote from the RMU such that the Operator does not need to stand in front of the RMU during local operation of the RMU and its CB’s, isolators and earth switches. This may be consolidated with the solar farm HMI.

    - Harmonic Emissions

Harmonic emissions, from all PV installations in a single grid under this project combined, must not contribute more than 10% of the planning limits established in the IEC 61000-3.12.

    - Earthing

The solar site earthing must ensure the safety of all personnel and equipment under all normal and abnormal operating conditions and all fault conditions.

General earthing shall be according to the Utility Regulatory Authority (URA) Installation Standards and IEC standards as listed in Section D.8., and shall include the following:

- PV Module to structure frame;

- PV arrays;

- DC electrical system;

- PCU earthing;

- Transformers and Neutral points;

- Fencing;

- Platforms and handrails and

- Buildings/enclosures.

Particular attention shall be given to:

- Achieving low-resistance connections that are resistant to degradation at all locations where grounding conductors or rods are bonded together

- Achieving the best possible contact with earth

- Verifications through tests that all electrical bonding within the grounding system has been properly affected

The design calculations shall include any area of the PV array exposed to step, touch and transfer potentials induced by earth potential rise, low frequency induction as well as electromagnetic and electric fields for the installation.

The LV/HV transformer earthing design is to use a common LV/HV grid. The design is to consider:

- The touch voltages limits for any local pipes as specified in AS 4853.

- The EPR transferred to the solar power station on an 11-kV earth fault.

    - Engineering studies

The Solar PV design process will produce the following, minimum set, of detail design reports to support the solar PV station electrical connection design:

- Power system studies including but not limited to the following:

  - Short-circuit analysis, minimum and maximum fault levels and locations;

  - Load flow;

  - System stability (Voltage & Frequency transients);

  - Ramping on/off requirements; and

  - Insulation co-ordination and lightning mitigation

  - Arc fault levels;

  - Harmonic response – injection levels to 99th order

  - Flicker levels

- Protection study that documents:

  - All protection devices and schemes;

  - Protection coordination with upstream devices;

  - CT and VT sizing calculations.

- Earthing study documenting:

  - Reporting site resistivity levels

  - Expected EPR contours at each site

  - Earthing system design methodology

  - Recommend mitigation / grid design

- Cable sizing report documenting:

  - Soil thermal resistivity reports

  - HV and LV AC cable Sizing calculations (capacity, voltage drop, fault capacity, design assumptions, losses etc.)

  - DC Cable Sizing calculations (capacity, voltage drop, fault capacity, design assumptions, losses etc.)

  - HV and LV Cable trench design parameters

  - LV connections

Where connection at 400 V (3 phase) or 230 V (single phase) is applicable, the connection arrangement as shown in Figures below is applicable. Note that there are three grid connection options that can be used, subject to site conditions:

- Building Distribution board,

- LV, 400V, street Distribution board,

- Distribution Substation LV, 400V, board.

Figure7: LV plant connection configuration

Figure 8: LV plant connection options

    - LV grid connection

For LV connections, the Seller is responsible for undertaking the connection to the grid. Where the connection point is not compliant with existing URA standards for electrical installations in the Maldives, remediation of the relevant hardware by the Seller is required.

    - LV metering

LV sites will be fitted with metering as described in section ‎D.3.4 above.

LV sites of less than 175kW installed PV capacity will not be required to fit a separate Power Quality Meter. The Revenue Meter may be used to provide required PQM data.

LV sites of greater than or equal to 175kW installed PV capacity will be required to fit a separate Power Quality Meter in addition to the Revenue meter as described in section ‎D.3.4 above.

    - Engineering studies

The Seller will be required to submit for review and approval the following, minimal set of Engineering studies to support the LV site design.

- Power system studies including but not limited to the following:

  - Short-circuit analysis, minimum and maximum fault levels and locations;

  - Insulation co-ordination and lightning mitigation

  - Arc fault levels;

- Protection study that documents:

  - Protection coordination with upstream devices;

- Cable sizing report documenting:

  - LV AC cable Sizing calculations (capacity, voltage drop, fault capacity, design assumptions, losses etc.)

  - DC Cable Sizing calculations (capacity, voltage drop, fault capacity, design assumptions, losses etc.)

  - Cable trench design parameters

  - Grid support

Solar PV plant of 35kW and larger installed PV capacity is required to provide autonomous and automatic grid support functionality for frequency, voltage control and fault ride through events.

Solar PV plant of 100kW and larger installed PV capacity is also required to respond to dispatch instructions (external command) to vary the operating grid support mode or settings, and to curtail active and reactive power output.

    - Automatic grid support functionality

      - Frequency withstand capability

Under frequency variations, the solar PV plant must remain connected and fully operational for duration as shown in the following table.

| Frequency | Duration (s) |
| --- | --- |
| f >56 | Instantaneous disconnection |
| 54< f ≤ 56 | 1 |
| 52 < f ≤ 54 | 20 |
| 51 < f ≤ 52 | 180 |
| 49≤ f ≤ 51 | Continuous |
| 49< f ≤ 47.5 | 180 |
| 47.5< f ≤ 46 | 30 seconds |
| 46< f ≤ 44 | 1 second |
| f < 44 | Instantaneous disconnection |

Ride through settings must be configurable in at least six bands between 44 Hz and 56 Hz.

If default capability of equipment exceeds this requirement, the default capability must be maintained and accessible to the Employer without restriction.

      - Voltage withstand capability

For fault events, the solar PV plant must remain connected and fully operational for duration as shown in the following table:

| Voltage (p.u.) | Duration (s) |
| --- | --- |
| V>1.5 | Instantaneous disconnection |
| 1.15≤ V ≤ 1.2 | 0.2 |
| 1.12≤ V ≤ 1.15 | 70 |
| 0.85≤ V ≤ 1.12 | Continuous |
| 0.75< V ≤ 0.85 | 70 |
| 0.65< V ≤ 0.75 | 15 |
| 0.45< V ≤ 0.65 | 2 |
| 0.25< V ≤ 0.45 | 0.8 |
| V ≤ 0.25 | 0.15 |

If default capability of equipment exceeds this requirement the default capability must be maintained and accessible to the Employer without restriction.

Ride through settings must be configurable within the above requirements.

Solar PV plant should not consume reactive power during fault events.

      - Voltage support

The solar PV plant shall be capable of contributing to voltage control at the point of connection by regulation of its reactive power (within its prescribed range) to maintain a voltage set point (voltage control mode).

The solar PV plant shall be capable of maintaining its reactive power contribution (within its prescribed range) at the point of connection at a set-point by regulation of its voltage.

The solar PV plant shall be capable of maintaining its power factor (within its prescribed range) at the point of connection at a set-point by regulating voltage and reactive power.

The prescribed range for reactive power capability is shown in the following table:

| Active power (100% = declared AC power of the plant) | Reactive power / power factor range |
| --- | --- |
| P = 100% | -45% Q < 45% |
| 10% < P ≤ 100% | 0.9 lagging < pf < 0.9 leading |
| P ≤ 10% | 0 |

If default capability of equipment exceeds this requirement the default capability must be maintained and accessible to the Employer without restriction.

Voltage control through settings must be configurable within the above requirements.

      - Active power control

The solar PV plant may be required to reduce active power in response to over-frequency events, or, if curtailed, to increase active power to the extent possible in response to under frequency events. This droop control functionality must include a dead-band and be configurable. Nominally, the gain on active power control will be 20 p.u, with a 0.5 Hz dead-band.

      - Other

Except as specified elsewhere in this document, functionality of the solar PV plant, including automatic grid support functions must comply with:

- DIN VDE 0126-1-1 (2013) Automatic disconnection device between grid parallel power generating system and the public low voltage grid (for frequency and voltage disconnection limits), and

- VDE-AR-N 4105 (2019): Power generating plant in low voltage grid

Or alternatively, any of the following:

- G83/1-1, EA Engineering Recommendation G83/1-1: Amendment 1-June 2008, Recommendation for the connection of small-scale embedded generators in parallel with the public low-voltage distribution networks.

- AS 4777.2-2005: Grid connection of energy systems via inverters – inverter requirements:

- EN 50438, Requirements for the connection of micro-generators in parallel with public low-voltage distribution networks

- UL1741, Inverters, Converters, Controllers and Interconnection System Equipment for Use with Distributed Energy Resources

- IEEE 1547: Standard for Interconnecting Distributed Resources with Electric Power Systems

    - Dispatch control

The solar PV plant must respond to instructions from the grid control system, where safe to do so, as follows:

- Change upper limit on active power output:

Match commanded limit within 2.0 s of receipt of signal via ramp in active power limit.

- Loss of communications:

Maintain previous active power limit; or

Include optional setting to revert to pre-set active power limit

- Change in voltage control mode:

Change to commanded mode within 30 seconds.

- Shutdown:

Reduce active power to zero within 2.0 s of receipt of signal via ramp.

- Start:

Commence standard safe start procedure to be determined during design.

- Emergency stop:

Open remotely operated circuit breakers and initiate OEM rapid shutdown procedure.

  - Communications interface

To support centralised grid operation and dispatch control, data from the PV plant must be available via a router / switch / patch-panel installed as part of the solar PV Plant. The communications connection point must include gateway options for single mode fibre optic connection and redundant 3G/4G connection. For LV-connected solar PV plant, 3G/4G connection alone is acceptable. For MV-connected plant, connection to the grid communications infrastructure will be undertaken by others. Communication infrastructure must be installed in a readily accessible panel.

All communications must be Modbus compliant.

All IO modules shall include 25% spare capacity.

The following information shall be provided to the grid:

- Operation status of the solar PV plant, including consolidated warnings and alarms

- Voltage at MV busbar of the Solar PV plant

- Active Power, Reactive Power and electric current interchanged at the Metering point

- Status of the MV circuit breaker(s) and isolator switches

- Solar PV controller and inverter default data (including but not limited to status, alarms, warnings, configuration settings, operating mode, DC and AC power / voltage / current). Inverters must be certified as SunSpec Modbus compliant.

- Weather station data

- Heartbeat.

Section ‎D.9 presents a typical medium scale HV connected solar farm IO list. Numbers of IO will vary with chosen site configurations and equipment specifications. The list is provided as indicative of the expected level of data to be transmitted to the SCADA system.

The solar PV plant shall receive, acknowledge and act on the following dispatch commands:

- Modes of control and set-points for Active Power control;

- Instructions for Active Power curtailment;

- Modes of control of voltage regulation and set points;

- Start/stop instructions.

- Indicative communications architecture diagram, including remainder of the grid, is shown in figure below.

Figure 9: communications architecture (for 11kV connection of solar PV)

  - Weather station

A solar PV plant (or local cluster of plants) with capacity >175kW must include a weather station and integrate the weather station output seamlessly with the solar PV plant data available to the grid. The weather station must, at a minimum, include:

- Global horizontal irradiance Pyranometer (Secondary standard)

- Plane of array Pyranometer (Secondary standard) – one only, oriented to match predominant tilt and orientation

- If bifacial modules are included, an Albedometer

- Combined temperature (+/-0.5 degrees C accuracy), wind speed, pressure and relative humidity sensor

- Soiling measurement

  - Standards

All equipment supplied under these specifications shall conform to the latest editions of the International Electro technical Commission (IEC) standards, or where no IEC standards, to British Standard (BS), or equivalent national standards as may be approved by the Employer.

- IEC 60694:  common specifications for switchgear & control gear

- IEC 62271-100: High Voltage AC Breakers

- IEC 60265: High Voltage AC Switches

- IEC 62052-11, IEC 62053-21, IEC 62052-22, IEC 62053-23 Electricity metering equipment (AC)

- IEC 62271-200:  metal Enclosed Switchgear & Control Gear

- IEC 62271-102: HV AC Disconnectors & Earthing Switches

- IEEE 80 - Guide for Safety in AC Substation Grounding

- IEC/BS EN 62305 – Protection against lightning – all parts as applicable

- EN50160 on voltage characteristics of electricity supplied by public distribution systems

- IEEE519 IEEE Recommended Practice and Requirements for Harmonic Control in Electric Power Systems

- IEC 61000 Electromagnetic compatibility (EMC) all parts as applicable

- IEC 60044 Instrument transformers – all parts as applicable

- IEC 61936-1 Power installations exceeding 1 kV a.c. - Part 1: Common rules

- ENA TS 41-26:  UK Energy Network Association Technical Specification for Distribution Switchgear*

In case the equipment or materials offered from a country where the relevant standards to which the equipment or materials offer better performance or safeguards for the Principal than IEC or BS Specifications, these are acceptable. The Seller must substantiate any such claims by submitting an independent assessment, by an appropriately qualified person, that identifies differences in the standards and demonstrates the benefit for the Principal.

All installations and materials and cabling shall be in accordance with the IEEE Wiring Regulations. All works shall conform to the requirements of the URA.

  - Typical SCADA IO list

Type Legend

| ACO Analogue Control ALM Digital Alarm Status ANA Analogue Status Input | DCO Digital Control STA Digital Status Input |
| --- | --- |

| SOURCE | TYPE | DESCRIPTION | Units | COMMENTS |
| --- | --- | --- | --- | --- |
| CUBICLE/S | ALM | CUBICLE DOOR OPEN ALARM |  | Required for all control cubicle types Including communications and power supply cubicles |
| ETHERNET SWITCH/S | STA | ETHERNET SWITCH ETHERNET SWITCH HEALTHY |  |  |
|  | ALM | ETHERNET SWITCH ETHERNET SWITCH COMMUNICATIONS ERROR |  |  |
| OLM (Optical Link Module) | ALM | OLM OPTICAL LINK MODULE 1 FAULT |  |  |
|  | ALM | OLM OPTICAL LINK MODULE 2 FAULT |  |  |
| HV CB | STA | HV CB CIRCUIT BREAKER OPENED STATUS |  |  |
|  | STA | HV CB CIRCUIT BREAKER CLOSED STATUS |  |  |
|  | STA | HV CB EARTH SWITCH OPENED STATUS |  |  |
|  | STA | HV CB EARTH SWITCH CLOSED STATUS |  |  |
|  | DCO | HV CB CIRCUIT BREAKER OPEN COMMAND |  |  |
|  | DCO | HV CB CIRCUIT BREAKER CLOSE COMMAND |  |  |
|  | DCO | HV CB EARTH SWITCH OPEN COMMAND |  | Remote earthing command |
|  | DCO | HV CB EARTH SWITCH CLOSE COMMAND |  | Remote earthing command |
|  | STA | HV CB LOCAL CONTROL SELECTED |  |  |
|  | STA | HV CB REMOTE CONTROL SELECTED |  |  |
| PROTECTION RELAY | ANA | PROTECTION RELAY ACTIVE POWER (P) | kW |  |
|  | ANA | PROTECTION RELAY REACTIVE POWER (Q) | kVAR |  |
|  | ANA | PROTECTION RELAY MAX. ACTIVE POWER (MP) | kW |  |
|  | ANA | PROTECTION RELAY MAX. REACTIVE POWER (MQ) | kVAR |  |
|  | ANA | PROTECTION RELAY ACTIVE ENERGY (KWH) | kWh |  |
|  | ANA | PROTECTION RELAY REACTIVE ENERGY (KVARH) | kVARh |  |
|  | ANA | PROTECTION RELAY POWER FACTOR (PF) | - |  |
|  | ANA | PROTECTION RELAY FREQUENCY (HZ) | Hz |  |
|  | ANA | PROTECTION RELAY CURRENT I1 | A |  |
|  | ANA | PROTECTION RELAY CURRENT I2 | A |  |
|  | ANA | PROTECTION RELAY CURRENT I3 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT I1 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT I2 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT I3 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT N | A |  |
|  | ANA | PROTECTION RELAY PHASE-PHASE V1 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-PHASE V2 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-PHASE V3 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-GROUND V1 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-GROUND V2 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-GROUND V3 | kV |  |
|  | STA | PROTECTION RELAY PROTECTION RELAY HEALTHY |  |  |
|  | ALM | PROTECTION RELAY PROTECTION RELAY FAIL |  |  |
|  | ALM | PROTECTION RELAY VT OR MOTOR MCB TRIP |  |  |
|  | ALM | PROTECTION RELAY PROTECTION RELAY TRIP |  |  |
|  | ALM | PROTECTION RELAY PROTECTION RELAY WATCHDOG |  |  |
|  | ALM | PROTECTION RELAY COMMUNICATION FAILURE |  | Derived internally |
|  | ANA | PROTECTION RELAY PANEL BACK SURFACE TEMPERATURE | degC | One required for each switchgear |
|  | ALM | PROTECTION RELAY ANSI CODE 'XX' TRIP ALARM |  | One alarm to be provided for each ANSI protection function |
| HV SW | STA | HV SW SWITCH OPENED STATUS |  | Required for each item of switchgear |
|  | STA | HV SW SWITCH CLOSED STATUS |  |  |
|  | STA | HV SW EARTH SWITCH OPENED STATUS |  |  |
|  | STA | HV SW EARTH SWITCH CLOSED STATUS |  |  |
|  | DCO | HV SW SWITCH OPEN COMMAND |  |  |
|  | DCO | HV SW SWITCH CLOSE COMMAND |  |  |
|  | DCO | HV SW EARTH SWITCH OPEN COMMAND |  |  |
|  | DCO | HV SW EARTH SWITCH CLOSE COMMAND |  |  |
|  | STA | HV SW LOCAL CONTROL SELECTED |  |  |
|  | STA | HV SW REMOTE CONTROL SELECTED |  |  |
| HV BUS VT | STA | HV BUS VT - VT MCB TRIP |  |  |
| METERING | ANA | METER ACTIVE POWER (P) | kW |  |
|  | ANA | METER REACTIVE POWER (Q) | kVAR |  |
|  | ANA | METER MAX. ACTIVE POWER (MP) | kW |  |
|  | ANA | METER MAX. REACTIVE POWER (MQ) | kVAR |  |
|  | ANA | METER ACTIVE ENERGY (KWH) | kWh |  |
|  | ANA | METER REACTIVE ENERGY (KVARH) | kVARh |  |
|  | ANA | METER POWER FACTOR (PF) | - |  |
|  | ANA | METER FREQUENCY (HZ) | Hz |  |
|  | ANA | METER CURRENT I1 | A |  |
|  | ANA | METER CURRENT I2 | A |  |
|  | ANA | METER CURRENT I3 | A |  |
|  | ANA | METER MAX. CURRENT I1 | A |  |
|  | ANA | METER MAX. CURRENT I2 | A |  |
|  | ANA | METER MAX. CURRENT I3 | A |  |
|  | ANA | METER MAX. CURRENT N | A |  |
|  | ANA | METER PHASE-PHASE V1 | kV |  |
|  | ANA | METER PHASE-PHASE V2 | kV |  |
|  | ANA | METER PHASE-PHASE V3 | kV |  |
|  | ANA | METER PHASE-GROUND V1 | kV |  |
|  | ANA | METER PHASE-GROUND V2 | kV |  |
|  | ANA | METER PHASE-GROUND V3 | kV |  |
|  | ALM | METER METER FAIL ALARM |  |  |
|  | ALM | METER METER COMMUNICATION FAILURE |  |  |
| STEPUP TRANSFORMER | ALM | Transformer (oil) OIL TEMPERATURE HIGH |  | Applicable for both power and auxiliary transformers. |
|  | ALM | Transformer (oil) OIL LEVEL LOW |  |  |
|  | ALM | Transformer (oil) OIL PRESSURE HIGH |  |  |
|  | ALM | Transformer (oil) BUND LEVEL REACHED |  |  |
| INVERTER | ANA | INVERTER TEMPERATURE AC CUBICLE | degC | Additional points to be included per manufacturer recommendations. |
|  | ANA | INVERTER TEMPERATURE DC CUBICLE | degC |  |
|  | ANA | INVERTER TEMPERATURE IGBT | degC |  |
|  | STA | INVERTER AC CIRCUIT BREAKER OPEN |  |  |
|  | STA | INVERTER AC CIRCUIT BREAKER CLOSED |  |  |
|  | STA | INVERTER DC CIRCUIT BREAKER OPEN |  |  |
|  | STA | INVERTER DC CIRCUIT BREAKER CLOSED |  |  |
|  | ALM | INVERTER DC INSULATION FAULT ALARM |  | Fault on incoming DC cable insulation |
|  | ALM | INVERTER INVERTER GENERAL ALARM |  |  |
|  | ALM | INVERTER TEMPERATURE ALARM |  |  |
|  | ALM | INVERTER INVERTER REDUCED OUTPUT TEMP. ALARM |  |  |
|  | ALM | INVERTER LOSS OF GRID ALARM |  |  |
|  | ALM | INVERTER AC CIRCUIT BREAKER TRIP ALARM |  |  |
|  | ALM | INVERTER DC CIRCUIT BREAKER TRIP ALARM |  |  |
|  | ALM | INVERTER HARMONIC CURRENT DISTORTION ALARM |  | As measured at AC terminals |
|  | ALM | INVERTER EMERGENCY STOP CIRCUIT STATUS |  | Emergency stop/shut down engaged |
|  | ALM | INVERTER COMMUNICATION FAILURE |  |  |
|  | STA | INVERTER AUTO MODE STATUS |  |  |
|  | STA | INVERTER MANUAL MODE STATUS |  |  |
|  | STA | INVERTER LOCAL CONTROL SELECTED |  |  |
|  | STA | INVERTER REMOTE CONTROL SELECTED |  |  |
|  | ANA | INVERTER ACTIVE POWER (P) | kW |  |
|  | ANA | INVERTER REACTIVE POWER (Q) | kVAR |  |
|  | ANA | INVERTER MAX. ACTIVE POWER (MP) | kW |  |
|  | ANA | INVERTER MAX. REACTIVE POWER (MQ) | kVAR |  |
|  | ANA | INVERTER ACTIVE ENERGY (KWH) | kWh |  |
|  | ANA | INVERTER REACTIVE ENERGY (KVARH) | kVARh |  |
|  | ANA | INVERTER POWER FACTOR (PF) | - |  |
|  | ANA | INVERTER FREQUENCY (HZ) | Hz |  |
|  | ANA | INVERTER CURRENT I1 | A |  |
|  | ANA | INVERTER CURRENT I2 | A |  |
|  | ANA | INVERTER CURRENT I3 | A |  |
|  | ANA | INVERTER MAX. CURRENT I1 | A |  |
|  | ANA | INVERTER MAX. CURRENT I2 | A |  |
|  | ANA | INVERTER MAX. CURRENT I3 | A |  |
|  | ANA | INVERTER MAX. CURRENT N | A |  |
|  | ANA | INVERTER TOTAL HARMONIC CURRENT DISTORTION PH. A | % |  |
|  | ANA | INVERTER TOTAL HARMONIC CURRENT DISTORTION PH. B | % |  |
|  | ANA | INVERTER TOTAL HARMONIC CURRENT DISTORTION PH. C | % |  |
|  | ANA | INVERTER PHASE-PHASE V1 | kV |  |
|  | ANA | INVERTER PHASE-PHASE V2 | kV |  |
|  | ANA | INVERTER PHASE-PHASE V3 | kV |  |
|  | ANA | INVERTER PHASE-GROUND V1 | kV |  |
|  | ANA | INVERTER PHASE-GROUND V2 | kV |  |
|  | ANA | INVERTER PHASE-GROUND V3 | kV |  |
|  | ANA | INVERTER DC CURRENT MEASUREMENT | A |  |
|  | ANA | INVERTER GROUND CURRENT MEASUREMENT | A |  |
|  | ANA | INVERTER DC VOLTAGE MEASUREMENT | V |  |
| COMBINER BOX | ALM | COMBINER BOX FUSE CIRCUIT 'N' BLOWN |  | Quantity as required - 1 for each sub-circuit |
|  | ALM | COMBINER BOX INSULATION FAULT ALARM CIRCUIT 'N' |  | Quantity as required - 1 for each sub-circuit |
|  | ANA | COMBINER BOX DC CURRENT CIRCUIT 'N' | A | Quantity as required - 1 for each sub-circuit |
|  | ANA | COMBINER BOX DC VOLTAGE CIRCUIT 'N' | V | Quantity as required - 1 for each sub-circuit |
|  | ALM | COMBINER BOX COMMUNICATION FAILURE |  |  |
| WEATHER STATION | ANA | WEATHER STATION POA SOLAR IRRADIATION | W/m2 |  |
|  | ANA | WEATHER STATION HORIZONTAL SOLAR IRRADIATION | W/m2 |  |
|  | ANA | WEATHER STATION AMBIENT AIR TEMPERATURE | degC |  |
|  | ANA | WEATHER STATION BACK OF MODULE TEMPERATURE | degC |  |
|  | ANA | WEATHER STATION WIND SPEED | m/s |  |
|  | ANA | WEATHER STATION WIND DIRECTION | deg |  |
|  | ANA | WEATHER STATION AIR PRESSURE | hPa |  |
|  | ANA | WEATHER STATION RELATIVE HMIDITY | % |  |
|  | ANA | WEATHER STATION RAINFALL | mm |  |
|  | ANA | WEATHER STATION SOILING STATION OUTPUT | W |  |
|  | ALM | WEATHER STATION CONTROLLER FAULT |  |  |
|  | ALM | WEATHER STATION COMMUNICATION FAILURE |  |  |
| BATTERY CHARGER | ALM | BATTERY CHARGER AC SUPPLY FAILED |  |  |
|  | STA | BATTERY CHARGER BATTERY HEALTHY |  |  |
|  | ALM | BATTERY CHARGER CHARGER FAILED |  |  |
|  | STA | BATTERY CHARGER BATTERY VOLTAGE HIGH |  |  |
|  | STA | BATTERY CHARGER BATTERY VOLTAGE LOW |  |  |
|  | ALM | BATTERY CHARGER BATTERY EARTH FAULT |  |  |
|  | STA | BATTERY CHARGER BOOST STATUS |  |  |
| SOLAR PPC (Power Plant Controller) | STA | SOLAR PPC RUNNING STATUS |  | Solar power station is running |
|  | STA | SOLAR PPC SHUT DOWN STATUS |  | Solar power station is shut down |
|  | ACO | SOLAR PPC START UP COMMAND |  | Remote command to start up the solar power station |
|  | ACO | SOLAR PPC SHUT DOWN COMMAND |  | Remote command to Shut down the solar power station |
|  | STA | SOLAR PPC AUTO MODE STATUS |  |  |
|  | STA | SOLAR PPC MANUAL MODE STATUS |  |  |
|  | ACO | SOLAR PPC AUTO MODE COMMAND |  | Remote command |
|  | ACO | SOLAR PPC MANUAL MODE COMMAND |  | Remote command |
|  | DCO | SOLAR PPC SET HV VOLTAGE CONTROL MODE |  | Remote command - set mode |
|  | DCO | SOLAR PPC SET POWER FACTOR CONTROL MODE |  | Remote command - set mode |
|  | DCO | SOLAR PPC SET CONSTANT REACTIVE POWER MODE |  | Remote command - set mode |
|  | DCO | SOLAR PPC SET CONSTANT REACTIVE POWER NIGHT MODE |  | Remote command - set mode |
|  | DCO | SOLAR PPC SET MAX POWER POINT MODE |  | Remote command - set mode |
|  | DCO | SOLAR PPC SET ACTIVE POWER CURTAILMENT MODE |  | Remote command - set mode |
|  | DCO | SOLAR PPC SET FREQUENCY CONTROL MODE |  | Remote command - set mode |
|  | ACO | SOLAR PPC SET HV VOLTAGE OUTPUT LEVEL | kV | Remote command - set point |
|  | ACO | SOLAR PPC SET DROOP | % | Remote command - set point |
|  | ACO | SOLAR PPC SET POWER FACTOR | - | Remote command - set point |
|  | ACO | SOLAR PPC SET REACTIVE POWER LIMIT | kVAR | Remote command - set point |
|  | ACO | SOLAR PPC SET POWER OUTPUT (MPPT) CURTAILEMENT | MW | Remote command - set point |
|  | ACO | SOLAR PPC SET RAMP RATE RISING | kW/sec | Remote command - set point |
|  | ACO | SOLAR PPC SET RAMP RATE LOWERING | kW/sec | Remote command - set point |
|  | ACO | SOLAR PPC SET FREQUENCY CONTROL | Hz | Remote command - set point |
|  | ANA | SOLAR PPC HV VOLTAGE OUTPUT LEVEL SET POINT | kV | Set point current setting |
|  | ANA | SOLAR PPC DROOP SET POINT | % | Set point current setting |
|  | ANA | SOLAR PPC POWER FACTOR SET POINT | - | Set point current setting |
|  | ANA | SOLAR PPC REACTIVE POWER SET POINT | kVAR | Set point current setting |
|  | ANA | SOLAR PPC MAX POWER POINT MODE SET POINT | - | Set point current setting |
|  | ANA | SOLAR PPC POWER OUTPUT (MPPT) SET POINT | MW | Set point current setting |
|  | ANA | SOLAR PPC RAMP RATE RISING SET POINT | kW/sec | Set point current setting |
|  | ANA | SOLAR PPC RAMP RATE LOWERING SET POINT | kW/sec | Set point current setting |
|  | ANA | SOLAR PPC FREQUENCY CONTROL SET POINT | kW/sec | Set point current setting |
|  | ANA | SOLAR PPC PERFORMANCE RATIO CALCULATION | % |  |
|  | STA | SOLAR PPC SOLAR PPC HEALTHY |  |  |
|  | ALM | SOLAR PPC GENERAL ALARM |  |  |
|  | ALM | SOLAR PPC PROGRAM LOADED FROM EEPROM |  |  |
|  | ALM | SOLAR PPC WATCHDOG |  |  |
|  | ALM | SOLAR PPC COMMUNICATIONS ERROR |  |  |

  - NETWORK EXTENSIONS

In certain instances, the installation of the PV plant shall also require LV network reinforcements and extensions, transformer and switch gear, and MV lines laying which shall become included within the scope of works.  In these cases, the interconnections themselves and required studies shall also form the scope.

    - Electrical cables

All cabling to be procured, as well as the design methodology and considerations, must strictly comply with Sections 3 to 5 of the Utility Regulatory Authority (URA) Installation Standards.

- MV cables must be 3C x Cu/XLPE/SCT/PVC/SWA/PVC, 6.35/11kV to British Standard or IEC 60502.

- LV cables must be 4C x CU/XLPE/SWA/PVC, 0.6/1kV to British Standard or IEC 60502.

Additionally:

- Cables shall be labelled at both ends, with permanent labels.

- Above ground cabling shall be placed and protected such that DC clamp meters can be used to confirm no current flow for safety isolation purposes. No tools shall be required to allow such cable access. Service loops shall be placed in all cables external to the combiner box to allow re-termination if required.

- All outdoor enclosure cable entries are to be done from the bottom of the enclosure, to prevent water ingress.

- For underground cables, cable markers shall be installed at each change of direction, road crossing, and every 200 m of straight-line length. Cable markers should designate the underground service details, depth, and relevant contact details. Cable markers should be selected to last the design life. Cable markers should be sensitive to the location (for example, flush mounted where they would obstruct other activities) and agreed with the Employer.

- Underground cables shall be protected from damage by vermin. A termite-protection layer shall be included in all underground cables. Water blocking shall be included in all 11 kV cables.

    - Low voltage Distribution Box

The electrical distribution boxes will be installed at the locations marked on the relevant LV distribution plans or as determined during detailed design. The distribution boxes shall be designed, manufactured and installed in accordance with the Installation Standards, and the IEC 60364 Electrical Installations for Buildings. The distribution boards will meet the following requirements:

- The distribution board shall be lockable, using the local utility FENEKA’s standard key.

- The distribution board shall be certified to at least IP56.

- The base of the distribution board shall be mounted at least 1 m from finished surface to avoid water damage from flooding.

- The distribution board shall be earthed in accordance with the earthing and fault loop requirements as specified in the Installation Standards and IEC 60364 Electrical Installations for Buildings.

- The feeder cables shall be fitted with permanent mechanical protection.

- The distribution boards shall be clearly and permanently labelled with the board number and circuit number.

- Each distribution board shall be fitted with the following components as shown in Figure ‎3:1.

Figure 3:1: The distribution box wiring diagram

- The distribution boards shall have 12, 18 or 24 circuits as required depending on the location and determined through detailed design.

    - Low voltage Busbar on Transformer Substation

Substations with transformers for customer supply shall be fitted with a 400V distribution board, including a main isolation switch, check metering and a minimum of six (6) sub distribution feeder circuits (or as determined during detailed design). Each sub distribution feeder circuit shall be fitted with a circuit breaker with 300 A rating, unless otherwise specified or determined during design.

    - Distribution transformers

As per Section D.3.5 Step-up transformer.

    - RMU switchgear

As per Section D.3.3 Switchgear.

      - RMU Configuration

Substation RMU’s shall have the following general configuration:

| - Ring switches | 2 |
| --- | --- |
| - Circuit breakers | Qty as required |

Enclosure

| - IP Rating | IP65 |
| --- | --- |
| - Rain shield | Yes |
| - Lifting rings | minimum2, OEM to confirm suitability |
| - Colour | to be specified |
| - Paint | ISO C5 Marine Grade Paint coated enclosures |
| - Height above ground | Base must be mounted a minimum of 500 mm above the local ground surface to reduce potential for inundation. |

Circuit Breakers

| - Type | Vacuum |
| --- | --- |
| - Rated current | Depends on the load capacity |
| - Closing (Motor driven charging) | Yes |
| - Spring recharge after closing | Yes |

Earth Switches

| - Type | Fault making |
| --- | --- |
| - Making capacity | kA peak depending on the FPV capacity |
| - Circuit earth switch interlock | Yes, with associated circuit breaker |
| - Remote operation capability | Yes |

Feeder CTs & VTs

- Contractor to specify

Feeder Protection Relay

- Required

- Functions – as detailed in section ‎D.3.6 .

Capacitive Voltage Indication

| - Required | Yes |
| --- | --- |
| - Electrical interlock | Contractor to specify |

Surge Arrestor

| - Required | Contractor to specify |
| --- | --- |

Auxiliary Power

- Not required

Metering

| - Required | Yes, as per section ‎D.3.4 |
| --- | --- |

    - Earthing of network extension works

General earthing shall be according to the section: D.8 Standards and shall include the following at minimum:

- Transformers and Neutral points;

- Fencing;

- Platforms and handrails and

- Buildings/enclosures.

Particular attention shall be given to:

- Achieving low-resistance connections that are resistant to degradation at all locations where grounding conductors or rods are bonded together

- Achieving the best possible contact with earth

- Verifications through tests that all electrical bonding within the grounding system has been properly affected

The design calculations shall include any area exposed to step, touch and transfer potentials induced by earth potential rise, low frequency induction as well as electromagnetic and electric fields for the installation.

The LV/HV transformer earthing design is to use a common LV/HV grid. The design is to take into account:

- The touch voltages limits for any local pipes as specified in the Standards.

- The EPR transferred to the solar power station on an 11-kV earth fault.

    - Final cable routes

The Seller is to use cable routes as per the Data Room Supplementary Information, however, micro siting may be required based on site investigations. Final design cable routes are to be approved by the Employer.

Final design cable routes shall be presented as a comprehensive and accurate GIS data set, freely accessible to the Employer via online viewer (and archive submitted).

Final design cable routes shall minimize road crossings and disturbance of any existing infrastructure. Final design cable routes shall be wholly within roadways or other easements, which will be provided by the Employer.

    - Engineering studies

The MV network design process will produce the following, minimum set, of detail design reports to support the design. Studies shall be undertaken on modified regions of the network only, and as applicable to the modifications.

- Power system studies including but not limited to the following:

  - Short-circuit analysis, minimum and maximum fault levels and locations;

  - Load flow;

  - Insulation co-ordination and lightning mitigation

  - Arc fault levels;

- Protection study that documents:

- All protection devices and schemes;

- Anti-islanding schemes and backups;

- Protection coordination with upstream devices;

- CT and VT sizing calculations.

- Earthing study documenting:

- Reporting site resistivity levels

- Expected EPR contours at each site

- Earthing system design methodology

- Recommend mitigation / grid design

- Cable sizing report documenting:

- Soil thermal and electrical resistivity reports

- HV AC cable Sizing calculations (capacity, volt drop, fault capacity, design assumptions, losses etc.)

- HV Cable trench design parameters

The LV network design process will produce the following, minimum set, of detail design reports to support the design:

- Protection sizing report documenting:

- Selection of fuses at each distribution board (Employer to specify)

- Protection compatibility with upstream devices

- Protection requirements for connection of solar PV into the LV distribution grid.

- Cable sizing report documenting:

- Soil thermal and electrical resistivity reports

- LV AC cable Sizing calculations (capacity, volt drop, fault capacity, design assumptions, losses etc.)

- LV Cable trench design parameters

- Earthing design parameters

The communications infrastructure design process will produce the following, minimum set, of detail design reports (note that LV networks require only installation of communication equipment at the power station, allowing wireless / 4G communications to solar PV plant):

    - Compact substations and substation buildings

All new substations, MV-Solar RMU’s, compact pre-assembled substations and transformer upgrades shall occupy minimum space and fit current building standards adopted by FENAKA.

For standard substation buildings

- Refer to standard Drawings for Substation in the Data-room,

- Refer to Part E for the civils quality requirements.

For compact pre-assembled substations

- Containerized substation shall follow the type and routine testing as prescribed in IEC 62271-202-2022.

- Substation shall be installed atop concrete plinth, and if not already secured be further protected by fence and roof covering as per picture in Data-room.

- Refer to Part E for the metal work and civils quality requirements.

  - Description of the INTERCONNECTION AND NETWORK EXTENSION WORKS

In certain instances, the installation of the PV plant shall also require LV network reinforcements and extensions, transformer and switch gear, and MV lines laying which shall become included within the scope of works, and included within the PPA price offered.  Bidders are required to conduct costing assessments for their own purposes.

Table 9: Description and estimates for network extension for each site

Please refer to the “Master list and GU plus feeders.xlsx file in data room for details on required upgrades

- Array Structure Requirements

E.1: General requirements for PV array structures (narrative)

E.2: Array structure specific requirements

E.3: Diagrams of typical array structures and representative conceptual designs

E.4. Construction specification for general civil works

  - General REQUIREMENTS FOR PV ARRAY STRUCTURES

    - Introduction

15 MWp of ground and roof mounted solar PV system is planned, in locations ranging from roadways and pedestrian paths, vehicle parks, farmland areas, community parks and such other public open spaces, in addition to coastal areas near island harbours subjected to regular loading/unloading activities.

Array structure types include low rise ground mount structures for airports, and functional elevated arrays providing shading for car-parks, shading for pedestrians' walkways, and accessible shading of public open spaces. Therefore, retained functionality and access to spaces under the elevated arrays is critical, as well as aesthetic considerations.  The PV systems are referred to in Part C.

The structures for solar arrays are required to meet multiple criteria in order to be acceptable for installation along these routes.  These criteria include:

- Minimum array capacity (kWp);

- Compatibility with existing roof structure and roof space for roof mount structures;

- Array structure clearances for pedestrians, leisure and vehicular traffic;

- Sub-array span foot-print limitations and heights;

- Sub-array foundation constraints caused by new or existing underground cabling, other foundations, etc;

- Sub-array tilt and orientation to avoid airport glare as per Maldives Civil Aviation Authority requirements, or road glare, at specified sites; and

- Sub-array height limitations as a function of distance from runways, as per Aviation Obstacle Surface Limit guidelines, at specified sites.

Further description of constraints is in Part E.2 and E.3.

    - General requirements

      - General

- The entire array structure shall comprise of the following:  foundations, array frames which provide the main mechanical support, and array super-structure onto which the PV modules are bolted.

- In case of need for any emergency maintenance of coastal breakwaters along the array route, and to allow access for construction equipment under that scenario all array frames are to be removable from foundation via bolts, and all bolts holding the entire structure are to be stainless or removeable.

      - Foundations

- Array foundations to strictly observe the available foot prints to avoid interference and damage to existing cables, pipework.

- Array foundations may be screw piles, or concrete piles or any other design as necessary.

- Refer to Section E.4. Construction Specification.

      - Array frames

- Array frames may be either anodised aluminium, or steel.

- Array frames of steel to be hot-dipped-galvanised against corrosion in sea salt environment, Refer to Section E.4. Construction Specification.  (E.4.5)

      - Array superstructure

- Array super-structure for module mounting is recommended to be anodised aluminium.

- All module attachments to be via standard clamp mounting methods, with in-built module earth continuity, similar to Part Section E.1.2.5 Roof mount structures.

      - Roof Mounting Systems

- For rooftop sites, the mounting structures installed under the Roof Lease Agreement shall meet minimum standards as follows:

- The array support structures shall be non-tracking (fixed), after installation. The tilt angle to the horizontal shall be in the plane of the roof sheets. Height of the lowest part of any module from the roof shall be 50mm and maximum 200mm.

- The array structure shall comprise of two main components supplied by the contractor:

  - Array roof attachment:  the means of attachment shall be multiple mountings onto the corrugated roof sheet profiles for better weight distribution, and not drilled into or attached to the rafters themselves.  A clamp type system or specialised system compatible with the trapezoidal roof sheet profiles shall be used with inbuilt waterproofing mechanisms, and are subject to approval of the Purchaser. Any attachments requiring drilling into the purlins or trusses shall require special prior approval and must be substantiated by roof loading calculations and weight distribution calculations.  The array mounting superstructure shall be bolted to these roof attachments.  The roofs are in all cases corrugated sheets of standing-seam type or trapezoidal/box type profile (typically MSP SeadeckTM roof sheets profile 26.5mm high, 26,0mm top edge, and 60mm at base, but dimensions and profiles of sheets to be confirmed by Supplier prior to order).

  - Array roof mounting superstructure: a standard approved anodised aluminium array mounting structure or profile for clamp-mounting of modules (refer for example, to Gracesolar™, Schletter™ systems or any other approved substantially functionally equivalent methods)

- The structure assembly shall accommodate such cable trunking and any array junction boxes as may be required to meet the requirements for module interconnection.

  - Cable trays shall be aluminium anodised or galvanized, and shall not heat to more than 80 degrees Celsius.

  - All junction boxes shall be IP65, and all cable gland seals shall be IP65 to prevent dangerous water ingress and safety hazard.

- All aluminium shall be bare anodised. Any damage shall be treated.  Stainless steel nuts and bolts shall be used for holding the components together.

- All precaution shall be undertaken to avoid any risk of corrosion due to electrolytic reaction between modules and the roof top mounting structure and building roof.

- The array support frames and mounting superstructure shall be provided in several identical sections (or sub-arrays) to allow for any thermal expansions and contractions without damage to roof or modules.

- Each panel shall be attached to the array mounting super-structure in four places using the clamp-mount method on the module frames, and the panel shall not itself form part of the support structure, to prevent torsional forces on the panel. The mounting structure and clamping arrangement shall be sufficiently versatile to accommodate the panels.

- The structure and clamp mounting arrangements shall be compatible with the earthing requirements. Earthing clamps may additionally be required.

      - Orientation and tilt and FAA/MCAA glare mitigation compliance

- Array orientation and tilt angle to be as per Part E.2: Specific Requirements for each Array.  This requirement is non-negotiable and shall be strictly applied.  No further analysis is required by Bidders other than to comply with these requirements at time of bidding however at detailed design stage contractor shall verify the glare assessments conducted by the client and ensure glare mitigation compliance.

- For specified sites in close proximity to airports, the objective is to ensure glare mitigation compliance for glare to aircraft and airport control tower.

  - Glare mitigation compliance as per the following requirements of Federal Aviation Administration, USA and Maldives Civil Aviation Authority as demonstrated by SGHATTM.:  Solar Glare Hazard Analysis Tool.

- The basic requirements as per FAA Interim Policy 2013-24729 FAA – Review of Solar Energy Systems on federally obligated airports document are as follows: - No potential for glint or glare in the existing or planned Airport Traffic Control Tower (ACTC) cab - No potential for glare or “low potential for after-image” along the final approach path for any existing landing threshold or future landing thresholds (including any planned interim phases of the landing thresholds) as shown on the current FAA-approved Airport Layout Plan. The final approach path is defined as two (2) miles from fifty (50) feet above the landing threshold using a standard three (3) degree glide path) .

  - Requisite SGHAT fight path analyses have been undertaken by purchaser to ensure preliminary compliance. After contract award, contractor shall ensure sane compliance.

- For specified road-side sites, road pathway glare mitigation has been analysed and mitigated by specification of array tilt and orientation.

- Array frames shall be of fixed orientation or azimuth.

- Limited tilt adjustment is required for airport arrays.

  - The adjustment range shall be both plus & minus 3 degrees in one increment each way. This adjustment shall be used post-installation for corrective purposes and any fine-tuning necessary to minimise glare to airport.

  - Either array frame or array superstructure to be tilt-adjustable to the requirements above.

      - Mechanical strength and wind loading

- Entire structure and foundations of final design to be certified by engineer.

- Bidders are to base wind loading calculation on their best estimates for applicable wind variations factors.   Bidder to follow standard engineering practice with regard to ensuring sustained structural integrity.  Refer to Section E.4. Construction Specification.

- A provisional design of the structure is to be submitted with this tender showing strength and size of metal structures, cross-connectors and module brackets. The successful Bidder is obliged to provide a final design of the PV array structure and the module layout to the Employer for approval prior to finalization.

  - Array structure specific requirements

    - Site summary

Notes:

- Arrays in proximity to airports shall comply with the exact stated tilt and orientations, as per glare mitigation requirements of section E.1.2.6.

- Roadside arrays may minimize road glare by careful consideration of orientation and tilt.

- All other arrays may adjust tilt and orientation to suit.

- Helioscope Analyses & Glare Analysis in online Data Room is based on maximum site carrying capacity kWp, not RFP capacity bid out which may be lower due to other constraints.

Table 10: Array structure specific requirements

|  |  |  |  |  | Helioscope sub-arrays (may differ from RFP requirement) |  |  |  |  | Glare Analysis |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Island | Location | Site Ref | Array structure | Location | Helioscope site no. | tilt | orientation | kWp | Total | Glare consideration | Level |
| Sh. Funadhoo | Funadhoo Airport | 13.1 | Elevated array | Area 1 Airport North | Segment 1 | 10 | 100 and/or 280 | 280.5 | 681.9 | Airport | Critical |
|  |  | 13.2 | Elevated array | Area 2 Airport South | Segments 1-2 | 10 | 100 and/or 280 | 191 |  | Airport | Critical |
|  |  |  |  |  | Segments 3-4 | 10 | 86 and/or 266 | 74.5 |  | Airport | Critical |
|  |  | 13.3 | Elevated array | Area 3 Airport East | Segments 1-2 | 10 | 100 | 21.5 |  | Airport | Critical |

  - Diagrams of Typical array structures and REPRESENTATIVE conceptual designs

## Typical array structure drawings for the main types cover:

  - Elevated array:  A wide array (span exceeding 3m) requiring safe pedestrian and leisure access beneath, with lighting

  - Elevated walkway: Narrow array (span below 3m) requiring safe pedestrian access beneath, with lighting

  - Elevated carport: Carport size requiring safe car access to standard dimensions beneath, with lighting

  - Road Canopies: Arrays covering full widths of sections of roads open to traffic

  - Road Median Arrays: Arrays restricted to median areas of link road

The following height requirements apply for the categories of installation structures and this is non-negotiable:

  - Elevated arrays, Elevated walkways and Elevated carports:  Minimum “clear height” required is 3m in general. However, if the installation is for areas with requirements for clear view like harbour, beach or tourisms this should be 3.5m.

  - Road Canopies & Median Arrays: Clear height of minimum 4.5 m

The blueprint solutions below are proof of concept of array frame and foundation designs, considering all constraints elaborated in Sections E.1: General requirements for PV array structures, and Section E.2: Array structure specific requirements.

## Refer to Data Room:  for detailed high-resolution concept drawings for each concept category mentioned below.

Table 11: Array structure conceptual designs for sub-array categories

|  | Drawings |  |
| --- | --- | --- |
| Array structure category | Drawing reference | Drawings in Data Room |
| Elevated array | Concept | Elevated Arrays Concept.pdf |
| Elevated walkway | Concept | Elevated walkway Concept.pdf |
| Elevated carport | Concept | Elevated carport Concept.pdf |
| Road canopies | Concept | Road canopies concept.pdf |
| Road median arrays | Concept | Road median concept.pdf |
| Road median arrays | 3D Renders | Road median render folder |

  - CIVIL WORKS CONSTRUCTION SPECIFICATION

Contents

E.4.1.	Standard and Codes	138

E.4.2.	Drawings and Specifications	138

E.4.3.	Loading Specifications	138

E.4.4.	Site Clearance	139

E.4.5.	Metal works and Corrosion resistance	140

E.4.6.	Concrete Works	140

E.4.7.	Concrete Formwork and Falsework	144

E.4.8.	Steel Reinforcement	145

    - Standard and Codes

- The successful Bidder (herein referred to as the “Seller” as the term is defined in the PPA) shall, perform the Works in compliance with all regulations, standard specifications or statutes of the Government of Maldives unless otherwise conform to this specification.

- Any physical works can commence following the required Environmental and Social Assessments and clearance of such assessments from both the World Bank and Environmental Protection Agency (EPA). All mitigation measures and monitoring requirements under the respective ESIA or ESMP needs to be adhered by the Seller both during construction and operational phase of the project.

- The current British Standard Specifications and Codes of Practice shall apply to and form part of these specifications unless otherwise specified in respect of all materials and works to which they have application.

    - Drawings and Specifications

- Drawings and Specifications are intended to complement each other, so that if anything is shown on the Drawings, but not mentioned in the specifications or vice versa, it is to be furnished and built as though specifically set forth in all three. If any discrepancies, errors, ambiguities or omissions occur in the Drawings or Specifications, the same shall be referred to the Employer before proceeding with the Works, and the Employer’s decision on such discrepancies, errors, ambiguities or omissions shall be final.

- In addition to the Drawings and Specifications attached hereto, the Seller will during the progress of the Works furnish additional Drawings, Specifications, and instructions as may be necessary, in the opinion of the Employer for the purpose of the proper and adequate execution and maintenance of the Works, and the Seller shall make his work conform.

    - Loading Specifications

- Applicable design standards are but not limited to;

  - BS 8110: 1- 1997 - Code of practice for design and construction

  - BS 8110: 3- 1985 - Code of practice for special circumstances

  - BS 8110: 3- 1985 - Design charts for beams and columns

  - BS 6399: 1 - 1996 ‐ Code of practice for dead and imposed loads

  - BS 6399: 1 - 1997 – Code of practice for wind loads

  - BS5950: 1‐2000 ‐ Structural use of Steelwork in Building

  - BS 648: Weights of building materials

- Applied loads on the PV structures excluding self-weight of material and any superimposed load due to Solar panels are;

  - Basic Wind Speed 	= 35 m/s (Based on BS 6399-2: 1997) or 120km/h

  - Base Wind Pressure 	= 0.6 kPa

- Initial Allowable soil bearing capacity can be assumed as 100 kPa. To be determined after a detail soil investigation.

- Density of Materials;

  - Normal reinforced Cement Concrete	24 kN/m3

  - Structural Steel			78.5 kN/m3

    - Site Clearance

    - The term “Consultant” used here means a person with relevant expertise representing the Employer and hired for the purpose of monitoring the civil works of the project.

- All setting out points, benchmarks, site rails, pegs and other survey points shall be clearly marked and protected from damage or disturbance during the execution of the Works

- A survey of the existing site shall be made and the results of same submitted to the Consultant before commencement of any cut and fill work or excavation works. In this survey, the nature of the soil, cut area or any fill areas are to be identified. The Seller shall also identify where to collect and stack the materials for which necessary site clearance shall have to be made at his own cost.

- The Site shall be cleared of all vegetation, rock, boulders, etc. and surface soil shall be removed as directed by the Consultant. Any neighbouring trees that are to be retained and not interfering with the PV array structures shall be protected from damage. Where applicable through the respective environmental clearances, some identified trees may need to be translocated to an alternative location of the island.

- Spreading, levelling and consolidating on site where required, shall be made with suitable surplus excavated material obtained from the Site. Other soils used for filling shall be approved by the Consultant

- The Seller shall dispose all unsuitable and surplus excavated material

- The Seller shall tidy up and leave the Site in a clean and sanitary condition at all times during the execution of the Works.

- Excavation shall be performed to the required depth as shown in the Drawings.

- Excavation area shall be protected from any water flowing in. Sides of excavations must be shored or inclined to retain excavation unless otherwise specified

- Excavation shall extend a sufficient distance footings and tie beams to allow space for placing and removing shoring and formwork, for performing all work in the excavations and for the inspection of same.

- Excavated material shall be deposited within specified areas as directed unless otherwise specified.

- Stacking or excavated materials shall be done at places approved by the Consultant and he shall have recorded the original ground levels of such places jointly with the Seller before commencement of stacking operation.

- All foundation trenches shall be excavated to the full widths and depths shown on the drawings or to such greater or smaller depths as may be found necessary in the opinion of the Consultant and so instructed by his representative.

- All foundation pits shall be refilled to the original surface of the ground with approved materials, which shall be well consolidated as instructed by the Consultant.

- The Seller shall erect temporary barricades around the excavations and if necessary, make provisions of red lamps.

- Where the excavation level is below the natural water table and it is necessary to pump continuously from the excavation or to install a specialist type of dewatering equipment around the perimeter of the site or excavation, the Seller will be responsible for ensuring the safety and stability of all adjoining structures and services or utilities above or below ground level.

- Continuous or permanent de‐watering of the excavation or Site may not be undertaken without the written approval of the Consultant and the methods to be employed shall also comply with Codes of Practice and Local Authority requirements.

- The water pumped from the excavations or well points shall be pumped to disposal points or sumps approved by the Consultant and the relevant government authority and if so required be passed through settling tanks before disposal.

Unless prior approval has been obtained no water must be disposed of in the sewer systems.

- All earth used for filling shall unless otherwise stated, be selected hard dry material from the excavation. The maximum dry density of the fill material shall be not less than 1600 kg/m3.

- The backfill of excavations shall be placed in horizontal layers not exceeding 300mm in thickness. Each layer shall be compacted by hand or other mechanical means to the required density before the next layer is added

- Care shall be taken when filling or back‐filling to avoid any wedging action or eccentric action upon or against the structure of the work.

- Before placing of fill, the surface of the sub‐grade shall be compacted at optimum water content to the same percentage of maximum dry density required of subsequent lay.

- The Consultant will inspect all compacting devices that the Seller proposes and shall have the right to reject any device which he feels is unsuitable for the job.

- Each layer shall be compacted to 90% of the modified compaction. No back filling shall be carried out until the wall concrete has achieved its full works cube strength and care shall be exercised so as not to damage the external tanking membrane and its protection.

    - Metal works and Corrosion resistance

- The following requirements shall apply to all steel elements

- EN ISO 14713-1 (Zinc coatings – Guidelines and recommendations for the protection against corrosion of iron and steel in structures; Part 1: General principles of design and corrosion resistance) to be followed for specifications regarding corrosion protection of all superstructure steel.

- Corrosivity category for the superstructure shall be taken as C5 (Temperate and subtropical zones, atmospheric environment with very high pollution (SO2: 90 µg/m3 to 250 µg/m3) and/or important effect of chlorides, e.g. industrial areas, coastal areas, sheltered positions on coastline) table 1 BS EN ISO 14713-1:2009

- The durability class shall be taken as H from 10 years to 20 years.

- For aluminium elements, ISO 7599:2018 (Anodizing of aluminium and its alloys — Method for specifying decorative and protective anodic oxidation coatings on aluminium) to be followed for corrosion coating.

- Any screw piles used as foundation for the support structure of PV installations are to undergo performance tests and confirm with BS 8004:2015 (Code of practice for Foundations).

    - Concrete Works

- Concrete generally: To BS 8500-2:2015.

- Other requirements: For concrete in the ground, requirements for concrete quality in BRE Special Digest 1: 2005 take precedence over those in BS 8500-1.

- BS 882 Specification for Aggregates from natural source for concrete

- BS 5328 Part 1:1997 Guide to specifying concrete

- BS 5328 Part 2:1997 Method for specifying concrete mixes

- Exchange of information: Provide concrete producer with information required by BS 8500-1:2015, clauses 4 and 5.

- Not allowed for using OPC for concrete works in contact with sea water. Special requirements for cement/ combinations: Sulphate Resistant Cement for concrete according to the soil investigation report. To BS 4027:1996 or ASTM Type 5.

- Cement shall conform to BS 12

- Cement shall be stored in a manner to prevent weathering.

- Cement caked even to the slightest extent shall not be used. Such cement and rejected cement shall be immediately separated from other bags of cement so that they shall not be mistaken for others.

- Water to follow the related BS and shall be clear and free from organic impurities, having a pH value in the basic range of 7-9.  The organic impurities should not exceed the following limits:

| SN | Maximum Concentration | Limits, ppm |
| --- | --- | --- |
| 1. | Chlorides as Cl- | 250 |
| 2. | Sulphates as SO42- | 350 |
| 3. | Alkali Carbonate and Bicarbonate | 500 |
| 4. | Total dissolve ions, incl. 1, 2 and 3 above | 2000 |

- For concrete mixing on site Accuracy of measuring devices: To BS EN 206-1

- Tolerances for quantity of constituent material: To BS EN 206-1, table 21.

- Mixing: To BS 8000-2.1, wherever applicable.

- For concrete testing at early age strength tests of 7 days and Conformance testing of 28 days.

- Testing: To BS EN 206-1, Annex B and BS 8500-1, Annex B.

- All foundations and beams below ground surfaces to be laid on lean concrete with min thickness of 50mm prior laying building foundation and foundation tie/Ground beams, and also the contractor to highlight the proposed water proofing system for sub structure items.

- Materials used in the Works shall be new, of the qualities and kinds specified herein and equal to approved samples. Delivery shall be made sufficiently in advance to enable further samples to be taken and tested if required. No materials shall be used until approved and materials not approved shall be immediately removed from the Works.

- Cement shall be of recent manufacturer and used within 6 months of manufactured date

- The Seller shall with each fresh consignment of cement delivered to the site furnish the Consultant/Employer with a copy of the Manufacturer's statement of compliance with the above Standard Specifications together with the date of manufacture, certified by an independent agency in the country of origin and its date of delivery to Site

- Check tests will be required by the Consultant/Employer. These tests shall be carried out at the Seller's expense

- Any cement failing to meet the required standards will be rejected and replaced at the Seller's expense

- Any cement not conforming to BS 12 shall not be used unless otherwise approved by the Consultant/Employer

- Fine aggregate shall be river sand conforming to BS 882.

- Coarse aggregate shall be crushed stone excluding limestone or derivatives of limestone conforming to BS 812.

- Aggregate shall not contain injurious amount of rubbish, dirt, organic impurities and other foreign matters.

- Strength of aggregate shall be more than that of hardened concrete paste.

- Shape of coarse aggregate shall not be flat or slender.

- Aggregate to be used in concrete shall possess the qualities indicated in the following tables.

- In case of using fine aggregate of 0.01% or more water soluble chloride content, the necessary measures for corrosion inhibiting of reinforcement shall be instructed by the Consultant/Employer

- The maximum size of coarse aggregate shall be 25 mm

- Sources of aggregate shall be to the approval of the Consultant/Employer and samples of aggregate from the proposed source shall be submitted to the Consultant/Employer at least 28 days before its intended use.

- Aggregate shall be stored in a manner effectively separating coarse and fine aggregate according to type and shall be prevented from inclusion of dirt, rubbish and other undesirable foreign matters

- Coarse aggregate shall be unloaded and piled in a manner not to cause segregation of small and large particles. Aggregate to be stored in piles shall be in mounds of moderate height and at a location where good drainage is provided

- Water shall not contain injurious amount of impurities that may adversely affect concrete and reinforcement

- Ground water shall not be used for concrete works

- Water shall be obtained from a public supply where possible, and shall be taken from any other sources only if approved by the Consultant/Employer

- Only water of approved quality shall be used for washing out formwork, curing concrete and similar surfaces.

- Mix ratio for reinforced concrete shall be determined based on the design drawings. A minimum base reinforced concrete strength shall be 25 MPa

- The required slump of concrete shall be 100 mm.

- Construction joints, shall be made at locations indicated on the Approved Design Drawings, or as specified or directed by the engineer. Construction joints, shall not be made at other locations, without the concurrence of the Resident Engineer. All joints shall be provided in compliance with the structural Engineer Practice and shall comply with BS 8007 and 8110.

- In Field-mixed Concrete all materials shall be measured by volume for each batch and water may be measured volumetrically.

- Mixing time for each batch shall be not less than 2 minutes and not more than 20 minutes

- The Seller shall have all quality control tests report ready for submission as required by the Consultant/Employer.

- For the estimation of compressive strength of concrete in compressive strength tests, when the average value of compressive strength of concrete obtained in a test is not less than the specified design strength, it shall be qualified to have passed the test. In case of failure to the above requirements, the Seller shall take necessary measures such as to perform appropriate test as instructed by the Consultant/Employer.

- The Seller shall establish manner and schedule for transporting and placing of concrete and obtain approval of the Consultant/Employer.

- Concrete shall be transported in a manner to minimize segregation, spill, age and other changes in quality thereof.

- Concrete shall be placed and consolidated in a manner to insure uniformity and optimum density.

- In case of rain or other conditions that may affect the quality of concrete during concreting, the Seller shall take necessary measures as instructed by the Consultant/Employer.

- Concrete placing shall be proceeded to keep the surface of placed concrete as horizontal as possible.

- Concrete shall be continuously poured to compact around reinforcing bars and corners of formwork.

- The maximum time interval between placement of continuous concreting shall not exceed 0.5 hours. However, when special measures are taken this time limit may be changed according to instruction or approval of the Consultant/Employer.

- Vibrating of concrete and tapping of formwork shall be performed to wall, column and other places difficult for concrete to proceed. Proper number of workers for placing and compacting concrete shall be arranged.

- Vibrator shall be operated for concrete called for water tightness, difficult portion for concrete to proceed and other cases directed by the Consultant/Employer. However, vibrator shall not be touched reinforcing bars and shall not be operated more than 30 seconds at same spot.

- After concrete has been placed, the concrete surface shall be kept moist by sprayed with water or by other appropriate methods, and shall be protected from direct sunlight and rapid drying. This curing period shall be for not less than 14 days.

- As a rule, no foot traffic or loads shall be permitted on concrete for at least 24 hours after placement.

- Tests to be provided by the contractor for approval from the consultants are as stated below;

  - Cement Tests;

    - Setting test (shall be conducted once in every manufacturer)

    - Soundness test (shall be conducted once in every 2,000 bags)

    - Compressive strength test (shall be conducted once in every 2,000 bags)

- Aggregate test:

  - Grading and fineness modules.

- Fresh concrete

  - Slump, air content, shall be conducted daily, and more often at request of the Consultant/Employer.

- Compressive strength test of concrete

  - In order to assume estimated strength of concrete in structure, compressive strength test shall be conducted for prepared test pieces on the 7th day and 28th day and those test pieces shall be made for sampling at placing of concreting.

  - Strength test shall be conducted for each of the following conditions: each day pour, each class of concrete, each change of supplies or source and each 100 cubic meters of concrete or fraction thereof. The number of test pieces to be used in a test shall be not less than 3 for each test of the 7th day and the 28th day unless otherwise instructed by the Consultant/Employer.

  - Test pieces shall be made in accordance with British Standards, and sampling shall be taken as near as possible at the point of placement.

    - Concrete Formwork and Falsework

- Form works to comply with BS 5975:1996.

- Formwork shall be performed to obtain accurate concrete in accordance with the designated drawings.

- Formwork shall be firmed and secured to bear the force of concreting and tightened to avoid cement paste seeping.

- Sheathing for formwork shall be waterproof plywood of not less than 12 mm thick. Joint of sheathing shall be butt joint and firmly assembled. In case of using wood board for sheathing, boards shall be 15 mm thick and applied planer. Joint shall be tongued and grooved unless otherwise approved by the Consultant/Employer.

- Timber form boards for sheathing where used for fair-faced concrete shall be of such new materials as not to cause any defects to the surface of the concrete. Special care shall be taken in fabrication, storage and protection of these boards.

- Form oil shall not have injurious effects on quality of concrete nor to bonding of surface finishing materials and shall be subject to approval of the Consultant/Employer.

- Formwork shall be designed to withstand construction leads during concreting, lateral pressure of fresh concrete, shock and vibrators due to concrete placing.

- Formwork shall be free of injurious leakage of water, easy to remove, and shall not damage concrete at removal.

- Supports shall be provided with the adequate horizontal and diagonal bracing and/or stays to prevent collapsing, heaving and twisting of formwork due to horizontal loads working during concrete placing.

- Erection of formwork, and transportation and storage of materials thereof shall be started only after previously placed concrete has reached an age which acceptance of these loads will not have any adverse effect on the concrete.

- Sheathing shall be installed tightly so as not to permit cement paste or mortar to escape from joints.

- Pipes, boxes and other embedded hardware shall be properly secured to sheathing or others so that they will not move during concrete placing.

- Shoring shall be erected paying special attention to safety.

- If sheathing is reused, the surface in contact with the concrete shall be thoroughly cleaned off and sufficiently repaired before reuse. In case of using for fair-faced concrete, the same sheathings shall be used twice after approval of the Consultant/Employer.

- Formwork shall be inspected by the Consultant/Employer prior to placing of concrete.

- Preparation prior to placing of concrete, the place where concrete is to be deposited shall be cleaned and sheathing shall be sprinkled with water. Subsequently, water accumulated in the form shall be removed.

- The minimum period for keeping the forms in position and for watering after laying the concrete shall be as stated below, except otherwise specified in drawings. Forms shall be removed in such a manner as to ensure the complete safety of the structure, so that there is no shock or vibration as would damage the reinforced concrete.

- The responsibility for the safety of the concrete shall rest entirely with the Seller and the Seller shall be held liable for any damage done and shall have to make good the same at his own expenses.

- The Seller shall inform the Consultant/Employer when he intends to remove shuttering and shall obtain his consent, but the consent of the Consultant/Employer shall not relieve the Seller of their responsibility.

- The minimum time for formwork to remain in place shall be as stated below

Vertical sides of beams and columns	24 hours

    - Steel Reinforcement

- General Standards for reinforcing steel to follow BS 4449, BS 4482, BS 4483 or BS 6744.

- Cutting and bending: To BS 8666.

- Fixing reinforcement Standard: To BS 7973-1 and -2.

- Source of reinforcement: Companies holding valid certificates of approval for product conformity issued by the Maldivian Government

- Plain Bar Reinforcement to Comply with: Standard: To BS 4482, 8110.  Yield Strength: 250 MPa

- Ribbed bar reinforcement to Comply with: Standard: To BS 4449, 8110.  Yield Strength: 460 MPa

- Any other non-specified reinforcing steel shall be used only with the approval of the Consultant/Employer.

- Reinforcing bars shall be cleaned before use so that it is free from rust, oil, dirt or other coatings that reduce bond.

- The reinforcement shall be bent cold in an approved bar bending machine.

- Preferably bars of full length shall be used. Lapping of bars where necessary shall conform to BS1487 ‘Bending Dimensions of Bars of Concrete reinforcement.’

- Concrete cover for reinforcement shall be as follows unless otherwise specified in the design drawings:

  - Structural members below ground with waterproofing membrane = 50mm

  - Structural Members Below Ground in Contact with Sea Level or Soil = 75mm

  - Columns= 35-40mm

  - Beams= 35-40mm

- Reinforcement intended for contact when passing each other shall be securely tied together with binding wire

- Binding wire shall be turned in from the formwork and shall not project beyond reinforcing bars.

- All reinforcement shall be inspected by the Consultant/Employer and approved before concrete is placed in the forms.

END

- Environmental, Social, Health and Safety Requirements

## 4.1 Information Provided in Data Room

The following information is provided in the Data Room. Link for Data Room is provided in Part G - Supplementary Information.

- Environmental and Social Screening reports for all the sites with screening decisions for all the sites. Screening was undertaken both through Environment Protection Agency (EPA) and the World Bank. In terms of level of assessment, the more stringent of the screening assessment needs to be undertaken. As per the screening decisions Environmental and Social Management Plan (ESMP) is required for all the islands.

- Glare Assessment for Sh. Funadhoo (Note: As per Environmental and Social Management Framework (ESMF) developed for the project it is the responsibility of the successful bidder to repeat and verify these assessments).

- Structural Assessment of all the buildings to be utilized for the project (Note: As per ESMF developed for the project it is the responsibility of the successful Bidder to repeat and verify these assessments).

- Environmental and Social Management Framework (ESMF), Stakeholder Engagement Plan (SEP) and Labour Management Procedure (LMP) for ARISE project.

## 4.2 Specific Requirements

### 4.2.1 At the bidding Stage

- Bidders shall submit copy of the Environmental and Social Management System (ESMS) of the company[1].

- Bidders shall submit copy of their Environmental Certifications (ISO14000 series or other equivalent [e.g.: European Eco-Management Audit Scheme][2][3].

- Bidders shall submit copy of their Occupational Health and Safety Certifications (ISO 45001, OHAS 18001 or other equivalent)2.

- All Bidders shall submit a Draft Community Engagement Plan indicating an approach for disseminating project information and establishing dialogues with the island community through training, employment opportunities, awareness programs, educational seminars for locals and others initiatives. The plan should cover yearly activities that will be undertaken and should focus on all the island communities where the project is implemented. At minimum, the Plan should specify the following:

- Awareness/Educational activities that will be undertaken on a regular basis in project locations.

- Plan to engage local communities in employment, trainings and other Project initiatives.

- Plan to disseminate project information to local communities.

- Schedule of implementation of the Plan

- All Bidders shall submit its Code of Conduct that will apply to Bidder’s Personnel (as defined in Project Agreements), to ensure compliance with the Contractor’s Environmental and Social (ES) obligations under ESMF and Project Agreements. The code of conduct should focus on general, health and safety of Contractor’s Personnel. In addition, should cover aspects related to prevention of sexually transmitted diseases and prevention of women and child trafficking, gender-based violence, sexual harassment, and sexual exploitation and abuse. At the implementation phase, the code of conduct should be translated and provided in a language that is understandable to the contractors 'personnel.

[1] If a JV ESMS of each individual member should be submitted

[2] If a JV certificates for each individual member should be submitted

[3] Only Bidders with verified certification or another equivalent will qualify to undertake this Project. Bidders who do not have the specified certification should provide a written commitment to obtain the required certification prior to execution of Project Agreements.

### 4.2.2 Post Contract Awarding

- The Employer will review the ESMS of the Company identifying and clearly indicating if there are any gaps in line with the pre-requisites of the IFC Performance Standards. Where there are any gaps the successful Bidder will be required to amend the ESMS accordingly.

- The Employer will verify the authenticity of the ISO 14001, ISO 45001, OHAS 18001 or another equivalent certificate submitted by the successful Bidder.

- As per the contractual operations of the ARISE operation the successful Bidder shall ensure the following:

  - Environmental and Social Management Plan (ESMP) report(s) for each project location shall be submitted to MCCEE and EPA within 90 days of contract effectiveness.

  - Allocate 2.5 percent of the total contract value as Environmental Social Health Safety (ESHS) Performance Security. The security should be submitted within 60 days of letter of acceptance.

  - A revised and updated Community Engagement Plan should be submitted to MCCEE following community consultation and feedback within 90 days of contract effectiveness

  - The ESIA will be carried out and meet the criteria presented in the Environmental and Social Management Framework (ESMF) of the ARISE operation and adhere to the stipulated standards including those on management of labour as per the Labour Management Procedures (LMP) and Stakeholder Engagement Procedure (SEP) of the ARISE operation (link:  https://www.environment.gov.mv/v2/en/download/10026 )

  - The ESMP reports will be subject to the clearances of the World Bank and EPA and the successful Bidder cannot proceed with any interventions on the site prior to receiving the said clearance.

  - The successful Bidder shall submit monthly monitoring reports as per the ESMP to the MCCEE and EPA.  The successful Bidder shall hire a qualified Environmental Specialist and Social Specialist prior to carrying out any works on the project site and submit details of the hired personnel to the Employer. With relevant experience and qualification same person can assume these two roles. The ToR for ES Specialist is provided in Annex 18 of the ESMF.

  - All sites will be subject to independent supervision by the Employer during project implementation stage for adherence to ESMP requirements.

  - If any non-compliance issues respective to ESMP/ ESMS/ ESMF/ LMP/ Code of Conduct or any other WB or project safeguards requirements are identified the winning bidder should be notified by the Employer clearly identifying the nature of the failure and the timeframe given to remedy the failure. If the failure is not remedied within the timeframe identified in the written notice, the Employer will consider the winning bidder as non-compliant towards environmental and social safeguards requirements and necessary remedial action will be taken by the Employer through a third party. However, if such failure to perform is not reasonably capable of being remedied within the period stipulated in the notice but is reasonably capable of being remedied, the winning bidder shall have such additional time, not exceeding sixty (60) Days, as is reasonably necessary to remedy such non-performance, (before the Employer  shall have the right to invoke the Environmental, Social, Health and Safety Performance Security) so long as the winning bidder promptly commences and diligently pursues such remedies. The cost of third party and any incurred monitoring charges will be deducted from ESHS Performance Security.

## 4.3 General Safeguards Requirements

In addition to site specific requirements, the successful Bidder is required to adhere to Environmental and Social Management Framework (ESMF), Labour management Procedures (LMP), Stakeholder Engagement Plan (SEP) developed for the project in accordance to World Banks Environmental and Social Framework (ESF) and the applicable Environmental Social Standards (ESS) for the project. Specific requirements for Contracted Workers[2]  are defined sunder the Labour Management Procedures (LMP).

These documents and translation of executive summary of these documents can be downloaded from the data room and also from the link below:

https://www.environment.gov.mv/v2/en/download/10026

As per the LMP, the following mitigation measures in relation to contracted workers need to be followed (page 29 to 31):

### 4.3.1 General Provisions

- List of workers to be utilized in relation to the project, with proof of employment will be required to be submitted to Project Management Unit (PMU) of the Employer by all investors/contractors.

- Construction work can only commence once the following conditions are met:

- Toolbox training completed by all staff employed by the contractor

- All the required Personal Protective Equipment are acquired by the contractor for all workers

- Any newly employed party by the contractor will be required to complete the toolbox prior to commencing any physical work.

- As per the provisions of the employment, all parties employed by any contracted party will be above 16 years of age. For those between 16 to 18 years of age, consent of the parent will be required as per Law No. 2/2008(Employment Act). In addition, all other provisions of the Act highlighted previously regarding employment of a minor will apply. All contractors and investors will be required to provide document evidence (passport, identity card or birth certificate) confirming age of employees to PMU prior to involving them on activities of the project. In addition, for minors consent of the parent shall be provided in writing together with evidence of legal guardianship.

- Maximum working hours for staff will not exceed the maximum limit set in the Employment Act, i.e. 48 hours a week. To confirm this, monthly attendance and duty sheets need to be submitted to PMU during the construction phase.

- An internal transparent and accountable system will be established within the Project Company to tackle issues of sexual harassment, physical and psychological harassment and workplace bullying. Details of this system will be shared with PMU prior to signing any contracts.

- All contracted staff will be made aware of grievance redress mechanism available for the staff.

- The leave policy of the company will be shared and confirmed that it is in line with national laws and regulations.

- All foreign parties employed by all contractors/investors will have valid work permit. The work permit details will be shared with PMU.

- All vehicles used by any contractor/investor for the purpose of the project will have valid registration, insurance and road worthiness.

- Should take specific health and safety measures to prevent spread of Covid 19 within labour force and from labour force to community as per best practice guidance given by Health Protection Agency of Maldives.

### 4.3.2 Project work Site

- All provisions that are required under Health and Safety Regulation for Construction Industry (2019/R-156) will be strictly adhered to.

- All workers will be provided with Personal Protective Equipment (PPE) by the contractor/Investor. In this regard the following will be observed:

- Hard hats should be used by all workers when undertaking construction and when undertaking inspections at height.

- Enclosed safety shoes should be worn by all construction workers.

- Safety harness should be used by all workers when climbing heights at project sites.

- Electrical Protective gloves should be provided to workers when dealing with electrical components.

- Chemical protective gloves should be provided to all workers when dealing with any chemicals.

- Construction safety goggles should be worn by all construction workers.

- Ear plugs should be worn by all construction workers working in environments with high noise (working above 75 decibels).

- Masks should be worn when dealing with chemicals and when working in dusty environments.

- All chemicals will be stored on hard surfaces and should be covered.

- Portable drinking water will be made available at the construction site during construction phase.

- Adequate safety signs will be installed at the work site giving clear direction. These will be provided in addition to English in the language of the workforce.

- Construction work site will be demarcated & fenced, and warning signs will be displayed both in English and Dhivehi.

- When construction is undertaken, clearly demarcated bins for waste disposal will be placed and emptied daily.

- Open pits will not be left for water to accumulate for a long time.

- Any stockpiled sand will be covered to prevent sand particles from being airborne.

- All vehicles and equipment used for the project will be used by well trained personnel.

- Any scaffolding used will be to British Standard (BS1139).

- When working at night, adequate lighting will be provided.

- A designated toilet facility will be available within 10 minutes of the construction site.

- Breaks will be given to the workforce during mealtimes.

- The site will be cleaned daily following completion of day’s work.

### 4.3.3 At contractors’ offices and temporary accommodation site(s)

- Constant and reliable electricity supply will be available at project office and accommodation site.

- Shower and toilet facilities will be available at temporary accommodation site.

- Toilet and drainage will be connected to local sewer system, where not available septic tanks will be used for treatment prior to disposal.

- A minimum ratio of 01 toilet/shower per 20 workers will be maintained. Separate facilities will be provided for men and women.

- Individual bedding will be provided to all workers.

- Storage space for individual belongings will be provided for all workers.

- Male and Female workforce will be housed separately.

- Designated locations for waste disposal with clearly marked bins will be established. Bins will be emptied daily.

- Sufficient lighting and cooling systems will be established.

- Portable drinking water will be provided.

- The site will be cleaned daily.

- Monthly inspections to determine pest infestation of the site will be undertaken.

- Meals to the site will be prepared from a Health Protection Agency (HPA) certified facility (whether food prepared on site or off site).

To ensure enforcement of the aspects highlighted for the contracted workers by the contractor, the conditions highlighted under this section will be included in the contracts signed with all contractors.

4.3.4 Generic ESMP recommended to be followed when preparing ESIA/ESMP

Given below is the generic ESMP that is recommended to be followed when preparing project specific ESIA/ESMP

| Aspect | Indicative Mitigation Measures |
| --- | --- |
| Construction Site and Construction Workers | - All provisions that are required under Health and Safety Regulation for Construction Industry (2019/R-156) should be strictly adhered. - All workers should be provided with Personal Protective Equipment (PPE) by the contractor/Investor. In this regard the following needs to be observed: - Hard hats should be used by all workers when undertaking construction and when undertaking inspections at height. - Enclosed safety shoes should be worn by all construction workers. - Safety harness should be used by all workers when climbing heights at project sites. - Electrical Protective gloves should be provided to workers when dealing with electrical components. - Chemical protective gloves should be provided to all workers when dealing with any chemicals. - Construction safety goggles should be worn by all construction workers. - Ear plugs should be worn by all construction workers working in environments with high noise (working above 75 decibels). - Masks should be worn when dealing with chemicals and when working in dusty environments. - All chemicals should be stored on hard surfaces and should be covered. - Portable drinking water should be available at the construction site during construction phase. - Adequate safety signs should be installed at the work site giving clear direction. These should be provided in addition to English, Dhivehi and in the language of the workforce. - Construction work site should be demarcated & fenced, and warning signs should be displayed both in English and Dhivehi. - When construction is undertaken clearly demarcated bins for waste disposal needs to be placed and emptied daily. - Open pits should not be left for water to accumulate for a long time. - Any stockpiled sand needs to be covered to prevent sand particles from being airborne. - All vehicles and equipment used for the project needs to be used by well trained personnel. - Any scaffolding used should be to British Standard (BS1139). - When working at night adequate lighting should be provided. - A designated toilet facility should be available within 10 minutes of the construction site. - Breaks should be given to the workforce during mealtimes. - Firefighting equipment should be available at the construction site, at the workers accommodation and any storage areas used for the project. - The site needs to be cleaned daily following completion of days’ work. - The maximum working hours of all construction workers should be 48 hours per week as per the Employment Act of Maldives. |
| Storage and use of hazardous chemicals | - Any chemicals, fuels, waste oil and hazardous waste should be handled and transported carefully. All such chemicals and wastes should be stored and transported in sealed containers. Such chemicals and wastes should be stored in concrete hard surfaces to prevent impacts through any leakages. - Stored containers should be regularly inspected to identify any leakages. - The storage for any hazardous material and any refuelling activities should be undertaken outside the 20m Environmental Protection Zone of the island. - Any hazardous material storage areas should have firefighting equipment. - All vehicle/machinery and equipment operation, maintenance and refuelling will be carried out in such a fashion that spillage of fuels and lubricants does not contaminate the ground. - All activities should be undertaken in presence of an experienced supervisor. - Chemical protective gloves, goggles, masks and safety shoes need to be worn when handling any hazardous material. |
| Transport, handling and Storage of Solar PV | - Mechanical equipment (forklift) should be used when handling the containers with PV Panels during transport. - When moving packaged boxes to construction site, forklift should be used. - Transport should be coordinated with island council and Police. - If opening the box outside, please avoid rainy conditions. The rain will soften the box, may damage the modules and cause physical harm to the staff. - If the wind is too heavy avoid handling solar panels - The box should be placed horizontally to avoid tilting. - All staff involved in transport, storage and handling of Solar PV should wear gloves, safety shoes, safety goggles and hard hats. - Do not step on cartons containing PV modules |
| Operation of Batching plant | - Maintenance of the general site operations - Maintain all the equipment including dust collection equipment to prevent any leaks. - Concrete batching operation needs to be undertaken away from residential locations to minimize dust and noise impacts. - Concrete batching operation should be undertaken away from the Protected Areas. - All concrete mixing operations should be undertaken during daytime to minimize noise impacts. - All staff involved in batch plant operation should wear, safety hats, dust masks, safety shoes, goggles and gloves. - Required safety signs should be installed at the batching plant site with warnings for dust and noise highlighted. - Material handling and storage - Aggregates and sand required for concrete mixing should be handled and stored in an enclosed space. Enclosed storage bins or enclosed sealed bags. - As much as possible avoid using chemical concrete additives since they are more toxic. Instead, use sugar or wood based admixers. - Where chemical additives are approved to be used, need to store them in an enclosed space on a hard-impermeable surface. - Mixer feed operations - Use the enclosed batch mixer feed as dust prevention and visible emissions. - Use the spray device to prevent dust emissions. - Conduct all the mixing operations from an enclosed space to help prevent emission of dust. - Conveyors - To prevent dust emissions, the belt conveyors should be enclosed on both sides. - All conveyor transfer points should be enclosed by fitting the flexible seals to prevent dust. - The turning point of any conveyor should be provided with scrappers to prevent dust collection on the surface belt - Mixing and loading operations - Loading concrete should be in such a way that minimizes dust emissions. - All the air borne dust emission generated by material loading and mixing operations should be vented to fabric filtering system. - The concrete mixers and other vehicles should be cleaned off after the loading and mixing operations to wash off the mud, dust deposited on the wheels and body. - Fugitive dust - Use water sprays or dust suppression agents to reduce dust. - An air extraction and filtration system for collecting the generated dust should be installed. - Waste concrete - Collect the waste concrete in suitable washout pits where it becomes gravel, sludge and sand which can later be reused. - Waste water - Waste and contaminated water should be directed to onsite settling ponds and it can be reused later in for dust control, rinsing trucks exteriors. |
| Vegetation Removal and levelling | - Where trees and palms fall within the project footprint, option to relocate any trees and palms should be considered first. - If relocation is not feasible due to status of the tree/palm (for example palms that are too old and unlikely to survive elsewhere) or due to lack of available space to replant for every tree/palm removed two trees /palms need to be planted at a location identified by the city council. - No vegetation within the 20 m coastal zone should be removed for the purpose of the project. - No protected trees should be removed as part of the project. - Any construction area needs to be levelled to pre-existing levels. |
| Solid and construction waste during construction phase | - For domestic waste produced by the staff clearly demarcated bins for waste disposal needs to be placed and emptied daily. - For construction solid waste should be cleared from work site every day and placed in a designated location. |
| Solar Panel waste following lifetime | - The panels should be either recycled or taken to a certified e-waste management facility. Preference should be given to recycling. Prior approval needs to be attained from Ministry prior to undertaking this activity. |
| Emissions from vehicles | - All vehicles used for the project should have an up to date road worthiness. |
| Dust, Noise and Vibration | - Restricting working hours from morning 06 to evening 06. - Keeping construction equipment properly stored and secured at a location approved by the council - Materials that are stockpiled at the location for a long period of time should be covered to minimize impact of dust generation due to windy conditions. - Ensure that the construction site is wetted regularly to minimize impact of dust as a result of the project. |
| Groundwater | - All chemicals used should be stored on hard surfaces on enclosed spaces. - All chemicals should be handled using chemical protective gloves. - All storage containers need to be inspected regularly for any leaks. - Where dewatering is required, the dewatering permit should be attained as per the requirements of Dewatering Regulation (R-1697/2013). - Dewatering activities where required needs to be completed within the shortest possible time. |
| Road closure and road safety | - All closures need to be preannounced - All road closures need to be coordinated with the council and Police - Clear markings need to be placed on roads during road closure with indicative lights and warning signs. - Following backfilling and resurfacing where required, must ensure that pre-existing levels are maintained. - The solar panels need to be placed at a height and angle such that glare doesn’t become an issue for the vehicles. |
| Impacts on recreational spaces close to installation site | - The construction work should be limited to the footprint of the planned PV installation. - No equipment, vehicles should be left unattended. - Area in which construction work is undergoing should be closed off for public access. - Appropriate safety signs should be placed at the construction site in both English and Dhivehi. |
| Damage to Utility lines and other cables | - The investor/contractor should come into agreement with each and every service provider regarding how any damage is going to be fixed. - Identify the cable routes, utility lines prior to construction commencement and ensure that such areas are avoided. - Where chance damage occurs, the investor needs to make arrangements to fix the damage within 24 hours of damage. |
| Labour related impacts | - If foreign labour is used the labour force needs to be briefed on the language, culture and customs of Maldives. - The labour force needs to be provided information on the rules and regulations pertaining to protected areas of Addu. - It is imperative that the comprehensive Labour Management Procedures (LMP) developed for the project is followed (link: https://www.environment.gov.mv/v2/en/download/10026) - Constant and reliable electricity supply should be available at project office and accommodation site. - Shower and toilet facilities should be available at temporary accommodation site. - Toilet and drainage should be connected to local sewer system, where not available septic tanks should be used for treatment prior to disposal. - A minimum ratio of 01 toilet/shower per 20 workers should be maintained. Separate facilities should be provided for men and women. - Individual bedding should be provided to all workers. - Storage space for individual belongings should be provided for all workers. - Male and Female workforce needs to be housed separately. - Designated locations for waste disposal with clearly marked bins needs be established. Bins need to be emptied daily. - Sufficient lighting and cooling systems need to be established. - Portable drinking water should be provided. - The site needs to be cleaned daily. - Monthly inspections to determine pest infestation of the site should be undertaken. - Meals if prepared from a local café or restaurant should be from a Maldives Food and Drug Authority certified facility. - If foreign labour is used, prior to mobilization the construction workers should be briefed in their language on customs of Maldives. - If Covid19 restrictions are in place all guidelines issued by Health Protection Agency of Maldives need to be followed. - If Covid19 restrictions are in place, investor/contract needs to attain advice Health Protection Agency of Maldives prior to mobilization and any guidance needs to be strictly followed. |

## 4.4 Grievance Redress Mechanism for Contracted Work Force

The selected Bidder (herein referred to as the “Seller” as the term is defined in the PPA) should assign a member of the staff to look into any grievances raised by contracted work force and provide details of how the mechanism will be run as per the established norms of the Seller. This information should be provided to the Employer prior to signing the contract agreement.

Table 12 Grievance Redress Mechanism for contracted workers

| Tiers of Grievance Mechanism | Nodal Person for Contact | Contacts, Communication and Other Facilitation by Project | Timeframe to address grievance |
| --- | --- | --- | --- |
| First Tier: Contractor/ Investor | Designated person by Seller/ Investor to specifically look into complaints (if no such person exists within the company can go straight to tier 2) | As per the established system of the investor/Seller | As per established norms of the Seller/investor (not exceeding 30 days). |
| Second Tier: Labour Relations Authority | Designated Employment Officer for the case | If the aggrieved party is not happy with the response from the Seller/Investor, the party may upgrade the grievance to second tier (i.e. Labour Relations Authority). The aggrieved person may submit the complaint through: https://lra.gov.mv/submit-a-complaint-form/ | As per the established norms of the Authority |
| Third Tier: Judiciary | An individual has the option of going to established judiciary system of the country | The legal system is accessible to all aggrieved persons. | As per established judicial procedures in Maldives |

Details of the GRM, with the details of First Tier incorporated need to be communicated to all contracted workers mobilized for the purpose of the project. The information should be given in a language that is understandable to the employed staff. Minutes of meetings held in relation to sharing this information to contracted workers with the required photographic evidence needs to be provided to the Employer.

The grievance redress mechanism for the contracted work force will need to be displayed in the worker accommodation and worker sites in a language which is understandable to the workers employed for the purpose of the project.

## 4.5 Grievance Redress Mechanism for the public

The Seller will be required to designate a person to deal with public grievances and the information of the person responsible needs to be provided to Employer prior to signing the contract.

The Seller will be required to print and display the Grievance Redress Mechanism for the project based on the design submitted by the Employer on a whether proof material at all sites where work is undertaken, including any storage and temporary locations utilized for the purpose of the project by the Seller.

This mechanism was developed using the mechanism highlighted in the ESMF as a basis. The Seller is responsible to implement the Tier 1 requirements during the construction phase of the project. A log record of the grievances should be made available in a real time viewable format to the Employer.  The details of the mechanism are highlighted below:

| Tiers of Grievance Mechanism | Nodal Person for Contact | Contacts, Communication and Other Facilitation by Project | Timeframe to address grievance |
| --- | --- | --- | --- |
| First Tier: Seller (During Construction phase) Independent Power Producer (IPP) (for solar) / Electricity Service Provider (ESP) (for battery and grid) (During Operation Phase) | A person designated for the task need to be identified for the purpose by IPP and Electricity Service Provider. | - In the ESP or IPP or Seller offices and the project site there will be an Information Board providing details of the Grievance redress mechanism listing the names and contact telephones/emails. - Grievances can be registered by contacting the designated person through phone/email or by submitting a letter of complaint or by filling a Tier-1 complaint form. The Tier-1 form must be available online on the websites of the IPP or ESP or Seller, Ministry of Climate Change, Environment and Energy (MCCEE) and from the front office counters of the respective offices. (note PMU of MECT should supply the form to respective parties). - For those who cannot properly write, a staff should assist in filling the complaint form and get it signed by the aggrieved party. - A formal receipt of the complaint should be provided to the aggrieved party. - The IPP/ESP/Seller will screen the grievance to determine whether the grievance is related to ARISE project or not. - If it is related to the project the aggrieved party should be informed in writing (copied to MCCEE) how the case will be processed as per this grievance redress mechanism. This should occur within 03 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - Alternatively, if it is not related to the project the aggrieved party should be informed that it is not related to the project in writing (copied to MCCEE) and should inform how the case will be handled. This communication should occur within 03 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - Where the grievance is related to the project, the IPP/ESP/Seller should come up with a solution either by (i) discussing internally; (ii) joint problem solving with the aggrieved parties, MCCEE and Island Council or; (iii) a combination of both options. - The IPP/ESP/Seller should communicate the final decision in writing, in terms how the grievance was handled to the aggrieved party within 14 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - The aggrieved party must acknowledge the receipt of decision and submit their agreement or disagreement with the decision within 10 days. - If no acknowledgement is submitted from the aggrieved party then the decision will be considered as accepted. - If the grievance is not resolved to the satisfaction of the aggrieved party within 14 working days of submission of the grievance to tier 1 then the aggrieved party may notify local council in writing, of the intention to move to tier 2. | 14 working days |
| Second Tier: Local Council (Island or City Council or any other party which performs such a function) | Local Council will be the second point of contact. Designated contact persons should be established within the Council with a designated contact number. | - Where the aggrieved party is not happy with the outcome of the decision by the IPP/ESP/Seller or where the aggrieved party is of the view that the council is not capable of justly solve the issue or where the grievance is not resolved within 14 working days the grievance can be upgraded to tier 2. - In the council office and the project site there will be an Information Board providing details of the Grievance redress mechanism listing the names and contact telephones/emails. - Grievances can be registered by contacting the local council directed contact person(s) or by submitting a letter of complaint addressed to the Mayor or Council president or by filling a Tier 2 Complaint Form. The Tier-2 form must be available online on the websites of the Island Council, Ministry of Climate Change, Environment and Energy (MCCEE) and from the front office counters of the respective offices. (note PMU of MCCEE should supply the form to respective parties). - For those who cannot properly write, a staff should assist in filling the complaint form and get it signed by the aggrieved party. - A formal receipt of the complaint should be provided to the aggrieved party. - The aggrieved party must submit a copy of the decision from tier 1 and the letter submitted raising their disagreement to decision where the reason for upgrading to tier 2 is the disagreement with the decision from tier 1. - The aggrieved party must submit a copy of the grievance form submitted through tier 1 or the grievance letter submitted to council, where the reason for upgrading to tier 2 is due to lack of response from the IPP/ESP/Seller. - The council must screen the grievance to determine if the issues and concerns raised in the complaint falls within the mandate of the project. - If it is related to the project council should inform the aggrieved party in writing (copied to MCCEE) how the case will be processed as per this grievance redress mechanism. This should occur within 03 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - Alternatively, if it is not related to the project the council should inform the aggrieved party that it is not related to the project in writing (copied to MCCEE) and should inform how the case will be handled. This communication should occur within 03 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - Where the grievance is related to the project, the council should come up with a solution either by (i) discussing within the council; (ii) joint problem solving with the aggrieved parties, MCCEE, ESP and the Seller/IPP or; (iii) a combination of both options. - The council should communicate the final decision in writing, in terms how the grievance was handled to the aggrieved party within 14 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - The aggrieved party must acknowledge the receipt of decision and submit their agreement or disagreement with the decision within 10 days. - If no acknowledgement is submitted from the aggrieved party then the decision will be considered as accepted. - If the grievance is not resolved to the satisfaction of the aggrieved party within 14 working days of submission of the grievance to tier 2 then the aggrieved party may notify MECT, in writing, of the intention to move to tier 3. | 14 working days |
| Third Tier: Ministry of Climate Change, Environment and Energy | MCCEE will forward the grievance to the Project Management Unit (PMU) of the Ministry. A dedicated number should be allocated to | - Where the aggrieved party is not happy with the outcome of the decision by the council or where the aggrieved party is of the view that the council is not capable of justly solve the issue or where the grievance is not resolved within 14 working days the grievance can be upgraded to tier 3. - Grievances can be registered by contacting MCCEE (directed to the contact person(s) or by submitting a letter of complaint addressed to the Minister of Environment or by filling a Tier 3 complaint form. - For those who cannot properly write, the MCCEE staff will fill a complaint form and get it signed by the aggrieved party. - A formal receipt of the complaint should be provided to the aggrieved party. - The aggrieved party must submit a copy of the decision from the council and the letter submitted to council raising their disagreement to decision where the reason for upgrading tier 2 is the disagreement with the council decision. - The aggrieved party must submit a copy of the grievance form submitted to council or the grievance letter submitted to council, where the reason for upgrading to tier 2 is due to lack of response from the council. - Ministry will forward all the grievances related to the project to the Project Management Unit. - PMU will screen the grievance to determine if it is related to the project. - If it is related to the project PMU should inform the aggrieved party in writing how the case will be processed as per this grievance redress mechanism. This should occur within 03 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - Alternatively, if it is not related to the project PMU should inform the aggrieved party that it is not related to the project in writing and should inform how the case will be handled. This communication should occur within 03 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - Where the grievance is related to the project, the PMU should come up with a solution either by (i) Discussing in the project steering committee; (ii) joint problem solving with the aggrieved parties, the council, Energy Service Provider and the Seller/IPP (iii) undertaking site visits and holding onsite discussions or; (iii) a combination of all these options. - The PMU will be responsible to ensure that there is no cost imposed on the aggrieved person, due to the grievance mechanism at the third tier. - MCCEE should communicate the final decision in writing, in terms how the grievance was handled to the aggrieved party within 14 working days of receiving the complaint. If the aggrieved party is unable to read (for whatever reason) the issued letter should be read to the person in presence of a witness and the witness should declare their witness to this event. - The aggrieved party must acknowledge the receipt of decision and submit their agreement or disagreement with the decision within 10 days. - If no acknowledgement is submitted from the aggrieved party then the decision will be considered as accepted. | 14 Working Days |

## 4.6. Applicable Laws and Policies

The following applicable laws, regulations and policies and any other relevant laws and regulations of the Maldives should be adhered by the Seller at all times.

### 4.6.1 Employment Act 2008 [2/2008]

Employer/employee relationships are governed under the Employment Act (2/2008) and the subsequent amendments to it. An employer is defined in the Act as, “any person, company, government or association of persons providing employment pursuant to an employment agreement which includes the use of services of non-independent contractors, successors, assigns of such employers, and any person to whom the rights of such employers are transferred in accordance with the law”. An employee is any person seeking to work pursuant to an employment agreement. Maldives National Defence Force and Maldives Police Service are exempted from the Act. The Act prohibits forced employment, and discrimination in granting of employment, increase in remuneration, provision of training, determination of conditions and manner of employment, dismissal and resolution of other employment related issues; based on race, colour, social standing, religion, political beliefs or affiliation with any political party, sex, marital status, family obligations, age or disability.

#### Minors

The law considers a minor to be a person under the age of 18. Chapter 3 of the Employment Act allows minors between the ages of 16 and 18 to be engaged in employment, provided consent is obtained from their legal guardian. Minors under the age of 16 are prohibited from engaging in employment, unless it is as part of a training for their education. A minor may also be employed in a family business with the consent of such minor and their family. All children are protected from employment that would have a detrimental effect on their health, education, safety or conduct. These rights are further stipulated in the Rights of the Child Act [19/2019] under which the Labour Relations Authority (LRA), is mandated to enact necessary regulations and monitoring the implementation of the same, for the prevention of child labour.

#### Employment Agreement

All employers are required to enter in to an employment agreement in writing, with their employees. The Act recognizes three types of employment agreements, which are, (a) fixed term contracts or agreements with a definite term, (b) agreements with an indefinite term or permanent employment agreements, and (c) agreements for a specific task or project. Direct workers or project staff in the PMU falls under this latter category. Such agreements are considered neither permanent nor fixed term contract. And they are considered terminated upon the completion of the specific task or project.

All agreements must at minimum have included in them the following details;

- The name of the employee, permanent address, current address, identity card number or passport number, date of birth, nationality, emergency contact person's name, address and phone number;

- Whether employment is permanent or temporary;

- Date of commencement of employment agreement;

- Salary and other benefits;

- Method and guidelines for calculation of salary;

- Pay day;

- Days on which leave may be granted;

- Principles pursuant to which disciplinary measures may be taken against the employee due to his conduct;

- Staff appraisal; and

- Manner of dismissal from employment.

Employers are also obligated to provide employees with a job description.

#### Working Hours

Working hours of employees, under the Employment Act must not exceed 48 hours per week. This however does not cover overtime work. Employees may not work for more than six consecutive days without taking a day off. The employment agreement must stipulate how overtime work can be obtained from an employee. Employees working overtime are entitled to a pay of 1 ¼ times their hourly wage and if working on a public holiday, 1 ½ times their hourly wage.

#### Dismissal

Employees have a right not to be dismissed unfairly, without cause. The Act provides a list of disciplinary measures that can be taken reasonably against an employee due to misconduct and which must ordinarily be exhausted before any dismissal. This includes, cautioning verbally, a written warning, 14-day suspension and demotion, in that order.

Employers must establish procedural fairness and substantive fairness before an employee is dismissed. Procedural fairness is ensuring that due process of the law is followed in any decision to dismiss an employee, including among other things, providing the employee with due notice or money in lieu of such notice and ensuring that the employee is given ample opportunity to defend themselves. Substantive fairness means the actual reason or the misconduct of the employee preceding such dismissal must be one that warrants dismissal. It must be reasonable and fair. The employers must take in to account the circumstances surrounding the case, the previous records of the employee, and actions taken for similar conduct in previous cases.

#### Leaves

Entitled leaves for employees under the Act includes, 30 (thirty) days of paid annual leave, 30 (thirty)  days of paid sick leave, 60 (sixty) days of paid maternity leave, upon expiry of which either parent may choose to take up to 01 (one) year of unpaid leave, 03 (three) days of paid paternity leave, 10 (ten) days of paid leave for family responsibility, and 05 (five) days of paid leave for a parent of a child undergoing circumcision.

On March 2019, the government decided to grant all government employees with a paid maternity leave and paternity leave of 06 (six) months and 01 (one) month, respectively. This practice has since been taken up by state owned enterprises as well.

#### Training

Employees may be engaged with training, on the job or otherwise, subject to a separate agreement entered in to with the employer, for the purpose. The agreement must have in them at minimum, the details of the employer and the employee along with, details of the type of training, the period it would take to complete the training, costs incurred by the employee in relation to the training and the rights and obligations of each party if the training is not completed.

#### Health and Safety

All employers are obligated under the Act to take measures for the safety and protection of their employees, without any charge. These measures include;

- providing a safe work place environment and procuring of secure tools and machinery for carrying out work, and ensuring the continued safety of the same;

- provide resources necessary to carry out the work with safety;

- provide protective attire and equipment in the event that the nature of work is such that it is not possible to eliminate or control health hazards arising out of work;

- provide education and training to employees on the use of protective gear and safety equipment, and disseminate information to employees on all issues of related concern;

- conduct regular health checks for employees involved in any work that may cause physical ill health or for employees working with chemical or biological materials that may pose a threat to their health;

- provide or arrange for appropriate medical care for employees injured during the course of their employment; and

- facilitate first aid to employees who are involved in emergencies or accidents.

Employees are required to;

- maintain safe practices at work to avoid danger to the safety and wellbeing of the employee and co‐workers, which may be caused by inattentiveness to safety and security measures;

- assist the employer and co‐workers in maintenance of measures designed to ensure health and safety in the work place;

- use safety equipment and protective gear as instructed in accordance with the training and education provided for use of such equipment and gear;

- report to the employer any damage, loss of or destruction of protective gear or safety equipment;

- inform the employer or his designated supervisor immediately of the occurrence of any incident which the employee believes may cause danger and which the employee is unable to resolve; and

- inform the employer or his designated supervisor of any accidents or damage sustained at work or related to work.

Employees have the right to abstain from work where there is serious threat to health or life.

#### Unionizing, collective bargaining and the right to strike

The Employment Act 2008 is notably silent on the right to strike or the right to form trade unions and is lacking of any provisions on collective bargaining. While these are constitutional rights, and Maldives remain party to the ILO Convention on Right to Organize and Collective Bargaining (No. 98), there is a lack of a specific legislative framework ensuring the right to organize and collectively bargain. Employees can however create clubs and associations, which are governed under the Associations Act (1/2003). Such clubs and association are required under the law to be registered at the ministry with the relevant mandate.

The Regulation on Resolving Disputes between Employers and Employees (2011/R-12), issued by Labour Relations Authority outlines principles for employees to comply with in exercising the right to strike and abstain from work. To strike, under the Regulation is defined as, to abstain from work by peaceful exercise of the employees’ freedom of assembly and speech. Under the Regulation, before any decision is taken to conduct a strike due to a dispute between the employers, the employees are to carry out discussions with their respective employers. The Regulation provides for a three-tier process to be followed in carrying out such discussions. First step involves informal discussion between the parties failing which formal discussions are to be held at a sectional or departmental level. Second tier involves lodging the grievances to a Grievance Committee made up of the head of the respective organization, heads of the relevant departments, and parties representing the aggrieved employee(s). If the Grievance Committee fails to resolve the dispute, the matter is to be forwarded to the Labour Relations Authority. If either party is dissatisfied with the decision of the Authority, the matter can be submitted to the Employment Tribunal for adjudication.

#### Redress, Labour Relation Authority and Employment Tribunal

Labour Relations Authority (LRA) formed under Article 77 of the Employment Act (2008) is mandated with implementing the necessary administrative measures to ensure compliance with the Act. The Authority also issues regulations governing employer/employee relationships. As such employees can lodge complaints to LRA, regarding an employer’s action which they deem is in contravention of the law, and request to enforce compliance.

LRA has the authority to enter in to and inspect work places and obtain documents through Employment Officials. Officials have the authority to order an employer to make changes, within a specified time, to the machinery or the manner in which an equipment is set up, to ensure health and safety of the employees as stipulated under law.  An official can also order urgent steps to be taken in order to avert a danger where the risk of a danger to the employee’s health and safety exists in the opinion of such official.

If an employer is unhappy with the decision or order of LRA, they can appeal to Employment Tribunal.

The Tribunal established under Article 85 of the Employment Act consists of 07 (seven) members appointed by the President. The members hold office for a tenure of 05 (five) years and should have the educational qualifications and experience to comprehend and resolve employment related issues.

The Tribunal reviews and deliberates at the first instance on matters of employment. Decisions of the Tribunal are appealed at the High Court.

### 4.6.2 Health and Safety Regulation for Construction industry (2019/R-156)

The aim and objective of this regulation is to provide minimum standard for safety and security of the community and labour force. The regulation suggests that if the value of the project exceeds 1.5 million Maldivian Rufiyaa, health and safety aspects regarding the project needs to be defined and training given to the labour force. It states that safety nets need to be installed and other precautionary measures taken such that the neighbouring households are not impacted as a result of the project2. It also stipulates that Personal Protective Equipment (PPE) that is relevant to the work undertaken should be worn. In this regard, it states that safety helmets, safety shoes, safety goggles, welding mask and gloves need to be used where required. The same article stipulates that, it is the responsibility of the employer to provide PPE to the employee.   It also stipulates that steps need to be undertaken during excavation to ensure damage to nearby properties are avoided. It also stipulates that appropriate safety signs need to be installed in construction site.

Furthermore, Emergency Response Plan (ERP) is required for projects that exceeds MVR 1.5 Million.  The provision requires the emergency response plan to be visible and to undertake drill for emergency response plan at least twice every year. Moreover, a complete first aid kit and a trained first aid person should always be available at the construction site for such projects.  The contractor is also required to assign a site safety supervisor. Such a person should have a minimum five-year experience working as a site supervisor.

The regulation also stipulates that for projects above MVR 5 million third party insurance needs to be taken to cover for damages. The regulation also has provisions that highlights that all open pits should be covered or demarcated with fence, to have pedestrian detour if work is undertaken next to a road, if work is undertaken in height safety warning signs or warning flags or lights need to be installed at the site and all idle equipment’s need to be switched off. The regulation also suggest that the construction boundary needs to be hoarded. As per the regulation, the minimum height of the hoarding should be 1800 millimetres.

If working above 03 meters it is stated that a guardrail should be there to prevent falling from height. Moreover, it is stated that safety harness and belt need to be used when working at such heights. The regulation also has special provisions when working on roofs.  Use of static line and inertia reel when working on roofs and ensuring that they are installed appropriately. Preassembling the materials required as much as possible prior to lifting to the roof, to minimize work undertaken on the roof. Scaffolding should be installed by a person who has special training and experience for installing scaffolding9. The regulation also states that While installing safety net work should be undertaken using a mobile scaffolding or a tower scaffolding9.  All scaffolding used on site needs to be tested at least once a week.

Specific provisions are also there regarding electricity supply. In this regard one of the following conditions should be met:

- All electric equipment should be connected to a supply that does not exceed 230 V.

- To install an earth circuit monitor on the electricity supply line.

- Use of equipment that have double insulation.

- Utilize earth leakage circuit breaker.

The switchboard installed to provide temporary power should be covered to prevent weather damage.

The regulation stipulates that all electrical equipment used on the site needs to be tested every 03 months to ensure functionality and safety. The regulation also highlights that where chemicals and hazardous materials are used each contractor needs to identify a plan to handle such material and the identified plan needs to be implemented in the work site. It is also suggested when handling hazardous materials, the workers need to be fully covered.

If any flammable materials are on site firefighting equipment should be available and fire protection clothing should be available on site.  The regulation suggests that heavy machinery like cranes should not be used in any areas where public could access. Moreover, the same article states that cranes should operate 04 meters away from any overhead electric lines. Moreover, cranes should be inspected every 12 months and the records of the inspection should be kept available in the crane.

To keep log records of any accidents that occur in site and reporting any such incident to police is also specified in the regulation. The regulation also specified non-compliance penalties.

### 4.6.3 Prevention of Sexual Harassment Act (16/2014)

Prevention of Sexual Harassment Act (16/2014) prohibits employers and employees from subjecting those who work under them or their co-workers to any extent any type of sexual harassment. Sexual Harassment is defined in the Act as, any sexual act committed against a person without their consent. A sexual act, for the purposes of the Act, is any action, whether physical, verbal or otherwise, which according to a reasonable person, suggests a sexual intent towards the victim. Any such act is to be proven on the balance of probability. It is the duty of the employer to take reasonable steps to ensure that the work environment is an environment that is free from sexual harassment and one in which such acts does not negatively affect the work of employees. Employers are obliged to establish policies to prevent sexual harassment and have such policies published,

Every government office including the presidents’ office, independent institutions, parliament, the courts and all work places with more than 30 employees must have, under the Act, a Sexual Harassment Prevention Committee, with the function, among other things, of hearing complaints, investigating potential acts of harassment and take proper action against perpetrators in accordance with the Employment Act.  The Committee consists of 03 members out of which one must be female. The Committee can, depending on the gravity of the action, take disciplinary actions ranging from cautioning, suspension, demotion and dismissal. Decisions must be taken within 60 days of receiving a complaint. Decisions of the Committee can be appealed at Employment Tribunal.

### 4.6.4 Gender Equality Act 2016 (18/2016)

Employers are further mandated under the Gender Equality Act (18/2016), to ensure non- discrimination based on gender. The Act stipulates that all government offices and private businesses must take appropriate measures to achieve the following goals;

-  	Abolish gender-based discrimination, including direct and indirect discrimination.

- 	Abolish all systemic discrimination caused through established systems with unequal practices.

-  	Promote equal opportunities for men and women.

-  	Promote notions and ideas of gender equality to eliminate undesired preconceptions against a certain gender.

Providing equal opportunity under the Act includes, (a) eliminating weaknesses or difficulties caused by inequality between men and women, (b) reducing the negative effects of inequality between men and women, (c) facilitating the special needs of a particular gender to achieve ease of attainment of services, and (d) evaluating the degree of participation of each gender in public life and public services and take appropriate steps to balance such participation.

Public and private sector employers are further mandated under the Act to;

- Provide equal opportunity to men and women in the employment, training and advancement of position.

- Provide equal wages to men and women who perform the same responsibilities at the same place of employment.

- Men and women at the same place of employment with work adequately equal in value and weight shall be given equal wages, overtime compensation, benefits and allowances.

- Employment opportunities shall not be offered or advertised to restrict a particular gender, except in circumstances the work is required to be undertaken by a particular gender.

- Announcements and advertisements for work that is likely to attract more men than women must be designed to invite and not to exclude women.

- Take all possible steps to eliminate obstructions to employment of women and to create conducive work environments for women.

- Establish a complaints mechanism.

### 4.6.5 Maldives Pension Act (18/2016)

Employers must enrol their employees in the Maldives Retirement Pension Scheme, and it is obligatory on the employees to participate in the scheme, under Article 12 of the Maldives Pension Act (18/2016). Failure to do so would amount to an offense under the Act. And as such the employment agreement is required to have provisions for deductions for pension contributions by the employee.

Each person who is considered a participant of the Retirement Pension Scheme of the Maldives, is required to pay a minimum of 7% of the employee’s pensionable wage, and the employer must also pay a minimum of 7% of the pensionable wage to the scheme.

### 4.6.6 Migrant Workers

Foreigners are required to obtain an employment approval as per applicable law, and deposit a security with the relevant government agency. This deposit is to be used by the government for costs incurred to remedy an employers’ default of their responsibilities under relevant Regulation on Employment of Expatriates in Maldives (2011/R-22), or as payment for any unpaid fees related to work permit or work visa, or for travel expenses of the worker, where government decides to deport such worker. Article 62 of the Employment Act gives the minister with the relevant government mandate to issue regulations related to the employment of foreigners.

Under the Regulation on Employment of Expatriates in Maldives (2011/R-22), government issues a specific number of “Quotas” for companies, upon request in order to employ expatriates. No foreigner is allowed to work in the Maldives without a valid work permit and a work visa. Employers are required to treat their foreign employees in accordance with the Employment Act and other applicable law. They are responsible for paying any fees related to the work permit or visa accordingly and of returning the worker to their home country once the work permit expires, or if for any reason the government decides that the worker should leave the country.  Employers are also required to, upon the death of a worker, to return the body to their family in their home country.

### 4.6.7 International Labour Organization Conventions

Maldives have ratified a number of International Labour Organization Conventions on 04th January 2013. These conventions are described in brief below:

- Forced Labour Convention, 1930 (No. 29): “This fundamental convention prohibits all forms of forced or compulsory labour […] Exceptions are provided for work required by compulsory military service, normal civic obligations, as a consequence of a conviction in a court of law […], in cases of emergency, and for minor communal services performed by the members of a community in the direct interest of the community. The convention also requires that the illegal extraction of forced or compulsory labour be punishable as a penal offence, and that ratifying states ensure that the relevant penalties imposed by law are adequate and strictly enforced.” (See Rules of the game: a brief introduction to international labour standards, p. 35)

- Freedom of Association and Protection of the Right to Organise Convention, 1948 (No. 87): “This fundamental convention sets forth the right for workers and employers to establish and join organizations of their own choosing without previous authorization. Workers' and employers' organizations shall organize freely and not be liable to be dissolved or suspended by administrative authority, and they shall have the right to establish and join federations and confederations, which may in turn affiliate with international organizations of workers and employers.” (See Rules of the game: a brief introduction to international labour standards, p. 28).

- Right to Organise and Collective Bargaining Convention, 1949 (No. 98): “This fundamental convention provides that workers shall enjoy adequate protection against acts of anti-union discrimination […] Workers' and employers' organizations shall enjoy adequate protection against any acts of interference by each other […] The convention also enshrines the right to collective bargaining” (See Rules of the game: a brief introduction to international labour standards, pp. 28-29).

- Equal Remuneration Convention, 1951 (No. 100): “This fundamental convention requires ratifying countries to ensure the application of the principle of equal remuneration for men and women workers for work of equal value. The term ‘remuneration’ is broadly defined to include the ordinary, basic or minimum wage or salary and any additional emoluments payable directly or indirectly, whether in cash or in kind, by the employer to the worker and arising out of the worker’s employment” (See Rules of the game: a brief introduction to international labour standards, p. 40).

- Abolition of Forced Labour Convention, 1957 (No. 105): “This fundamental convention prohibits forced or compulsory labour as a means of political coercion or education or as a punishment for holding or expressing political views or views ideologically opposed to the established political, social or economic system; as a method of mobilizing and using labour for purposes of economic development; as a means of labour discipline; as a punishment for having participated in strikes; and as a means of racial, social, national or religious discrimination” (See Rules of the game: a brief introduction to international labour standards, p. 35).

- Discrimination (Employment and Occupation) Convention, 1958 (No. 111): “This fundamental convention defines discrimination as any distinction, exclusion or preference made on the basis of race, colour, sex, religion, political opinion, national extraction or social origin, which has the effect of nullifying or impairing equality of opportunity or treatment in employment or occupation. [...] It requires ratifying states to declare and pursue a national policy designed to promote, by methods appropriate to national conditions and practice, equality of opportunity and treatment in respect of employment and occupation, with a view to eliminating any discrimination in these fields. The Convention covers discrimination in relation to access to education and vocational training, access to employment and to particular occupations, as well as terms and conditions of employment.” (See Rules of the game: a brief introduction to international labour standards, p. 42).

- Minimum Age Convention, 1973 (No. 138): “This fundamental Convention sets the general minimum age for admission to employment or work at 15 years (13 for light work) and the minimum age for hazardous work at 18 (16 under certain strict conditions). It provides for the possibility of initially setting the general minimum age at 14 (12 for light work) where the economy and educational facilities are insufficiently developed.” (See Rules of the game: a brief introduction to international labour standards, p. 37).

- Worst Forms of Child Labour Convention, 1999 (No. 182): “This fundamental Convention defines as a “child” a person under 18 years of age. It requires ratifying states to eliminate the worst forms of child labour, including: all forms of slavery or practices similar to slavery, such as the sale and trafficking of children, debt bondage and serfdom and forced or compulsory labour, including forced or compulsory recruitment of children for use in armed conflict; child prostitution and pornography; using children for illicit activities, in particular for the production and trafficking of drugs; and work which is likely to harm the health, safety or morals of children. The Convention requires ratifying states to provide the necessary and appropriate direct assistance for the removal of children from the worst forms of child labour and for their rehabilitation and social integration. It also requires states to ensure access to free basic education and, wherever possible and appropriate, vocational training for children removed from the worst forms of child labour.” (See Rules of the game: a brief introduction to international labour standards, p. 37).

In addition, the following environmental laws and policies that are applicable to the project as identified in pages 35 to 39 of the ESMF needs to be followed by the contractor. Including attaining all the required permits where required other than the approvals required through Environmental Impact Assessment Regulations (No. 2012/R-27). As per the requirement of ESMF of the project the approval required through No. 2012/R-27 regulation will be attained by the Employer.

### 4.6.8 The Environment Protection and Preservation Act (4/93)

The basic environment law, Law No.4/93 Environment Protection and Preservation Act (EPPA) was enacted in April 1993 as an umbrella law to protect and preserve the environment of the country. The main elements of the EPPA are as follows:

Introduction: The natural environment and its resources are a national heritage that needs to be protected and preserved for the benefit of future generations. The protection and preservation of the country’s land and water resources, flora and fauna as well as the beaches, reefs and lagoons and all-natural habitats are important for the sustainable development of the country.

Environmental Guidance: The concerned government authority shall provide the necessary guidelines and advise on environmental protection in accordance with the prevailing conditions and needs of the country. All concerned parties shall take due considerations of the guidelines provided by the government authorities.

Environmental Protection and Conservation: The Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy] shall be responsible for formulating policies, as well as rules and regulations regarding the environment in areas that do not already have a designated government authority already carrying out such functions.

Protected Areas and Natural Reserves: The Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy] shall be responsible for identifying protected areas and natural reserves and for drawing up the necessary rules and regulations for their protection and preservation. Anyone wishing to establish any such area as mentioned in (a) of this clause, as a protected area or a reserve shall register as such at the Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy] and abide by the rules and regulations laid by the Ministry.

Environmental Impact Assessment (EIA): An impact assessment study shall be submitted to the Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy] before implementing any development project that may have a potential impact on the environment. The Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy] shall formulate the guidelines for EIA and shall determine the projects that need such assessment as mentioned in paragraph (a) of this clause.

The Termination of Projects: The Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy] has the authority to terminate any project that has any undesirable impact on the environment. A project so terminated shall not receive any compensation.

Waste Disposal, Oil and Poisonous Substances: Any type of waste, oil, poisonous gases or any substance that may have harmful effect on the environment shall not be disposed within the territory of the Maldives. In case where the disposal of the substance stated in paragraph (a) of this clause becomes absolutely necessary, they shall be disposed only within the areas designated for the purpose by the government. If such waster is to be incinerated, appropriate precautions shall be taken to avoid any harm to the health of the population.

Hazardous/ Toxic or Nuclear Wastes: Hazardous/Toxic or Nuclear Wastes that is harmful to human health and the environment shall not be disposed anywhere within the territory of the country. Permission shall be obtained from the relevant government authority at least 3 months in advance for any trans-boundary movement of such wastes through the territory of the Maldives.

The Penalty for Breaking the Law and Damaging the Environment: The penalty for minor offenses in breach of this law or any regulations made under this law shall be a fine ranging between MVR 5.00 (five Rufiyaa) and MVR 500.00 (five hundred Rufiyaa) depending on the actual gravity of the offence. The fine shall be levied by the Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy] or by any other government authority designated by the ministry. Except for those offenses that are stated in (a) of this clause, all major offenses, under this law shall carry a fine of not more than Rf 100,000,000.00 (one hundred million Rufiyaa) depending on the seriousness of the offense. The fine shall be levied by the Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy].

Compensation: The Government of Maldives reserves the right to claim compensation for all the damages that are caused by the activities that are detrimental to the environment. This include all the activities that area mentioned in clause 7 of this law as well as those activities that take place outside the projects that are identified here as environmentally damaging.

Definitions: Under this Law: (a) The “environment” means all the living and non-living things that surround and effects the lives of human beings; and (b) A “project” is any activity that is carried out with the purpose of achieving a certain social or economic objective.

### 4.6.9 The Regulation on Environmental Liabilities (Regulation No. 2011/R-9)

The objective of this regulation is to prevent actions violating the Environmental Protection and Preservation Act 4/93 and to ensure compensations for all the damages that are caused by activities that are detrimental to the environment.

The regulation sets mechanisms and standards for different types of environmental liabilities and equal standards that shall be followed by the implementing agency while implementing the regulation.

According to this regulation, the Government of Maldives reserves the right to claim compensation for all the activities which have breached the Environmental Protection and Preservation Act 4/93.

### 4.6.10 Environmental Impact Assessment Regulation (No. 2012/R-27) and Amendments

EPA stipulates under Article 5, any development work or project that have a significant impact on the environment should have an Environmental Impact Assessment consented to by the Ministry of Environment, Energy and Water [now the Ministry of Climate Change, Environment and Energy].

The EIA regulation defines the procedure to follow when attaining environmental approval for development projects. The regulations lists those projects that require EIA (schedule D), those projects that do not require EIA (Schedule T) and those projects that can be undertaken as per the mitigation plan provided by EPA (Schedule U).  Roof mounted solar PV projects are listed in Schedule T, thus locally environmental assessments are not required for roof mounted solar PV.

All the other projects need to go through a screening process identified in article 08 of the regulation. Following screening EPA decides the level of assessment required. In this regard, an EIA maybe required, EMP maybe required, project may be undertaken with mitigation plan or project can be undertaken with no assessment. For all other solar projects, ground mounted and floating solar, need to go through the screening process specified in the regulation

For projects that require EIA the regulation details the scoping process that needs to be following in article 11. Following scoping a Terms of Reference will be issued which will guide the level of assessment required.

EIA can be prepared by a consultant who is registered in EPA under article 16 of the regulation. The consultant registration process is administered by a consultant registration board. The functions and composition of this board is detailed in article 17 of the regulations.

Once the EIA report is submitted, EPA sends the review to two independent reviewers as per article 13 of the Regulation. The review period depends on the amount paid by the proponent for review. In this regard the following payment structure is specified in the regulations (article 07 and article 13):

      - For a review fee of MVR5000 15 days for review

      - For a review fee of MVR 10,000 10, days for review

      - For a review fee of MVR 5000 05 days for review

Following review EPA informs the proponent if any addition information is required, or approval can be given for the project, or the EIA report needs to be rejected or the project needs to be rejected due to irreversible damage to the environment.

Article 15 lists procedure for appeal the decision. The appeal decision will be made by Minister of Environment. Article 20 lists fining mechanism for non-compliance.

### 4.6.11 Regulation Governing Reclamation and Dredging of Islands and Lagoons of Maldives 2013/R-15

The Article 22 of the Constitution states that the State shall undertake and promote desire based economic and social goals through ecologically balanced sustainable development and shall take measures necessary to foster conservation, prevention pollution, the extinction of any species and ecological degradation from any such goals and this regulation is constituted for the purpose of pursuing this undertaking. It determines the guidelines that would minimize the damage caused to the environment due to reclamation and dredging pursuant to Article 3 of Environment Protection and Preservation Act. This regulation is enforced by the Environmental Protection Agency.

The aim of this regulation is to minimize environmental damage associated with dredging and reclamation activities. All dredging and reclamation activities requires EPA approval through this regulation. The regulation identifies the following conditions:

- Beach replenishment is restricted to a maximum extent of 10 m from the registered shoreline.

- The following restrictions apply to dredging:

- 500 m from the ocean side reef edge

- 50 m from the shoreline

- An environmentally sensitive site

- Reclamation cannot take place within 200 m of an environmentally sensitive or protected area.

- Reclamation should not exceed 30% of the house reef.

### 4.6.12 Stone, Coral and Sand Mining Regulation

This regulation addresses sand mining from islands and bird nesting sand bars. Sand and aggregate mining from beaches of any island whether inhabited or uninhabited is banned for protection of the islands. Permissions for sand and aggregate mining from other areas shall be obtained from the relevant authorities.

There is another similar regulation named “Regulation on Coral Mining (1990), which is only applicable to coral mining from the ‘house reef’ of islands and the atoll rim reefs.

### 4.6.13 By‐law ‐ Cutting Down, Uprooting, Digging Out and Export of Trees and Palms from One Island to Another

This regulation is enacted under Act 4/93 (environment Protection and Preservation Act). As such, this regulation is a compilation of guidelines to be adhered towards cutting-down, uprooting, removing and transfer between islands, of palms and trees in the Maldives.

Palms and trees may only be cut, uprooted, removed or transferred between islands out of mere necessity.  No one shall be exempted from this regulation except the parties/exemptions mentioned in Article 4 of this regulation.

Article 8 of the regulation requires permission to be obtained if more than ten coconut palms that have grown to height of 15ft or if more than 10 plants that have grown to a height of 08ft are to be removed.

Article 2 (d) of the regulation also enforces replacement of the vegetation that is lost as a result of re-plantation. In this regard, 02 palms or trees need to be replanted for every palm or tree removed.

Pursuant to the Environmental Protection and Preservation Act of the Maldives, the Ministry of Environment and Energy [now the Ministry of Climate Change, Environment and Energy] has developed this by‐law in order to educate and guide developers about acceptable practices for the management of trees and palms. The by‐law prohibits the cutting down, uprooting, digging out and export of trees and palms from one island to another unless there is no other viable alternative. It also requires that for every tree or palm removed at least 2 should be replanted on the same island. The by‐law also provides particular protection to the following:

- coastal vegetation extending 15 metres into the island;

- all trees and palms growing in mangrove and wetland areas;

- all trees and palms growing in Government protected areas; and

- trees and palms that are abnormal in structure.

### 4.6.14 Waste Management Regulation (No. 2013/R-58)

The Waste Management Regulation of the Maldives was enacted based on Article 22 of the Constitution of the Republic of Maldives and under powers vested in the Ministry of Environment and Energy [now the Ministry of Climate Change, Environment and Energy] under the Article 3 of the Environmental Preservation Act 4/93 in relation to Article 7 and 8 of the same Act. The regulation is implemented by the Environmental Protection Agency. This regulation focus on following five areas:

- Waste management standards: Defines standards for waste collection, transfer, treatment, storage, waste site management, landfills and managing hazardous waste;

- Waste management Permits: Defines approval procedures for waste sites;

- Waster transfer: Standards and permits required for waste transport on land and sea, including trans-boundary movements;

- Reporting requirements: Defines reporting and monitoring requirements and procedures; and

- Enforcement: Defines procedures to implement WRM and penalties for non-compliance.

### 4.6.15 Dewatering Regulation (2013/R-1697)

This regulation is constituted for the purpose of ensuring that the drainage of water in the islands of The Maldives in the process of dewatering and subsequent dumping of discharge water into the soil or to the sea, is conducted with minimal impact to the environment. Given water is the source of life and one of the essential elements forming the environment, the purpose of this regulation is to avoid contamination of the groundwater table, to mitigate the damage caused to the water table; and to protect the habitat, the environment, the public and all living organisms from the impact of dewatering.

This regulation is enacted from the rights vested on the Ministry from article 3 of Act 4/93(Maldives Environment Protection and Preservation Act). This regulation is enforced by the Environment Protection Agency on behalf of the Ministry.

In addition to the institutions of the state, it is a responsibility of every individual to protect the groundwater table of the islands of the Maldives and to manage it in a sustainable manner. The process of dewatering for any industrial purpose shall be conducted on any island pursuant to the guidelines prescribed in this regulation and after having obtained permission in writing from the implementing agency or from their delegate.

### 4.6.16 Regulation on Protection of Old Trees

The regulation is made under article 04 of EPPA. Article 03 of the regulation lists four categories of trees that can be protected. This includes:

- All trees above 50 years of age

- Unique and threatened species in Maldives in general or in a specific island

- Trees of environmental significance

- Trees of cultural significance

As per article 04 of the regulation all protected trees need to be advertised by the Ministry. The list needs to be updated every 05 years. Article 06 of the regulations states that the boundary of a protected tree is within a 02-meter radius of the tree. Article 05 suggests that trees that are located within a private boundary are exempted from this regulation. Moreover, those trees that are grown for the purpose of agriculture are exempted from this regulation. The regulation also defines responsible parties for maintenance of such trees and also activities like trimming of old branches that can be undertaken for maintenance purpose.

### 4.6.17 Regulation on Migratory Birds (2014/R-126)

The aim of the regulation is to ensure that the migratory birds and their habitat are protected from damage and destruction. Article 06 of the regulation stipulates that it is prohibited to catch, use as pets, trade of birds or any parts and harm the birds or their nests in anyway. Article 07 of the regulation lists all birds except migratory birds found in the Maldives. The regulation also stipulates that exemptions. In this regard as per article 08, research purpose and in case of spread of disease is identified as exemptions.

### 4.6.18 Protected Area Regulation (2018/R-78)

The overall aim of the regulation to specify mechanisms to protect, conserve and manage areas designated as protected areas under article 04 of EPPA. Article 05 of the regulation stipulates that for each of the designated protected areas the following information needs to be announced:

- The name of the protected area

- The boundaries of the protected area with GPS coordinates

- Zonation plan of the area

- Activities that can and cannot be undertaken at a particular location

- The designated level of protection

- The reason for protection and the special significance

The regulation identifies 07 levels that could be designated to protected areas (article 06)

- Areas of International Significance

- Strict Nature Reserves

- Wilderness Area

- National Park

- National Monument

- Habitat Species Management Area

- Protected Area with Sustainable Use

A list of all protected areas need to be maintained by EPA and the list needs to be gazette as per article 7. With an agreement in place, as per article 09 management of protected areas can be handed over to any public or private party. As per article 12 each protected area should have a management plan in place for the management of the area.

## 4.7 Procedure for Management of Physical Cultural Resources – Protection and Chance Find procedures

The following procedure as identified in pages 86 to 87 of the ESMF needs to be followed by the selected Bidder (herein referred to as the “Seller” as the term is defined in the PPA) in case of chance find of physical cultural resources.

If any person discovers a physical cultural resource, such as (but not limited to) archaeological sites, historical sites, remains and objects, or a cemetery and/or individual graves during excavation or construction, the Seller shall:

- Stop the construction activities in the area of the chance find;

- Delineate the discovered site or area;

- Secure the site to prevent any damage or loss of removable objects. In cases of removable antiquities or sensitive remains, a night guard shall be arranged until the responsible authorities take over;

- Notify the Supervising Officer who in turn will notify the responsible authorities (island councils and National Center for Cultural Heritage) immediately (within 24 hours or less);

- Responsible authorities are in charge of protecting and preserving the site before deciding on subsequent appropriate procedures. This would require a preliminary evaluation of the findings to be performed by archaeologists.

- The significance and importance of the findings should be assessed according to the various criteria relevant to cultural heritage; those include the aesthetic, historic, scientific or research, social and economic values used by the GoM;

- Decisions on how to handle the finding shall be taken by the responsible authorities. This could include changes in the layout (such as when finding an irremovable remain of cultural or archaeological importance) conservation, preservation, restoration and salvage;

- Implementation for the authority decision concerning the management of the finding shall be communicated in writing by relevant local authorities; and

- Construction works could resume only after permission is granted from the responsible local authorities concerning safeguard of the physical cultural resource.

Source: https://data.worldbank.org/indicator/NY.GDP.MKTP.KD.ZG?locations=MV

Source: https://data.worldbank.org/indicator/SP.POP.TOTL?locations=MV

Source: https://www.environment.gov.mv/v2/en/download/10752

calculated as Stated DC Capacity (proposed) multiplied by Stated CUF (proposed) multiplied by 24 hours multipled by 365 days.

calculated as Fixed Energy for first year (kWh), divided by the Bidder’s proposed DC capacity divided by 24 hours divided by 365 days

The bus bar and isolators must withstand the system power flow since they may be installed in series with the existing lines

Article 26, [19/2019]

Article 13, [2/2008]

Article 32, [2/2008] as amended by Article 6 Second Amendment Act to the Employment Act [14/2008]

Article 38, Employment Act [2/2008]

High Court of Maldives case number: 209/HC/2010

Articles 39-49, [2/2008]

Article 70, [2/2008]

Articles 73-76, [2/2008]

Article 2, [2019/R-156]

Article 5, [2019/R-156]

Article 6, [2019/R-156]

Article 7, [2019/R-156]

Article 9, [2019/R-156]

Article 10, [2019/R-156]

Article 12, [2019/R-156]

Article 14, [2019/R-156]

Article 16, [2019/R-156]

Article 18, [2019/R-156]

Article 20, [2019/R-156]

Article 21, [2019/R-156]

Article 22, [2019/R-156]

Article 24, [2019/R-156]

Article 29, [2019/R-156]

Article 32, [2019/R-156]

Article 39, [2019/R-156]

Article 43 & 44, [2019/R-156]

Articles 2, 3 [16/2014]

Article 7, [16/2014]

Article 13, [16/2014]

Articles 17, 18, 19 [16/2014]

Article 22, [16/2014]

Article 26, [16/2014]

Article 18, [18/2016]

Article 19, [18/2016]

Article 20, [18/2016]

Article 14,[18/2016]