Republic of Maldives

Request for Bids

DESIGN, SUPPLY, INSTALLATION AND COMMISSIONING OF BATTERY ENERGY STORAGE SYSTEMS (BESS) IN SELECTED ISLANDS IN MALDIVES

_________________________________

LOT ONE: 23-MW/23-MWh Battery Energy Storage Systems (BESS) on locations at Addu City mainland and Hulhudhoo-Meedhoo, Fuvahmulah City, GDh. Thinadhoo, Kulhudhuffushi City, B. Eydhafushi and Lh. Hinnavaru

LOT TWO:  13.5-MW/17-MWh Battery Energy Storage Systems (BESS) on locations at L. Atoll Islands (Fonadhoo, Gan, Dhanbidhoo, Isdhoo-Kalaidhoo, Maabaidhoo, Maamendhoo, Kunahandhoo-Hithadhoo and Maavah), Lh. Naifaru, Dh. Kudahuvadhoo, GA. Villingili and Sh. Funadhoo

_________________________________

RFB No: MV-MEE-283164-GO-RFB

Accelerating Renewable Energy Integration and Sustainable Energy (ARISE)

Ministry of Environment, Climate Change and Technology

Republic of Maldives

Issued on: August 07, 2022

Issued by: National Tender

Ministry of Finance

Republic of Maldives

Standard Procurement Document

Table of Contents

PART 1 – Bidding Procedures	3

Section I - Instructions to Bidders	5

Section II - Bid Data Sheet	37

Section III - Evaluation and Qualification Criteria	43

Section IV - Bidding Forms	61

Section V - Eligible Countries	137

Section VI - Fraud and Corruption	139

PART 2 - Employer’s Requirements	141

Section VII - Employer’s Requirements	143

PART 3 – Conditions of Contract and Contract Forms	319

Section VIII - General Conditions of Contract	321

Section IX - Particular Conditions of Contract	415

Section X - Contract Forms	419

PART 1 – Bidding Procedures

# Section I - Instructions to Bidders

Contents

A.	General	7

1.	Scope of Bid	7

2.	Source of Funds	8

3.	Fraud and Corruption	8

4.	Eligible Bidders	8

5.	Eligible Plant and Installation Services	11

B.	Contents of Bidding Document	11

6.	Sections of  Bidding Document	11

7.	Clarification of Bidding Document, Site Visit, Pre-Bid Meeting	12

8.	Amendment of Bidding Document	13

C.	Preparation of Bids	14

9.	Cost of Bidding	14

10.	Language of Bid	14

11.	Documents Comprising the Bid	14

12.	Letter of Bid and Price Schedules	15

13.	Alternative Bids	15

14.	Documents Establishing the Eligibility of the Plant and Installation Services	15

15.	Documents Establishing the Eligibility and Qualifications of the Bidder	16

16.	Documents Establishing the Conformity of the Plant and  Installation Services	16

17.	Bid Prices and Discounts	16

18.	Currencies of Bid and Payment	19

19.	Period of Validity of Bids	19

20.	Bid Security	20

21.	Format and Signing of Bid	22

D.	Submission and Opening of Bids	22

22.	Submission, Sealing and Marking of Bids	22

23.	Deadline for Submission of Bids	23

24.	Late Bids	23

25.	Withdrawal, Substitution, and Modification of Bids	23

26.	Bid Opening	24

E.	Evaluation and Comparison of Bids	25

27.	Confidentiality	25

28.	Clarification of Bids	26

29.	Deviations, Reservations, and Omissions	26

30.	Determination of  Responsiveness	26

31.	Nonmaterial Nonconformities	27

32.	Correction of Arithmetical Errors	27

33.	Conversion to Single Currency	28

34.	Margin of Preference	28

35.	Evaluation of Bids	28

36.	Comparison of Bids	29

37.	Abnormally Low Bids	30

38.	Unbalanced or Front Loaded Bids	30

39.	Eligibility and Qualification of the Bidder	30

40.	Employer’s right to Accept Any Bid and to Reject Any or All Bids	31

41.	Standstill Period	31

42.	Notification of Intention to Award	32

F.	Award of Contract	32

43.	Award Criteria	32

44.	Notification of Award	32

45.	Debriefing by the Employer	33

46.	Signing of Contract	34

47.	Performance Security	34

48.	Procurement Related Complaint	35

# Section I - Instructions to Bidders

| - General |  |
| --- | --- |
| - Scope of Bid | - In connection with the Specific Procurement Notice - Request for Bids (RFB), specified in the Bid Data Sheet (BDS), the Employer, as specified in the BDS, issues this bidding document for the Design, Supply and Installation of Plant as specified in Section VII, Employer’s Requirements. The name, identification and number of lots (contracts) of this RFB are specified in the BDS. - Throughout this bidding document: ### the term “in writing” means communicated in written form (e.g. by mail, e-mail, fax, including if specified in the BDS, distributed or received through the electronic-procurement system used by the Employer) with proof of receipt; ### if the context so requires, “singular” means “plural” and vice versa; ### “Day” means calendar day, unless otherwise specified as “Business Day.” A Business Day is any day that is an official working day of the Borrower. It excludes the Borrower’s official public holidays; ### “ES” means environmental and social (including Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH)); ### “Sexual Exploitation and Abuse” “(SEA)” means the following: ### Sexual Exploitation is defined as any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another. ### Sexual Abuse is defined as the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions. ### “Sexual Harassment” “(SH)” is defined as unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature by the Contractor’s Personnel with other Contractor’s or Employer’s Personnel. ### “Contractor’s Personnel” is as defined in GCC Sub-Clause 1; and ### “Employer’s Personnel” is as defined in GCC Sub-Clause 1. A non-exhaustive list of (i) behaviors which constitute SEA and (ii) behaviors which constitute SH is attached to the Code of Conduct form in Section IV. |
| - Source of Funds | - The Borrower or Recipient (hereinafter called “Borrower”) indicated in the BDS has applied for or received financing (hereinafter called “funds”) from the World Bank (hereinafter called “the Bank”) in an amount specified in BDS, toward the project named in BDS. The Borrower intends to apply a portion of the funds to eligible payments under the contract(s) for which this bidding document is issued. - Payment by the Bank will be made only at the request of the Borrower and upon approval by the Bank in accordance with the terms and conditions of the Loan (or other financing) Agreement. The Loan (or other financing) Agreement prohibits a withdrawal from the loan account for the purpose of any payment to persons or entities, or for any import of goods, equipment, plant, or materials, if such payment or import is prohibited by a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations. No party other than the Borrower shall derive any rights from the Loan (or other financing) Agreement or have any claim to the proceeds of the Loan (or other financing). |
| - Fraud and Corruption | - The Bank requires compliance with the Bank’s Anti-Corruption Guidelines and its prevailing sanctions policies and procedures as set forth in the WBG’s Sanctions Framework, as set forth in Section VI. - In further pursuance of this policy, bidders shall permit and shall cause their agents (where declared or not), subcontractors, subconsultants, service providers, suppliers, and personnel, to permit the Bank to inspect all accounts, records and other documents relating to any initial selection process, prequalification process, bid submission, proposal submission and contract performance (in the case of award), and to have them audited by auditors appointed by the Bank. |
| - Eligible Bidders | - A Bidder may be a firm that is a private entity, a state-owned enterprise or institution subject to ITB 4.6, or any combination of such entities in the form of a joint venture (JV) under an existing agreement or with the intent to enter into such an agreement supported by a letter of intent. In the case of a joint venture, all members shall be jointly and severally liable for the execution of the entire Contract in accordance with the Contract terms. The JV shall nominate a Representative who shall have the authority to conduct all business for and on behalf of any and all the members of the JV during the Bidding process and, in the event the JV is awarded the Contract, during contract execution. Unless specified in the BDS, there is no limit on the number of members in a JV. - A Bidder shall not have a conflict of interest. Any Bidder found to have a conflict of interest shall be disqualified. A Bidder may be considered to have a conflict of interest for the purpose of this Bidding process, if the Bidder: ### directly or indirectly controls, is controlled by or is under common control with another Bidder; or ### receives or has received any direct or indirect subsidy from another Bidder; or ### has the same legal representative as another Bidder; or ### has a relationship with another Bidder, directly or through common third parties, that puts it in a position to influence the Bid of another Bidder, or influence the decisions of the Employer regarding this Bidding process; or ### or any of its affiliates participated as a consultant in the preparation of the design or technical specifications of the Plant and Installation Services that are the subject of the Bid; or ### or any of its affiliates has been hired (or is proposed to be hired) by the Employer or Borrower as Project Manager for the Contract implementation; or ### would be providing goods, works, or non-consulting services resulting from or directly related to consulting services for the preparation or implementation of the project specified in the BDS ITB 2.1 that it provided or were provided by any affiliate that directly or indirectly controls, is controlled by, or is under common control with that firm; or ### has a close business or family relationship with a professional staff of the Borrower (or of the project implementing agency, or of a recipient of a part of the loan) who: (i) are directly or indirectly involved in the preparation of the bidding document or specifications of the Contract, and/or the Bid evaluation process of such Contract; or (ii) would be involved in the implementation or supervision of such contract unless the conflict stemming from such relationship has been resolved in a manner acceptable to the Bank throughout the Bidding process and execution of the Contract. - A firm that is a Bidder (either individually or as a JV member) shall not participate as a Bidder or as JV member in more than one Bid except for permitted alternative Bids. Such participation shall result in the disqualification of all Bids in which the firm is involved. However, this does not limit the participation of a Bidder as subcontractor in another Bid or of a firm as a subcontractor in more than one Bid. - A Bidder may have the nationality of any country, subject to the restrictions pursuant to ITB 4.8. A Bidder shall be deemed to have the nationality of a country if the Bidder is constituted, incorporated or registered in and operates in conformity with the provisions of the laws of that country, as evidenced by its articles of incorporation (or equivalent documents of constitution or association) and its registration documents, as the case may be. This criterion also shall apply to the determination of the nationality of proposed subcontractors or subconsultants for any part of the Contract including related Services. - A Bidder that has been sanctioned by the Bank, pursuant to the Bank’s Anti-Corruption Guidelines, in accordance with its prevailing sanctions policies and procedures as set forth in the WBG’s Sanctions Framework as described in Section VI paragraph 2.2 d., shall be ineligible to be prequalified for, initially selected for, bid for, propose for, or be awarded a Bank-financed contract or benefit from a Bank-financed contract, financially or otherwise, during such period of time as the Bank shall have determined. The list of debarred firms and individuals is available at the electronic address specified in the BDS. - Bidders that are state-owned enterprises or institutions in the Employer’s Country may be eligible to compete and be awarded a Contract(s) only if they can establish, in a manner acceptable to the Bank, that they (i) are legally and financially autonomous (ii) operate under commercial law, and (iii) are not under supervision of the Employer. - A Bidder shall not be under suspension from Bidding by the Employer as the result of the operation of a Bid-Securing Declaration or Proposal-Securing Declaration. - Firms and individuals may be ineligible if so indicated in Section V and (a)as a matter of law or official regulations, the Borrower’s country prohibits commercial relations with that country, provided that the Bank is satisfied that such exclusion does not preclude effective competition for the supply of goods or the contracting of works or services required; or (b)by an act of compliance with a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations, the Borrower’s country prohibits any import of goods or contracting of works or services from that country, or any payments to any country, person, or entity in that country. Where the procurement is implemented across jurisdictional boundaries (and more than one country is a Borrower, and is involved in the procurement), then exclusion of a firm or individual on the basis of ITB 4.8 (a) above by any country may be applied to that procurement across other countries involved, if the Bank and the Borrowers involved in the procurement agree. - A Bidder shall provide such documentary evidence of eligibility satisfactory to the Employer, as the Employer shall reasonably request. - A firm that is under a sanction of debarment by the Borrower from being awarded a contract is eligible to participate in this procurement, unless the Bank, at the Borrower’s request, is satisfied that the debarment; (a) relates to fraud or corruption, and (b) followed a judicial or administrative proceeding that afforded the firm adequate due process. |
| - Eligible Plant and Installation Services | - The Plant and Installation Services to be supplied under the Contract and financed by the Bank may have their origin in any country in accordance with Section V, Eligible Countries. - For purposes of ITB 5.1 above, “origin” means the place where the Plant, or component parts thereof are mined, grown, produced or manufactured, and from which the services are provided. Plant components are produced when, through manufacturing, processing, or substantial or major assembling of components, a commercially recognized product results that is substantially different in its basic characteristics or in purpose or utility from its components. |
| - Contents of Bidding Document |  |
| - Sections of Bidding Document | - The bidding document consists of Parts 1, 2, and 3, which include all the sections indicated below, and should be read in conjunction with any Addenda issued in accordance with ITB 8. PART 1. Bidding Procedures - Section I - Instructions to Bidders (ITB) - Section II - Bid Data Sheet (BDS) - Section III - Evaluation and Qualification Criteria - Section IV - Bidding Forms - Section V - Eligible Countries - Section VI - Fraud and Corruption PART 2. Employer’s Requirements - Section VII -Employer’s Requirements PART 3. Conditions of Contract and Contract Forms - Section VIII - General Conditions of Contract (GCC) - Section IX -Particular Conditions of Contract (PCC) - Section X -Contract Forms - The Specific Procurement Notice-Request for Bids (RFB) issued by the Employer is not part of the bidding document. - Unless obtained directly from the Employer, the Employer is not responsible for the completeness of the document, responses to requests for clarification, the Minutes of the pre-Bid meeting (if any), or Addenda to the bidding document in accordance with ITB 8. In case of any contradiction, documents obtained directly from the Employer shall prevail. - The Bidder is expected to examine all instructions, forms, terms, and specifications in the bidding document and to furnish with its Bid all information or documentation as is required by the bidding document. |
| - Clarification of Bidding Document, Site Visit, Pre-Bid Meeting | - A Bidder requiring any clarification of the bidding document shall contact the Employer in writing at the Employer’s address indicated in the BDS or raise his enquiries during the pre-Bid meeting if provided for in accordance with ITB 7.4. The Employer will respond in writing to any request for clarification, provided that such request is received prior to the deadline for submission of Bids within a period specified in the BDS. The Employer shall forward copies of its response to all Bidders who have acquired the bidding document in accordance with ITB 6.3, including a description of the inquiry but without identifying its source. If so specified in the BDS, the Employer shall also promptly publish its response at the web page identified in the BDS. Should the clarification result in changes to the essential elements of the bidding document, the Employer shall amend the bidding document following the procedure under ITB 8 and ITB 23.2. - The Bidder is advised to visit and examine the site where the Plant is to be installed and its surroundings and obtain for itself on its own responsibility all information that may be necessary for preparing the Bid and entering into a Contract for the provision of Plant and Installation Services. The costs of visiting the site shall be at the Bidder’s own expense. - The Bidder and any of its personnel or agents will be granted permission by the Employer to enter upon its premises and lands for the purpose of such visit, but only upon the express condition that the Bidder, its personnel, and agents will release and indemnify the Employer and its personnel and agents from and against all liability in respect thereof, and will be responsible for death or personal injury, loss of or damage to property, and any other loss, damage, costs, and expenses incurred as a result of the inspection. - If so specified in the BDS, the Bidder’s designated representative is invited to attend a pre-Bid meeting and/or a site visit. The purpose of the meeting will be to clarify issues and to answer questions on any matter that may be raised at that stage. - The Bidder is requested to submit any questions in writing, to reach the Employer not later than one week before the meeting. - Minutes of the pre-Bid meeting, including the text of the questions raised without identifying the source, and the responses given, together with any responses prepared after the meeting, will be transmitted promptly to all Bidders who have acquired the bidding document in accordance with ITB 6.3. If so specified in the BDS, the Employer shall also promptly publish the Minutes of the pre-Bid meeting at the web page identified in the BDS. Any modification to the bidding document that may become necessary as a result of the pre-Bid meeting shall be made by the Employer exclusively through the issue of an Addendum pursuant to ITB 8 and not through the minutes of the pre-Bid meeting. Nonattendance at the pre-Bid meeting will not be a cause for disqualification of a Bidder. |
| - Amendment of Bidding Document | - At any time prior to the deadline for submission of Bids, the Employer may amend the bidding document by issuing addenda. - Any addendum issued shall be part of the bidding document and shall be communicated in writing to all who have obtained the bidding document from the Employer in accordance with ITB 6.3. The Employer shall also promptly publish the addendum on the Employer’s web page in accordance with ITB 7.1. - To give prospective Bidders reasonable time in which to take an addendum into account in preparing their Bids, the Employer may, at its discretion, extend the deadline for the submission of bids, pursuant to ITB 23.2. |
| - Preparation of Bids |  |
| - Cost of Bidding | - The Bidder shall bear all costs associated with the preparation and submission of its Bid, and the Employer shall not be responsible or liable for those costs, regardless of the conduct or outcome of the Bidding process. |
| - Language of Bid | - The Bid, as well as all correspondence and documents relating to the Bid exchanged by the Bidder and the Employer, shall be written in the language specified in the BDS. Supporting documents and printed literature that are part of the Bid may be in another language provided they are accompanied by an accurate translation of the relevant passages in the language specified in the BDS, in which case, for purposes of interpretation of the Bid, such translation shall govern. |
| - Documents Comprising the Bid | - The Bid shall comprise the following: - Letter of Bid prepared in accordance with ITB12.1; - Price Schedules completed in accordance with ITB 12 and ITB 17; - Bid Security or Bid Securing Declaration, in accordance with ITB 20; - Alternative Bid, if permissible, in accordance with ITB 13; - Authorization: written confirmation authorizing the signatory of the Bid to commit the Bidder, in accordance with ITB 21.3; - Eligibility of Plant and Installation Services: documentary evidence established in accordance with ITB 14.1 that the Plant and Installation Services offered by the Bidder in its Bid or in any alternative Bid, if permitted, are eligible; - Bidder’s Eligibility and Qualifications: documentary evidence in accordance with ITB 15.1 establishing the Bidder’s eligibility and qualifications to perform the Contract if its Bid is accepted; - Conformity: documentary evidence in accordance to ITB 16that the Plant and Installation Services offered by the Bidder conform to the bidding document; - Subcontractors: list of subcontractors in accordance with ITB 16.2; and - any other document required in the BDS. - In addition to the requirements under ITB 11.1, Bids submitted by a JV shall include a copy of the Joint Venture Agreement entered into by all members. Alternatively, a letter of intent to execute a Joint Venture Agreement in the event of a successful Bid shall be signed by all members and submitted with the Bid, together with a copy of the proposed Agreement. - The Bidder shall furnish in the Letter of Bid information on commissions and gratuities, if any, paid or to be paid to agents or any other party relating to this Bid |  |
| - Letter of Bid and Price Schedules | - The Letter of Bid and Price Schedules shall be prepared, using the relevant forms furnished in Section IV, Bidding Forms. The forms must be completed as instructed in each form without any alterations to the text, and no substitutes shall be accepted except as provided under ITB 21.3. All blank spaces shall be filled in with the information requested. |
| - Alternative Bids | - Unless otherwise specified in the BDS, alternative Bids shall not be considered. - When alternatives to the Time Schedule are explicitly invited, a statement to that effect will be included in the BDS, and the method of evaluating different time schedules will be described in Section III, Evaluation and Qualification Criteria. - Except as provided under ITB 13.4 below, Bidders wishing to offer technical alternatives to the Employer’s requirements as described in the bidding document must also provide: (i) a price at which they are prepared to offer a Plant meeting the Employer’s requirements; and (ii) all information necessary for a complete evaluation of the alternatives by the Employer, including drawings, design calculations, technical specifications, breakdown of prices, and proposed installation methodology and other relevant details. Only the technical alternatives, if any, of the Bidder with the Most Advantageous Bid conforming to the basic technical requirements shall be considered by the Employer. - When Bidders are invited in the BDS to submit alternative technical solutions for specified parts of the facilities, such parts will be identified in the BDS, as will the method for their evaluation, and described in Section VII, Employer’s Requirements. |
| - Documents Establishing the Eligibility of the Plant and Installation Services | - To establish the eligibility of the Plant and Installation Services in accordance with ITB 5, Bidders shall complete the country of origin declarations in the Price Schedule Forms, included in Section IV, Bidding Forms. |
| - Documents Establishing the Eligibility and Qualifications of the Bidder | - To establish its eligibility and qualifications to perform the Contract in accordance with Section III, Evaluation and Qualification Criteria, the Bidder shall provide the information requested in the corresponding information sheets included in Section IV, Bidding Forms. |
| - Documents Establishing the Conformity of the Plant and Installation Services | - The Bidder shall furnish the information stipulated in Section IV, Bidding Forms in sufficient detail to demonstrate substantial responsiveness of the Bidders’ proposal to the work requirements and the completion time. - For major items of Plant and Installation Services as listed by the Employer in Section III, Evaluation and Qualification Criteria, which the Bidder intends to purchase or subcontract, the Bidder shall give details of the name and nationality of the proposed Subcontractors, including manufacturers, for each of those items. In addition, the Bidder shall include in its Bid information establishing compliance with the requirements specified by the Employer for these items. Quoted rates and prices will be deemed to apply to whichever Subcontractor is appointed, and no adjustment of the rates and prices will be permitted. - The Bidder shall be responsible for ensuring that any Subcontractor proposed complies with the requirements of ITB 4, and that any Plant, or services to be provided by the Subcontractor comply with the requirements of ITB 5 and ITB 16.1. |
| - Bid Prices and Discounts | - Unless otherwise specified in the BDS, Bidders shall quote for the entire Plant and Installation Services on a “single responsibility” basis. The total Bid price shall include all the Contractor’s obligations mentioned in or to be reasonably inferred from the bidding document in respect of the design, manufacture, including procurement and subcontracting (if any), delivery, construction, installation and completion of the Plant. This includes all requirements under the Contractor’s responsibilities for testing, pre-commissioning and commissioning of the Plant and, where so required by the bidding document, the acquisition of all permits, approvals and licenses, etc.; the operation, maintenance and training services and such other items and services as specified in the bidding document, all in accordance with the requirements of the General Conditions. Items against which no price is entered by the Bidder will not be paid for by the Employer when executed and shall be deemed to be covered by the prices for other items. - Bidders are required to quote the price for the commercial, contractual and technical obligations outlined in the bidding document. - Bidders shall give a breakdown of the prices in the manner and detail called for in the Price Schedules included in Section IV, Bidding Forms. Depending on the scope of the Contract, the Price Schedules may comprise up to the six (6) schedules listed below. Separate numbered Schedules included in Section IV, Bidding Forms, from those numbered 1 to 4 below, shall be used for each of the elements of the Plant and Installation Services. The total amount from each Schedule corresponding to an element of the Plant and Installation Services shall be summarized in the schedule titled Grand Summary, (Schedule 5), giving the total Bid price(s) to be entered in the Letter of Bid. Bidders shall note that the plant and equipment included in Schedule Nos. 1 and 2 below exclude materials used for civil, building and other construction works. All such materials shall be included and priced under Schedule No. 4, Installation Services. The Schedules comprise: Schedule No. 1: Plant (including Mandatory Spare Parts) Supplied from Abroad Schedule No. 2: Plant (including Mandatory Spare Parts) Supplied from within the Employer’s Country Schedule No. 3: Design Services Schedule No. 4: Installation Services Schedule No. 5: Grand Summary (Schedule Nos.1 to 4) Schedule No. 6: Recommended Spare Parts - In the Schedules, Bidders shall give the required details and a breakdown of their prices as follows: - Plant to be supplied from abroad (Schedule No. 1): The price of the Plant shall be quoted on CIP-named place of destination basis as specified in the BDS. - Plant manufactured within the Employer’s Country (Schedule No. 2): (i) The price of the Plant shall be quoted on an EXW Incoterm basis (such as “ex-works,” “ex-factory,” “ex-warehouse” or “off-the-shelf,” as applicable), including all customs duties, sales and other taxes already paid or payable on the components and raw materials used in the manufacture or assembly of the Plant; (ii) Sales tax and all other taxes payable in the Employer’s Country on the Plant if the contract is awarded to the Bidder; - Design Services (Schedule No. 3); - Installation Services shall be quoted separately (Schedule No. 4) and shall include rates or prices for local transportation to named place of final destination as specified in the BDS, insurance and other services incidental to delivery of the Plant, all labor, contractor’s equipment, temporary works, materials, consumables and all matters and things of whatsoever nature, including operations and maintenance services, the provision of operations and maintenance manuals, training, etc., where identified in the bidding document, as necessary for the proper execution of the installation and other services, including all taxes, duties, levies and charges payable in the Employer’s Country as of twenty-eight (28) days prior to the deadline for submission of Bids; (e) Recommended spare parts shall be quoted separately (Schedule 6) as specified in either subparagraph (a) or (b) above in accordance with the origin of the spare parts. - The terms EXW, CIP, and other similar terms shall be governed by the rules prescribed in the current edition of Incoterms, published by the International Chamber of Commerce, as specified in the BDS. - The prices shall be either fixed or adjustable as specified in the BDS. - In the case of Fixed Price, prices quoted by the Bidder shall be fixed during the Bidder’s performance of the contract and not subject to variation on any account. A Bid submitted with an adjustable price quotation will be treated as non-responsive and rejected. - In the case of Adjustable Price, prices quoted by the Bidder shall be subject to adjustment during performance of the contract to reflect changes in the cost elements such as labor, material, transport and contractor’s equipment in accordance with the procedures specified in the corresponding Appendix to the Contract Agreement. A Bid submitted with a fixed price quotation will not be rejected, but the price adjustment will be treated as zero. Bidders are required to indicate the source of labor and material indices in the corresponding Form in Section IV, Bidding Forms. - If so indicated in ITB 1.1, Bids are being invited for individual lots (contracts) or for any combination of lots (packages). Bidders wishing to offer any price reduction (discount) for the award of more than one Contract shall specify in their Letter of Bid the price reductions applicable to each package, or alternatively, to individual Contracts within the package, and the manner in which the price reductions will apply. - Bidders wishing to offer any unconditional discount shall specify in their Letter of Bid the offered discounts and the manner in which price discounts will apply. |
| - Currencies of Bid and Payment | - The currency(ies) of the Bid and the currency(ies) of payments shall be the same. The Bidder shall quote in the currency of the Employer’s country the portion of the Bid price that corresponds to expenditures incurred in the currency of the Employer’s Country, unless otherwise specified in the BDS. - The Bidder may express the Bid price in any currency. If the Bidder wishes to be paid in a combination of amounts in different currencies, it may quote its price accordingly but shall use no more than three foreign currencies in addition to the currency of the Employer’s Country. |
| - Period of Validity of Bids | - Bids shall remain valid until the date specified in the BDS or any extended date if amended by the Employer in accordance with ITB 8. A Bid that is not valid until the date specified in the BDS, or any extended date if amended by the Employer in accordance with ITB 8, shall be rejected by the Employer as nonresponsive. - In exceptional circumstances, prior to the date of expiration of the Bid validity, the Employer may request Bidders to extend the period of validity of their Bids. The request and the responses shall be made in writing. If a Bid Security is requested in accordance with ITB 20, the Bidder granting the request shall also extend the Bid Security for twenty-eight (28) days beyond the deadline of the extended validity period. A Bidder may refuse the request without forfeiting its Bid Security. A Bidder granting the request shall not be required or permitted to modify its Bid, except as provided in ITB 19.3. - If the award is delayed by a period exceeding fifty-six (56) days beyond the expiry of the initial Bid validity specified in accordance with ITB 19.1, the Contract price shall be determined as follows: - in the case of fixed price contracts, the Contract price shall be the Bid price adjusted by the factor or factors specified in the BDS; - in the case of adjustable price contracts, no adjustment shall be made; or - in any case, Bid evaluation shall be based on the Bid price without taking into consideration the applicable correction from those indicated above. |
| - Bid Security | - The Bidder shall furnish as part of its Bid, either a Bid-Securing Declaration or a Bid Security as specified in the BDS, in original form and, in the case of a Bid Security, in the amount and currency specified in the BDS. - A Bid-Securing Declaration shall use the form included in Section IV Bidding Forms. - If a Bid Security is specified pursuant to ITB 20.1, the Bid security shall be a demand guarantee in any of the following forms at the Bidder’s option: - an unconditional guarantee issued by a bank or non-bank financial institution (such as an insurance, bonding or surety company); - an irrevocable letter of credit; - a cashier’s or certified check; or - another security indicated in the BDS, - from a reputable source from an eligible country. If an unconditional guarantee is issued by a non-bank financial institution located outside the Employer’s Country the issuing non-bank financial institution shall have a correspondent financial institution located in the Employer’s Country to make it enforceable unless the Employer has agreed in writing, prior to Bid submission, that a correspondent financial institution is not required. In the case of a bank guarantee, the Bid Security shall be submitted either using the Bid Security Form included in Section IV, Bidding Forms, or in another substantially similar format approved by the Employer prior to Bid submission. The Bid Security shall be valid for twenty-eight (28) days beyond the original date of expiry of the Bid validity , or beyond any extended date if requested under ITB 19.2. - If a Bid Security or a Bid-Securing Declaration is specified pursuant to ITB 20.1, any Bid not accompanied by a substantially responsive Bid Security or Bid-Securing Declaration shall be rejected by the Employer as nonresponsive. - If a Bid Security is specified pursuant to ITB 20.1, the Bid Security of unsuccessful Bidders shall be returned as promptly as possible upon the successful Bidder’s furnishing of the Performance Security pursuant to ITB 47. - The Bid Security of the successful Bidder shall be returned as promptly as possible once the successful Bidder has signed the Contract and furnished the required Performance Security. - The Bid Security may be forfeited: - if a Bidder withdraws its Bid prior to the expiry date of the Bid validity specified by the Bidder on the Letter of Bid or any extended date provided by the Bidder; or - if the successful Bidder fails to: - sign the Contract in accordance with ITB 46; or - furnish a Performance Security in accordance with ITB 47. - The Bid Security or the Bid-Securing Declaration of a JV shall be in the name of the JV that submits the Bid. If the JV has not been legally constituted into a legally enforceable JV at the time of bidding, the Bid Security or the Bid Securing Declaration shall be in the names of all future members as named in the letter of intent referred to in ITB 4.1 and ITB 11.2. - If a Bid Security is not required in the BDS: and - if a Bidder withdraws its Bid prior to the expiry date of the Bid validity specified by the Bidder on the Letter of Bid, or any extended date provided by the Bidder; or - if the successful Bidder fails to: - sign the Contract in accordance with ITB 46; or - furnish a Performance Security in accordance with ITB 47; - the Borrower may, if provided for in the BDS, declare the Bidder disqualified to be awarded a contract by the Employer for a period of time as stated in the BDS. |
| - Format and Signing of Bid | - The Bidder shall prepare one original of the documents comprising the bid as described in ITB 11 and clearly mark it “Original.” Alternative Bids, if permitted in accordance with ITB 13, shall be clearly marked “Alternative”. In addition, the Bidder shall submit copies of the Bid, in the number specified in the BDS and clearly mark them “Copy.” In the event of any discrepancy between the original and the copies, the original shall prevail. - Bidders shall mark as “Confidential” information in their Bids which is confidential to their business. This may include proprietary information, trade secrets or commercial or financially sensitive information. - The original and all copies of the Bid shall be typed or written in indelible ink and shall be signed by a person duly authorized to sign on behalf of the Bidder. This authorization shall consist of a written confirmation as specified in the BDS and shall be attached to the Bid. The name and position held by each person signing the authorization must be typed or printed below the signature. All pages of the Bid where entries or amendments have been made shall be signed or initialed by the person signing the Bid. - In the case that the Bidder is a JV, the Bid shall be signed by an authorized representative of the JV on behalf of the JV, and so as to be legally binding on all the members as evidenced by a power of attorney signed by their legally authorized representatives. - Any interlineations, erasures, or overwriting shall be valid only if they are signed or initialed by the person signing the Bid. |
| - Submission and Opening of Bids |  |
| - Submission, Sealing and Marking of Bids | - The Bidder shall deliver the Bid in a single, sealed envelope (one (1) envelope process). Within the single envelope the Bidder shall place the following separate, sealed envelopes: - in an envelope marked “Original”, all documents comprising the Bid, as described in ITB 11; and - in an envelope marked “Copies”, all required copies of the Bid; and - if alternative Bids are permitted in accordance with ITB 13, and if relevant: - in an envelope marked “Original–Alternative Bid” the alternative Bid; and - in the envelope marked “Copies – Alternative Bid” all required copies of the alternative Bid. - The inner and outer envelopes shall: - bear the name and address of the Bidder; - be addressed to the Employer in accordance with ITB 23.1; - bear the specific identification of this Bidding process indicated in accordance with ITB 1.1; and - bear a warning not to open before the time and date for Bid opening. - If all envelopes are not sealed and marked as required, the Employer will assume no responsibility for the misplacement or premature opening of the Bid. |
| - Deadline for Submission of Bids | - Bids must be received by the Employer at the address and no later than the date and time indicated in the BDS. When so specified in the BDS, Bidders shall have the option of submitting their Bids electronically. Bidders submitting Bids electronically shall follow the electronic Bid submission procedures specified in the BDS. - The Employer may, at its discretion, extend the deadline for the submission of Bids by amending the bidding document in accordance with ITB 8, in which case all rights and obligations of the Employer and Bidders previously subject to the deadline shall thereafter be subject to the deadline as extended. |
| - Late Bids | - The Employer shall not consider any Bid that arrives after the deadline for submission of Bids, in accordance with ITB 23. Any Bid received by the Employer after the deadline for submission of Bids shall be declared late, rejected, and returned unopened to the Bidder. |
| - Withdrawal, Substitution, and Modification of Bids | - A Bidder may withdraw, substitute, or modify its bid after it has been submitted by sending a written notice, duly signed by an authorized representative, and shall include a copy of the authorization in accordance with ITB 21.3, (except that withdrawal notices do not require copies). The corresponding substitution or modification of the Bid must accompany the respective written notice. All notices must be: - prepared and submitted in accordance with ITB 21 and ITB 22 (except that withdrawals notices do not require copies), and in addition, the respective envelopes shall be clearly marked “Withdrawal,” “Substitution,” “Modification”; and - received by the Employer prior to the deadline prescribed for submission of Bids, in accordance with ITB 23. - Bids requested to be withdrawn in accordance with ITB 25.1 shall be returned unopened to the Bidders. - No Bid may be withdrawn, substituted, or modified in the interval between the deadline for submission of Bids and the date of expiry of the Bid validity specified by the Bidder on the Letter of Bid or any extended date thereof. |
| - Bid Opening | - Except as in the cases specified in ITB 24 and ITB 25.2, the Employer shall publicly open and read out in accordance with ITB 26.5 all Bids received by the deadline at the date, time and place specified in the BDS in the presence of Bidders’ designated representatives and anyone who choose to attend. Any specific electronic Bid opening procedures required if electronic Bidding is permitted in accordance with ITB 23.1, shall be as specified in the BDS. - First, the written notice of withdrawal in the envelopes marked “Withdrawal” shall be opened and read out and the envelope with the corresponding Bid shall not be opened, but returned to the Bidder. No bid withdrawal shall be permitted unless the corresponding withdrawal notice contains a valid authorization to request the withdrawal and is read out at Bid opening. - Next, envelopes marked “Substitution” shall be opened and read out and exchanged with the corresponding Bid being substituted, and the substituted Bid shall not be opened, but returned to the Bidder. No Bid substitution shall be permitted unless the corresponding substitution notice contains a valid authorization to request the substitution and is read out at Bid opening. - Next, envelopes marked “Modification” shall be opened and read out with the corresponding Bid. No Bid modification shall be permitted unless the corresponding modification notice contains a valid authorization to request the modification and is read out at Bid opening. - Next, all remaining envelopes shall be opened one at a time, reading out: the name of the Bidder and the Bid Price(s), including any discounts and alternative Bids, and indicating whether there is a modification; the presence or absence of a Bid Security or Bid-Securing Declaration, if required; and any other details as the Employer may consider appropriate. - Only Bids, alternative Bids and discounts that are opened and read out at Bid opening shall be considered further. The Letter of Bid and the Price Schedules are to be initialed by representatives of the Employer attending Bid opening in the manner specified in the BDS. - The Employer shall neither discuss the merits of any Bid nor reject any Bid (except for late Bids, in accordance with ITB 24.1). - The Employer shall prepare a record of the Bid opening that shall include, as a minimum: - the name of the Bidder and whether there is a withdrawal, substitution, or modification; - the Bid Price, per lot if applicable, including any discounts; - any alternative Bids; and - the presence or absence of a Bid Security or a Bid-Securing Declaration. - The Bidders’ representatives who are present shall be requested to sign the record. The omission of a Bidder’s signature on the record shall not invalidate the contents and effect of the record. A copy of the record shall be distributed to all Bidders. |
| - Evaluation and Comparison of Bids |  |
| - Confidentiality | - Information relating to the evaluation of Bids and recommendation of contract award, shall not be disclosed to Bidders or any other persons not officially concerned with the Bidding process until information on Intention to Award the Contract is transmitted to all Bidders in accordance with ITB 42. - Any effort by a Bidder to influence the Employer in the evaluation of the bids or Contract award decisions may result in the rejection of its Bid. - Notwithstanding ITB 27.2, from the time of Bid opening to the time of Contract Award, if any Bidder wishes to contact the Employer on any matter related to the Bidding process, it should do so in writing. |
| - Clarification of Bids | - To assist in the examination, evaluation, and comparison of the Bids, and qualification of the Bidders, the Employer may, at its discretion, ask any Bidder for a clarification of its Bid. Any clarification submitted by a Bidder that is not in response to a request by the Employer shall not be considered. The Employer’s request for clarification and the response shall be in writing. No change in the prices or substance of the Bid shall be sought, offered, or permitted, except to confirm the correction of arithmetic errors discovered by the Employer in the evaluation of the Bids, in accordance with ITB 32. - If a Bidder does not provide clarifications of its Bid by the date and time set in the Employer’s request for clarification, its Bid may be rejected. |
| - Deviations, Reservations, and Omissions | - During the evaluation of Bids, the following definitions apply: (a) “Deviation” is a departure from the requirements specified in the bidding document; (b) “Reservation” is the setting of limiting conditions or withholding from complete acceptance of the requirements specified in the bidding document; and - “Omission” is the failure to submit part or all of the information or documentation required in the bidding document. |
| - Determination of Responsiveness | - The Employer’s determination of a Bid’s responsiveness is to be based on the contents of the Bid itself, as defined in ITB11. - A substantially responsive Bid is one that meets the requirements of the bidding document without material deviation, reservation, or omission. A material deviation, reservation, or omission is one that: - if accepted, would: #### affect in any substantial way the scope, quality, or performance of the Plant and Installation Services specified in the Contract; or #### limit in any substantial way, inconsistent with the bidding document, the Employer’s rights or the Bidder’s obligations under the proposed Contract; or - if rectified, would unfairly affect the competitive position of other Bidders presenting substantially responsive Bids. - The Employer shall examine the technical aspects of the Bid in particular, to confirm that all requirements of Section VII, Employer’s Requirements have been met without any material deviation, reservation, or omission. - If a Bid is not substantially responsive to the requirements of the bidding document, it shall be rejected by the Employer and may not subsequently be made responsive by correction of the material deviation, reservation, or omission. |
| - Nonmaterial Nonconformities | - Provided that a Bid is substantially responsive, the Employer may waive any nonconformity in the Bid that does not constitute a material deviation, reservation or omission. - Provided that a Bid is substantially responsive, the Employer may request that the Bidder submit the necessary information or documentation, within a reasonable period of time, to rectify nonmaterial nonconformities in the Bid related to documentation requirements. Requesting information or documentation on such nonconformities shall not be related to any aspect of the price of the Bid. Failure of the Bidder to comply with the request may result in the rejection of its Bid. - Provided that a Bid is substantially responsive, the Employer shall rectify quantifiable nonmaterial nonconformities related to the Bid Price. To this effect, the Bid Price shall be adjusted, for comparison purposes only to reflect the price of a missing or non-conforming item or component, by adding the average price of the item or component quoted by substantially responsive Bidders. If the price of the item or component cannot be derived from the price of other substantially responsive Bids, the Employer shall use its best estimate. |
| - Correction of Arithmetical Errors | - Provided that the Bid is substantially responsive, the Employer shall correct arithmetical errors on the following basis: - where there are errors between the total of the amounts given under the column for the price breakdown and the amount given under the Total Price, the former shall prevail and the latter will be corrected accordingly; - where there are errors between the total of the amounts of Schedule Nos. 1 to 4 and the amount given in Schedule No. 5 (Grand Summary), the former shall prevail and the latter will be corrected accordingly; and - if there is a discrepancy between words and figures, the amount in words shall prevail, unless the amount expressed in words is related to an arithmetic error, in which case the amount in figures shall prevail subject to (a) and (b) above. - Bidders shall be requested to accept correction of arithmetical errors. Failure to accept the correction in accordance with ITB 32.1, shall result in the rejection of the Bid. |
| - Conversion to Single Currency | - For evaluation and comparison purposes, the currency(ies) of the Bid shall be converted into a single currency as specified in the BDS. |
| - Margin of Preference | - No margin of domestic preference shall apply. |
| - Evaluation of Bids | - The Employer shall use the criteria and methodologies listed in this ITB and Section III, Evaluation and Qualification criteria. No other evaluation criteria or methodologies shall be permitted. By applying the criteria and methodologies the Employer shall determine the Most Advantageous Bid. This is the Bid of the Bidder that meets the qualification criteria and that has been determined to be: (a) substantially responsive to the bidding document; and - (b) the lowest evaluated cost. - Technical Evaluation. The Employer will carry out a detailed technical evaluation of the Bids not previously rejected to determine whether the technical aspects are in compliance with the bidding document. The Bid that does not meet minimum acceptable standards of completeness, consistency and detail, and the specified minimum (or maximum, as the case may be) requirements for specified functional guarantees, will be rejected for non-responsiveness. In order to reach its determination, the Employer will examine and compare the technical aspects of the Bids on the basis of the information supplied by the Bidders, taking into account the following: (a) overall completeness and compliance with the Employer’s Requirements; conformity of the Plant and Installation Services offered with specified performance criteria, including conformity with the specified minimum (or maximum, as the case may be) requirement corresponding to each functional guarantee, as indicated in the Specification and in Section III, Evaluation and Qualification Criteria; suitability of the Plant and Installation Services offered in relation to the environmental and climatic conditions prevailing at the site; and quality, function and operation of any process control concept included in the Bid; (b) type, quantity and long-term availability of mandatory and recommended spare parts and maintenance services; and (c) other relevant factors, if any, listed in Section III, Evaluation and Qualification Criteria. - Where alternative technical solutions have been allowed in accordance with ITB 13, and offered by the Bidder, the Employer will make a similar evaluation of the alternatives. Where alternatives have not been allowed but have been offered, they shall be ignored. - Economic Evaluation. To evaluate a Bid, the Employer shall consider the following: - the Bid price, excluding provisional sums and the provision, if any, for contingencies in the Price Schedules; - price adjustment for correction of arithmetic errors in accordance with ITB 32.1; - price adjustment due to discounts offered in accordance with ITB 17.11; - price adjustment due to quantifiable nonmaterial nonconformities in accordance with ITB 31.3; - converting the amount resulting from applying (a) to (c) above, if relevant, to a single currency in accordance with ITB 33; and - the evaluation factors specified in the BDS and in Section III, Evaluation and Qualification Criteria. - If price adjustment is allowed in accordance with ITB 17.7, the estimated effect of the price adjustment provisions of the Conditions of Contract, applied over the period of execution of the Contract, shall not be taken into account in Bid evaluation. - If this bidding document allows Bidders to quote separate prices for different lots (contracts), and the award to a single Bidder of multiple lots (contracts), the methodology to determine the lowest evaluated cost of the lot (contract) combinations, including any discounts offered in the Letter of Bid, is specified in Section III, Evaluation and Qualification Criteria. |
| - Comparison of Bids | - The Employer shall compare the evaluated costs of all substantially responsive Bids established in accordance with ITB 35.4 to determine the Bid that has the lowest evaluated cost. |
| - Abnormally Low Bids | - An Abnormally Low Bid is one where the Bid price, in combination with other elements of the Bid, appears so low that it raises material concerns as to the capability of the Bidder to perform the Contract for the offered Bid Price. - In the event of identification of a potentially Abnormally Low Bid, the Employer shall seek written clarifications from the Bidder, including detailed price analyses of its Bid price in correlation to the subject matter of the contract, scope, proposed methodology, schedule, allocation of risks and responsibilities and any other requirements of the bidding document. - After evaluation of the price analyses, in the event that the Employer determines that the Bidder has failed to demonstrate its capability to deliver the contract for the offered tender price, the Employer shall reject the Bid. |
| - Unbalanced or Front Loaded Bids | - If the Bid that is evaluated as the lowest evaluated cost is, in the Employer’s opinion, seriously unbalanced or front loaded the Employer may require the Bidder to provide written clarifications. Clarifications may include detailed price analyses to demonstrate the consistency of the Bid prices with the scope of works, proposed methodology, schedule and any other requirements of the bidding document. - After the evaluation of the information and detailed price analyses presented by the Bidder, the Employer may: - accept the Bid; or - if appropriate, require that the total amount of the Performance Security be increased, at the expense of the Bidder, to a level not exceeding twenty percent (20%) of the Contract Price; or - reject the Bid. |
| - Eligibility and Qualification of the Bidder | - The Employer shall determine to its satisfaction whether the Bidder that is selected as having submitted the lowest evaluated cost and substantially responsive Bid is eligible and meets the qualifying criteria specified in Section III, Evaluation and Qualification Criteria. - The determination shall be based upon an examination of the documentary evidence of the Bidder’s qualifications submitted by the Bidder, pursuant to ITB 15.1.The determination shall not take into consideration the qualifications of other firms such as the Bidder’s subsidiaries, parent entities, affiliates, subcontractors (other than Specialized Subcontractors if permitted in the bidding document) or any other firm(s) different from the Bidder. - Prior to Contract award, the Employer will verify that the successful Bidder (including each member of a JV) is not disqualified by the Bank due to noncompliance with contractual SEA/SH prevention and response obligations. The Employer will conduct the same verification for each subcontractor proposed by the successful Bidder. If any proposed subcontractor does not meet the requirement, the Employer will require the Bidder to propose a replacement subcontractor. - An affirmative determination shall be a prerequisite for award of the Contract to the Bidder. A negative determination shall result in disqualification of the Bid, in which event the Employer shall proceed to the Bidder who offers a substantially responsive Bid with the next lowest evaluated cost to make a similar determination of that Bidder’s qualifications to perform satisfactorily. - The capabilities of the manufacturers and subcontractors proposed in its Bid to be used by the Bidder with the Most Advantageous Bid for identified major items of supply or services will also be evaluated for acceptability in accordance with Section III, Evaluation and Qualification Criteria. Their participation should be confirmed with a letter of intent between the parties, as needed. Should a manufacturer or subcontractor be determined to be unacceptable, the Bid will not be rejected, but the Bidder will be required to substitute an acceptable manufacturer or subcontractor without any change to the Bid price. Prior to signing the Contract, the corresponding Appendix to the Contract Agreement shall be completed, listing the approved manufacturers or subcontractors for each item concerned. |
| - Employer’s right to Accept Any Bid and to Reject Any or All Bids | - The Employer reserves the right to accept or reject any Bid, and to annul the Bidding process and reject all Bids at any time prior to Contract Award, without thereby incurring any liability to Bidders. In case of annulment, all Bids submitted and specifically, Bid securities shall be promptly returned to the Bidders. |
| - Standstill Period | - The Contract shall not be awarded earlier than the expiry of the Standstill Period. The Standstill Period shall be ten (10) Business Days unless extended in accordance with ITB 45. The Standstill Period commences the day after the date the Employer has transmitted to each Bidder the Notification of Intention to Award the Contract. Where only one Bid is submitted, or if this contract is in response to an emergency situation recognized by the Bank, the Standstill Period shall not apply. |
| - Notification of Intention to Award | The Employer shall send to each Bidder the Notification of Intention to Award the Contract to the successful Bidder. The Notification of Intention to Award shall contain, at a minimum, the following information: - the name and address of the Bidder submitting the successful Bid; - the Contract price of the successful Bid; - the names of all Bidders who submitted Bids, and their Bid prices as readout, and as evaluated; - a statement of the reason(s) the Bid (of the unsuccessful Bidder to whom the notification is addressed) was unsuccessful, unless the price information in c) above already reveals the reason; - the expiry date of the Standstill Period; and - instructions on how to request a debriefing and/or submit a complaint during the standstill period. |
| - Award of Contract |  |
| - Award Criteria | - 43.1 Subject to ITB 40, the Employer shall award the Contract to the successful Bidder. This is the Bidder whose Bid has been determined to be the Most Advantageous Bid. This is the Bid of the Bidder that meets the qualification criteria and whose Bid has been determined to be: - substantially responsive to the bidding document; and - the lowest evaluated cost. |
| - Notification of Award | - Prior to the date of expiry of the Bid Validity, and upon expiry of the Standstill Period, specified in ITB 41.1 or any extension thereof, and upon satisfactorily addressing any complaint that has been filed within the Standstill Period, the Employer shall notify the successful Bidder, in writing, that its Bid has been accepted. The notification of award (hereinafter and in the Contract Forms called the “Letter of Acceptance”) shall specify the sum that the Employer will pay the Contractor in consideration of the execution of the contract (hereinafter and in the Conditions of Contract and Contract Forms called “the Contract Price”). - Within ten (10) Business Days after the date of transmission of the Letter of Acceptance, the Employer shall publish the Contract Award Notice which shall contain, at a minimum, the following information: - name and address of the Employer; - name and reference number of the contract being awarded, and the selection method used; - names of all Bidders that submitted Bids, and their Bid prices as read out at Bid opening, and as evaluated; - names of all Bidders whose Bids were rejected either as nonresponsive or as not meeting qualification criteria, or were not evaluated, with the reasons therefor; - the name of the successful Bidder, the final total contract price, the contract duration and a summary of its scope; and - successful Bidder’s Beneficial Ownership Disclosure Form, if specified in BDS ITB 46.1. - The Contract Award Notice shall be published on the Employer’s website with free access if available, or in at least one newspaper of national circulation in the Employer’s Country, or in the official gazette. The Employer shall also publish the contract award notice in UNDB online. - Until a formal contract is prepared and executed, the Letter of Acceptance shall constitute a binding Contract |
| - Debriefing by the Employer | - On receipt of the Employer’s Notification of Intention to Award referred to in ITB 42, an unsuccessful Bidder has three (3) Business Days to make a written request to the Employer for a debriefing. The Employer shall provide a debriefing to all unsuccessful Bidders whose request is received within this deadline. - Where a request for debriefing is received within the deadline, the Employer shall provide a debriefing within five (5) Business Days, unless the Employer decides, for justifiable reasons, to provide the debriefing outside this timeframe. In that case, the standstill period shall automatically be extended until five (5) Business Days after such debriefing is provided. If more than one debriefing is so delayed, the standstill period shall not end earlier than five (5) Business Days after the last debriefing takes place. The Employer shall promptly inform, by the quickest means available, all Bidders of the extended standstill period. - Where a request for debriefing is received by the Employer later than the three (3)-Business Day deadline, the Employer should provide the debriefing as soon as practicable, and normally no later than fifteen (15) Business Days from the date of publication of Public Notice of Award of contract. Requests for debriefing received outside the three (3)-day deadline shall not lead to extension of the standstill period. - Debriefings of unsuccessful Bidders may be done in writing or verbally. The Bidder shall bear their own costs of attending such a debriefing meeting. |
| - Signing of Contract | - The Employer shall send to the successful Bidder the Letter of Acceptance including the Contract Agreement, and, if specified in the BDS, a request to submit the Beneficial Ownership Disclosure Form providing additional information on its beneficial ownership. The Beneficial Ownership Disclosure Form, if so requested, shall be submitted within eight (8) Business Days of receiving this request. - The successful Bidder shall sign, date and return to the Employer, the Contract Agreement within twenty-eight (28) days of its receipt. - Notwithstanding ITB 46.2 above, in case signing of the Contract Agreement is prevented by any export restrictions attributable to the Employer, to the country of the Employer, or to the use of the Plant and Installation Services to be supplied, where such export restrictions arise from trade regulations from a country supplying those Plant and Installation Services, the Bidder shall not be bound by its Bid, always provided, however, that the Bidder can demonstrate to the satisfaction of the Employer and of the Bank that signing of the Contact Agreement has not been prevented by any lack of diligence on the part of the Bidder in completing any formalities, including applying for permits, authorizations and licenses necessary for the export of the Plant and Installation Services under the terms of the Contract. |
| - Performance Security | - Within twenty-eight (28) days of the receipt of the Letter of Acceptance from the Employer, the successful Bidder shall furnish the Performance Security in accordance with the General Conditions GCC 13.3, subject to ITB 38, using for that purpose the Performance Security Form included in Section X, Contract Forms, or another form acceptable to the Employer. If the Performance Security furnished by the successful Bidder is in the form of a bond, it shall be issued by a bonding or insurance company that has been determined by the successful Bidder to be acceptable to the Employer. A foreign institution providing a bond shall have a correspondent financial institution located in the Employer’s Country, unless the Employer has agreed in writing that a correspondent financial institution is not required. - Failure of the successful Bidder to submit the above-mentioned Performance Security or sign the Contract shall constitute sufficient grounds for the annulment of the award and forfeiture of the Bid Security. In that event the Employer may award the Contract to the Bidder offering the next Most Advantageous Bid. |
| - Procurement Related Complaint | - The procedures for making a Procurement-related Complaint are as specified in the BDS. |

| # Section II - Bid Data Sheet The following specific data for the Facilities to be procured shall complement, supplement, or amend the provisions in the Instructions to Bidders (ITB). Whenever there is a conflict, the provisions herein shall prevail over those in ITB. |  |
| --- | --- |
| A. General |  |
| ITB 1.1 | The reference number of the Request for Bids (RFB) is: MV-MEE-283164-GO-RFB The Employer is: Ministry of Environment, Climate Change and Technology, Green Building, Handhuvaree Hingun, Maafannu, Male', 20392, Republic of Maldives The name of the RFB is: Design, Supply, Installation and Commissioning of Battery Energy Storage Systems (BESS) in Selected Islands in Maldives The number and identification of lots (contracts) comprising this RFB is: LOT ONE: 23-MW/23-MWh Battery Energy Storage Systems (BESS) on locations at Addu City mainland and Hulhudhoo-Meedhoo, Fuvahmulah City, GDh. Thinadhoo, Kulhudhuffushi City, B. Eydhafushi and Lh. Hinnavaru. LOT TWO: 13.5-MW/17-MWh Battery Energy Storage Systems (BESS) on locations at L. Atoll Islands (Fonadhoo, Gan, Dhanbidhoo, Isdhoo-Kalaidhoo, Maabaidhoo, Maamendhoo, Kunahandhoo-Hithadhoo and Maavah), Lh. Naifaru, Dh. Kudahuvadhoo, GA. Villingili and Sh. Funadhoo. The current bidding is for both contracts: Lot 1 and Lot 2. Bidders may bid for one or both lots. If the bidders participating in the bidding for both lots, want to be awarded both contracts, they should meet the qualification requirements on an aggregate basis for both lots. |
| ITB 2.1 | The Borrower is: Government of the Republic of Maldives and the Employer Ministry of Environment, Climate Change and Technology is the implementing agency for the borrower. The amount of the financing is: USD 107 million The name of the Project is: Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) Project |

| ITB 4.1 | Maximum number of members in the Joint Venture (JV) shall be: Three (3) |
| --- | --- |
| ITB 4.5 | A list of debarred firms and individuals is available on the Bank’s external website: http://www.worldbank.org/debarr. |
| B. Bidding Document |  |
| ITB 7.1 | For Clarification of Bid purposes only, the Employer’s address is: National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives Tel: (+960) 3349102 E-Mail: ibrahim.aflah@finance.gov.mv Copy to: tender@finance.gov.mv Requests for clarification should be received by the Employer no later than: 28 days prior to Bid submission date. Web page: https://www.finance.gov.mv/tenders |
| ITB 7.4 | A Pre-Bid meeting shall take place at the following date, time and place: Date: September 01, 2022 Time: 10:00 AM Male’ Time Duration: 2 Hours Maximum Place: Employer will organize an Online Video Conference Meeting for the Pre-Bid meeting. Bidder must send by email clarifications they intend to ask in the Pre-Bid meeting by August 25, 2022 01:00 PM Male’ Time. Depending on the number of clarifications received and if time permits the Employer will allow for an open Q&A session in the Pre-Bid Meeting. Bidders can continue to send clarifications pursuant to ITB 7.1 after the pre-bid meeting. All Registered Bidders will receive an email with the link to join the meeting Three (3) calendar days before the meeting. The Employer shall not be responsible for any interruptions or disconnections during the Online Video Conference Meeting. A site visit conducted by the Employer shall not be organized. |

| C. Preparation of Bids |  |
| --- | --- |
| ITB 10.1 | The language of the Bid is: English All correspondence exchange shall be in English language. Language for translation of supporting documents and printed literature is English language. |
| ITB 11.1 (j) | The Bidder shall submit the following additional documents in its Bid: All necessary documents as required under Section VII - Employer’s Requirement. and Code of Conduct for Contractor’s Personnel (ES) The Bidder shall submit its Code of Conduct that will apply to the Contractor’s Personnel (as defined in GCC Sub- Clause 1) employed for the execution of Installation Services (defined in GCC Sub- Clause 1) at the Site (or other places in the country where the Site is located), to ensure compliance with the Contractor’s Environmental and Social (ES) obligations under the Contract. The Bidder shall use for this purpose the Code of Conduct form provided in Section IV. No substantial modifications shall be made to this form, except that the Bidder may introduce additional requirements, including as necessary to take into account specific Contract issues/risks. |
| ITB 13.1 | Alternative Bids shall not be considered. |
| ITB 13.2 | Alternatives to the Time Schedule shall not be permitted. |
| ITB 13.4 | Alternative technical solutions shall not be permitted. |
| ITB 17.1 | Bidders shall quote for the entire Plant and Installation Services on a “single responsibility” basis. |
| ITB 17.5 (a) and (d) | Place of destination: LOT ONE: Addu City mainland and Hulhudhoo-Meedhoo, Fuvahmulah City, GDh. Thinadhoo, Kulhudhuffushi City, B. Eydhafushi and Lh. Hinnavaru. LOT TWO: L. Atoll Islands (Fonadhoo, Gan, Dhanbidhoo, Isdhoo-Kalaidhoo, Maabaidhoo, Maamendhoo, Kunahandhoo-Hithadhoo and Maavah), Lh. Naifaru, Dh. Kudahuvadhoo, GA. Villingili and Sh. Funadhoo. Final destination (Project Site): Same as place of destination above. For further location specific details refer Appendix E – Project Site Specific Details. |
| ITB 17.6 | The Incoterms edition is: Incoterms 2020 |
| ITB 17.7 | The prices quoted by the Bidder shall not be subject to adjustment during the performance of the Contract. |
| ITB 18.1 | The Bidder is not required to quote in the currency of the Employer’s Country the portion of the Bid price that corresponds to expenditures incurred in that currency. |
| ITB 19.1 | The Bid shall be valid until: January 26, 2023 |
| ITB 19.3 (a) | The Bid price shall be adjusted by the following factor(s): SOFR+1% for foreign currency |
| ITB 20.1 | A Bid Security shall be required in its original form. The amount and currency of the Bid Security shall be: LOT ONE: USD 240,000.00 LOT TWO: USD 160,000.00 The Beneficiary Address of the Bid Security shall be: Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives |
| ITB 20.3 | The Bid Security shall be valid until: February 23, 2023 The Bid Security shall be unconditional guarantee issued by a reputable bank acceptable to the Employer, valid for twenty-eight (28) days beyond the original date of expiry of the Bid validity, or beyond any extended date if requested under ITB 19.2. |
| ITB 21.1 | In addition to the original of the Bid, the number of copies is: One (1) digital copy on a DVD or CD. The type of optical disk that should be used is DVD-R or CD-R. Any discrepancies between the hard copies and the DVD/CD, the original-hardcopy shall prevail. |
| ITB 21.3 | The written confirmation of authorization to sign on behalf of the Bidder shall consist of: Power of Attorney effective for the duration of the proposal validity, signed by legally authorized signatories of the bidder or all of the partners to a JV. Electronic Signature on Original Bid Document shall not be acceptable. |
| D. Submission and Opening of Bids |  |
| ITB 23.1 | For Bid submission purposes only, the Employer’s address is: National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives The deadline for Bid submission is: Date: October 27, 2022 Time: 01:00 PM Male’ Time Bidders shall not have the option of submitting their Bids electronically. |
| ITB 26.1 | The Bid opening shall take place at: National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives Date: October 27, 2022 Time: 01:01 PM Male’ Time |
| ITB 26.6 | The Letter of Bid and Price Schedules shall be initialed by 2 (Two) representatives of the Employer conducting Bid opening. |
| E. Evaluation, and Comparison of Bids |  |
| ITB 33.1 | The currency that shall be used for Bid evaluation and comparison purposes to convert (at the selling exchange rate) all Bid prices expressed in various currencies into a single currency is: United States Dollars The source of exchange rate shall be: Maldives Monetary Authority www.mma.gov.mv The date for the exchange rate shall be: October 13, 2022 |
| ITB 35.4 (f) | The adjustments shall be determined using the following criteria, from amongst those set out in Section III, Evaluation and Qualification Criteria: - Deviation in Time for Completion: No - Life cycle costs: No - Functional Guarantees of the Facilities: Yes - Work, services, facilities, etc., to be provided by the Employer: No |
| ITB 46.1 | The successful Bidder shall submit the Beneficial Ownership Disclosure Form. |
| ITB 48.1 | The procedures for making a Procurement-related Complaint are detailed in the “Procurement Regulations for IPF Borrowers (Annex III).” If a Bidder wishes to make a Procurement-related Complaint, the Bidder should submit its complaint following these procedures, in writing (by the quickest means available, that is either by email or fax), to: National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives Tel: (+960) 3349102 E-Mail: ibrahim.aflah@finance.gov.mv Copy to: tender@finance.gov.mv In summary, a Procurement-related Complaint may challenge any of the following: - the terms of the Bidding Documents; and - the Employer’s decision to award the contract. |

Section III - Evaluation and Qualification Criteria

This Section contains all the criteria that the Employer shall use to evaluate Bids and qualify Bidders. No other factors, methods or criteria shall be used other than those specified in this bidding document.  The Bidder shall provide all the information requested in the forms included in Section IV, Bidding Forms.

Wherever a Bidder is required to state a monetary amount, Bidders should indicate the USD equivalent using the rate of exchange determined as follows:

- For construction turnover or financial data required for each year - Exchange rate prevailing on the last day of the respective calendar year (in which the amounts for that year is to be converted) was originally established.

- Value of single contract - Exchange rate prevailing on the date of the contract.

Exchange rates shall be taken from the publicly available source identified in the ITB 33.1. Any error in determining the exchange rates in the Bid may be corrected by the Employer.

Table of Criteria

1. Evaluation	45

1.1 Technical Evaluation	45

1.2 Economic Evaluation	45

1.3 Multiple Contracts (ITB 35.6)	46

2. Qualification	48

2.5 Contractor’s Representative and other Key Personnel	59

2.6 Equipment	59

2.7 Subcontractors	59

The Employer shall use the criteria and methodologies listed in this Section to evaluate Bids. By applying the criteria and methodologies, the Employer shall determine the Most Advantageous Bid. This is the Bid of the Bidder that meets the qualification criteria and whose Bid has been determined to be:

(a) 	substantially responsive to the bidding document; and

(b) 	the lowest evaluated cost.

1. Evaluation

1.1 Technical Evaluation

In addition to the criteria listed in ITB 35.2 (a) and (b), the following factors shall apply:

None

1.2 Economic Evaluation

The following factors and methods will apply:

- Time Schedule

Time to complete the Plant and Installation Services from the effective date specified in Article 3 of the Contract Agreement for determining time for completion of pre-commissioning activities is: 10 Months for Lot 1 and 11 Months for Lot 2. No credit will be given for earlier completion.

- Life Cycle Costs

Not Applicable

- Functional Guarantees of the Facilities

The minimum (or maximum) requirements stated in the Specification for functional guarantees required in the Specification are:

| Functional Guarantee | Norm | Minimum (or Maximum, as appropriate) Requirement |
| --- | --- | --- |
| 1. Service Life | - Years | 2 Years |
| 2. Continuous Power | - | As per Employer Requirements, Section 1.13, BESS AC Continuous Power (MW) |
| 3.Round Trip Efficiency | 88% | 85% |
| 4.System availability | 98% | 97% |

For the purposes of evaluation, functional guarantees will be assessed in aggregate across all islands within a Lot.

For the purposes of evaluation, for each percentage point that the functional guarantee of the proposed Plant and Installation Services is below the norm specified in the Specification and in the above table, but above the minimum acceptable levels also specified therein, an adjustment of $240,000 (Lot 1) and $160,000 (Lot 2) will be added to the Bid price.  If the drop below the norm or the excess above the minimum acceptable levels is less than one percent, the adjustment will be prorated accordingly.

For the purposes of evaluation, for each percentage point that the functional guarantee of the proposed Plant and Installation Services is above the norm specified in the Specification and in the above table, an adjustment of $40,000 (Lot 1) and $30,000 (Lot 2) will be subtracted from the Bid price, to a maximum of $400,000 (Lot 1) and $300,000 (Lot 2).  If the excess above the norm is less than one percent, the adjustment will be prorated accordingly.

- Work, services, facilities, etc., to be provided by the Employer

Where Bids include the undertaking of work or the provision of services or facilities by the Employer in excess of the provisions allowed for in the Bidding document, the Employer shall assess the costs of such additional work, services and/or facilities during the duration of the contract.  Such costs shall be added to the Bid price for evaluation.

- Sustainable procurement

Not Applicable

- Alternative technical solutions for specified parts

The acceptability of alternative technical solutions for parts of the facilities, if permitted under ITB 13.4, will be determined as follows:

Not Applicable

- Specific additional criteria

The relevant evaluation method, if any, shall be as follows:

Not Applicable

Any adjustments in price that result from the above procedures shall be added, for purposes of comparative evaluation only, to arrive at an “Evaluated Bid Cost.”  Bid prices quoted by Bidders shall remain unaltered.

1.3 Multiple Contracts (ITB 35.6)

If in accordance with ITB 1.1, Bids are invited for more than one lot, the contract will be awarded to the Bidder or Bidders offering a substantially responsive Bid(s) and the lowest evaluated cost to the Employer for combined lots, subject to the selected Bidder(s) meeting the required qualification criteria Section III, Evaluation and Qualification Criteria for a lot or combination of lots as the case may be.

In determining Bidder or Bidders that offer the total lowest evaluated cost to the Employer, after considering all possible combination of lots, the Employer shall apply the following steps in sequence:

(a)	evaluate individual lots to determine the substantially responsive Bids and corresponding evaluated costs;

(b)	for each lot, rank the substantially responsive Bids starting from the lowest evaluated cost for the lot;

(c)	apply to the evaluated costs listed in b) above, any applicable discounts/price reductions offered by a Bidder (s) for the award of multiple contracts based on the discounts and the methodology for their application offered by the respective Bidder; and

(d)	determine contract award on the basis of the combination of lots that offer the total lowest evaluated cost to the Employer.

2. Qualification

| Factor | 1 Eligibility |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ##### Sub-Factor | ##### Criteria |  |  |  |  | ##### Documentation Required |
|  | ##### Requirement | ##### Bidder |  |  |  |  |
|  |  | Single Entity | ##### Joint Venture (existing or intended) |  |  |  |
|  |  |  | All members combined | Each Partner | At least one Partner |  |
| ## 1.1 Nationality | Nationality in accordance with ITB 4.4. | Must meet requirement | Must meet requirement | Must meet requirement | N / A | Form ELI –1.1 and 1.2, with attachments |
| ## 1.2 Conflict of Interest | No- conflicts of interests as described in ITB 4.2 | Must meet requirement | Must meet requirement | Must meet requirement | N / A | Letter of Bid |
| ## 1.3 Bank Ineligibility | Not having been declared ineligible by the Bank as described in 4.5. | Must meet requirement | Must meet requirement | Must meet requirement | N / A | Letter of Bid |
| ## 1.4 State Owned Enterprise or Institution | Compliance with conditions of ITB 4.6 | Must meet requirement | Must meet requirement | Must meet requirement | N / A | Form ELI –1.1 and 1.2, with attachments |
| ## 1.5 Ineligibility based on a United Nations resolution or Borrower’s country law | Not having been excluded as a result of the Borrower’s country laws or official regulations, or by an act of compliance with UN Security Council resolution, in accordance with ITB 4.8and Section V. | Must meet requirement | Must meet requirement | Must meet requirement | N / A | Letter of Bid |

| Factor | 2. Historical Contract Non-Performance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ##### Sub-Factor | ##### Criteria |  |  |  |  | Documentation Required |
|  | ##### Requirement | ##### Bidder |  |  |  |  |
|  |  | Single Entity | ##### Joint Venture (existing or intended) |  |  |  |
|  |  |  | All members combined | Each member | At least one member |  |
| ## 2.1 History of non-performing contracts | Non-performanceof a contract did not occur within the last Five (5) years prior to the deadline for Bid submission, based on all information on fully settled disputes or litigation. A fully settled dispute or litigation is one that has been resolved in accordance with the Dispute Resolution Mechanism under the respective contract, and where all appeal instances available to the Bidder have been exhausted. | Must meet requirement by itself or as member to past or existing JV | N / A | Must meet requirement | N / A | Form CON - 2 |
| ## 2.2 Suspension | Not under suspension based on execution of a Bid Securing Declaration or Proposal Securing Declaration pursuant to ITB 4.7 and ITB 20.9 | Must meet requirement | Must meet requirement | Must meet requirement | Must meet requirement | Letter of Bid |
| ## 2.3 Pending Litigation | ### Bidder’s financial position and prospective long-term profitability still sound according to criteria established in 3.1 below and assuming that all pending litigation will be resolved against the Bidder. | Must meet requirement | N / A | Must meet requirement | N / A | Form CON – 2 |
| ## 2.4 Litigation History | No consistent history of court/arbitral award decisions against the Biddersince 1st January 2017. | Must meet requirement | Must meet requirement | Must meet requirement | N/A | Form CON – 2 |
| ## 2.5 Declaration: Environmental and Social (ES) past performance | Declare any contract that has been suspended or terminated and/or performance security called by an employer for reasons of breach of environmental, or social (including Sexual Exploitation, and Abuse) contractual obligations in the past Five (5) years. | Must make the declaration. | N/A | Each must make the declaration. | N/A | Form CON-3 ES Performance Declaration |
| ## 2.6 Bank’s SEA and/or SH Disqualification | At the time of Contract Award, not subject to disqualification by the Bank for non-compliance with SEA/ SH obligations. If the Bid had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations, the Bidder shall either (i) provide evidence of an arbitral award on the disqualification made in its favour; or (ii) demonstrate that it has adequate capacity and commitment to comply with SEA/SH prevention and response obligations; or (iii) provide evidence that it has already demonstrated such capacity and commitment for another Bank financed works contract. | Must meet requirement (including each subcontractor proposed by the Bidder) | N/A | Must meet requirement (including each subcontractor proposed by the Bidder) | N/A | Letter of Bid, Form CON-4 |

| Factor | 3 Financial Situation |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sub-Factor | ##### Criteria |  |  |  |  |  |  | ##### Documentation Required |
|  | ##### Requirement | ##### Bidder |  |  |  |  |  |  |
|  |  | Single Entity | ##### Joint Venture (existing or intended) |  |  |  |  |  |
|  |  |  | All members combined | Each member |  | At least one member |  |  |
| ## 3.1 Financial Capabilities | Submission of independently audited and certified Financial Statements and Notes to Financial Statements or if not required by the law of the Bidder’s Country, other financial statements acceptable to the Employer, for the years 2018, 2019 and 2020 to demonstrate the current soundness of the Bidders financial position and its prospective long-term profitability. | Must meet requirement | N / A | Must meet requirement |  | N / A |  | Form FIN – 3.1 with attachments |
| ## 3.2 Average Annual Turnover | ### Minimum average annual turnover in the Power Sector as per the following, calculated as total certified payments received for contracts in progress or completed, within the years 2018, 2019 and 2020: Lot One: USD 24 Million Lot Two: USD 16 Million Bids for combined lots will be evaluated based on aggregate requirement for both lots. | Must meet requirement | Must meet requirement | Must meet at least Ten percent (10%) of the requirement |  | Must meet at least Fifty percent (50%) of the requirement |  | Form FIN –3.2 |
| ## 3.3 Financial Resources | The Bidder must demonstrate access to, or availability of, financial resources such as liquid assets, unencumbered real assets, lines of credit, and other financial means, other than any contractual advance payments to meet: (i) the following cash-flow requirement: Lot One: USD 5 Million Lot Two: USD 3 Million and (ii) the overall cash flow requirements for this contract and its current commitments. Bids for combined lots will be evaluated based on aggregate requirement for both lots. | Must meet requirement | Must meet requirement |  | Must meet at least Ten percent (10%) of the requirement |  | Must meet At lease Fifty percent (50%) of the requirement | Form FIN –3.3 |

| Factor | 4 Experience |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sub-Factor | ##### Criteria |  |  |  |  | ##### Documents Required |
|  | Requirement | ##### Bidder |  |  |  |  |
|  |  | Single Entity | Joint Venture (existing or intended) |  |  |  |
|  |  |  | All members combined | Each member | At least one member |  |
| ## 4.1 General Experience | Experience in the Power Sector under contracts in the role of contractor, subcontractor, or management contractor for at least the last Five (05) years starting 1st January 2017. | Must meet requirement | N / A | Must meet requirement | N / A | Form EXP-4.1 |
| ## 4.2(a) Specific Experience | ### (i) Participation as contractor, joint venture member, management contractor, or subcontractor in Designing, Engineering, Procurement, Construction, Installation, Testing and Commissioning of Grid Connected Battery Energy Storage Systems (BESS) with contract value as follows within the last Five (5) Years, that has been successfully and substantially completed and that are similar to the employer’s requirement: Lot One: at least Five USD 18 Million ### Lot Two: at least USD 13 Million ### Bids for combined lots will be evaluated based on aggregate requirement for both lots. | Must meet requirement | Must meet requirements | N / A | Must meet the following requirements for the key activities listed below: Participation as contractor, joint venture member , management contractor, or subcontractor in Designing, Engineering, Procurement, Construction, Installation, Testing and Commissioning of Grid Connected Battery Energy Storage Systems (BESS) with contract value as follows within the last Five (5) Years, that has been successfully and substantially completed and that are similar to the employer’s requirement. Lot One: at least Five USD 18 Million Lot Two: at least USD 13 Million | Form EXP 4.2(a) |
|  | (ii) Specific Experience as per 4.2 (a) (i) must include: Lot One: at least 02 (Two) Grid connected BESS Plants, having minimum capacity of 2 MWh each in a single installation (single point of connection). Lot Two: at least 01 (One) Grid connected BESS Plant, having minimum capacity of 1 MWh each in a single installation (single point of connection). The BESS Project must have been in satisfactory operation for at least 6 (Six) months from its date of commissioning. Bids for combined lots will be evaluated based on aggregated requirement for this criteria | Must meet requirements | Must meet requirements | N / A | Must meet the following requirements for key activities listed below: Lot One: at least 02 (Two) Grid connected BESS Plants, having minimum capacity of 2 MWh each in a single installation (single point of connection). Lot Two: at least 01 (One) Grid connected BESS Plant, having minimum capacity of 1 MWh each in a single installation (single point of connection). The BESS Project must have been in satisfactory operation for at least 6 (Six) months from its date of commissioning. | Form EXP 4.2(a) |
| ## 4.2(b) Specific Experience | For the above or other contracts executed during the period stipulated in 4.2(a) above, a minimum experience in the following activities: Experience as a prime contractor, joint venture member, management contractor or sub-contractor of having successfully completed Design, Engineering, Procurement, Construction, Installation, Testing and Commissioning of communications architecture and energy management system. (EMS) to maximize renewable energy use in at least 01 (one) isolated network with a peak load exceeding 500 KW. This criteria applies as written regardless of whether the bid is for Lot 1, Lot 2, or combined lots. | Must meet requirements | Must meet requirements | N / A | N / A | Form EXP-4.2(b) |
| ## 4.2 (c) Specific Experience in managing ES aspects | For the contracts in 4.2 (a) above and/or any other contracts substantially completed and under implementation as prime contractor, joint venture member, or Subcontractor between 1st January 2017 and Bid submission deadline, experience in managing ES risks and impacts in the following aspect(s): Preparation or implementation of project specific ESIA or ESMP or ESCP or other equivalent required by the law of the specific country. | Must meet requirements | Must meet requirements | N / A | N / A | Form EXP – 4.2 (c) |

Note: With reference to Qualification Criteria Clause No 4.2 (a) and (b):

- The list of projects commissioned at least 6 months prior to the last date of Bid Submission, indicating whether the project is grid connected, along with a scanned copy of the Commissioning certificate or Work order or Contract or Agreement/LOI from the Client (or Owner) shall be submitted in support of Clause above.

- The Performance Certificate must have been issued for a minimum duration of 06 (Six) months from the date of commissioning. The Performance Certificate should have been issued by any state/central owned agencies or power departments or authorized representative of Power off-taker (Power Distribution Company/Private Power purchaser).

- An “isolated” network is considered one where there is a primary generation location (power station, potentially with multiple generators) that must be available to maintain power to all connected loads in that network. That is, there are no interconnections to other networks with larger generation sources that can maintain power to load in the isolated network if the primary generation location is unavailable (disconnected / offline). This does not preclude having multiple distributed generation sources such as renewable plant in the isolated network. An isolated network does not need to be permanent, but must function as a fully operational grid serving all usual customer requirements for the period of isolation.

Note: General:

- The Employer may assess the capacity and capability of the bidder, to ascertain that the bidder can successfully execute the scope of work covered under the package within stipulated completion period. This assessment shall inter-alia include (i) document verification, (ii) details of works executed, works in hand, anticipated in future & the balance capacity available for the present scope of work, (iii) details of plant and machinery, testing facilities, design capabilities, manpower and financial resources, (iv) details of quality systems in place, (v) past experience and performance, (vi) customer feedback, (vii) banker’s feedback etc.

- Consolidated Financial Statements are NOT acceptable.

- Only the qualifications of the Bidder shall be considered. Qualifications of other firms, including the Bidder’s subsidiaries, parent entities, affiliates, subcontractors or any other firm(s) different from the Bidder SHALL NOT be considered.

2.5 Contractor’s Representative and other Key Personnel

The Bidder must demonstrate that it will have a suitably qualified Contractor’s Representative and other suitably qualified (and in adequate numbers) key personnel, as described in the Employer’s Requirements.

The Bidder shall provide details of the Contractor’s Representative and other key personnel and such other key personnel that the Bidder considers appropriate to perform the Contract, together with their academic qualifications and work experience. The Bidder shall complete the relevant Forms in Section IV, Bidding Forms.

2.6 Equipment

The Bidder must demonstrate that it will have access to the key Contractor’s equipment listed hereafter:

| No. | Equipment Type and Characteristics | Minimum Number required |
| --- | --- | --- |
| 1 | Trenching machinery: Chain or bucket trenching machinery suitable for sand soils | 2 |
| 2 |  |  |

The Bidder shall provide further details of proposed items of equipment using the relevant Form in Section IV.

2.7 Subcontractors

Subcontractors/manufacturers for the following major items of supply or services (‘Specialized Subcontractors’) must meet the following minimum criteria, herein listed for that item:

| Item No. | Description of Item | Minimum Criteria to be met |
| --- | --- | --- |
| 1 | Transformers | Refer to Employer Requirements, Appendix A, Section 10.1 |
| 2 | Switchgear |  |
| 3 | BESS modules |  |
| 4 | BESS inverters |  |

Failure to comply with this requirement will result in rejection of the subcontractor.

In the case of a Bidder who offers to supply and install major items of supply under the contract that the Bidder did not manufacture or otherwise produce, the Bidder shall provide the manufacturer’s authorization, using the form provided in Section IV, showing that the Bidder has been duly authorized by the manufacturer or producer of the related plant and equipment or component to supply and install that item in the Employer’s Country. The Bidder is responsible for ensuring that the manufacturer or producer complies with the requirements of ITB 4 and 5 and meets the minimum criteria listed above for that item.

Section IV - Bidding Forms

Table of Forms

Schedule of Rates and Prices: Lot 01	65

Schedule No. 1.1.  Plant and Mandatory Spare Parts Supplied from Abroad: Lot 01	65

Country of Origin Declaration Form	68

Schedule No. 2.1.  Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country: Lot 01	69

Schedule No. 3.1. Design Services: Lot 01	70

Schedule No. 4.1 Installation and Other Services: Lot 01	72

Schedule No. 5.  Grand Summary: Lot 01	73

Schedule No. 6.  Recommended Spare Parts	75

Schedule of Rates and Prices: Lot 02	76

Schedule No. 1.2.  Plant and Mandatory Spare Parts Supplied from Abroad: Lot 02	76

Country of Origin Declaration Form	81

Schedule No. 2.2.  Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country: Lot 02	82

Schedule No. 3.2. Design Services: Lot 02	83

Schedule No. 4.2 Installation and Other Services: Lot 02	86

Schedule No. 5.  Grand Summary: Lot 02	89

Schedule No. 6.  Recommended Spare Parts	90

Technical Proposal	91

Proposed Subcontractors for Major Items of Plant and Installation Services	111

Others - Time Schedule	112

Bidders Qualification without prequalification	113

Bidder Information Sheet	114

Party to JV Information Sheet	115

Historical Contract Non-Performance, Pending Litigation and Litigation History	116

Historical Financial Performance	122

General Experience	126

Form of Bid Security	133

Form of Bid Security – Bank Guarantee	133

Manufacturer’s Authorization	135

Letter of Bid

INSTRUCTIONS TO BIDDERS: DELETE THIS BOX ONCE YOU HAVE COMPLETED THE DOCUMENT The Bidder must prepare this Letter of Bid on stationery with its letterhead clearly showing the Bidder’s complete name and business address. Note: All italicized text is to help Bidders in preparing this form.

Date of this Bid submission: [insert date (as day, month and year) of Bid submission]

RFB No.: [insert number of RFB process]

Alternative No.:[insert identification No if this is a Bid for an alternative]

To: Ministry of Environment, Climate Change and Technology,

Male’ Republic of Maldives

DESIGN, SUPPLY, INSTALL, COMMISSION OF BATTERY ENERGY STORAGE SYSTEMS (BESS) ON SELECTED ISLANDS IN MALDIVES

[delete as appropriate if bidding for a single Lot]:

LOT ONE: 23-MW/23-MWh Battery Energy Storage Systems (BESS) on locations at Addu City mainland and Hulhudhoo-Meedhoo, Fuvahmulah City, GDh. Thinadhoo, Kulhudhuffushi City, B. Eydhafushi and Lh. Hinnavaru.

LOT TWO: 13.5-MW/17-MWh Battery Energy Storage Systems (BESS) on locations at L. Atoll Islands (Fonadhoo, Gan, Dhanbidhoo, Isdhoo-Kalaidhoo, Maabaidhoo, Maamendhoo, Kunahandhoo-Hithadhoo and Maavah), Lh. Naifaru, Dh. Kudahuvadhoo, GA. Villingili and Sh. Funadhoo.

We, the undersigned, declare that:

- No reservations: We have examined and have no reservations to the bidding document, including Addenda issued in accordance with ITB 8;

- Eligibility: We meet the eligibility requirements and have no conflict of interest in accordance with ITB 4;

- Bid-Securing Declaration: We have not been suspended nor declared ineligible by the Employer based on execution of a Bid Securing Declaration or Proposal-Securing Declaration in the Employer’s Country in accordance with ITB 4.7;

- Exploitation and Abuse (SEA) and/or Sexual Harassment (SH): [select the appropriate option from (i) to (iii) below and delete the others].

We [where JV, insert: “including any of our JV members”], and any of our subcontractors:

- [have not been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.]

- [are subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.]

- [had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations. An arbitral award on the disqualification case has been made in our favor.]

- Conformity: We offer to provide design, supply and installation services in conformity with the bidding document of the following: [insert a brief description of the Plant, Design, Supply and Installation Services];

- Bid Price: The total price of our Bid, excluding any discounts offered in item (f) below is: [Insert one of the options below as appropriate]

Option 1, in case of one lot:  Total price is: [insert the total price of the Bid in words and figures, indicating the various amounts and the respective currencies];

Or

Option 2, in case of multiple lots: (a) Total price of each lot [insert the total price of each lot in words and figures, indicating the various amounts and the respective currencies]; and (b) Total price of all lots (sum of all lots) [insert the total price of all lots in words and figures, indicating the various amounts and the respective currencies];

- Discounts: The discounts offered and the methodology for their application are:

(i) The discounts offered are: [Specify in detail each discount offered.]

(ii) The exact method of calculations to determine the net price after application of discounts is shown below: [Specify in detail the method that shall be used to apply the discounts];

- Bid Validity: Our Bid shall be valid until [insert day, month and year in accordance with ITB 19.1],  and it shall remain binding upon us and may be accepted at any time before the expiration of that period;

- Performance Security: If our Bid is accepted, we commit to obtain a Performance Security in accordance with the bidding document;

- One Bid Per Bidder: We are not submitting any other Bid(s) as an individual Bidder, and we are not participating in any other Bid(s) as a Joint Venture member, and meet the requirements of ITB 4.3, other than alternative Bids submitted in accordance with ITB 13;

- Suspension and Debarment: We, along with any of our subcontractors, suppliers, consultants, manufacturers, or service providers for any part of the contract, are not subject to, and not controlled by any entity or individual that is subject to, a temporary suspension or a debarment imposed by the World Bank Group or a debarment imposed by the World Bank Group in accordance with the Agreement for Mutual Enforcement of Debarment Decisions between the World Bank and other development banks. Further, we are not ineligible under the Employer’s Country laws or official regulations or pursuant to a decision of the United Nations Security Council;

- State-owned enterprise or institution: [select the appropriate option and delete the other] [We are not a state-owned enterprise or institution] / [We are a state-owned enterprise or institution but meet the requirements of ITB 4.6];

- Commissions, gratuities and fees: We have paid, or will pay the following commissions, gratuities, or fees with respect to the Bidding process or execution of the Contract: [insert complete name of each Recipient, its full address, the reason for which each commission or gratuity was paid and the amount and currency of each such commission or gratuity]

| Name of Recipient | Address | Reason | Amount |
| --- | --- | --- | --- |

(If none has been paid or is to be paid, indicate “none.”)

- Binding Contract: We understand that this Bid, together with your written acceptance thereof included in your Letter of Acceptance, shall constitute a binding contract between us, until a formal contract is prepared and executed;

- Not Bound to Accept: We understand that you are not bound to accept the lowest evaluated cost Bid, the Most Advantageous Bid or any other Bid that you may receive; and

- Fraud and Corruption: We hereby certify that we have taken steps to ensure that no person acting for us or on our behalf engages in any type of Fraud and Corruption.

Name of the Bidder: *[insert name of the Bidder]

Name of the person duly authorized to sign the Bid on behalf of the Bidder: **[insert complete name of person duly authorized to sign the Bid]

Title of the person signing the Bid: [insert complete title of the person signing the Bid]

Signature of the person named above: [insert signature of person whose name and capacity are shown above]

Date signed [insert date of signing] day of [insert month], [insert year]

*: In the case of the Bid submitted by joint venture specify the name of the Joint Venture as Bidder

**: Person signing the Bid shall have the power of attorney given by the Bidder to be attached with the Bid

Schedule of Rates and Prices: Lot 01

Schedule No. 1.1.  Plant and Mandatory Spare Parts Supplied from Abroad: Lot 01

| Item | Description | Code1 |  | Qty. |  |  | Unit Price2 |  | Total Price2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | CIP |  |
|  |  |  |  | (1) |  |  | (2) | (3) | (1) x (3) |
| 1 | ADDU CITY MAINLAND |  |  |  |  |  |  |  |  |
| 1.1 | Battery modules |  |  |  |  |  |  |  |  |
| 1.2 | Inverter |  |  |  |  |  |  |  |  |
| 1.3 | Transformer |  |  |  |  |  |  |  |  |
| 1.4 | EMS |  |  |  |  |  |  |  |  |
| 1.5 | Communications |  |  |  |  |  |  |  |  |
| 1.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 1.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 1.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 2 | ADDU HULHUDHOO MEEDHOO |  |  |  |  |  |  |  |  |
| 2.1 | Battery modules |  |  |  |  |  |  |  |  |
| 2.2 | Inverter |  |  |  |  |  |  |  |  |
| 2.3 | Transformer |  |  |  |  |  |  |  |  |
| 2.4 | EMS |  |  |  |  |  |  |  |  |
| 2.5 | Communications |  |  |  |  |  |  |  |  |
| 2.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 2.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 2.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 3 | FUVAH MULAH CITY |  |  |  |  |  |  |  |  |
| 3.1 | Battery modules |  |  |  |  |  |  |  |  |
| 3.2 | Inverter |  |  |  |  |  |  |  |  |
| 3.3 | Transformer |  |  |  |  |  |  |  |  |
| 3.4 | EMS |  |  |  |  |  |  |  |  |
| 3.5 | Communications |  |  |  |  |  |  |  |  |
| 3.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 3.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 3.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 4 | THINADHOO |  |  |  |  |  |  |  |  |
| 4.1 | Battery modules |  |  |  |  |  |  |  |  |
| 4.2 | Inverter |  |  |  |  |  |  |  |  |
| 4.3 | Transformer |  |  |  |  |  |  |  |  |
| 4.4 | EMS |  |  |  |  |  |  |  |  |
| 4.5 | Communications |  |  |  |  |  |  |  |  |
| 4.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 4.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 4.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 5 | EYDHAFUSHI |  |  |  |  |  |  |  |  |
| 5.1 | Battery modules |  |  |  |  |  |  |  |  |
| 5.2 | Inverter |  |  |  |  |  |  |  |  |
| 5.3 | Transformer |  |  |  |  |  |  |  |  |
| 5.4 | EMS |  |  |  |  |  |  |  |  |
| 5.5 | Communications |  |  |  |  |  |  |  |  |
| 5.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 5.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 5.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 6 | HINNAVARU |  |  |  |  |  |  |  |  |
| 6.1 | Battery modules |  |  |  |  |  |  |  |  |
| 6.2 | Inverter |  |  |  |  |  |  |  |  |
| 6.3 | Transformer |  |  |  |  |  |  |  |  |
| 6.4 | EMS |  |  |  |  |  |  |  |  |
| 6.5 | Communications |  |  |  |  |  |  |  |  |
| 6.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 6.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 6.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 7 | KULHUDHUFFUSHI CITY |  |  |  |  |  |  |  |  |
| 7.1 | Battery modules |  |  |  |  |  |  |  |  |
| 7.2 | Inverter |  |  |  |  |  |  |  |  |
| 7.3 | Transformer |  |  |  |  |  |  |  |  |
| 7.4 | EMS |  |  |  |  |  |  |  |  |
| 7.5 | Communications |  |  |  |  |  |  |  |  |
| 7.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 7.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 7.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| TOTAL SCHEDULE 1.1 (to Schedule No. 5. Grand Summary Lot 01) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Name of Bidder |  |  |  |
|  |  |  |  |  |  | Signature of Bidder |  |  |  |

1 Bidders shall enter a code representing the country of origin of all imported plant and equipment.

2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies.

Country of Origin Declaration Form

| Item | Description | Code | Country |
| --- | --- | --- | --- |

Schedule No. 2.1.  Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country: Lot 01

| Item | Description |  | Qty. |  | EXW Unit Price1 |  | Sales and other taxes payable per line item if Contract is awarded (in accordance with ITB 17.5 (b) (ii) |  | EXW Total Price1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | (1) |  | (2) |  | (3) |  | (1) x (2) |
| TOTAL SCHEDULE 2.1 (to Schedule No. 5. Grand Summary Lot 01) |  |  |  |  |  |  |  |  |  |
|  |  |  | Name of Bidder |  |  |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |  |  |
| 1 Specify currency in accordance with specifications in Bid Data Sheet under ITB 18.1 |  |  |  |  |  |  |  |  |  |

Schedule No. 3.1. Design Services: Lot 01

| Item | Description |  | Qty. | Unit Price1 |  |  |  | Total Price1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Local Currency Portion |  | Foreign Currency Portion |  |  |
|  |  |  | (1) | (2) |  | (optional) |  | (1) x (2) |
| 1 | ADDU MAINLAND |  |  |  |  |  |  |  |
| 1.1 | Preliminary design |  |  |  |  |  |  |  |
| 1.2 | Detailed design |  |  |  |  |  |  |  |
| 1.3 | Final design |  |  |  |  |  |  |  |
| 1.4 | EMS programming |  |  |  |  |  |  |  |
| 1.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 1.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and Decommissioning and Disposal Plan |  |  |  |  |  |  |  |
| 2 | ADDU HULHUDHOO MEEDHOO |  |  |  |  |  |  |  |
| 2.1 | Preliminary design |  |  |  |  |  |  |  |
| 2.2 | Detailed design |  |  |  |  |  |  |  |
| 2.3 | Final design |  |  |  |  |  |  |  |
| 2.4 | EMS programming |  |  |  |  |  |  |  |
| 2.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 2.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and Decommissioning and Disposal Plan |  |  |  |  |  |  |  |
| 3 | FUVAH MULAH |  |  |  |  |  |  |  |
| 3.1 | Preliminary design |  |  |  |  |  |  |  |
| 3.2 | Detailed design |  |  |  |  |  |  |  |
| 3.3 | Final design |  |  |  |  |  |  |  |
| 3.4 | EMS programming |  |  |  |  |  |  |  |
| 3.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 3.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and Decommissioning and Disposal Plan |  |  |  |  |  |  |  |
| 4 | THINADHOO |  |  |  |  |  |  |  |
| 4.1 | Preliminary design |  |  |  |  |  |  |  |
| 4.2 | Detailed design |  |  |  |  |  |  |  |
| 4.3 | Final design |  |  |  |  |  |  |  |
| 4.4 | EMS programming |  |  |  |  |  |  |  |
| 4.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 4.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and Decommissioning and Disposal Plan |  |  |  |  |  |  |  |
| 5 | EYDHAFUSHI |  |  |  |  |  |  |  |
| 5.1 | Preliminary design |  |  |  |  |  |  |  |
| 5.2 | Detailed design |  |  |  |  |  |  |  |
| 5.3 | Final design |  |  |  |  |  |  |  |
| 5.4 | EMS programming |  |  |  |  |  |  |  |
| 5.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 5.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and Decommissioning and Disposal Plan |  |  |  |  |  |  |  |
| 6 | HINNAVARU |  |  |  |  |  |  |  |
| 6.1 | Preliminary design |  |  |  |  |  |  |  |
| 6.2 | Detailed design |  |  |  |  |  |  |  |
| 6.3 | Final design |  |  |  |  |  |  |  |
| 6.4 | EMS programming |  |  |  |  |  |  |  |
| 6.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 6.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and Decommissioning and Disposal Plan |  |  |  |  |  |  |  |
| 7 | KULHUDHUFFUSHI |  |  |  |  |  |  |  |
| 7.1 | Preliminary design |  |  |  |  |  |  |  |
| 7.2 | Detailed design |  |  |  |  |  |  |  |
| 7.3 | Final design |  |  |  |  |  |  |  |
| 7.4 | EMS programming |  |  |  |  |  |  |  |
| 7.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 7.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and Decommissioning and Disposal Plan |  |  |  |  |  |  |  |
| TOTAL SCHEDULE 3.1 (to Schedule No. 5. Grand Summary Lot 01) |  |  |  |  |  |  |  |  |
|  |  |  |  | Name of Bidder |  |  |  |  |
|  |  |  |  | Signature of Bidder |  |  |  |  |

Schedule No. 4.1 Installation and Other Services: Lot 01

| Item | Description | Qty. | Unit Price1 |  |  |  | Total Price1 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Foreign Currency Portion |  | Local Currency Portion |  | Foreign |  | Local |
|  |  | (1) | (2) |  | (3) |  | (1) x (2) |  | (1) x (3) |
| 1 | ADDU MAIN LAND |  |  |  |  |  |  |  |  |
| 1.1 | Project management, monitoring and reporting |  |  |  |  |  |  |  |  |
| 1.2 | Freight and logistics |  |  |  |  |  |  |  |  |
| 1.3 | Site preparation and civil works |  |  |  |  |  |  |  |  |
| 1.4 | Equipment installation |  |  |  |  |  |  |  |  |
| 1.5 | Pre-commissioning and tests |  |  |  |  |  |  |  |  |
| 1.6 | Training |  |  |  |  |  |  |  |  |
| 1.7 | O&M period |  |  |  |  |  |  |  |  |
| 1.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |  |  |
| 2 | ADDU HULHUDHOO MEEDHOO |  |  |  |  |  |  |  |  |
| 2.1 | Project management, monitoring and reporting |  |  |  |  |  |  |  |  |
| 2.2 | Freight and logistics |  |  |  |  |  |  |  |  |
| 2.3 | Site preparation and civil works |  |  |  |  |  |  |  |  |
| 2.4 | Equipment installation |  |  |  |  |  |  |  |  |
| 2.5 | Pre-commissioning and tests |  |  |  |  |  |  |  |  |
| 2.6 | Training |  |  |  |  |  |  |  |  |
| 2.7 | O&M period |  |  |  |  |  |  |  |  |
| 2.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |  |  |
| 3 | FUVAH MULAH |  |  |  |  |  |  |  |  |
| 3.1 | Project management, monitoring and reporting |  |  |  |  |  |  |  |  |
| 3.2 | Freight and logistics |  |  |  |  |  |  |  |  |
| 3.3 | Site preparation and civil works |  |  |  |  |  |  |  |  |
| 3.4 | Equipment installation |  |  |  |  |  |  |  |  |
| 3.5 | Pre-commissioning and tests |  |  |  |  |  |  |  |  |
| 3.6 | Training |  |  |  |  |  |  |  |  |
| 3.7 | O&M period |  |  |  |  |  |  |  |  |
| 3.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |  |  |
| 4 | THINADHOO |  |  |  |  |  |  |  |  |
| 4.1 | Project management, monitoring and reporting |  |  |  |  |  |  |  |  |
| 4.2 | Freight and logistics |  |  |  |  |  |  |  |  |
| 4.3 | Site preparation and civil works |  |  |  |  |  |  |  |  |
| 4.4 | Equipment installation |  |  |  |  |  |  |  |  |
| 4.5 | Pre-commissioning and tests |  |  |  |  |  |  |  |  |
| 4.6 | Training |  |  |  |  |  |  |  |  |
| 4.7 | O&M period |  |  |  |  |  |  |  |  |
| 4.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |  |  |
| 5 | EYDHAFUSHI |  |  |  |  |  |  |  |  |
| 5.1 | Project management, monitoring and reporting |  |  |  |  |  |  |  |  |
| 5.2 | Freight and logistics |  |  |  |  |  |  |  |  |
| 5.3 | Site preparation and civil works |  |  |  |  |  |  |  |  |
| 5.4 | Equipment installation |  |  |  |  |  |  |  |  |
| 5.5 | Pre-commissioning and tests |  |  |  |  |  |  |  |  |
| 5.6 | Training |  |  |  |  |  |  |  |  |
| 5.7 | O&M period |  |  |  |  |  |  |  |  |
| 5.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |  |  |
| 6 | HINNAVARU |  |  |  |  |  |  |  |  |
| 6.1 | Project management, monitoring and reporting |  |  |  |  |  |  |  |  |
| 6.2 | Freight and logistics |  |  |  |  |  |  |  |  |
| 6.3 | Site preparation and civil works |  |  |  |  |  |  |  |  |
| 6.4 | Equipment installation |  |  |  |  |  |  |  |  |
| 6.5 | Pre-commissioning and tests |  |  |  |  |  |  |  |  |
| 6.6 | Training |  |  |  |  |  |  |  |  |
| 6.7 | O&M period |  |  |  |  |  |  |  |  |
| 6.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |  |  |
| 7 | KULHUDHUFFUSHI |  |  |  |  |  |  |  |  |
| 7.1 | Project management, monitoring and reporting |  |  |  |  |  |  |  |  |
| 7.2 | Freight and logistics |  |  |  |  |  |  |  |  |
| 7.3 | Site preparation and civil works |  |  |  |  |  |  |  |  |
| 7.4 | Equipment installation |  |  |  |  |  |  |  |  |
| 7.5 | Pre-commissioning and tests |  |  |  |  |  |  |  |  |
| 7.6 | Training |  |  |  |  |  |  |  |  |
| 7.7 | O&M period |  |  |  |  |  |  |  |  |
| 7.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |  |  |
| TOTAL Schedule No. 4.1 (to Schedule No. 5. Grand Summary Lot 01) |  |  |  |  |  |  |  |  |  |
|  |  |  | Name of Bidder |  |  |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |  |  |
| 1 Specify currency in accordance with ITB 18 |  |  |  |  |  |  |  |  |  |

Schedule No. 5.  Grand Summary: Lot 01

| Item | Description |  |  |  |  | Total Price1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Foreign |  | Local (MVR) |  |
| 1 | Total Schedule No. 1. Plant, and Mandatory Spare Parts Supplied from Abroad |  |  |  |  |  |  |  |  |
| 2 | Total Schedule No. 2. Plant, and Mandatory Spare Parts Supplied from Within the Employer’s Country |  |  |  |  |  |  |  |  |
| 3 | Total Schedule No. 3. Design Services |  |  |  |  |  |  |  |  |
| 4 | Total Schedule No. 4. Installation and Other Services |  |  |  |  |  |  |  |  |
| TOTAL Grand Summary: Lot 1 (to Letter of Bid) |  |  |  |  |  |  |  |  |  |
|  |  |  | Name of Bidder |  |  |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |  |  |
| 1Specify currency in accordance with ITB 18. Create and use as many columns for Foreign Currency requirement as there are foreign currencies |  |  |  |  |  |  |  |  |  |

Schedule No. 6.  Recommended Spare Parts

| Item | Description |  | Qty. | Unit Price |  |  | Total Price |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | CIF or CIP (foreign parts) |  | EXW (local parts) |  |  |
|  |  |  | (1) | (2) |  | (3) | (1) x (2) or(3) |  |
|  |  |  | Name of Bidder |  |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |  |

Schedule of Rates and Prices: Lot 02

Schedule No. 1.2.  Plant and Mandatory Spare Parts Supplied from Abroad: Lot 02

| Item | Description | Code1 |  | Qty. |  |  | Unit Price2 |  | Total Price2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | CIP |  |
|  |  |  |  | (1) |  |  | (2) | (3) | (1) x (3) |
| 1 | GA. VILLIGILI |  |  |  |  |  |  |  |  |
| 1.1 | Battery modules |  |  |  |  |  |  |  |  |
| 1.2 | Inverter |  |  |  |  |  |  |  |  |
| 1.3 | Transformer |  |  |  |  |  |  |  |  |
| 1.4 | EMS |  |  |  |  |  |  |  |  |
| 1.5 | Communications |  |  |  |  |  |  |  |  |
| 1.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 1.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 1.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 2 | LH. NAIFARU |  |  |  |  |  |  |  |  |
| 2.1 | Battery modules |  |  |  |  |  |  |  |  |
| 2.2 | Inverter |  |  |  |  |  |  |  |  |
| 2.3 | Transformer |  |  |  |  |  |  |  |  |
| 2.4 | EMS |  |  |  |  |  |  |  |  |
| 2.5 | Communications |  |  |  |  |  |  |  |  |
| 2.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 2.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 2.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 3 | L. FONADHOO |  |  |  |  |  |  |  |  |
| 3.1 | Battery modules |  |  |  |  |  |  |  |  |
| 3.2 | Inverter |  |  |  |  |  |  |  |  |
| 3.3 | Transformer |  |  |  |  |  |  |  |  |
| 3.4 | EMS |  |  |  |  |  |  |  |  |
| 3.5 | Communications |  |  |  |  |  |  |  |  |
| 3.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 3.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 3.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 4 | L. GAN |  |  |  |  |  |  |  |  |
| 4.1 | Battery modules |  |  |  |  |  |  |  |  |
| 4.2 | Inverter |  |  |  |  |  |  |  |  |
| 4.3 | Transformer |  |  |  |  |  |  |  |  |
| 4.4 | EMS |  |  |  |  |  |  |  |  |
| 4.5 | Communications |  |  |  |  |  |  |  |  |
| 4.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 4.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 4.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 5 | L. ISDHOO, L. KALAIDHOO, L. DHABIDHOO |  |  |  |  |  |  |  |  |
| 5.1 | Battery modules |  |  |  |  |  |  |  |  |
| 5.2 | Inverter |  |  |  |  |  |  |  |  |
| 5.3 | Transformer |  |  |  |  |  |  |  |  |
| 5.4 | EMS |  |  |  |  |  |  |  |  |
| 5.5 | Communications |  |  |  |  |  |  |  |  |
| 5.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 5.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 5.8 | -Mandatory spares |  |  |  |  |  |  |  |  |
| 6 | L. MAABAIDHOO |  |  |  |  |  |  |  |  |
| 6.1 | Battery modules |  |  |  |  |  |  |  |  |
| 6.2 | Inverter |  |  |  |  |  |  |  |  |
| 6.3 | Transformer |  |  |  |  |  |  |  |  |
| 6.4 | EMS |  |  |  |  |  |  |  |  |
| 6.5 | Communications |  |  |  |  |  |  |  |  |
| 6.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 6.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 6.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 7 | L. MAAMENDHOO |  |  |  |  |  |  |  |  |
| 7.1 | Battery modules |  |  |  |  |  |  |  |  |
| 7.2 | Inverter |  |  |  |  |  |  |  |  |
| 7.3 | Transformer |  |  |  |  |  |  |  |  |
| 7.4 | EMS |  |  |  |  |  |  |  |  |
| 7.5 | Communications |  |  |  |  |  |  |  |  |
| 7.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 7.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 7.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 8 | L. MAAVAH |  |  |  |  |  |  |  |  |
| 8.1 | Battery modules |  |  |  |  |  |  |  |  |
| 8.2 | Inverter |  |  |  |  |  |  |  |  |
| 8.3 | Transformer |  |  |  |  |  |  |  |  |
| 8.4 | EMS |  |  |  |  |  |  |  |  |
| 8.5 | Communications |  |  |  |  |  |  |  |  |
| 8.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 8.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 8.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 9 | L. KUNAHANDHOO |  |  |  |  |  |  |  |  |
| 9.1 | Battery modules |  |  |  |  |  |  |  |  |
| 9.2 | Inverter |  |  |  |  |  |  |  |  |
| 9.3 | Transformer |  |  |  |  |  |  |  |  |
| 9.4 | EMS |  |  |  |  |  |  |  |  |
| 9.5 | Communications |  |  |  |  |  |  |  |  |
| 9.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 9.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 9.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 10 | L. HITHADHOO |  |  |  |  |  |  |  |  |
| 10.1 | Battery modules |  |  |  |  |  |  |  |  |
| 10.2 | Inverter |  |  |  |  |  |  |  |  |
| 10.3 | Transformer |  |  |  |  |  |  |  |  |
| 10.4 | EMS |  |  |  |  |  |  |  |  |
| 10.5 | Communications |  |  |  |  |  |  |  |  |
| 10.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 10.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 10.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| 11 | SH. FUNDAHOO |  |  |  |  |  |  |  |  |
| 11.1 | Battery modules |  |  |  |  |  |  |  |  |
| 11.2 | Inverter |  |  |  |  |  |  |  |  |
| 11.3 | Transformer |  |  |  |  |  |  |  |  |
| 11.4 | EMS |  |  |  |  |  |  |  |  |
| 11.5 | Communications |  |  |  |  |  |  |  |  |
| 11.6 | Balance of plant: Civil |  |  |  |  |  |  |  |  |
| 11.7 | Balance of plant: Electrical |  |  |  |  |  |  |  |  |
| 11.8 | Mandatory spares |  |  |  |  |  |  |  |  |
| TOTAL SCHEDULE 1.2 (to Schedule No. 5. Grand Summary Lot 02) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Name of Bidder |  |  |  |
|  |  |  |  |  |  | Signature of Bidder |  |  |  |
| 1 Bidders shall enter a code representing the country of origin of all imported plant and equipment. 2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies. |  |  |  |  |  |  |  |  |  |

Country of Origin Declaration Form

| Item | Description | Code | Country |
| --- | --- | --- | --- |

Schedule No. 2.2.  Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country: Lot 02

| Item | Description |  | Qty. |  | EXW Unit Price1 |  | Sales and other taxes payable per line item if Contract is awarded (in accordance with ITB 17.5 (b) (ii) |  | EXW Total Price1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | (1) |  | (2) |  | (3) |  | (1) x (2) |
| TOTAL SCHEDULE 2.2 (to Schedule No. 5. Grand Summary Lot 02) |  |  |  |  |  |  |  |  |  |
|  |  |  | Name of Bidder |  |  |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |  |  |
| 1 Specify currency in accordance with specifications in Bid Data Sheet under ITB 18.1 |  |  |  |  |  |  |  |  |  |

Schedule No. 3.2. Design Services: Lot 02

| Item | Description |  | Qty. | Unit Price1 |  |  |  | Total Price1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Local Currency Portion |  | Foreign Currency Portion |  |  |
|  |  |  | (1) | (2) |  | (optional) |  | (1) x (2) |
| 1 | GA. VILLIGILI |  |  |  |  |  |  |  |
| 1.1 | Preliminary design |  |  |  |  |  |  |  |
| 1.2 | Detailed design |  |  |  |  |  |  |  |
| 1.3 | Final design |  |  |  |  |  |  |  |
| 1.4 | EMS programming |  |  |  |  |  |  |  |
| 1.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 1.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 2 | LH. NAIFARU |  |  |  |  |  |  |  |
| 2.1 | Preliminary design |  |  |  |  |  |  |  |
| 2.2 | Detailed design |  |  |  |  |  |  |  |
| 2.3 | Final design |  |  |  |  |  |  |  |
| 2.4 | EMS programming |  |  |  |  |  |  |  |
| 2.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 2.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 3 | L. FONADHOO |  |  |  |  |  |  |  |
| 3.1 | Preliminary design |  |  |  |  |  |  |  |
| 3.2 | Detailed design |  |  |  |  |  |  |  |
| 3.3 | Final design |  |  |  |  |  |  |  |
| 3.4 | EMS programming |  |  |  |  |  |  |  |
| 3.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 3.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 4 | L. GAN |  |  |  |  |  |  |  |
| 4.1 | Preliminary design |  |  |  |  |  |  |  |
| 4.2 | Detailed design |  |  |  |  |  |  |  |
| 4.3 | Final design |  |  |  |  |  |  |  |
| 4.4 | EMS programming |  |  |  |  |  |  |  |
| 4.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 4.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 5 | L. ISDHOO, L. KALAIDHOO, L. DHABIDHOO |  |  |  |  |  |  |  |
| 5.1 | Preliminary design |  |  |  |  |  |  |  |
| 5.2 | Detailed design |  |  |  |  |  |  |  |
| 5.3 | Final design |  |  |  |  |  |  |  |
| 5.4 | EMS programming |  |  |  |  |  |  |  |
| 5.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 5.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 6 | L. MAABAIDHOO |  |  |  |  |  |  |  |
| 6.1 | Preliminary design |  |  |  |  |  |  |  |
| 6.2 | Detailed design |  |  |  |  |  |  |  |
| 6.3 | Final design |  |  |  |  |  |  |  |
| 6.4 | EMS programming |  |  |  |  |  |  |  |
| 6.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 6.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 7 | L.MAAMENDHOO |  |  |  |  |  |  |  |
| 7.1 | Preliminary design |  |  |  |  |  |  |  |
| 7.2 | Detailed design |  |  |  |  |  |  |  |
| 7.3 | Final design |  |  |  |  |  |  |  |
| 7.4 | EMS Programming |  |  |  |  |  |  |  |
| 7.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 7.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| _8 | L. MAAVAH |  |  |  |  |  |  |  |
| _8.1 | Preliminary design |  |  |  |  |  |  |  |
| _8.2 | Detailed design |  |  |  |  |  |  |  |
| _8.3 | Final design |  |  |  |  |  |  |  |
| _8.4 | EMS programming |  |  |  |  |  |  |  |
| _8.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 8.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 9 | L. KUNAHANDHOO |  |  |  |  |  |  |  |
| 9.1 | Preliminary design |  |  |  |  |  |  |  |
| 9.2 | Detailed design |  |  |  |  |  |  |  |
| 9.3 | Final design |  |  |  |  |  |  |  |
| 9.4 | EMS programming |  |  |  |  |  |  |  |
| 9.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 9.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 10 | L. HITHADHOO |  |  |  |  |  |  |  |
| 10.1 | Preliminary design |  |  |  |  |  |  |  |
| 10.2 | Detailed design |  |  |  |  |  |  |  |
| 10.3 | Final design |  |  |  |  |  |  |  |
| 10.4 | EMS programming |  |  |  |  |  |  |  |
| 10.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 10.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| 11 | SH. FUNDAHOO |  |  |  |  |  |  |  |
| 11.1 | Preliminary design |  |  |  |  |  |  |  |
| 11.2 | Detailed design |  |  |  |  |  |  |  |
| 11.3 | Final design |  |  |  |  |  |  |  |
| 11.4 | EMS programming |  |  |  |  |  |  |  |
| 11.5 | Inspection and test plans |  |  |  |  |  |  |  |
| 11.6 | Updating ESCP & preparation of OHSMP, HMMP, ERP, OMP and DDP |  |  |  |  |  |  |  |
| TOTAL SCHEDULE 3.2 (to Schedule No. 5. Grand Summary Lot 02) |  |  |  |  |  |  |  |  |
|  |  |  |  | Name of Bidder |  |  |  |  |
|  |  | Signature of Bidder |  |  |  |  |  |  |

Schedule No. 4.2 Installation and Other Services: Lot 02

| Item | Description | Qty. | Unit Price1 |  |  | Total Price1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Foreign Currency Portion | Local Currency Portion |  | Foreign | Local |
|  |  | (1) | (2) | (3) |  | (1) x (2) | (1) x (3) |
| 1 | GA. VILLIGILI |  |  |  |  |  |  |
| 1.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 1.2 | Freight and logistics |  |  |  |  |  |  |
| 1.3 | Site preparation and civil works |  |  |  |  |  |  |
| 1.4 | Equipment installation |  |  |  |  |  |  |
| 1.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 1.6 | Training |  |  |  |  |  |  |
| 1.7 | O&M period |  |  |  |  |  |  |
| 1.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 2 | LH. NAIFARU |  |  |  |  |  |  |
| 2.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 2.2 | Freight and logistics |  |  |  |  |  |  |
| 2.3 | Site preparation and civil works |  |  |  |  |  |  |
| 2.4 | Equipment installation |  |  |  |  |  |  |
| 2.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 2.6 | Training |  |  |  |  |  |  |
| 2.7 | O&M period |  |  |  |  |  |  |
| 2.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 3 | L. FONADHOO |  |  |  |  |  |  |
| 3.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 3.2 | Freight and logistics |  |  |  |  |  |  |
| 3.3 | Site preparation and civil works |  |  |  |  |  |  |
| 3.4 | Equipment installation |  |  |  |  |  |  |
| 3.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 3.6 | Training |  |  |  |  |  |  |
| 3.7 | O&M period |  |  |  |  |  |  |
| 3.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 4 | L. GAN |  |  |  |  |  |  |
| 4.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 4.2 | Freight and logistics |  |  |  |  |  |  |
| 4.3 | Site preparation and civil works |  |  |  |  |  |  |
| 4.4 | Equipment installation |  |  |  |  |  |  |
| 4.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 4.6 | Training |  |  |  |  |  |  |
| 4.7 | O&M period |  |  |  |  |  |  |
| 4.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 5 | L. ISDHOO, L. KALAIDHOO, L. DHABIDHOO |  |  |  |  |  |  |
| 5.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 5.2 | Freight and logistics |  |  |  |  |  |  |
| 5.3 | Site preparation and civil works |  |  |  |  |  |  |
| 5.4 | Equipment installation |  |  |  |  |  |  |
| 5.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 5.6 | Training |  |  |  |  |  |  |
| 5.7 | O&M period |  |  |  |  |  |  |
| 5.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 6 | L. MAABAIDHOO |  |  |  |  |  |  |
| 6.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 6.2 | Freight and logistics |  |  |  |  |  |  |
| 6.3 | Site preparation and civil works |  |  |  |  |  |  |
| 6.4 | Equipment installation |  |  |  |  |  |  |
| 6.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 6.6 | Training |  |  |  |  |  |  |
| 6.7 | O&M period |  |  |  |  |  |  |
| 6.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 7 | L. MAAMENDHOO |  |  |  |  |  |  |
| 7.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 7.2 | Freight and logistics |  |  |  |  |  |  |
| 7.3 | Site preparation and civil works |  |  |  |  |  |  |
| 7.4 | Equipment installation |  |  |  |  |  |  |
| 7.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 7.6 | Training |  |  |  |  |  |  |
| 7.7 | O&M period |  |  |  |  |  |  |
| 7.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 8 | L. MAAVAH |  |  |  |  |  |  |
| 8.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 8.2 | Freight and logistics |  |  |  |  |  |  |
| 8.3 | Site preparation and civil works |  |  |  |  |  |  |
| 8.4 | Equipment installation |  |  |  |  |  |  |
| 8.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 8.6 | Training |  |  |  |  |  |  |
| 8.7 | O&M period |  |  |  |  |  |  |
| 8.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 9 | L. KUNAHANDHOO |  |  |  |  |  |  |
| 9.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 9.2 | Freight and logistics |  |  |  |  |  |  |
| 9.3 | Site preparation and civil works |  |  |  |  |  |  |
| 9.4 | Equipment installation |  |  |  |  |  |  |
| 9.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 9.6 | Training |  |  |  |  |  |  |
| 9.7 | O&M period |  |  |  |  |  |  |
| 9.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 10 | L. HITHADHOO |  |  |  |  |  |  |
| 10.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 10.2 | Freight and logistics |  |  |  |  |  |  |
| 10.3 | Site preparation and civil works |  |  |  |  |  |  |
| 10.4 | Equipment installation |  |  |  |  |  |  |
| 10.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 10.6 | Training |  |  |  |  |  |  |
| 10.7 | O&M period |  |  |  |  |  |  |
| 10.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| 11 | SH. FUNDAHOO |  |  |  |  |  |  |
| 11.1 | Project management, monitoring and reporting |  |  |  |  |  |  |
| 11.2 | Freight and logistics |  |  |  |  |  |  |
| 11.3 | Site preparation and civil works |  |  |  |  |  |  |
| 11.4 | Equipment installation |  |  |  |  |  |  |
| 11.5 | Pre-commissioning and tests |  |  |  |  |  |  |
| 11.6 | Training |  |  |  |  |  |  |
| 11.7 | O&M period |  |  |  |  |  |  |
| 11.8 | Implementation including monitoring of ESCP, OHSMP & Code of conduct |  |  |  |  |  |  |
| TOTAL Schedule 4.2 (to Schedule No. 5.2 Grand Summary Lot 02) |  |  |  |  |  |  |  |
|  |  |  | Name of Bidder |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |
| 1 Specify currency in accordance with ITB 18 |  |  |  |  |  |  |  |

Schedule No. 5.  Grand Summary: Lot 02

| Item | Description |  |  |  | Total Price1 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Foreign |  |  | Local (MVR) |  |
| 1 | Total Schedule No. 1. Plant, and Mandatory Spare Parts Supplied from Abroad |  |  |  |  |  |  |  |  |
| 2 | Total Schedule No. 2. Plant, and Mandatory Spare Parts Supplied from Within the Employer’s Country |  |  |  |  |  |  |  |  |
| 3 | Total Schedule No. 3. Design Services |  |  |  |  |  |  |  |  |
| 4 | Total Schedule No. 4. Installation and Other Services |  |  |  |  |  |  |  |  |
| TOTAL Grand Summary Lot 02. (to Letter of Bid) |  |  |  |  |  |  |  |  |  |
|  |  |  | Name of Bidder |  |  |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |  |  |
| 1Specify currency in accordance with ITB 18. Create and use as many columns for Foreign Currency requirement as there are foreign currencies |  |  |  |  |  |  |  |  |  |

Schedule No. 6.  Recommended Spare Parts

| Item | Description |  | Qty. | Unit Price |  |  | Total Price |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | CIF or CIP (foreign parts) |  | EXW (local parts) |  |  |
|  |  |  | (1) | (2) |  | (3) | (1) x (2) or(3) |  |
|  |  |  | Name of Bidder |  |  |  |  |  |
|  |  |  | Signature of Bidder |  |  |  |  |  |

Technical Proposal

- Site Organization

- Method Statement

- Mobilization Schedule

- Construction Schedule

- ES Management Strategies and Implementation Plans

- Code of Conduct for Contractor’s Personnel (ES)

- Plant

- Contractor’s Equipment

- Personnel

- Proposed Subcontractors for Major Items of Plant and Installation Services

- Others

Form TECH- 1: Site Organisation

Details of Proposed Site Organisation

Bidders should provide the details of their proposed site organization, which must address the following points. The format and structure of this form is not specified.

Please provide a high-level description on a stage by stage basis, aligned with the mobilization and construction schedule, of the proposed site organization, including laydown of parts and equipment, site security, and any temporary facilities or buildings. Please include sketches of site organization where necessary.

In particular, site organization should highlight capacity for:

- Sensitivity to the needs and impact on the local island community

- Delivery of equipment, and its storage and security on site

- Safe access and egress for emergencies

- Any provisions for securing the site in the event of natural disasters

Required to attach:

☐General description of site organization, addressing above points (max 3 pages)

☐Sample work method statement for:

- Site civil works

- commissioning BESS

Form TECH- 2: Method Statement

Proposed Method Statement

Bidders should provide the details of their proposed method for carrying out the contract, which must address the following points. The format and structure of this form is not specified.

Provide a method statement for each of the following:

- Overall project logistics, demonstrating how works on successive islands projects will be staged and coordinated. Also demonstrating how the challenging sea and land transport requirements for the islands will be met.

- Carrying out the required design services, including submission and document management and clarification processes.

- Carrying out inspection and test for the project. Please include a high-level plan and examples of test plans for battery, EMS.

- FAT plan for BESS and EMS

- Installation works, also include explanation staffing, team structure, accommodation and provisions for any non-local workers considering any limitations of local facilities and services.

- Capacity building and training, including details of proposed involvement of relevant local personnel in the planning, design, and construction of the plant, expected training modes, number and duration of training sessions, and documentation to be delivered.

- Details and evidence of the potential for the Employer to recycle battery cells at the end of life.

- Process for grid connection, including any shutdowns and their duration.

Required to attach:

☐Method statement for logistics (max. 2 pages)

☐Method statement for carrying out design services (max. 2 pages)

☐Overview of inspection and test plan (max. 2 pages)

☐Sample FAT plans (e.g. from previous project – no page limit)

☐Method statement for installation, including workflow and team structures (max. 2 pages)

☐Description of training and capacity building. State number and duration of sessions. State type of training delivery.

☐Specify 2-5 names and locations of facilities able to receive and recycle battery cells at end of life

☐Description of the grid connection process (max. 2 pages)

Form TECH- 3: Schedule

Time Schedule

Bidders shall stipulate that their time to completion complies with the Employer Requirements

Bidders shall provide a Gantt Chart for project delivery, which shall include, at a minimum:

- Design submission milestones

- Placement of procurement orders for major equipment

- FAT dates for major equipment

- Shipment dates for major equipment

- Site work dates for each island

- BESS and EMS installation, pre-commissioning and commissioning dates for each island

The Gantt Chart shall show schedule in Calendar days from contract effectiveness date.

Required to attach:

☐Statement of Time to Completion

☐Gantt chart addressing above requirements

Construction Schedule

Note to the Bidder:

The minimum content of the Code of Conduct form as set out by the Employer shall not be substantially modified. However, the Bidder may add requirements as appropriate, including to take into account Contract-specific issues/risks.

The Bidder shall initial and submit the Code of Conduct form as part of its bid.

Code of Conduct for Contractor’s Personnel (ES) Form

CODE OF CONDUCT FOR CONTRACTOR’S PERSONNEL

We are the Contractor, [enter name of Contractor].  We have signed a contract with [enter name of Employer] for [enter description of the Facilities]. The Plant for the Facilities will be installed at [enter the Site]. Our contract requires us to implement measures to address environmental and social risks, related to the Installation Services i.e. services ancillary to the supply of the Plant for the Facilities, such as inland transportation, site preparation works/ associated civil works, installation, testing, precommissioning, commissioning, operations and maintenance etc. as the case may require.

This Code of Conduct is part of our measures to deal with environmental and social risks related to the Installation Services.

All personnel that we utilize in the execution of the Contract, including staff, labor and other employees of us and of each Subcontractor, and any other personnel assisting us in the execution of the Contract, are referred to as Contractor’s Personnel.

This Code of Conduct identifies the behavior that we require from the Contractor’s Personnel employed for the execution of Installation Services at the Site (or other places in the country where the Site is located).

Our workplace is an environment where unsafe, offensive, abusive or violent behavior will not be tolerated and where all persons should feel comfortable raising issues or concerns without fear of retaliation.

REQUIRED CONDUCT

Contractor’s  Personnel employed for the execution of Installation Services at the Site (or other places in the country where the Site is located) shall:

- carry out his/her duties competently and diligently;

- comply with this Code of Conduct and all applicable laws, regulations and other requirements, including requirements to protect the health, safety and well-being of other Contractor’s Personnel and any other person;

- maintain a safe working environment including by:

  - ensuring that workplaces, machinery, equipment and processes under each person’s control are safe and without risk to health;

  - wearing required personal protective equipment;

  - using appropriate measures relating to chemical, physical and biological substances and agents; and

  - following applicable emergency operating procedures.

- report work situations that he/she believes are not safe or healthy and remove himself/herself from a work situation which he/she reasonably believes presents an imminent and serious danger to his/her life or health;

- treat other people with respect, and not discriminate against specific groups such as women, people with disabilities, migrant workers or children;

- not engage in any form of sexual harassment including unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature with other Contractor’s or Employer’s Personnel;

- not engage in Sexual Exploitation, which means any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another;

- not engage in in Sexual Abuse,  which means the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions;

- not engage in any form of sexual activity with individuals under the age of 18, except in case of pre-existing marriage;

- complete relevant training courses that will be provided related to the environmental and social aspects of the Contract, including on health and safety matters, and Sexual Exploitation and Abuse, and Sexual Harassment (SH);

- undertake all project activities as per Environmental and Social Code of Practice (20220112-pub-escp-battery-energy-storage-system-installation-arise-project.pdf (environment.gov.mv) developed for the project;

- have a valid work permit to undertake project activities for the project duration;

- report violations of this Code of Conduct; and

- not retaliate against any person who reports violations of this Code of Conduct, whether to us or the Employer, or who makes use of the grievance mechanism for Contractor’s Personnel or the project’s Grievance Redress Mechanism.

RAISING CONCERNS

If any person observes behavior that he/she believes may represent a violation of this Code of Conduct, or that otherwise concerns him/her, he/she should raise the issue promptly. This can be done in either of the following ways:

- Contact [enter name of the Contractor’s Social Expert with relevant experience in handling sexual exploitation, sexual abuse and sexual harassment cases, or if such person is not required under the Contract, another individual designated by the Contractor to handle these matters] in writing at this address [   ] or by telephone at [   ] or in person at [   ]; or

- Call [  ]  to reach the Contractor’s hotline (if any) and leave a message.

The person’s identity will be kept confidential, unless reporting of allegations is mandated by the country law. Anonymous complaints or allegations may also be submitted and will be given all due and appropriate consideration. We take seriously all reports of possible misconduct and will investigate and take appropriate action. We will provide warm referrals to service providers that may help support the person who experienced the alleged incident, as appropriate.

There will be no retaliation against any person who raises a concern in good faith about any behavior prohibited by this Code of Conduct.  Such retaliation would be a violation of this Code of Conduct.

CONSEQUENCES OF VIOLATING THE CODE OF CONDUCT

Any violation of this Code of Conduct by the Contractor’s Personnel may result in serious consequences, up to and including termination and possible referral to legal authorities.

FOR CONTRACTOR’s PERSONNEL:

I have received a copy of this Code of Conduct written in a language that I comprehend.  I understand that if I have any questions about this Code of Conduct, I can contact [enter name of Contractor’s contact person(s) with relevant experience] requesting an explanation.

Name of Contractor’s Personnel: [insert name]

Signature: __________________________________________________________

Date: (day month year): _______________________________________________

Countersignature of authorized representative of the Contractor:

Signature: ________________________________________________________

Date: (day month year): ______________________________________________

ATTACHMENT 1: Behaviors constituting SEA and behaviors constituting SH

ATTACHMENT 1 TO THE CODE OF CONDUCT FORM

BEHAVIORS CONSTITUTING SEXUAL EXPLOITATION AND ABUSE (SEA) AND BEHAVIORS CONSTITUTING SEXUAL HARASSMENT (SH)

The following non-exhaustive list is intended to illustrate types of prohibited behaviors.

- Examples of sexual exploitation and abuse include, but are not limited to:

- A Contractor’s Personnel tells a member of the community that he/she can get them jobs related to the work site (e.g. cooking and cleaning) in exchange for sex.

- A Contractor’s Personnel that is connecting electricity input to households says that he can connect women headed households to the grid in exchange for sex.

- A Contractor’s Personnel rapes, or otherwise sexually assaults a member of the community.

- A Contractor’s Personnel denies a person access to the Site unless he/she performs a sexual favor.

- A Contractor’s Personnel tells a person applying for employment under the Contract that he/she will only hire him/her if he/she has sex with him/her.

- Examples of sexual harassment in a work context

- A Contractor’s Personnel comment on the appearance of another Installation Services Personnel (either positive or negative) and sexual desirability.

- When a Contractor’s Personnel complains about comments made by another Contractor’s Personnel on his/her appearance, the other Contractor’s Personnel comment that he/she is “asking for it” because of how he/she dresses.

- Unwelcome touching of a Contractor’s Personnel or Employer’s Personnel by another Contractor’s Personnel.

- A Contractor’s Personnel tells another Contractor’s Personnel that he/she will get him/her a salary raise, or promotion if he/she sends him/her naked photographs of himself/herself.

Form TECH- 6: Plant

Proposed Plant

Bidders should provide the details of their proposed Plant, which must address the following points.

- A plain English summary of the components, operation, and expected performance of the system.

- Summary of the proposed type, quantity and specifications of major components on an island-by-island basis

- Details of any areas of minor non-conformity with the Employer Requirements[1]. Only minor non-conformities identified at this stage may be considered as exceptions to the Employer Requirements in the contract, should the bidder be successful.

- All Original Equipment Manufacturer (OEM) warranty terms, conditions and warranted levels.

- Tables for each island showing guaranteed energy storage capacity for year 0 – 10, also showing energy throughput modelled in each year.

- Specifications (full data sheets and certifications) of major components. Major components include battery cells and modules, inverters, transformers, switchgear. Employer may request data sheets of other equipment during evaluation.

- Summary of the data and reporting capabilities of the proposed technical solution, and the HMI offered.

- One line electrical and communications / control diagrams of the proposed solution on each island.

- Dimensioned concept drawings (plan view) of the proposed physical layout of each site (typical).

- Typical dimensioned drawings of the internal layout proposed for the BESS

- The fire safety measures included in the BESS.

- HVAC system proposed for the BESS.

- Earthing arrangement of the BESS (and BESS transformer as applicable).

- A detailed description of the functional capabilities of the BESS. Include specification of parameters that can be modified by the user (and the allowable range). Describe all modes of operation. Describe behavior under typical fault conditions, including time to disconnect and fault current provision. Provide typical test data (high frequency) for the BESS for step-load acceptance.

- Details of how auxiliary loads of the BESS will be supplied. Also specify any options for disconnect of the transformer when BESS is not in use, noting inrush currents on energisation.

- Information and contacts on three (3) projects using the same or equivalent models of BESS.

- For the EMS:

  - Hardware platform used.

  - Functional description of the software capabilities, including scope for expanded future application.

  - Information and contacts on three (3) projects using the same or equivalent models of EMS in a solar-battery-diesel hybrid system.

- Balance of plant:

  - Proposed BESS and transformer foundations and access platform if used.

  - Site communications architecture, including interface to diesel master controller, centralised SCADA and remote solar PV sites.

- List of spares included in the offer, and any recommended spares not included in the offer.

Required to attach:

☐ Plain English summary of the proposed solution (max. 1 page)

☐ Table of quantities of major equipment (Major equipment comprises: battery modules, inverters, Transformers, switchgear and EMS.)

☐ Details of any minor non-conformities with Employer Requirements

☐ Warranty terms for all major equipment

☐ Table of guaranteed energy storage capacity of BESS

☐ Equipment data sheet for all major equipment.

☐ Certificates of conformance with standards

☐ Single line drawings (electrical and communications) for each island

☐ Dimensioned drawings

☐ Description of BESS fire safety measures (max 1 page)

☐ Description of BESS earthing, HVAC, auxiliary systems (max 2 pages)

☐ BESS functional description (max 2 pages)

☐ EMS hardware platform, and functional description (max 3 pages)

☐ List reference projects for same EMS and BESS

☐ Describe BESS foundations (max 1 page)

☐ List of included spares

☐ Basic technical information as below. Complete one form per island / network:

BATTERY RACK

| Parameter | Value / Response |
| --- | --- |
| Form factor (e.g. Standalone external pod, internal battery rack) |  |
| Module manufacturer name |  |
| Module part number |  |
| Module power (kW) |  |
| Module energy (nominal, BoL) (kWh) |  |
| Module voltage (nominal) (V) |  |
| Module configuration (series / parallel connection of cells) |  |
| Number of modules per rack |  |
| Number of racks per enclosure |  |
| Number of enclosures for this site |  |
| Total BoL nominal energy (kWh) |  |
| Expected service life (y) |  |
| Design life (y) |  |
| Cell chemistry |  |
| Module certifications and independent tests | - … |
| Type of HVAC system used |  |
| Fire suppression included (Y/N) |  |
| Fire suppressant gas |  |
| Ambient temperature range – operating |  |
| Ambient temperature range – not operating / store |  |
| Level of corrosion resistance |  |

PCU

| Parameter | Value / Response |
| --- | --- |
| Form factor (e.g. Standalone external pod, internal within battery container |  |
| Inverter manufacturer name |  |
| Inverter part number |  |
| Inverter rated power (kW) |  |
| Inverter 60s power (kW) |  |
| Inverter 1s power (kVA) |  |
| Number of inverters for this site |  |
| Inverter cooling system |  |
| Inverter design life (y) |  |
| Inverter certifications and independent tests | … |
| Inverter ingress protection |  |
| Transformer included (Y/N) |  |
| Transformer type |  |
| Transformer rated power (kVA) |  |
| Transformer winding |  |
| Transformer design life |  |
| Level of corrosion resistance |  |

INTEGRATED SYSTEM

| Parameter | Value / Response |
| --- | --- |
| Form factor |  |
| Required footprint (m2) |  |
| Round trip efficiency (%) |  |
| Rated power (kW) |  |
| 60s power (kW) |  |
| 1s power (kVA) |  |
| Total BoL usable energy (kWh) |  |
| Total usable energy after Year 1 (kWh) |  |
| 2 (kWh) |  |
| 3 (kWh) |  |
| 4 (kWh) |  |
| 5 (kWh) |  |
| 6 (kWh) |  |
| 7 (kWh) |  |
| 8 (kWh) |  |
| 9 (kWh) |  |
| 10 (kWh) |  |

EMS SYSTEM

| Parameter | Value / Response |
| --- | --- |
| Hardware platform |  |
| Software platform |  |
| Software developer |  |
| Interface and control offered BESS (Y/N) |  |
| Interface and schedule to control Diesel generator via Deepsea controller (Y/N) |  |
| Interface to control distributed solar PV generation remotely (Y/N) |  |
| HMI and operator workstation included (Y/N) |  |
| Transition to / from diesel off operation (Y/N) |  |

[1] The bid evaluation process applies a stringent process to deviations from the Employer Requirements. It is in the interest of bidders to minimise any deviations.

Form EQU

Contractor’s Equipment

The Bidder shall provide adequate information to demonstrate clearly that it has the capability to meet the requirements for the key Contractor’s equipment listed in Section III, Evaluation and Qualification Criteria. A separate Form shall be prepared for each item of equipment listed, or for alternative equipment proposed by the Bidder.

| Item of equipment |  |  |
| --- | --- | --- |
| Equipment information | Name of manufacturer | Model and power rating |
|  | Capacity | Year of manufacture |
| Current status | Current location |  |
|  | Details of current commitments |  |
| Source | Indicate source of the equipment o Owned o Rented o Leased o Specially manufactured |  |

Omit the following information for equipment owned by the Bidder.

| Owner | Name of owner |  |
| --- | --- | --- |
|  | Address of owner |  |
|  | Telephone | Contact name and title |
|  | Fax | Telex |
| Agreements | Details of rental / lease / manufacture agreements specific to the project |  |

Form FUNC

Functional Guarantees

The Bidder shall copy in the left column of the table below, the identification of each functional guarantee required in the Specification and stated by the Employer in para. 1.2 (c) of Section III, Evaluation and Qualification Criteria, and in the right column, provide the corresponding value for each functional guarantee of the proposed plant and equipment.

| Required Functional Guarantee | Value of Functional Guarantee of the Proposed Plant and Equipment |
| --- | --- |
| 1. Service Life |  |
| 2. Continuous Power |  |
| 3. Round Trip Efficiency |  |
| 4. System availability |  |

Form PER -1

Personnel

Contractor’s Representative and other Key Personnel Schedule

Bidders should provide the names of suitably qualified personnel to meet the specified requirements stated in Section VII. The data on their experience should be supplied using the Form below for each candidate.

Contractor’ Representative and Key Personnel

| 1. | Title of position: Contractor’s Representative |  |
| --- | --- | --- |
|  | Name of candidate: |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| 2. | Title of position: [Environmental Specialist] |  |
|  | Name of candidate: |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| 3. | Title of position: [Health and Safety Specialist] |  |
|  | Name of candidate: |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| 4. | Title of position: [Social Specialist] |  |
|  | Name of candidate: |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| 5 | Title of position: Sexual Exploitation, Abuse and Harassment Expert [Where a Project SEA risks are assessed to be substantial or high, key personnel shall include an expert/s with relevant experience in addressing sexual exploitation, sexual abuse and sexual harassment cases] |  |
|  | Name of candidate |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| 6 | Title of position: [insert title] |  |
|  | Name of candidate |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
|  | Title of position: [insert title] |  |

Form PER-2

Resume of Proposed Personnel

Name of Bidder

| Position |  |  |
| --- | --- | --- |
| Personnel information | Name | Date of birth |
|  | Professional qualifications |  |
| Present employment | Name of employer |  |
|  | Address of employer |  |
|  | Telephone | Contact (manager / personnel officer) |
|  | Fax | E-mail |
|  | Job title | Years with present employer |

Summarize professional experience over the last 20 years, in reverse chronological order. Indicate particular technical and managerial experience relevant to the project.

| From | To | Company / Project / Position / Relevant technical and management experience |
| --- | --- | --- |

Proposed Subcontractors for Major Items of Plant and Installation Services

A list of major items of Plant and Installation Services is provided below.

The following Subcontractors and/or manufacturers are proposed for carrying out the item of the facilities indicated.  Bidders are free to propose more than one for each item

| Major Items of Plant and Installation Services | Proposed Subcontractors/Manufacturers | Nationality |
| --- | --- | --- |

Others - Time Schedule

(to be used by Bidder when alternative Time for Completion is invited in ITB 13.2)

Not Applicable

Bidders Qualification without prequalification

To establish its qualifications to perform the contract in accordance with Section III, Evaluation and Qualification Criteria the Bidder shall provide the information requested in the corresponding Information Sheets included hereunder.

Form ELI 1.1

Bidder Information Sheet

Date:  ______________________

RFB No.: ___________________

Page ________ of _______ pages

1. Bidder’s Legal Name

2. In case of JV, legal name of each party:

3. Bidder’s actual or intended Country of Registration:

4. Bidder’s Year of Registration:

5. Bidder’s Legal Address in Country of Registration:

6. Bidder’s Authorized Representative Information Name: Address: Telephone/Fax numbers: Email Address:

7. Attached are copies of original documents of  Articles of Incorporation (or equivalent documents of constitution or association), and/or documents of registration of the legal entity named above, in accordance with ITB 4.4  In case of JV, letter of intent to form JV or JV agreement, in accordance with ITB 4.1  In case of state-owned enterprise or institution, in accordance with ITB 4.6, documents establishing: - Legal and financial autonomy - Operation under commercial law - Establishing that the Bidder is not under the supervision of the Employer 8. Included are the organizational chart, a list of Board of Directors, and the beneficial ownership. [If required under BDS ITB 46.1, the successful Bidder shall provide additional information on beneficial ownership, using the Beneficial Ownership Disclosure Form.]

Form ELI 1.2

Party to JV Information Sheet

Date: ______________________

RFB No.: ___________________

Page ________ of_ ______ pages

1. Bidder’s Legal Name:

2. JV’s Party legal name:

3. JV’s Party Country of Registration:

4. JV’s Party Year of Registration:

5. JV’s Party Legal Address in Country of Registration:

6. JV’s Party Authorized Representative Information Name: Address: Telephone/Fax numbers: Email Address:

7. Attached are copies of original documents of  Articles of Incorporation (or equivalent documents of constitution or association), and/or registration documents of the legal entity named above, in accordance with ITB 4.4.  In case of a state-owned enterprise or institution, documents establishing legal and financial autonomy, operation in accordance with commercial law, and that they are not under the supervision of the Employer, in accordance with ITB 4.6. 8. Included are the organizational chart, a list of Board of Directors, and the beneficial ownership. [If required under BDS ITB 46.1, the successful Bidder shall provide additional information on beneficial ownership for each JV member using the Beneficial Ownership Disclosure Form.]

Form CON – 2

Historical Contract Non-Performance, Pending Litigation and Litigation History

Bidder’s Legal Name:  _______________________

Date:  _____________________

JV Member Legal Name:  _______________________

RFB No.:  __________________

Page _______ of _______ pages

| Non-Performed Contracts in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
| --- | --- | --- | --- |
|  Contract non-performance did not occur since 1st January [insert year] specified in Section III, Evaluation and Qualification Criteria, Sub-Factor 2.1.  Contract(s) not performed since 1st January [insert year] specified in Section III, Evaluation and Qualification Criteria, Sub-Factor 2.1 |  |  |  |
| Year | Non- performed portion of contract | Contract Identification | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for nonperformance: [indicate main reason(s)] | [insert amount] |
| Pending Litigation, in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
|  No pending litigation in accordance with Sub-Factor 2.3. |  |  |  |
|  Pending litigation in accordance with Sub-Factor 2.3 as indicated below. |  |  |  |

| Year of dispute | Amount in dispute (currency) | Contract Identification | Total Contract Amount (currency), USD Equivalent (exchange rate) |
| --- | --- | --- | --- |
|  |  | Contract Identification: _________ Name of Employer: ____________ Address of Employer: __________ Matter in dispute: ______________ Party who initiated the dispute: ____ Status of dispute: ___________ |  |
|  |  | Contract Identification: Name of Employer: Address of Employer: Matter in dispute: Party who initiated the dispute: Status of dispute: |  |
| Litigation History in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
|  No Litigation History in accordance with Sub-Factor 2.4.  Litigation History in accordance with Sub-Factor 2.4 as indicated below. |  |  |  |
| Year of award | Outcome as percentage of Net Worth | Contract Identification | Total Contract Amount (currency), USD Equivalent (exchange rate) |
| [insert year] | [insert percentage] | Contract Identification: [indicate complete contract name, number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Matter in dispute: [indicate main issues in dispute] Party who initiated the dispute: [indicate “Employer” or “Contractor”] Reason(s) for Litigation and award decision [indicate main reason(s)] | [insert amount] |

Form CON – 3

Environmental and Social Performance Declaration

[The following table shall be filled in for the Bidder, each member of a Joint Venture and each Specialized Subcontractor]

Bidder’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member’s or Specialized Subcontractor’s Name: [insert full name]
RFB No. and title: [insert RFB number and title]
Page [insert page number] of [insert total number] pages

| Environmental and Social Performance Declaration in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
| --- | --- | --- | --- |
|  No suspension or termination of contract: An employer has not suspended or terminated a contract and/or called the performance security for a contract for reasons related to Environmental or Social (ES) performance since the date specified in Section III, Evaluation and Qualification Criteria, Sub-Factor 2.5.  Declaration of suspension or termination of contract: The following contract(s) has/have been suspended or terminated and/or Performance Security called by an employer(s) for reasons related to Environmental or Social (ES) performance since the date specified in Section III, Evaluation and Qualification Criteria, Sub-Factor 2.5. Details are described below: |  |  |  |
| Year | Suspended or terminated portion of contract | Contract Identification | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for suspension or termination: [indicate main reason(s) e.g. gender-based violence; sexual exploitation or sexual abuse breaches] | [insert amount] |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for suspension or termination: [indicate main reason(s)] | [insert amount] |
| … | … | [list all applicable contracts] | … |
| Performance Security called by an employer(s) for reasons related to ES performance |  |  |  |
| Year | Contract Identification |  | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for calling of performance security: [indicate main reason(s) e.g. for gender-based violence; sexual exploitation, or sexual abuse breaches] |  | [insert amount] |

Form CON – 4

Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment Performance Declaration

[The following table shall be filled in by the Bidder, each member of a Joint Venture and each subcontractor proposed by the Bidder]

Bidder’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member’s or Subcontractor’s Name: [insert full name]
RFB No. and title: [insert RFB number and title]
Page [insert page number] of [insert total number] pages

SEA and/or SH Declaration in accordance with Section III, Evaluation and Qualification Criteria

We:  (a) have not been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations  (b) are subject to disqualification by the Bank for non-compliance with SEA/ SH obligations  (c) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations. An arbitral award on the disqualification case has been made in our favor.

[If (c) above is applicable, attach evidence of an arbitral award reversing the findings on the issues underlying the disqualification.]

Form CCC

Current Contract Commitments / Works in Progress

Bidders and each member to a JV should provide information on their current commitments on all contracts that have been awarded, or for which a letter of intent or acceptance has been received, or for contracts approaching completion, but for which an unqualified, full completion certificate has yet to be issued.

| Name of contract | Employer, contact address/tel/fax | Value of outstanding work (current US$ equivalent) | Estimated completion date | Average monthly invoicing over last six months (US$/month) |
| --- | --- | --- | --- | --- |
| 1. |  |  |  |  |
| 2. |  |  |  |  |
| 3. |  |  |  |  |
| 4. |  |  |  |  |
| 5. |  |  |  |  |
| etc. |  |  |  |  |

Bidder should submit documentary evidence in accordance with ITB 11.1 & 15.1.

Form FIN – 3.1

Financial Situation

Historical Financial Performance

Bidder’s Legal Name: _______________________

Date:  _____________________

JV Member Legal Name: _______________________

RFB   No.:  __________________

Page _______ of _______ pages

To be completed by the Bidder and, if JV, by each member

| Type of Financial information in (currency) | Historic information for year 2018, 2019 and 2020, |  |  |
| --- | --- | --- | --- |
|  | (amount in currency, currency, exchange rate*, USD equivalent) |  |  |
|  | 2018 | 2019 | 2020 |
| Statement of Financial Position (Information from Balance Sheet) |  |  |  |
| Total Assets (TA) |  |  |  |
| Total Liabilities (TL) |  |  |  |
| Total Equity/Net Worth (NW) |  |  |  |
| Current Assets (CA) |  |  |  |
| Current Liabilities (CL) |  |  |  |
| Working Capital (WC) (WC = CA – CL) |  |  |  |
| Information from Income Statement |  |  |  |
| Total Revenue (TR) |  |  |  |
| Profits Before Taxes (PBT) |  |  |  |
| Cash Flow Information |  |  |  |
| Cash Flow from Operating Activities |  |  |  |

Attached are copies of financial statements (balance sheets, including all related notes, and income statements) for the years required above complying with the following conditions:

- Must reflect the financial situation of the Bidder or member to a JV, and not sister or parent companies

- Historic financial statements must be audited by a certified accountant

- Historic financial statements must be complete, including all notes to the financial statements

- Historic financial statements must correspond to accounting periods already completed and audited (no statements for partial periods shall be requested or accepted)

Form FIN – 3.2

Average Annual Turnover

Bidder’s Legal Name:  ___________________________

Date:  _____________________

JV Member Legal Name: ____________________________

RFB No.:  __________________

Page _______ of _______ pages

| Annual turnover data |  |  |
| --- | --- | --- |
| Year | Amount and Currency | US$ equivalent |
|  | _________________________________________ | ____________________ |
|  | _________________________________________ | ____________________ |
|  | _________________________________________ | ____________________ |
|  | _________________________________________ | ____________________ |
|  | _________________________________________ | ____________________ |
| *Average Annual Turnover | _________________________________________ | ____________________ |

*Average annual turnover calculated as total certified payments received for work in progress or completed, divided by the number of years specified in Section III, Evaluation Criteria, Sub-Factor 2.3.2.

Form FIN3.3

Financial Resources

Specify proposed sources of financing, such as liquid assets, unencumbered real assets, lines of credit, and other financial means, net of current commitments, available to meet the total cash flow demands of the subject contract or contracts as indicated in Section III, Evaluation and Qualification Criteria

| Source of financing | Amount (US$ equivalent) |
| --- | --- |
| 1. Working Capital (to be taken from 1. Financial Data) |  |
| 2. Line of credit |  |
| 3. Liquid assets |  |
| 4. Unencumbered real assets |  |
| Others |  |
| Total |  |

The above sources of finance indicated shall be supported with proof of documents, including but not limited to:

- auditor certificate certifying all the sources of finance or

- letter from the bank issuing line of credit or

- letter from the bank declaring no encumbrances, no credit claims, no liens for unencumbered real assets or

- references to the financial statements pursuant Section III, Qualifications Criteria and Requirements, Sub-factor 3.1 for any other financial means

Form EXP 4.1

Experience

General Experience

Bidder’s Legal Name:  ____________________________

Date:  _____________________

JV Member Legal Name:  ____________________________

RFB No.:  __________________

Page _______ of _______ pages

| Starting Month / Year | Ending Month / Year | Years* | Contract Identification | Role of Bidder |
| --- | --- | --- | --- | --- |
| ______ | ______ |  | Contract name: Brief Description of the Contract performed by the Bidder: Name of Employer: Address: | _________ |
| ______ | ______ |  | Contract name: Brief Description of the Contract performed by the Bidder: Name of Employer: Address: | _________ |
| ______ | ______ |  | Contract name: Brief Description of the Contract performed by the Bidder: Name of Employer: Address: | _________ |
| ______ | ______ |  | Contract name: Brief Description of the Contract performed by the Bidder: Name of Employer: Address: | _________ |
| ______ | ______ |  | Contract name: Brief Description of the Contract performed by the Bidder: Name of Employer: Address: | _________ |
| ______ | ______ |  | Contract name: Brief Description of the Contract performed by the Bidder: Name of Employer: Address: | _________ |

*List calendar year for years with contracts with at least nine (9) months activity per year starting with the earliest year

Form EXP –4.2(a)

Specific Experience

Bidder’s Legal Name:  ___________________________

Date:  _____________________

JV Member Legal Name: _________________________

RFB No.:  __________________

Page _______ of _______ pages

| Similar Contract Number: ___ of ___ required. |  |  | Information |  |  |
| --- | --- | --- | --- | --- | --- |
| Contract Identification |  |  | __________________________________ |  |  |
| Award date Completion date |  |  | __________________________________ __________________________________ |  |  |
| Role in Contract | Prime Contractor  | Member in JV  |  | Management Contractor  | Subcontractor  |
| Total contract amount | US$__________ |  |  |  |  |
| If member in a JV or subcontractor, specify participation of total contract amount | __________% |  |  | __________ | US$_______ |
| Employer’s Name: |  |  | _________________________________ |  |  |
| Address: Telephone/fax number: E-mail: |  |  | _________________________________ _________________________________ _________________________________ _________________________________ |  |  |

Form EXP –4.2(a) (cont.)

Specific Experience (cont.)

Bidder’s Legal Name:  ___________________________     	Page _______ of _______ pages

JV Member Legal Name:  ___________________________

| Similar Contract No. __[insert specific number] of [total number of contracts] ___ required | Information |
| --- | --- |
| Description of the similarity in accordance with Sub-Factor 4.2a) of Section III: |  |
| Amount | _________________________________ |
| Physical size | _________________________________ |
| Complexity | _________________________________ |
| Methods/Technology | _________________________________ |
| Physical Production Rate | _________________________________ |

Form EXP –4.2(b)

Specific Experience in Key Activities

Bidder’s Legal Name:  ___________________________

Date:  ___________________

JV Member Legal Name: _________________________

RFB No.:  __________________

Subcontractor’s Legal Name: ______________

Page _______ of _______ pages

|  | Information |  |  |
| --- | --- | --- | --- |
| Contract Identification |  |  |  |
| Award date Completion date | _______________________________________ _______________________________________ |  |  |
| Role in Contract | Prime Contractor  | Management Contractor  | Subcontractor  |
| Total contract amount | US$ |  |  |
| If member in a JV or subcontractor, specify participation of total contract amount | __________% | _____________ | US$________ |
| Employer’s Name: | _______________________________________ |  |  |
| Address: Telephone/fax number: E-mail: | _______________________________________ _______________________________________ _______________________________________ _______________________________________ |  |  |

Form EXP –4.2 (b)(cont.)

Specific Experience in Key Activities (cont.)

Bidder’s Legal Name:  ___________________________     	Page _____ of _____ pages

JV Member Legal Name:  ___________________________

Subcontractor’s Legal Name: __________________________

| Description of the key activities in accordance with Sub-Factor 4.2b) of Section III: | Information |
| --- | --- |
| Experience as a prime contractor, joint venture member, management contractor or sub-contractor of having successfully completed Design, Engineering, Procurement, Construction, Installation, Testing and Commissioning of communications architecture and energy management system. (EMS) to maximize renewable energy use in at least 01 (one) isolated network with a peak load exceeding 500 KW. |  |

Form EXP –4.2(c)

Specific Experience in Managing ES aspects

Bidder’s Legal Name:  ___________________________     	Date:  _____________________

JV Member Legal Name: _________________________	RFB No.:  __________________

Subcontractor’s Legal Name: ______________	Page _______ of _______ pages

      - Key Requirement no 1 in accordance with 4.2 (c): __

____________________

| Contract Identification |  |  |  |  |
| --- | --- | --- | --- | --- |
| Award date |  |  |  |  |
| Completion date |  |  |  |  |
| Role in Contract | Prime Contractor  | Member in JV  | Management Contractor  | Subcontractor  |
| Total Contract Amount | US$ ____________ |  |  |  |
| Details of relevant experience |  |  |  |  |

      - Key Requirement no 2 in accordance with 4.2 (c): ______________________

      - Key Requirement no 3 in accordance with 4.2 (c): ______________________

Form of Bid Security

Form of Bid Security – Bank Guarantee

[The bank shall fill in this Bank Guarantee Form in accordance with the instructions indicated.]

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:  Ministry of Finance, Male’ , Republic of Maldives

RFB No.:[Employer to insert reference number for the Request for Bids]

Date:[Insert date of issue]

BID GUARANTEE No.:[Insert guarantee reference number]

Guarantor:  [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ______ [insert name of the Bidder, which in the case of a joint venture shall be the name of the joint venture (whether legally constituted or prospective) or the names of all members thereof](hereinafter called "the Applicant") has submitted or will submit to the Beneficiary its Bid (hereinafter called "the Bid") for the execution of ________________ under RFB No. ____________

Furthermore, we understand that, according to the Beneficiary’s conditions, Bids must be supported by a Bid guarantee.

At the request of the Applicant, we, as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ (____________) upon receipt by us of the Beneficiary’s complying demand, supported by the Beneficiary’s statement, whether in the demand itself or a separate signed document accompanying or identifying the demand, stating that either the Bidder:

(a) 	has withdrawn its Bid prior to the Bid validity expiry date set forth in the Applicant’s Letter of Bid, or any extended date provided by the Applicant; or

(b) 	having been notified of the acceptance of its Bid by the Beneficiary prior to the expiry date of the Bid validity or any extension thereto provided by the Applicant, (i) has failed to execute the Contract Agreement, or (ii) has failed to furnish the Performance Security, in accordance with the Instructions to Bidders (“ITB”) of the Beneficiary’s bidding document.

This guarantee will expire: (a) if the Applicant is the successful Bidder, upon our receipt of copies of the contract agreement signed by the Applicant and the Performance Security issued to the Beneficiary in relation to such contract agreement; or (b) if the Applicantis not the successful Bidder, upon the earlier of (i) our receipt of a copy of the Beneficiary’s notification to the Applicant of the results of the Bidding process; or (ii) twenty-eight days after the expiry date of the Bid validity.

Consequently, any demand for payment under this guarantee must be received by us at the office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758.

_____________________________

[Signature(s)]

Note:  All italicized text is for use in preparing this form and shall be deleted from the final product.

Manufacturer’s Authorization

Date: __________________

RFB No.: _________________

To:  ________________________

WHEREAS

We ___________________, who are official manufacturers of____________________, having factories at _____________________, do hereby authorize ______________________ to submit a Bid the purpose of which is to provide the following goods, manufactured by us _______________________, and to subsequently negotiate and sign the Contract.

We hereby extend our full guarantee and warranty in accordance with Clause 27 of the General Conditions, with respect to the goods offered by the above firm.

Signed: _______________________________________

Name: ______________________________________

Title:______________________________________

Duly authorized to sign this Authorization on behalf of: ______________________________________

Dated on ____________ day of __________________, _______

Section V - Eligible Countries

Eligibility for the Provision of Goods, Works and Non-Consulting Services in 
Bank-Financed Procurement

In reference to ITB 4.8 and 5.1, for the information of the Bidders, at the present time firms, goods and services from the following countries are excluded from this Bidding process:

Under ITB 4.8 (a) and 5.1: None

Under ITB 4.8 (b) and 5.1: None

Section VI - Fraud and Corruption

- Purpose

  - The Bank’s Anti-Corruption Guidelines and this annex apply with respect to procurement under Bank Investment Project Financing operations.

- Requirements

- The Bank requires that Borrowers (including beneficiaries of Bank financing); bidders (applicants/proposers), consultants, contractors and suppliers; any sub-contractors, sub-consultants, service providers or suppliers; any agents (whether declared or not); and any of their personnel, observe the highest standard of ethics during the procurement process, selection and contract execution of Bank-financed contracts, and refrain from Fraud and Corruption.

- To this end, the Bank:

- Defines, for the purposes of this provision, the terms set forth below as follows:

- “corrupt practice” is the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party;

- “fraudulent practice” is any act or omission, including misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain financial or other benefit or to avoid an obligation;

- “collusive practice” is an arrangement between two or more parties designed to achieve an improper purpose, including to influence improperly the actions of another party;

- “coercive practice” is impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party;

- “obstructive practice” is:

- deliberately destroying, falsifying, altering, or concealing of evidence material to the investigation or making false statements to investigators in order to materially impede a Bank investigation into allegations of a corrupt, fraudulent, coercive, or collusive practice; and/or threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or

- acts intended to materially impede the exercise of the Bank’s inspection and audit rights provided for under paragraph 2.2 e. below.

- Rejects a proposal for award if the Bank determines that the firm or individual recommended for award, any of its personnel, or its agents, or its sub-consultants, sub-contractors, service providers, suppliers and/ or their employees, has, directly or indirectly, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices in competing for the contract in question;

- In addition to the legal remedies set out in the relevant Legal Agreement, may take other appropriate actions, including declaring misprocurement, if the Bank determines at any time that representatives of the Borrower or of a recipient of any part of the proceeds of the loan engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices during the procurement process, selection and/or execution of the contract in question,  without the Borrower having taken timely and appropriate action satisfactory to the Bank to address such practices when they occur, including by failing to inform the Bank in a timely manner at the time  they knew of the practices;

- Pursuant to the Bank’s Anti- Corruption Guidelines and in accordance with the Bank’s prevailing sanctions policies and procedures, may sanction a firm or individual, either indefinitely or for a stated period of time, including by publicly declaring such firm or individual ineligible (i) to be awarded or otherwise benefit from a Bank-financed contract, financially or in any other manner; (ii) to be a nominated sub-contractor, consultant, manufacturer or supplier, or service provider of an otherwise eligible firm being awarded a Bank-financed contract; and (iii) to receive the proceeds of any loan made by the Bank or otherwise to participate further in the preparation or implementation of any Bank-financed project;

- Requires that a clause be included in bidding/request for proposals documents and in contracts financed by a Bank loan, requiring (i) bidders (applicants/proposers), consultants, contractors, and suppliers, and their sub-contractors, sub-consultants, service providers, suppliers, agents personnel, permit the Bank to inspect all accounts, records and other documents relating to the procurement process, selection and/or contract execution, and to have them audited by auditors appointed by the Bank.

PART 2 - Employer’s Requirements

Section VII - Employer’s Requirements

Contents

Scope of Supply of Plant and Installation Services by the Contractor	148

1	Description of the Works	149

1.1	Country and Project Overview	149

1.2	General requirements and description of works	150

1.2.1        Standards and codes	150

1.2.2        Scope of Project	150

2	Specification	153

2.1	Detailed specifications	153

2.2	Division of responsibilities matrix	153

2.3	Engineering	156

2.4	Procurement	156

2.5	Construction	157

2.6	Commissioning	157

2.7	Operations and maintenance	157

2.8	Battery Limits	158

2.9	Employer Provided Items	158

2.10	Permits, Certificates, Licenses, Registrations and Approvals	159

2.11	Indicative equipment requirements	159

2.12	Functional Guarantees	162

2.13	Project management and delivery requirements	163

3	Implementation Period	164

4	Site and Other Data	165

5	Contractor’s Representative and Key Personnel	166

Appendix A – General and Electrical requirements	167

1	Relationship to other parts of the Employer Requirements	168

2	Definitions	169

3	Standards	170

4	Language and units	172

4.1	Language	172

4.2	Units of Measurement	172

5	Site requirements	173

5.1	Work Practices	173

5.2	Miscellaneous requirements	175

6	Reporting, documentation, and meetings	179

6.1	Management plans	179

6.2	Document management system	182

6.3	Documentation deliverables	183

6.4	Equipment naming convention and hierarchy	188

6.5	Asset register	188

6.6	Meetings	188

7	Training and capacity building	190

7.1	Emergency response	190

7.2	BESS operations	190

8	Environmental and Social Risk	191

9	Equipment requirements	192

9.1	Design life	192

9.2	PLCs, Control systems, cabinets and junction boxes	192

9.3	Switchgear	195

9.4	Metering	197

9.5	Step-up Transformer	199

9.6	Environmental Protection	200

9.7	Protection	201

9.8	Earthing	201

9.9	Cabling and cable management	202

9.10	Fixings and fasteners	202

9.11	DC Combiner panels	203

10	Civil and structural works requirements	205

10.1	Service conditions	205

10.2	Scope of civil works	206

10.3	Civil works requirements	206

10.4	Scope of structural works	206

10.5	Requirements of structural works	207

11	Engineering studies	208

12	Quality control	210

12.1	Witness and Hold Points	210

12.2	Inspection and testing	210

13	Warranty requirements	218

14	Remote commissioning	219

Appendix B – Battery Energy Storage System (BESS) requirements	220

1	Relationship to other parts of the Employer Requirements	221

2	Definitions	222

3	Standards	224

4	Intended Purpose	226

4.1	Key performance requirements	226

4.2	Functionality	226

4.3	Duty cycle	228

4.4	Expected service life	229

4.5	Robustness to failure	229

5	Scope of work	230

6	Architecture	232

6.1	Point of Connection (POC) arrangement	232

6.2	Communications interface	233

7	Physical and installation requirements	235

7.1	Design life and workmanship	235

7.2	Service conditions	235

7.3	Heating, ventilation and air-conditioning	236

7.4	Miscellaneous requirements	237

7.5	Human machine interface	238

7.6	Operation and maintenance	239

7.7	Spares and tools	239

7.8	Fire safety	240

8	Performance requirements	241

8.1	Metering point	241

8.2	Power	241

8.3	Power System models	243

8.4	Energy storage	243

8.5	Roundtrip efficiency	244

8.6	Transitions	244

8.7	Frequency withstand capability	244

8.8	Power quality	245

8.9	Self-discharge	245

9	Equipment Requirements	246

9.1	Compatibility	246

9.2	Battery modules	246

9.3	Power conversion units	246

10	Environmental risk	248

11	Safety and risk mitigation requirements	249

11.2	Additional requirements	249

12	Inspection and testing	252

12.1	Factory acceptance tests (FAT)	252

12.2	Site acceptance tests (SAT)	252

13	Warranty requirements	254

14	Capacity guarantee tests	255

Appendix C – Energy Management System (EMS) requirements	257

1	Relationship to other parts of the Employer Requirements	258

2	Intended Purpose	259

2.1	Operation	260

2.2	Robustness to failure	260

2.3	Compatibility for future operations	261

3	Scope of work	262

4	Safety, reliability and power quality requirements	263

4.1	Safety	263

4.2	Reliability	263

4.3	Power quality requirements	264

5	System states	265

6	Performance requirements	267

6.1	Ramp rate control	267

7	Interfaces	268

7.1	Thermal generation	268

7.2	BESS and Solar PV	268

7.3	Data and parameter lists	268

8	Physical and installation requirements	270

8.1	Design life and workmanship	270

8.2	Installation	270

8.3	Equipment	270

8.4	Human machine interface	271

8.5	Operation and maintenance	271

8.6	Spares and tools	271

9	Quality management	273

9.1	Inspection and testing	273

10	Performance test	275

Appendix D – Battery Energy Storage System (BESS) and Energy Management System (EMS) Operation and Maintenance Requirements	277

1	Standards	278

2	Operations and Maintenance	279

2.1	Duration of support	280

2.2	Indicative support requirements	281

3	Asset Management Plan	285

Appendix E – Project Site Specific Details	294

Appendix F - Environmental and Social Safeguards Requirements	295

Forms and Procedures	303

# Scope of Supply of Plant and Installation Services by the Contractor

# Description of the Works

## Country and Project Overview

The Republic of Maldives is a South Asian island country, located southwest of Sri Lanka and India. It is comprised of 1,192 coral islands grouped into 26 geographical atolls, spreading over an area of 115,300 km2 and occupying a total land area of 224 km2. Maldives is recognized as an upper middle-income economy by the World Bank with a GDP growth rate of 8.1% in 2018

Out of the total 1,192 islands, 187 are inhabited, 123 are self-contained tourist resorts and 128 are used for other industrial and commercial activities. The current population of Maldives is 543,088. The dispersed nature of the islands requires each island to have a separate power generation and distribution system. The powerhouses are operated mainly by three utility companies namely, State Electric Company Limited (STELCO), FENAKA Corporation Ltd. (FENAKA) and Male’ Water and Sewerage Company Pvt. Ltd. (MWSC).

Maldives achieved universal access to electricity in 2008, with 24 hours electricity service in all inhabited islands and resorts in the country. However, with no conventional fuel source, the country relies on imported diesel for electricity production and is seeking to overcome its economic and environmental burdens by adopting to renewable based power generation methods, specifically solar PV.

Renewable energy supportive policies and programs of the Maldivian Government has set PV growth on an upward trend over the past decade. The installed solar PV capacity has reached 21.52 MW in 2019 from 1.64MW in 2009. The National Strategic Action Plan (2019-2023) (SAP) sets targets to further increase the share of renewable energy by 20% compared to 2018 levels and in order to meet this target and beyond, the Ministry of Environment, Climate Change and Technology aims to increase the share of renewable energy to 70% of the national energy mix by 2030. Currently the energy from renewables make only 4% of the national energy mix and significant growth is anticipated for the Maldives energy sector with an approximate doubling of energy demand forecasted for many of the project islands over the next 10 years.

Developing renewable energy projects through private sector financing is an attractive way for Maldives to accelerate the development of renewable energy. Support from World Bank Group (WBG) has made tremendous contributions to improve the renewable energy investment climate in Maldives for the private sector. Through technical assistances and financial leverages delivered under the World Bank’s Accelerating Sustainable Private Investment in Renewable Energy (ASPIRE) project (ongoing since December 2014) two rounds of solar PV IPP bids with a total generation capacity of 6.5MW has been complete and PPA tariffs has reduced substantially for these two consecutive bids with the trend expected to continue. Prequalification of eligible bidders for the third phase of ASPIRE is ongoing which includes 11 MW of solar PV installations across various islands.

The current RE targets for Maldives require a high penetration of Variable Renewable Energy (VRE) in the island grids, thus modernizing and upgrading of the existing grid infrastructures are needed along with complementing technology options for energy storage. Building on the efforts of the ASPIRE initiative, during December 2020 WB has approved a second project, i.e. Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) project to further accelerate the energy transition occurring in Maldives and support a sustainable post COVID-19 recovery.

The development objective of the ARISE project is to increase the generation capacity from renewable energy sources and facilitate the integration of VRE in the mini grids of Maldives islands. The ARISE project includes a target of bringing in 36 MW new solar PV installations with an estimated cumulative 50MWh of Battery Energy Storage Systems (BESS), and grid infrastructure upgrades.

The works will draw on a mix of loan and grant financing mobilized under the ARISE project. The funding for the BESS component of ARISE is through a US$ 23 million concessional loan allocated from Clean Technology Fund. The BESS procurement covered by this prequalification will support grids where solar PV is deployed under ASPIRE Phase III (11 MW) and first two phases of ARISE (10 MW Floating PV and another 11-14 MW land-based PV installations).

## General requirements and description of works

The works related to this Contract is for delivering (design, supply, installation and commissioning) BESS and Energy Management Systems (EMS) to achieve effective operation of solar PV diesel hybrid power systems in the selected island grids.

The BESS herein referred to includes energy storage units (batteries), Battery Management Systems (BMS), power conversion systems (for integrating the DC energy from the batteries to the connection point of the grid), cabling and any other Balance of Systems (BOS) for the integration of energy from the batteries.

The EMS herein referred to include a stand-alone control panel with communications interfaces for monitoring status of all grid connected generators (BESS, Solar PV, and diesel), network and load conditions. The EMS shall determine the optimal dispatch of generators based on the system state and issue mode, dispatch and scheduling commands to generators (and potentially trigger load shedding of feeders). The EMS includes an operator workstation with Human Machine Interface and link to a centralized SCADA.

## 1.2.1        Standards and codes

The equipment installation and electrical works under the contract must be carried out in accordance with the latest revisions and amendments of relevant IEC standards as in force in Maldives. Furthermore, the installations must comply with the technical requirements prescribed by the Utility Regulatory Authority (URA) as well as any other laws or regulations of Maldives.

Further details are included in Section 1.3 Specifications.

## 1.2.2        Scope of Project

Scope of Project and requirements included in this section is to provide a general understanding of the nature of work to be delivered under the contract. Detailed specifications are included in Section 1.3 Specifications.

- Design and supply of BESS along with EMS. Carry out comprehensive factory acceptance tests (FAT) on all equipment.

- Logistics and delivery of all equipment to the installation site.

- Construction site management including site supervision, site monitoring and security, connection of amenities such as power, water etc. required for construction purposes (if necessary).

- Preparatory and permanent civil works for BESS and EMS installation on site where needed. This includes but is not limited to setting up construction site fencing, site levelling and foundation for batteries and transformers, making cable trenches and pathways for safely routing the power cables from battery to grid connection points, permanent fencing and locking of the installation sites if the BESS site is in an area publicly accessible.

- System assembly and electrical installation works including earthing and other electrical safety measures as needed for batteries, power converting units (inverting units, transformers), safety devices and any BOS and grid integration of the BESS. This includes comprehensive design, modelling and test to be conducted by the Contractor.

- Installation of communication devices and setup of communication architecture for interfacing of BMS, PV communication devices, generator controllers, feeder load shedding devices etc. to the EMS and its integration to a central SCADA, and in coordination with operators of other generators where required. The BMS and EMS shall be programmed to maintain safe operation of batteries and provide various operational strategies specified. The BMS and EMS are to be programmed to achieve efficient operation of existing diesel generators, allow maximal feed in of renewable power while maintaining grid stability and to achieve grid forming batteries in instances needed. EMS functional requirements, including equipment to interface with, command instructions available for lower level controllers, operating configurations of generation equipment that it must manage, performance requirements for maximizing instantaneous use of VRE and application of the BESS for spinning reserve. Furthermore, an Human-Machine Interface (HMI)shall be installed for operators to communicate with the control system and monitor the power system and its components.

  - Some networks (currently 4 of 20) have existing or proposed solar generators incorporating local energy storage and a micro-grid controller. In such situations, the EMS will form the master controller for the network and must be capable of interfacing with and issuing dispatch instructions to other micro-grid controllers. Contractor will be required to complete interfacing to other micro-grid controllers in cooperation with the suppliers of these systems. Alternatively, Contractor may elect to make redundant the existing micro-grid controller and interface the EMS directly to existing solar and energy storage.

- Design, installation, programming and commissioning of HVAC systems, fire mitigation and safety etc. in compliance to the safety standards specified by the Employer

- Conduct testing at component level and system level upon installation and ensure that all performance parameters are met to the satisfaction of the Employer. Also, as part of assuring quality control and functional compliance of the equipment selected for the product, the contractor shall conduct all factory and site tests as per the specifications and produce documents of proof as required.

- Commissioning of the systems with testing at integrated level and ensure successful operation of the system as per the operational configuration required for the hybrid system. All tests and final checks along with the documents to be submitted for acceptance of the system shall be met for system commissioning to be declared.

- Perform O&M activities for a specified 2 year period, along with providing and maintaining spares and consumables.

- Providing training and ensure plant operators are equipped with the knowledge and skill necessary for effectively operating systems and to conduct maintenance of the system and components.

- Provide options for recycling of the batteries at the end life through an approach such as entering into a recycling program from the manufacturer.

# Specification

## Detailed specifications

Detailed specifications for this project are included in the following Appendices.

- Appendix A – General and Electrical

  - This specifies the electrical standards applicable to all equipment, as well as general provisions for work practices, studies, document submission, and management of project, design, and quality.

- Appendix B – Battery Energy Storage System (BESS):

  - This document provides key technical and functional requirements of the Battery Energy Storage System (BESS).

- Appendix C – Energy Management System:

  - This document provides key technical and functional requirements of the Energy Management System (EMS) that must be provided independent of the BESS to provide system wide generation dispatch management.

- Appendix D – Operations and maintenance:

  - This document provides key technical and functional requirements of the Battery Energy Storage System (BESS) and Energy Management System (EMS) Operation and Maintenance Requirements.

- Appendix E – Project Site Specific Details:

  - This document includes a range of reliance and supplementary information relevant to the project.

- Appendix F – Environmental and Social Requirements:

  - This appendix provides the environmental social safeguards requirements and reference is made to relevant safeguards documents of the project.

Where any conflict arises between this document, and the Appendices, or between any of the appendices, the more onerous requirement shall apply unless otherwise agreed by the Employer.

## Division of responsibilities matrix

The following tables set out the division of responsibilities. Please note that where responsibility is not ‘Contractor’ Contractor’s inputs may still be required. Any requirements to deliver the project that are not explicitly listed below (or elsewhere in this Employer Requirements) are Contractor’s responsibility.

|  | Description | Employer | Utility | Contractor | Notes |
| --- | --- | --- | --- | --- | --- |
|  | Environmental and social screening reports | Yes |  | Yes | Contractor to update |
|  | Environment and social code of practice | Yes |  | Yes | Contractor to update |
|  | Land agreements | Yes | Yes |  |  |
|  | Site Survey |  |  | Yes |  |
|  | Geotechnical Survey |  |  | Yes |  |
|  | Permits and licenses | Assist | Assist | Yes |  |
|  | Design, technical studies |  |  | Yes |  |
|  | Inspection and test |  |  | Yes |  |
|  | HV Submission |  |  | Yes |  |
|  | Site Offices & temporary facilities |  |  | Yes | If required |
|  | Contractors temporary site (material storage) |  |  | Yes |  |
|  | Internet (temporary services) |  |  | Yes |  |
|  | Accommodation |  |  | Yes |  |
|  | Select Fill / Excavated Fill |  |  | Yes |  |
|  | Waste Disposal |  |  | Yes |  |
|  | Dust Suppression |  |  | Yes | If required |
|  | Site Clearing, Grubbing |  |  | Yes |  |
|  | Internal Roads |  |  | Yes | If required |
|  | Access Roads |  |  |  | N/A – use existing roads |
|  | Laydown |  | Assist | Yes |  |
|  | Site Grading, cut and fill |  |  | Yes |  |
|  | Equipment shipping |  |  | Yes |  |
|  | Equipment land transport and cranage |  |  | Yes |  |
|  | Staff flights and land transport |  |  | Yes |  |
|  | Mobilisation & Demobilisation |  |  | Yes |  |
|  | Aggregate and Concrete |  |  | Yes |  |
|  | Trench bedding sand |  |  | Yes |  |
|  | Management Plans and documentation |  |  | Yes |  |
|  | OEM Equipment |  |  | Yes |  |
|  | Site surveying /pegging |  |  | Yes |  |
|  | Site clean-up |  |  | Yes |  |
|  | Labelling |  |  | Yes |  |
|  | As-Built drawings and documentation |  |  | Yes |  |
|  | Testing and Commissioning Reports |  |  | Yes |  |
|  | Spare Parts |  |  | Yes |  |
|  | Perimetral Fence |  |  | Yes | If required |
|  | Steel Gates |  |  | Yes | If required |
|  | Earthing and lightning protection |  |  | Yes |  |
|  | Energy management system |  |  | Yes |  |
|  | Communications Cabinet in Power Station |  |  | Yes |  |
|  | Centralised SCADA |  | Provide | Interface to | Contractor to interface each island to existing FENAKA SCADA |
|  | Interface to solar PV plants and grid intelligent electronic devices (RMU protection) | Physical |  | Data | Employer will engage others to install solar PV and grid. Contractor to test and confirm all interfaces. |
|  | Meteorological stations |  |  | Yes |  |
|  | Commissioning |  |  | Yes |  |
|  | Procurement |  |  |  |  |
|  | Electrical Cabling |  |  | Yes |  |
|  | Battery modules and racks, including all OEM supporting hardware and software |  |  | Yes |  |
|  | DC Combiner Box |  |  | Yes |  |
|  | Battery enclosures |  |  | Yes |  |
|  | Battery Inverter |  |  | Yes |  |
|  | Battery Transformer |  |  | Yes |  |
|  | Battery Switchgear |  |  | Yes | If required |
|  | Battery System Freight |  |  | Yes |  |
|  | Fire Protection System |  |  | Yes |  |
|  | HVAC |  |  | Yes |  |
|  | Control and communications cabling |  |  | Yes |  |
|  | Control and communications racks and power supply |  |  | Yes |  |
|  | Workstation, routers, media converters, server / local historian |  |  | Yes |  |
|  | Energy management system |  |  | Yes |  |
|  | Sensors, meters, instrumentation |  |  | Yes |  |

## Engineering

The Contractor shall design and engineer the works in accordance with the Contract, including this Employer’s Requirements and the Detailed Specifications in Section 2.1.

## Procurement

The Contractor is to procure all items necessary for its scope of works. The Contractor is to provide a comprehensive Bill of Materials in its reporting to the Employer and detail the status of procurement and delivery within each report.

## Construction

The Contractor is required to carry out all construction activities (as per the division of responsibilities matrix) to prepare the site, install and connect the equipment, and ensure it is in a fit and sound state ready for energisation. Construction planning and activities must give due consideration to the requirements of working on remote islands with limited resources.

Contractor is required to liaise with the Employer’s staff for connection and all necessary pre-commissioning tests of electrical and communications interfaces.

Further details on Construction requirements are included in the Technical Specifications.

## Commissioning

The Contractor shall prepare a comprehensive commissioning plan. In cooperation with the Employer, the Contractor shall liven the plant in accordance with the commissioning plan. The Contractor shall carry out necessary tests, including performance tests of equipment and provide a detailed commissioning report.

Further details on Commissioning requirements are included in the Detailed Specifications in Section 1.3.

## Operations and maintenance

The Contractor shall provide comprehensive operations and maintenance manuals, procedures, data sheets, as-built drawings other information as required in the Detailed Specifications in Section 2.1.

The Contractor will be required to operate the plant for a period prior to hand-over to the Employer for a 2 year period. Contractor shall also include OEM technical support (to support diagnosis and rectification of issues, as well as minor system modifications) for the BESS and EMS for corresponding periods.

During hand-over, Contractor shall:

- Offer a period of 12 months (included within the O&M period) working side by side with the Employer’s staff and providing instruction on all operational matters that arise.

- Provide dedicated training to fully instruct the Employer’s staff in operation and maintenance of the plant. This shall include hands on training and testing of the trainees.

- All manuals, documents, materials, spares, tools, etc. as required under the Contract must be itemised and inventoried and provided to the Employer’s staff.

Further details of the operations and maintenance period, training and handover are included in Appendix D – Operations and Maintenance.

## Battery Limits

The project battery limits are:

- The physical limits of:

  - The specified BESS envelope adjacent to the thermal power station, including any defined cable routes

  - The physical space designated at each power station for installation of communication rack(s) and EMS

- The electrical interface:

  - The point of connection, being the circuit breakers provided on the 11 kV or 415 V (as relevant) thermal power station bus (Contractor to terminate)

- The communications interface:

  - The existing communications ports on the deep sea electronics diesel master controllers

  - The fibre optic cables (installed by others) to remote solar PV plant (termination by Contractor)

  - The radio link to remote solar PV plant (ethernet interface to Contractor’s plant)

  - Third party internet service provider (internet connection point to be provided by Contractor).

## Employer Provided Items

The Employer shall provide any items or support as defined in the division of responsibilities matrix.

## Permits, Certificates, Licenses, Registrations and Approvals

The Contractor shall identify, make allowance for, and secure all necessary permits, certificates, licenses, registrations and approvals required for the project.

## Indicative equipment requirements

The Contractor must determine the required equipment to meet this specification. The following table provides an indication of the expected equipment only:

Lot 1

| Island | Addu-mainland | Hulhumeedhoo | Fuvahmulah | Thinadhoo | Hinnavaru | Eydhafushi | Kulhudhuffushi |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Atoll | Seenu | Seenu | Gnaviyani | Gaafu Dhaalu | Lhaviyani | Baa | Haa Dhaalu |
| Electrical cable to point of connection | Y (<50 m) |  |  |  |  |  |  |
| Voltage at point of connection (kV) | 11 |  |  |  |  |  |  |
| Step-up transformer | Required. Rating to allow full required output of BESS under continuous and overload conditions. |  |  |  |  |  |  |
| BESS Inverter (MVA) (mandatory minimum) | 13.4 | 2.2 | 2.2 | 2.8 | 1.1 | 1.7 | 2.22 |
| BESS AC Continuous Power (MW) (mandatory minimum) | 12 | 2 | 2 | 2.5 | 1 | 1.5 | 2 |
| BESS DC Energy Storage (MWh) | 12 | 2 | 2 | 2.5 | 1 | 1.5 | 2 |
| BESS BMS | Y |  |  |  |  |  |  |
| BESS local HMI panel and e-stops | Y |  |  |  |  |  |  |
| Workstation with HMI | Y |  |  |  |  |  |  |
| Communications and control panel | Y |  |  |  |  |  |  |
| EMS and integration requirements | Y |  |  |  |  |  |  |

Lot 2

| Island | Fonadhoo | Gan | Dhanbidhoo, Isdhoo, Kalaidhoo | Maabaidhoo | Maamendhoo | Kunahandhoo |
| --- | --- | --- | --- | --- | --- | --- |
| Atoll | Laamu |  |  |  |  |  |  |
| Electrical cable to point of connection | <50m | <50m | <50m | <50m | <50m | <50m |
| Voltage at point of connection (kV) | 11 |  |  | 0.4 |  |  |
| Step-up transformer | Required. Rating to allow full required output of BESS under continuous and overload conditions. |  |  | Recommended not to include and utilise BESS inverter output at grid voltage. Contractor may include transformer at its discretion. If transformer is included, rating to allow full required output of BESS under continuous and overload conditions. |  |  |
| BESS Inverter (MVA) (mandatory minimum) | 2.8 | 3.7 | 1.5 | 0.5 | 0.6 | 0.5 |
| BESS AC Continuous Power (MW) (mandatory minimum) | 2.5 | 3.3 | 1.3 | 0.4 | 0.5 | 0.4 |
| BESS DC Energy Storage (MWh) | 2.5 | 6.6 | 1.3 | 0.4 | 0.5 | 0.4 |
| BESS BMS | Y |  |  |  |  |  |  |
| BESS local HMI panel and e-stops | Y |  |  |  |  |  |  |
| Workstation with HMI | Y |  |  |  |  |  |  |
| Communications and control panel | Y |  |  |  |  |  |  |
| EMS and integration requirements | Y |  |  |  |  |  |  |

Lot  2 (continued)

| Island | Hithadhoo | Maavah | Naifaru | Villingili | Funadhoo |
| --- | --- | --- | --- | --- | --- |
| Atoll | Laamu | Laamu | Lhaviyani | Gaafu Alif | Shaviyani |
| Electrical cable to point of connection | <50m | <50m | <50m | <50m | <50m |
| Voltage at point of connection (kV) | 0.4 | 0.4 | 11 | 11 | 11 |
| Step-up transformer | Recommended not to include and utilise BESS inverter output at grid voltage. Contractor may include transformer at its discretion. If transformer is included, rating to allow full required output of BESS under continuous and overload |  | Required. Rating to allow full required output of BESS under continuous and overload conditions. |  |  |
| BESS Inverter (MVA) (mandatory minimum) | 0.4 | 0.5 | 2.2 | 1.8 | 1.3 |
| BESS AC Continuous Power (MW) (mandatory minimum) | 0.3 | 0.4 | 1.9 | 1.6 | 1.1 |
| BESS DC Energy Storage (MWh) | 0.3 | 0.4 | 1.9 | 1.6 | 1.1 |
| BESS BMS | Y |  |  |  |  |
| BESS local HMI panel and e-stops | Y |  |  |  |  |
| Workstation with HMI | Y |  |  |  |  |
| Communications and control panel | Y |  |  |  |  |
| EMS and integration requirements | Y |  |  |  |  |

## Functional Guarantees

Following Completion and commencement of operation, the BESS will be subject to a Commissioning test period that extends over 2 years.

Initially, within 30 days of Completion, the Contractor shall undertake guarantee tests of the Functional Guarantees. Tests are as specified in the Detailed Specifications in Section 1.3. On completion of such tests, and in accordance with the Contract, a Provisional Operational Acceptance Certificate may be issued.

Subsequently, the Contractor shall repeat the guarantee tests 365 days after completion and at 730 days after completion (or within 30 days of those dates). Availability shall be measured on a continuous basis over each 365 day period following completion.

Contractor is responsible for all testing, analysis and reporting.

Functional guarantees are as follows.

| Production measure | Unit | Specified level | Rate of liquidated damages per 1% or part thereof that the measured performance is below the specified level |
| --- | --- | --- | --- |
| 1. BESS Service life* | Years | 10 | 0.8% of contract sum |
| 2. Continuous power at point of BESS connection to grid | MW | Per island – See Section 1.13 | 0.8% of contract sum |
| 3. BESS round trip efficiency (%) | % | 88 | 0.2% of contract sum |
| 4. BESS availability (%) | % | 98 | 1% of contract sum |

*See definition of Service Life in Appendix B. Service Life is the period during which the BESS can meet all performance requirements of this specification. Service life provides a measure of degradation in battery module performance, which will be assessed by comparing performance test results at commissioning and subsequent repeat tests against the Contractor’s design degradation profile.

Testing and evaluation of the production measures is defined in detail in Appendix B – BESS.

Performance shall not be less than 90% of the Specified level on any island. Any identified performance below Specified level will be treated as a defect.

Performance liquidated damages for BESS Service Life, Continuous power at point of BESS connection to the grid, and BESS round trip efficiency are payable as follows:

- For performance below the specified level at the initial test, 10% (equivalent to 1 year of operation) of the liquidated damages amount is payable.

- For performance below the specified level at the first subsequent test, 10% (equivalent to 1 year of operation) of the liquidated damages is payable.

- For performance below the specified level at the first subsequent test, 80% (equivalent to 8 years of operation) of the liquidated damages is payable.

Performance liquidated damages for BESS availability are payable as follows:

- For performance below the specified level averaged over the first 365 days, 10% (equivalent to 1 year of operation) of the liquidated damages is payable.

- For performance below the specified level averaged over the second 365 days, 10% (equivalent to 1 year of operation) of the liquidated damages is payable.

## Project management and delivery requirements

Detailed requirements for project management, including quality and safety management, design processes, testing and commissioning, meetings, and documentation are specified in Appendix A – General and Electrical.

# Implementation Period

BESS under this Contract will be delivered in two lots; where lot 1 and lot 2 of BESS will supplement the PV installations under ASPIRE Phase III and ARISE Phase I, Phase II respectively. In order to reliably feed in the energy from these PV systems the BESS are expected to be commissioned and in a fully functional state by the time the PV systems are interfaced with the grid. The implementation schedule is designed to support this requirement.

Expected key milestone durations are given in the below table.

| Milestone | Months from Effectiveness |  |
| --- | --- | --- |
|  | Lot I | Lot II |
| Design – issued for construction | 02 | 02 |
| Procurement – main equipment orders placed | 03 | 03 |
| Site works commenced | 04 | 05 |
| Site works completed | 06 | 07 |
| BESS FAT completed | 07 | 07 |
| BESS installation commenced | 08 | 09 |
| BESS installation complete | 10 | 11 |
| BESS and EMS commissioned | 11 | 12 |

Contractor’s monthly reporting must clearly show progress against the above milestones. Any progress delays shall include a detailed explanation, schedule impact assessment, and plan to minimize any effect on subsequent milestones.

The Contractor’s workflow is expected to include multiple teams working in parallel across multiple islands at any time. Islands shall be commissioned progressively with the intent of minimizing disruption and optimizing the availability of works.

The sequence of work shall be determined in cooperation with the Employer, with the objective of aligning individual island completion dates with the installation of other infrastructure (Solar PV and Grid-Upgrading). The Employer shall advise the desired sequencing not more than 1 month from effectiveness. Contractor shall comply with this sequencing.

# Site and Other Data

Site data is provided in Appendix E – Site data.

# Contractor’s Representative and Key Personnel

| Item No. | Position/specialization | Relevant academic qualifications | Minimum years of relevant work experience |
| --- | --- | --- | --- |
| 1 | Contractor’s Representative | Certificate or higher in project management | 10 |
| 2. | Construction Manager | Engineering degree or diploma | 10 |
| 3. | Site Manager A | N/A | 10 |
| 4. | Site Manager B | N/A | 10 |
| 5. | Lead electrical | Electrical engineering degree | 10 |
| 6. | Lead control | Electrical or control engineering, or related degree | 5 |
| 7. | Environmental and Social Safeguards Officer | Environmental science or engineering degree | 5 |
| 8. | Health and Safety | N/A | 10 |

# Appendix A – General and Electrical requirements

# Relationship to other parts of the Employer Requirements

This part of the Employer Requirements (Appendix A –BESS requirements), provides key technical requirements for all electrical systems required under this project (including BESS and EMS). It shall be read in conjunction with other parts of the Employer’s Requirements.

In particular, note:

- Employer Requirements:

  - This document provides the necessary overview information on the project scope and general requirements. It also includes summary information on the island specific capacities and requirements.

- Appendix B –Battery Energy Storage System (BESS):

  - This document provides key technical and functional requirements of the Battery Energy Storage System (BESS).

- Appendix C –Energy Management System:

  - This document provides key technical and functional requirements of the Energy Management System (EMS) that must be provided independent of the BESS to provide island wide generation dispatch management.

- Appendix D –Operations and Maintenance requirements:

  - This document provides details of the support that Contractor’s are required to provide for the electrical standards and equipment requirements that the Plant must meet.

- Appendix E –Project Site Specific Details:

  - This document provides details of the requirements at each site. It includes site descriptions and data, capacity requirements, details on existing equipment and infrastructure, details of the point(s) of connection, and other related information for each island.

- Appendix F – Environmental and Social Requirements:

  - This appendix provides the environmental social safeguards requirements and reference is made to relevant safeguards documents of the project

# Definitions

Unless explicitly stated in this document, or the Employer Requirements, definitions are as per the Standards.

# Standards

All equipment shall be installed and all work shall be carried out in accordance with statutory requirements of the relevant jurisdiction (including amendments). The primary regulatory requirement for electrical installations in the Maldives is the Electrical Installation Standards of the Utilities Regulatory Authority (URA).

The Maldives typically adopts the use of International Electrotechnical Commission (IEC) standards, and International Standards Organisation (ISO) standards. Where there is no requirement under the Electrical Installation Standards, all equipment and works supplied under these specifications shall conform to the latest editions of the IEC or ISO standards, or where no IEC or ISO standards, to British Standard (BS), or equivalent national standards as may be approved by the Employer. Such standards include, but are not limited to:

- IEC 60529: Degree of protection

- IEC 62052-11, IEC 62053-21, IEC 62052-22, IEC 62053-23 Electricity metering equipment (AC)

- IEC 62271-1: Common specifications for alternating current switchgear and control gear

- IEC 62271-102: HV AC Disconnectors & Earthing Switches

- IEC 62271-103: Switch disconnectors

- IEC 62271-105: Switch-disconnector/fuse combination

- IEC 62271-106: Vacuum contactors

- IEC 62271-200:  metal Enclosed Switchgear & Control Gear

- IEEE 80: Guide for Safety in AC Substation Grounding

- IEEE 81:  IEEE guide for measuring earth resistivity, ground impedance and earth surface potentials of a grounding system

- IEC/TR 60479-5: Effects of current on human beings and livestock – Part 5 touch voltage threshold values for physiological effects

- IEC/BS EN 62305 – Protection against lightning – all parts as applicable

- EN50160 on voltage characteristics of electricity supplied by public distribution systems

- IEEE519 IEEE Recommended Practice and Requirements for Harmonic Control in Electric Power Systems

- IEC 60071: Insulation coordination

- IEC 61000: Electromagnetic compatibility (EMC) all parts as applicable

- IEC 61869: Instrument transformers – all parts as applicable

- IEC 61936-1: Power installations exceeding 1 kV a.c. - Part 1: Common rules

- ENA TS 41-26:  UK Energy Network Association Technical Specification for Distribution Switchgear*

In case the equipment or materials offered from a country where the relevant standards to which the equipment or materials offer better performance or safeguards for the Employer than IEC or BS Specifications, these are acceptable. The Contractor must substantiate any such claims by submitting an independent assessment, by an appropriately qualified person, that identifies differences in the standards and demonstrates the benefit for the Employer.

All listed standards must be complied with unless exception is granted, or noted in these Employer Requirements. If a requirement included in the Employer Requirements exceeds a standard listed, then the requirement within the Employer Requirements shall be adhered to.

Standard(s) referred to shall mean the current Edition / Revision together with Amendments issued.

All installations and materials and cabling shall be in accordance with the IEC 60364 Electrical Installations for Buildings. All works shall conform to the requirements of the URA.

# Language and units

## Language

The English language shall be used on all drawings and in all documents and wherever anything is required by the Contract, to be written, marked, printed or engraved.

Where noted (typically for operational procedures), documents shall also be produced in, or include, Maldives language.

## Units of Measurement

Systeme International d’Unites (SI) units shall be used.

# Site requirements

Specific limitations and requirements for work practices are included in the Environmental and Social Code of Practice (20220112-pub-escp-battery-energy-storage-system-installation-arise-project.pdf (environment.gov.mv)). This section sets out general expectations for site works.

## Work Practices

The Contractor will submit a set of work practices applicable to this project along with the general Health and Safety plan before site mobilization. The procedures will be subject to acceptance by the Employer. The procedures shall meet the following requirements.

### Site Hours and Roster

The Contractor may work a rotation for all site-based personnel. No more than 14 days shall be worked straight by any site personnel without days off work. The Contractor will not work more than 12 hours per shift onsite, subject to working hours and exceptions as listed in the Contract.

### Site Facilities and Temporary Services

As per division of responsibilities matrix. Contractor to note that any facilities noted in the division of responsibilities matrix are limited to that currently available at the power station area. If the Contractor requires additional facilities, then it shall make allowance for such.

### Mobilisation & Demobilisation

Mobilisation and demobilisation shall include but not be limited to the following:

•	Supply, installation and maintenance of Contractor’s Site office and facilities;

•	Mobilisation of all facilities, construction plant and personnel necessary for the Works; and

•	Demobilisation of all facilities, Plant and Equipment and Contractor’s Personnel from Site, and the rehabilitation of all Temporary Work Sites to the approval of the Employer.

The Contractor shall be responsible for the mobilisation of facilities, plant and equipment, and personnel.

### Test energy

Test energy for initial pre-commissioning tests once equipment is connected to the grid will be provided free of charge by the Employer. Subsequent or repeat tests may be subject to electricity consumption charges at standard published tariffs.

### Site Access and Vehicle Parking

The Contractor shall utilise only existing site access and vehicle parking areas, unless by prior approval by the Employer. The Contractor shall liaise with the Employer to ensure that access to the site and the daily business operations of the Employer, community members, and other contractors are not adversely affected.

Bidders should note that access to the site and parking facilities are very limited, and arrangement of alternative vehicle parking may be necessary.

### Laydown and Security

The Contractor is permitted to use the specified sites for laydown or equipment storage as may be required. Use of any other areas for laydown, storage, parking, or other such activities is generally not permitted, except by express consent of the Employer.

In general equipment storage and additional facilities for contractor's workers are at designated temporary sites within the island and equipment storage at the installation site is restricted to the equipments and tools needed for immediate works.

The Contractor shall be responsible for the security within the Site of Works.  The Contractor shall be responsible for inspection of any existing security fencing at the site and determining its fitness for purpose. The Contractor shall be responsible for any additional measures, or upgrades and maintenance to the security fencing for the duration of the Contract.

### Site Clean Up

The Contractor shall make every effort to keep the Site of Works in a clean and tidy condition for the duration of the Works.  The Contractor shall, from time to time, and on completion of any area of the works or where directed by the Employer, remove rubbish, surplus materials or any other construction debris from such areas as may be attributable to the Work under the Contract and generally leave them in a satisfactory condition and to the approval of the Employer.

Upon completion of the Works, the Contractor shall remove all rubbish, debris, temporary earthworks or surplus materials from the site of the Works.  The site shall be left in a neat and tidy condition to the satisfaction of the Employer.

### Site Control Measures

The Contractor shall provide for appropriate measures to manage and/or control traffic, water, dust and weed in and around the Site of Works.  Such measures shall be implemented during the entire duration of the Contract, and as specified in these Specifications, shown on the Drawings and/or as deemed necessary by the Contractor for performance of the Contract to the Employer’s satisfaction.

In the event of the Contractor failing to comply with its responsibilities under this Clause, the Employer may, without further notice, take such steps as it considers necessary, to provide for the safe passage and safety of traffic or to remove any obstruction or to repair damage, including, if it considers it necessary, the employment of workmen and watchmen to complete work and the cost thereof may be deducted from any monies due to the Contractor under the Contact.

### Traffic and Exclusion Zones

The Contractor shall provide for continuous operation of normal traffic along all roads, pedestrian and vehicular access ways in and around the Site of Works or that are otherwise affected by the Works. The Contractor shall, where necessary, provide side tracks which shall be constructed, sign posted, and maintained to the satisfaction of the road owner and the Employer.

The Contractor shall erect and maintain exclusion zones beneath and adjacent to all work at heights and shall be responsible for the safety of all pedestrian and vehicular traffic within the Site of Works and any adjacent areas affected by them.  The Contractor shall provide for all necessary watchmen, lights, barriers, notices and signs, and shall provide and maintain the same to the satisfaction of the road owner and the Employer.

The Contractor shall not cause obstruction to any road, drain and/or watercourse and shall not break down or remove any gates or fences without prior approval of the Employer.  Where such obstructions or breakages cannot be avoided, the Contractor shall remove such obstruction or repair such breakages, to the satisfaction of the Employer, as soon as possible.

### Site Meetings

The Contractor shall provide for its relevant staff to attend required meetings with the Employer at the project site or the Employer’s offices for the duration of the Contract. Consideration will be given to remote meetings (teleconference / videoconference) for instances where it can be shown that these will not affect the satisfactory outcomes of the meeting.

## Miscellaneous requirements

### Contactor’s Personnel Qualifications

Contractor shall provide the names of the nominated Site Supervisor for each site, and other site personnel. The Contractor shall also provide evidence of qualifications, including:

- Contractor’s general safety induction and site-specific induction

- Formal first aid training, including CPR - must be at least two qualified First Aid personnel on each site

- Qualification or endorsed training as applicable to work being undertaken, including but not limited to:

  - All LV electrical works by qualified electrician

  - All works on proprietary components to be conducted by personnel meeting OEM requirements

  - All MV electrical works by personnel with demonstrated experience in installation, termination and jointing of high voltage systems

  - Earthing works by personnel with demonstrated experience in installation of earthing systems

  - Communications installations, including fibre terminations, by trained and experienced technician

Contractor’s should refer to URA requirements for work to be completed by or supervised by URA licensed electrical workers.

### Workmanship and Materials

Workmanship shall be of first-class commercial quality and in accordance with the best shop practice. Like parts shall be interchangeable. Machining of fits on renewable parts shall be accurate and shall be to specified dimensions, so that replacement parts may be readily installed.

Unless otherwise specified, materials and components used for the Works specified shall be new and unused. Materials and components shall conform to the standards current at the time of execution of the Agreement.

### Packing and Shipping

#### Packing

All items of Plant supplied by the Contractor shall be adequately packed and protected for shipment and outdoor storage at Site.

The Contractor shall ensure that the Plant shall be protected against corrosion, weather damage, condensation, distortion, and damage by vermin and the ingress of foreign matter.

Packing of any Plant shall comply with the approved shipping preparation and packing procedures and shall include but not be limited to the following:

- Plant shall be properly packed.

- Plant shall be shipped in weather proof and watertight containers unless otherwise agreed with the Employer.

- Containers, crates or packages shall be checked for defects internally and externally prior to packing.

- Weights and lifting points shall be clearly visible on each package.

- Plant shall be not wrapped in plastic unless it is coupled with adequate moisture absorbent material, such as silica gel and the like.

- Bright metal parts shall be greased coated or similar rust inhibitor applied commensurate with the type of machinery.

- Machined surfaces shall be protected with wood blocks or similar approved means and reinforced externally with metal bands or plates.

- Exposed threaded joints shall be encased or plugged as required.

For imported components, packing material shall comply with import and export regulations. All wood packing in each consignment shall be free from bark and all visible signs of insect and fungal attack at the time of shipment. Furthermore, the importation of packing materials such as second- hand sacking, hays, straw, chaff, rice husks and peat shall be prohibited. The Contractor shall be responsible for obtaining approval of the packing timber and materials before delivery. Packing lists shall state the type of packing used and certify that none of the prohibited material has been included.

The Employer may require to inspect and approve the packing before the items are dispatched but the Contractor shall be entirely responsible for ensuring the packing is suitable for transit and such inspection shall not exonerate the Contractor from any loss or damage to faulty packing.

Waste packing material, and in particular non-biodegradable waste material such as plastic packaging, shall be minimised.

#### Unloading and Storage at Site

The Contractor shall at Site place the equipment in the Contractor’s storage area in the following manner:

- Place any containers or any packages in locations as directed by the Employer.

- Certify that the contents of any container or any package agree with the said packing lists.

- Remove from Site any unwanted packing debris and any empty containers immediately after completion of unloading at Site.

### Existing Works and Underground Services

The Contractor shall note that the drawings of existing services are incomplete and not accurate. The Contractor shall ascertain the location of any buried services in the vicinity of the Works before commencing construction. If services are identified, then the Contractor shall give notice of this to the Employer at least three (3) working days prior to the commencement of any construction activity that may affect those services(s).

The Contractor shall take all reasonable actions and provide all things reasonably necessary to protect and maintain existing services to the satisfaction of the Employer.  In the case of damage occurring to existing services, the Contractor shall immediately report the damage to the Employer.  The cost of the necessary repairs or renewals shall be borne entirely by the Contractor.

If it is found to be necessary to alter the location or level of any existing services to conform with the Works, the Contractor shall relocate, redirect or alter any existing services as required to execute the Works and to the satisfaction of the Employer.  This will include altering finished surface levels of existing services.

If uncharted services are encountered during excavation, the Employer shall be notified before proceeding.

Any connections to live equipment will only be permitted with the consent and under the supervision of the Employer. The Contractor shall notify the Employer prior to carrying out any such work, detailing the method to be employed.

Any connection requiring statutory or other approvals shall be the Contractor’s responsibility.

#### Services Shutdown

Where it is a requirement to temporarily shutdown or disconnect services (such as electricity or water) for the completion of the works the Contractor shall notify the Employer at least three (3) days prior.

Generally the Contractor will be required to undertake shutdowns outside of normal business hours unless by prior approval by the Employer.

The Contractor will have been deemed to have included all costs associated with any shutdowns in the agreed Contract Sum.

#### MV Switching and Isolations

The Employer will provide/organise for all MV switching and isolations for equipment connections. The Contractor shall provide a minimum of five (5) working days’ notice for MV equipment isolation requirements.

### Structural Integrity

The Contractor shall be responsible for ensuring the structural integrity of any temporary works, and of any existing works where impinged upon by new works.

### Hazardous Areas

No sections of the installation are within hazardous areas or require hazardous equipment ratings.

### Site Clearance and Demolition

The Contractor shall be responsible for obtaining all site permits or approvals and equipment isolations before commencing clearance of the Works. All equipment isolations will be completed by Employer’s Power Station staff in conjunction with the Contractor.

The Contractor shall carry out all demolition necessary to complete the Works and shall be responsible for the removal and disposal as directed by the Employer of all demolished and decommissioned equipment.

### Building Permits

The Contractor must obtain the building permits and local council authorisation for the new civil structures designed by the Contractor. Contractor must provide all required design inputs and documentation to facilitate submission.

### Site Induction Requirements

The Contractor shall be required to comply with all of the site requirements including compliance to all isolation, induction, site safety, first aid, and emergency procedures. The Contractor shall ensure that all site personnel have all of the requisite certification for site.

### Project information board

During construction, Contractor is required to install a temporary project information board, setting out (at a minimum):

- Title and brief description of the works being undertaken

- Expected duration of site works

- Work hours

- Where to access Grievance Redress Mechanism and other project information

- Any notices of interruptions that may affect local community, such as road closures

- Contact person and phone number(s).

Contractors are to supply and install a permanent project information board at a prominent location (to be agreed with the Employer) at the project site. This shall be of a material and construction suitable to last at least 10 years in site conditions. The information board shall be approximately 2 m wide by 1 m high. Graphics to be prepared by the Contractor and approved by the Employer (must be supplied in a readily exchangeable electronic format). Graphics should depict the installation, show project title, headline system parameters, and key project stakeholder information.

### Community relations

Contractor will take advice from the Employer, obtaining a full brief of current situations and establish a plan that will complement the local culture and leave zero legacy.

Contractor will be obligated to:

•	abide by the local laws and regulations;

•	recognise and respect the culture, values and traditions of those communities; and

•	behave in a socially responsible manner during both working and after hours.

In all respects, the Contractor must comply with the Environmental and Social Code of Practice (20220112-pub-escp-battery-energy-storage-system-installation-arise-project.pdf (environment.gov.mv)).

# Reporting, documentation, and meetings

Documentation required for submission under the implementation stage of the project, including all engineering and test documentation, management plans and studies, progressive reporting and other documentation, is described in this section.

## Management plans

### Project execution plan (PEP)

The Contractor shall prepare a Project Execution Plan for the project and will comply with the requirements of the Project Execution Plan upon approval by the Employer.

The PEP shall define in detail the implementation methodology and strategy for delivering the design, procurement, construction and commissioning, successfully in accordance with the requirements of the Employer and the agreed Project objectives.

The PEP shall provide a roadmap for the effective execution of the project and shall be disseminated to all project team members.  The PEP shall outline the objectives, processes and strategies that will be employed by the Contractor to manage and execute the works and establish the framework to ensure the project expectations and key performance indicators are met.

The PEP shall include a work organisational chart and contact details of Contractor representative and site supervisors. A communications matrix shall also be included.

The PEP shall be the primary document of the suite of documents listed below which apply specifically to the project and which outline the Contractor’s management principles for the project.

- Project Execution Plan

- Construction Safety Management Plan

- Construction Environmental Management Plan

- Human Resources and Industrial Relations Management Plan

- Quality Management Plan

- Project Controls Plan

- Risk Management Plan

#### Project Schedule

The Contractor must provide a baseline project schedule for approval of the Employer, and consistent with the required project schedule.

The schedule must be fully resourced, logic linked and follow best industry practice.

The Contractor must provide progress updates to the approved schedule weekly and monthly.

### Construction safety management plan

Contractor shall perform activities associated with managing, monitoring and controlling health and safety for the services and construction in accordance with its Safety Management Plan.

Contractor’s Safety Management Plan will provide the fundamental basis upon which direction, management and communication by all stakeholders and personnel on the Project are focused to ensure that the Project provides for the following:

- a safe and healthy working environment;

- safe systems of work;

- safe plant, equipment and work practices;

- continuous promotion of HSE initiatives as an integral component of timely project completion; and

- HSE awareness programmes.

A copy of the Safety Management Plan will be provided to the Employer within 2 weeks of the execution of contract, or otherwise as agreed between the parties.

### Construction environmental management plan (CEMP)

The Contractor shall prepare a CEMP in accordance with the Environmental and Social Requirements, relevant legislation, permit conditions, and generally in accordance with best practice. The CEMP shall include at least:

- Regulatory and other requirements

- Division of responsibilities

- Management personnel and contacts

- Complaint or disputes process

- Subplans for management of each category of environmental impact.

### Human Resources and Industrial Relations Management Plan

The Contractor shall prepare a Human Resources and Industrial Relations Management Plan in accordance with best practice for work in a remote mine location, and taking into consideration specific requirements of the Contract and this Technical Specification.

### Risk Management Plan

The Contractor shall prepare a Risk Management Plan, with cross project coverage and coordinating systems and actions under procurement, design, construction, safety, environment, social, operations.

### Regular reporting

Monthly Report

The Contractor shall establish an agreed template in conjunction with the Employer for Monthly Reporting which shall include the following:

- Contract program status (planned activities, actual activities achieved), including a 4 week lookahead;

- Milestone Status (planned v actual);

- Quantity / Labour Hour Report;

- Workforce summary;

- Plant and Equipment Summary;

- Early Warning Register;

- HSE Statistics

- Contract program issued including status (planned activities, actual activities achieved) in Primavera P6 format;

- Risk Register;

- Issues List;

- Document Register;

- Change/Variation Register;

- EOT Register;

- TQ/RFI Register;

- Other items as reasonably requested by the Employer.

Key personnel from both the Employer and the Contractor shall meet once a week to discuss all elements of project execution. The location of these meetings may be onsite or remote.

### Quality management plan (QMP)

The Quality Management Plan (QMP) shall define how the Contractor assures itself that its procurement, manufacturing, supply, construction, and installation complies with the requirements of the Contract and addresses all activities relevant to the Works and shall demonstrate how all Work under the Contract performed by the Contractor will conform to the requirements of the Contract.

The QMP shall be adequate to cover all construction operations, including both onsite and offsite manufacturing, fabrication, assembly and installation works, and shall include the controls to be implemented by the Contractor and its Subcontractors, both directly and indirectly by identifying the Quality System documentation that the Subcontractors are required to produce to meet the Contract requirements.

The QMP shall define the documented quality system to be implemented by the Contractor throughout the Works, in accordance with the requirements of ISO 9001, and shall refer to all of the Contractor's relevant procedures and manuals.

The QMP shall address the interfaces between the Employer and the Contractor and other relevant entities. The QMP shall include an organisation chart showing the Contractor's corporate and project organization responsible for managing, performing and verifying the Works. The organisation chart shall be supported with a reporting and functional description of the Contractor's project organisation and identification of the quality related responsibilities of key positions.

The quality management function within the Contractor’s project organization shall be completely independent from the construction and engineering operations to guarantee the independence of the decisions.

The QMP shall be developed in accordance with the Employer’s requirements and in accordance with ISO 9001.

The QMP will clearly identify all Inspection and testing requirements related to completion of the Work under the Contract.

The Contractor shall conduct inspection and testing as per the agreed QMP. The Contractor will ensure the Employer is invited to attend, prior to commencing any tests for which the Employer has an agreed Witness or Hold Point.

The Contractor bears the full risk and liability of proceeding, inclusive of any rework and/or re-performance of the work instructed by the Employer due to the Contractor’s non-compliance with this provision.

Waiver of Employer attendance at inspections and testing can only be given in writing by the Employer.

The Contractor shall notify the Employer of items requiring inspection and testing. In the event of the Employer’s nonattendance, the Contractor shall ensure a comprehensive inspection report is available for review by the Employer.

Further details of quality control, to be covered under the QMP, are included in Section Error! Reference source not found..

#### Quality Management System

The Contractor will maintain a Quality Management System accredited to ISO 9001 requirements and shall be capable of demonstrating that all the requirements of the Contract and all applicable Laws and applicable codes and standards are being met. Third party certification of assessed capability (i.e. approval to ISO 9001) is not considered a demonstration that the specified Quality Management System (QMS) requirements of the Contract have been met.

## Document management system

The Contractor is to provide and use a web-based document management system for project document and drawing submissions, and tracking of all information requests and responses, as well as the Employer’s review responses. The selected system must be fit for purpose and is subject to approval of the Employer. A single system is to be implemented project-wide.

The Contractor is to ensure the Employer has free access to the system.

The system shall maintain a document register which lists all documents and drawings submitted by the Contractor along with:

- title, document number and revision;

- planned issue date for Employer’s review;

- actual issue date for Employer’s review;

- review status; and

- actual date of approval.

All drawings are to be submitted in PDF and native format. Naming of all documents and drawings must be sufficient to facilitate sorting by Section, discipline, and other logical categorisation.

Submissions shall be planned and executed in a coordinated and consolidated manner, meeting the following minimum requirements:

- A planned document and drawing register for design; inspection and test; and manufacturer data shall be provided at commencement of design and updated at least monthly.

- Design submissions at the design submission milestones must include all documents and drawings required for all document categories at the corresponding submission schedule milestone (30% / 80% / IFC), packaged together.

- Inspection and test plans shall be consolidated according to upcoming works

- Inspection and test certificates shall be consolidated by island, section of works, progress milestone or similar logical category.

- Manufacturer data records (MDRs), certificates, and factory acceptance test reports shall be consolidated by island, lot, shipment, type, or similar logical category.

- Minor or occasional individual or small sets of documents and drawings may be submitted separate to the above requirements subject to Employer agreement.

The Contractor is to provide the Employer with access to the project and document management system until completion of the Defects Liability Period.

On completion of Works, the Contractor is to export from the project management system and provide to the Employer a full copy of all correspondence, documents and drawings including as-built drawings for all elements of the Project in native format and in PDF format. The export shall include a logical document and folder structure, and reference key / table of contents to enable easy location of all elements.

## Documentation deliverables

Where noted, documentation to be provided on a per-island basis. Other documents shall include island specific sections where applicable.

Where noted, documents are to be provided in Maldives language as well as English.

|  | Deliverable | Typical revisions (IFU=issued for use; IFC=issued for construction) | Per island | Maldives language version |
| --- | --- | --- | --- | --- |
|  | Preliminary (within 3 months of commencement) |  |  |  |
| 1 | HSE safety management plan (SMP), work method statements, job hazard analysis, safety in design review and emergency evacuation plan. | Draft/IFU |  |  |
| 2 | Drawing and design management plan including document naming and revisions / mark-up systems | Draft/IFU |  |  |
| 3 | Project management plan (PMP) | Draft/IFU |  |  |
| 4 | Quality Management Plan (QMP) and draft quality assurance manual (QAM) | Draft/IFU |  |  |
| 5 | Document register | Draft/IFU, update when documents issued |  |  |
| 6 | Notification prior to procurement of long lead time items | Draft/IFU |  |  |
| 7 | Summary / overview of inspection test plan (ITP), inspection test checklists (ITC) and factory acceptance tests (FAT), including matrix of tests | Draft/IFU |  |  |
| 8 | Hazardous material management plan, Emergency response plan, Decommission & disposal plan |  |  |  |
|  | Design |  |  |  |
| 1 | Design drawing package to include, at a minimum: |  |  |  |
| a | Basis of design report, including as attachments, detailed functional specifications for the BESS and EMS | 30%/80%/IFC |  |  |
| b | Site layout | 30%/80%/IFC |  |  |
| c | Sub-surface works layout | 80%/IFC |  |  |
| d | Grading plan for any earthworks | 30%/80%/IFC |  |  |
| e | Site drainage plan, erosion and sediment control plan | 80%/IFC |  |  |
| f | Detailed design and architectural drawings for powerhouse | 30%/80%/IFC |  |  |
| g | Fencing drawings | 80%/IFC |  |  |
| h | Detailed layout drawings of switchboards and panels and building / switchroom electrical fit-out | 80%/IFC |  |  |
| i | AC and DC electrical single line diagrams | 30%/80%/IFC |  |  |
| j | Electrical schematics of all systems | 80%/IFC |  |  |
| k | PV array structural details, including footing and framing designs | 30%/80%/IFC |  |  |
| l | BESS and switchroom footing / mounting designs | 30%/80%/IFC |  |  |
| m | Protection details | 80%/IFC |  |  |
| n | Earthing drawings | 30%/80%/IFC |  |  |
| o | Trench and cable tray section drawings | 30%/80%/IFC |  |  |
| p | Combiner box layout | 80%/IFC |  |  |
| q | Details of auxiliary power distribution | 30%/80%/IFC |  |  |
| r | Communications network drawing | 30%/80%/IFC |  |  |
| s | Electrical, mechanical and civil Specifications documents, including detailed installation and materials compliance requirements | 80%/IFC |  |  |
| t | Protection single line diagram | 30%/80%/IFC |  |  |
| 2 | Equipment schedules for the following, at a minimum | 80%/IFC |  |  |
| a | battery modules, inverters, racking, junction / combiner boxes | 80%/IFC |  |  |
| b | Cable schedule, including terminations | 80%/IFC |  |  |
| c | Protection equipment and ratings schedule | 80%/IFC |  |  |
| 3 | Studies: |  |  |  |
| a | Power systems studies, including fault scenarios | 80% |  |  |
| b | Protection study | 80% |  |  |
| c | Earthing study | 30%/80% |  |  |
| d | Civil and structural engineering reports | 80% |  |  |
| e | Cable sizing calculations | 30%/80%/IFC |  |  |
| f | Arc flash study | 80% |  |  |
| g | Short circuit study | 80% |  |  |
| h | lightning study | 80% |  |  |
|  | Factory |  |  |  |
| 1 | Factory acceptance test report for major equipment |  |  |  |
| 2 | Certificates, standards compatibility statements |  |  |  |
|  | Prior to site works |  |  |  |
| 1 | ITP and ITC containing, as a minimum, the following information for each significant activity identified in the relevant process: | Draft / IFU |  |  |
| a | Description of activity |  |  |  |
| b | Specification requirements/reference |  |  |  |
| c | Person responsible for activity (title) |  |  |  |
| d | Hold Points and Witness Points |  |  |  |
| e | Activity checklists |  |  |  |
| f | Inspection and test type |  |  |  |
| g | Tolerances or other acceptance criteria |  |  |  |
| h | Identification of relevant procedure and quality records |  |  |  |
| i | Test/inspection frequency |  |  |  |
| j | Work item or work lot identification |  |  |  |
| k | The Employer may request the Contractor to include additional Hold Points or Witness Points and the Contractor must make provision for the Contractor and the Employer to sign off at such points. |  |  |  |
| 2 | Transport and logistics management plan | Draft / IFU |  |  |
| 3 | General safety training plan | Draft / IFU |  |  |
| 4 | Health awareness program plan | Draft / IFU |  |  |
| 5 | Installation method, including construction schedule, site utilisation (laydown areas etc.), logistics, staff facilities (toilets, site office), waste management etc. | Draft / IFU |  |  |
| 6 | Construction environmental management plan (CEMP) | Draft / IFU |  |  |
| 7 | Safety data sheets (SDS) for all substances used on site | Draft / IFU |  |  |
| 8 | Training and capacity building plan | Draft / IFU |  |  |
| 9 | Commissioning management plan | Draft / IFU |  |  |
|  | During site works |  |  |  |
| 1 | Monthly progress report, including safeguards monitoring | Final |  |  |
| 2 | Register of entries and exits on site and pre-start meetings | Final | YES |  |
| 3 | Safety incident reporting | Final |  |  |
| 4 | Environmental incident reporting | Final |  |  |
| 5 | Completed ITCs and quality documentation | Final | YES |  |
|  | Prior to Completion |  |  |  |
| 1 | ‘As Installed’ control system programs, configuration settings, and protection relay settings | Final | YES |  |
| 2 | Technical data sheets of all major components | Final |  |  |
| 3 | Manufacturer’s software packages needed for future operation/maintenance. | Final |  |  |
| 4 | Asset register hierarchy | Draft | YES |  |
| 5 | List of maintenance tools supplied | Final | YES |  |
| 6 | List of other tools Employer should hold | Final | YES |  |
| 7 | List of spare parts and consumables supplied | Final | YES |  |
| 8 | Signage for standard operational procedures | Draft / IFU | YES | YES |
| 9 | Six hard copies and one soft copy (in a freely printable format) of Operations and Maintenance Manuals of the facilities including all OEM documentation and any required log books | Draft / IFU | YES |  |
| 10 | Ten year maintenance schedule | Draft / IFU | YES | YES |
| 11 | Preventative maintenance requirements | Draft / IFU | YES |  |
| 12 | Asset management plan | Draft / IFU | NO |  |
| 13 | Detailed pre-commissioning and test report | Draft / Final | YES |  |
| 14 | Red line drawings suitable for operation (at handover/completion) | IFU |  |  |
| 15 | Electrical safety certificate | Preliminary / Final |  |  |
|  | Within four (4) months of Completion |  |  |  |
| 1 | Commissioning / Functional guarantee test report | Draft / Final | YES |  |
| 2 | ‘As Installed or As-built’ drawings & data sheets (electrical, layout, structural, communications and civil). | Final | YES |  |
| 3 | Completed asset register | Final | YES |  |
| 4 | Warranty novation agreements | Draft |  |  |
| 5 | Completed ITCs and quality documentation (consolidated package) | Final |  |  |

## Equipment naming convention and hierarchy

Employer may provide naming convention and hierarchy to apply for drawings and physical tagging of all equipment. If not provided by Employer, Contractor must provide an internally consistent / logical, unique, and easy-to-follow naming convention and apply.

## Asset register

Contractor must provide an asset register that lists all equipment installed, its name, number / tag / designation, reference technical specification, manufacturer, barcode, installed location (GPS referenced). Cable routes shall be surveyed and GPS route included in the register.

## Meetings

The Contractor must allow for the following meetings, at a minimum:

| Meeting description | Location |
| --- | --- |
| Kick-off meeting | May be video conference or on site |
| HAZOPS | May be video conference or on site |
| Safety in design review at 30% design stage | Video conference |
| 30% design review meeting | Video conference |
| Weekly or fortnightly (as needed) engineering meetings to clarify information or issues arising in the design process | Video conference |
| 80% design review meeting | Video conference |
| Daily / weekly prestart meetings | On site |
| Fortnightly quality meetings during construction to discuss and resolve site issues | Video conference, including site representative |
| Initial training sessions with local staff (minimum 3 days per island) | On site |

# Training and capacity building

## Emergency response

Prior to arrival of BESS on site, the Contractor must provide comprehensive training to power station and emergency services personnel on emergency response procedures for BESS incidents. Training must be developed on the basis of the Contractor’s HAZOPs assessment and BESS fire risk assessment, and in accordance with the ESCP. Refresher training for emergency response shall be held a) at commissioning and b) prior to hand-over of the operations and maintenance to the Employer.

## BESS operations

The Contractor must provide comprehensive training and capacity building sufficient to enable the Employer’s staff to take over the operations and maintenance tasks for the Plant, following the initial operations and maintenance period that is the responsibility of the Contractor. To this end, the Contractor must supply:

- A training and capacity building plan, including:

  - Plan for initial training sessions with local staff

  - Plan for ongoing local staff engagement and capacity building, with transition of responsibilities over O&M period

  - Matrix of skills and qualifications required, and mapping to existing local staffing with gap analysis

  - Identification of areas that require specialist OEM training (for instance, to avoid voiding warranty), and options for local staff to receive such training

  - Plan for assessment of local staff capability to carry out all O&M tasks prior to end of O&M period.

- Comprehensive operations and maintenance manuals

- Equipment data sheets

- 10-year schedule of maintenance

Further details are included in the Operations and Maintenance section of this specification.

# Environmental and Social Risk

Environmental and Social requirements are provided in Appendix F.

# Equipment requirements

All equipment must be selected to ensure it is suitable for site conditions, reliable, compatible with subsystems and equivalent products, readily serviced, and that spare parts are readily available. To this end, all components must be selected from suppliers continuously servicing utilities in major international markets including Europe and the USA for a minimum of 10 years. Specific products or their product chains must have been offered for at least 5 years, and manufacturers must offer a commitment to support the product for a minimum of 10 years.

## Design life

All equipment shall have a minimum design life of 15 years.

## PLCs, Control systems, cabinets and junction boxes

### General

If PLCs, Control systems are installed as part of the Contractor design, then the Contractor shall implement the following design requirements.

### PLCs / Control Systems

PLCs and Control Systems shall be provided where necessary to monitor, control, display, alarm, and record operation of the installation. The PLCs and Control Systems shall fully integrate with the Employers systems and incorporate comprehensive system diagnostics to assist in maintenance and trouble-shooting.

PLCs and Control Systems shall include processor modules, power supplies, input/output cards, communication cards or any other specialty cards to provide a fully functioning system. The Processor and I/O bus shall have minimum of 25% spare capacity at the end of the commissioning for future works at the PV site.

PLCs and Control systems are to be installed in cabinets or enclosures as detailed in this section.

### Cabinet General Requirements

There are two types of cabinets to be used in the Contactor designs;

- PLC / Control Cabinets Indoor Installation - standard cabinet designs

- PLC / Control Cabinets Outdoor Installation - Purpose built stainless steel cabinets

These PLC cabinets shall contain PLC components, and their standard I/O connections, as well as the fibre, small wiring, AC and DC distribution systems and all of the PLC / control system components.

The PLC / Control Cabinets scope shall include the following:

- Supply of the PLC cabinets for the installation in accordance with the following specific and common drawings, completely wired with all terminals, and ancillary equipment

- Supply and installation of all PLC components, backplanes, connectors, terminators, power supplies and the like

- Supply and installation of the associated 24Vdc charger, battery, and DC distribution systems

- Supply and installation of the associated fibre terminations and connection systems, fibre patch lead, and fibre to copper converters, copper patch leads, network switches and the like

- Provision of any workshop drawings where the designs are altered from the arrangements provided herein

- Inspection and testing plans and testing documentation

- Assembly at the manufacturer’s works and first livening

- Allowance for a hardware Factory Acceptance Test (FAT) at the manufacturer’s works by the Employer and their representatives

- Delivery to site following acceptance by the Employer of the manufactured panels

### Indoor PLC Cabinets

Summary of key component specifications below;

- Dimensions – As required by Contractor Design

- Colour – Light grey

- Cabinet Rating - IP55

- All equipment mounted on a removable painted gear plate

- Full width two piece undrilled aluminium gland plate

- Plinth for floor mounted cubicles

- Strengthened backplate or superstructure for wall mounted units

- Three point securing location lockable doors with lockable operating handles

- Earth bar and copper earth straps to all doors

- External panel label (traffolyte or similar)

- All internal wiring tinned copper

- All instrument earth bars, phase, neutral and earth bars to be tinned copper

- No nickel fittings, nor exposed copper

- Internal wiring secured in slotted cable PVC trunking

- Plinths;

  - PLC Cabinets – 100mm x 50mm steel channel (minimum)

  - Gland Plates – Aluminium

- PLC Cabinets to be complete with;

  - Internal lights (one per cubicle) operated from door switches

  - RCD GPO

  - Thermostat and Heater

- Equipment Labels;

  - All internal equipment to be labelled (PLC, PLC cards, communications equipment, IO termination blocks, monitoring equipment, power supplies etc.) – engraved traffolyte

  - Exterior labels – engraved stainless steel

### Outdoor PLC Cabinets

The PLC cabinets are to be purpose built stainless steel cabinets. Summary of key component specifications below;

- Cabinets – Purpose built, stainless steel

- Dimensions – As required by Contractor Design

- Cabinet Rating – IP56

- Include servicable desiccant pack or equivalent to protect components for excess humidity  and moisture.

- All equipment mounted on a removable painted gear plate

- Full width two piece undrilled aluminium gland plate

- Plinth for floor mounted cubicles

- Strengthened backplate or superstructure for wall mounted units

- Three point securing location lockable doors with lockable operating handles

- Earth bar and copper earth straps to all doors

- External panel label (traffolyte or similar)

- All internal wiring tinned copper

- All instrument earth bars, phase, neutral and earth bars to be tinned copper

- No nickel fittings, nor exposed copper

- Internal wiring secured in slotted cable PVC trunking

- Plinths – Integral to cabinet

- Gland Plates – Aluminium

- PLC Cabinets to be complete with;

  - Internal lights (one per cubicle) operated from door switches

  - RCD GPO

  - Thermostat and Heater

- Equipment Labels;

  - All internal equipment to be labelled (PLC, PLC cards, communications equipment, IO termination blocks, monitoring equipment, power supplies etc.) – engraved traffolyte

  - Exterior labels – engraved stainless steel

Factory Acceptance Testing and Client witness testing of all PLC cabinets, Control Cabinets, and the like is to be completed before equipment is sent to site.

### Junction Boxes

All Junction Boxes shall be manufactured from standard cubicle designs complete with:

- Original supplier’s surface finish

- IP65 rating minimum for all floor mounted cubicles

- IP65 rating minimum for all wall mounted cubicles

- All equipment mounted on a removable painted gear plate

- Full width single piece undrilled aluminium gland plate

- Plinth for floor mounted cubicles

- Strengthened backplate or superstructure for wall mounted units

- Three point securing location lockable doors with lockable operating handles

- Earth bar and copper earth straps to all doors

- External panel label (traffolyte or similar)

- All equipment labelled with schematic item designation (traffolyte or similar)

- All internal wiring tinned copper

- All instrument earth bars, phase, neutral and earth bars to be tinned copper

- No nickel fittings, nor exposed copper

- Internal wiring secured in slotted cable PVC trunking

## Switchgear

### Nominal system values

|  | Parameter | Value |
| --- | --- | --- |
| 1 | Nominal System Voltage | 11kV |
| 2 | Maximum Continuous System Voltage | 12kV |
| 3 | Circuit Breaker Nominal Current (Ir) | 200A |
| 4 | Lighting Impulse Withstand Voltage (Up) | 95 kV |
| 5 | Power Frequency Voltage Withstand (Ud) | 38 kV |
| 6 | System Frequency | 50 Hz |
| 7 | Rated Short Circuit Current | 21 kA |
| 8 | Duration of Short Circuit | 3s |
| 9 | Peak making current (Ip) | 53 kA |
| 10 | Time constant | > 45ms |
| 11 | Bus bar and Isolators Nominal current (Ir) | 630A |

### RMU Configuration

Any RMU shall have the following general configuration, unless otherwise specified:

- Ring switches: 2

- Circuit breakers: 1

Enclosure

- IP Rating: IP65

- Rain shield: Yes

- Lifting rings: minimum2, OEM to confirm suitability

- Colour: to be specified

- Paint: ISO C5 Marine Grade Paint coated enclosures

- Height above ground: Base must be mounted a minimum of 500 mm above the local ground surface to reduce potential for inundation.

Circuit Breakers

- Type: Vacuum

- Rated current: 200A

- Closing (Motor driven charging): Yes

- Spring recharge after closing: Yes

Ring Switches

- Remote operation capability: Yes
Safe operating procedures for closure to be established between Contractor and Grid Operator. Grid Operator shall have authority for remote disconnect if required for system safety or stability (dispatch control to be used preferentially).

Earth Switches

- Type: Fault making

- Making capacity: 40 kA peak

- Circuit earth switch interlock: Yes, with associated circuit breaker

- Remote operation capability: Yes

Feeder CTs & VTs

- Contractor to specify

Feeder Protection Relay

- Required

- Functions – as detailed in section ‎9.6 below.

Communications interfaces: Modbus TCP/IP

SCADA interface: Modbus TCP/IP

Capacitive Voltage Indication

- Required: Yes

- Electrical interlock: Contractor to specify

Surge Arrestor

- Required: Contractor to specify

Auxiliary Power

- Required: Yes

- Auxiliary equipment AC voltage: 400/230 V AC

- Tripping and closing supply voltage: 110 V DC

- Indication supply voltage: 110 V DC

- Spring charge motor voltage: 110 V DC

- Alarm supply voltage: 110 V DC

- Redundant trip coils: Yes

- Redundant trip supplies: Yes

- Load: To be calculated by Contractor

- UPS power: Yes, to comprise of rectifier and battery bank

- Backup duration: Minimum 12 hours  without AC supply

- Redundant DC supplies: required

Metering

- Required: Yes as per section ‎9.4 below

## Metering

All MV sites shall have installed a revenue meter and Power Quality Meter on each feeder at the point of connection to the network.

Revenue Meters and Power Quality Meters shall be fed from separate CT cores.

Revenue Meters and Power Quality Meters may share VT secondary supplies.

All MV metering, including CTs / VTs used in metering, shall comply strictly with requirements specified below.

### Revenue Meters

Revenue meter: Class 0.5

Voltage input

57.7 to 240V

Burden IEC 62053-61 compliant

Current input

CT range 1/10A, 5/10A, 5/20A

CT limit 20 x Imax for 0.5 sec

Burden <0.5VA/phase

Frequency 45 to 65Hz

Four quadrant metering – 3 elements

Import/Export/Absolute Wh, varh and VAh

Fundamental Wh

Per quadrant Wh, varh and VAh

Phase A,B,C and Total - W, var, VA, Vrms, Irms

Power factor, frequency, phasor angles

Communications

Optical ports and RS485 multi drop (2 or 4 wire RJ45 or screw terminals)

DLMS

MODBUS TCP/IP

PQM - Total Harmonic distortion THD

PQM – Unbalance (sequence components)

PQM – programmable sag and swell

recording to 5 cycle resolution

record time/date/phase/duration/average and worst excursion

Load profiling over 5000 days

Time of use records

Tamper detection and alarms

Conforms to IEC 62052-11, 62053-21, 62052-31, 62053-22, 62053-23, 62053-24

### Power Quality Meters

Power Quantities:

All 3-phase configurations.

Active power [kW], Reactive power [kVAr], Apparent power [kVA], Power Factor and cos phi displacement factor, Active Energy [kWh], Reactive energy [kVArh], Apparent energy [kVAh]

Energy accuracy class 0.2S (IEC 62053-22)

Frequency nominal 50Hz system

Harmonics data:

100 individual harmonics of voltage

100 individual harmonics of current

Power harmonics  - Harmonic power with direction

Flicker – Calculate IFL, Pst and Plt to IEC 61000-4-30 Class A

Voltage channels

minimum 4

resolution 24 bit

accuracy 0.1%

High speed voltage channels

+/-2.8kV peak level

Detection rate up to 31 000 p/c @50Hz

Current inputs

minimum 4 isolated inputs

resolution 24 bit

accuracy 0.1%

User configurable Analogue inputs

minimum 6

voltage or current

Communication and remote read:

Modbus compatible

Modbus TCP/IP preferred

Tamper detection and alarm: Yes

Data logging: Minimum 1 year storage at 30 minute intervals

Battery backup: Yes

Display: Configurable

Complies with:

EMC: EN 50081-1,2, EN 50082-1,2 Voltage characteristics: EN 50160, EN 61000-2-2, EN 61000-2-12

Harmonics: IEC 61000-4-7

Flicker: IEC 61000-4-15

Power quality measurement methods: IEC 61000-4-30, Class A

IEC 62052-11, IEC 62053-21, IEC 62052-22, IEC 62053-23 compliant

## Step-up Transformer

Step-up transformers shall be rated for inverter source operation and the environment in which each system will operate and shall be provided with protection and monitoring devices such as, but not limited to, pressure relay, oil and winding temperature and oil level.

Transformers will be sized by the tenderer to accommodate the BESS full load capacity over the full design output, active and reactive power range. An allowance of a 5% capacity shall be added to the final transformer calculation.

Transformers will be provided with off load tap changers. The number and range of taps shall be determined by the tendered during detail design of the site. Tap position indications will be incorporated with site control system for remote monitoring.

It is recommended that the Contractor consider specify the transfer with a capacitive shield to reduce high frequency harmonics injected into the MV side of the transformer and connected cables.

Note: Throughout the specification two winding transformers have been referred to as indicative of the requirements for the sites. This specification does not prohibit the use of thee winding transformers. Three winding transformers will be considered where load size and or harmonic constraints would suggest a three winding transformer is the cost-effective solution.

Construction Characteristics

Type: Oil immersed transformer of sealed type construction

Oil type: Mineral oil

Primary insulation level: 12 kV

Primary voltage: 11 kV

Secondary voltage (no load): TBA

Impedance: Contractor to specify

Winding configuration: Dyn# (#=contractor to specify)

Impulse withstand: 95 kVpeak

Harmonic K factor: TBA

Power frequency withstand: 38 kVrms

Frequency: 50 Hz

Rating: Contractor to specify

Cooling: ONAN

MV connection: Bottom (conduit)

LV connection: Bottom (conduit)

IP Rating (Enclosure): 56

Operating temperature: -4°… + 45 °C without de-ratings

Altitude: < 1000 m

Environmental class: E2

Climate class: C1

Fire class: F1

Accessories

Oil and winding temperature monitoring;

Oil level indicator;

Oil drain valve and filler cap;

Ratings plate in English

4 flat bi-directional rollers

2 earthing points

Anti-vibration pads

## Environmental Protection

RMU’s, Transformers and associated auxiliary equipment shall be ground mounted and enclosed in a substation shed for protection against the elements.

Transformers shall be self-bunded, or bunding may be incorporated within the substation shed floor / foundation design.

Substation sheds shall provide adequate ventilation and lighting, walkways and access areas will conform to the requirements of IEC 61936-1:2010.  Protective barriers are to be installed where approach distances cannot be maintained.

RMU arc flash exhaust gases to be ducted to external atmosphere through controlled ducting, overhead, rear of floor exits will be permitted.

Transformer explosion vents to be ducted to external atmosphere.

## Protection

Contractor is responsible for protection of the design and implementation of protection systems for the BESS.

For sites where there is an 11 kV connection for the BESS, the Contractor shall connect the MV side of the transformer to a circuit breaker, to be provided by others, on the power station main switchboard.

For sites where there is an 11 kV connection for the BESS, the Contractor shall connect the MV side of the transformer to a circuit breaker, to be provided by others, on the power station main switchboard.

In either case, the circuit breaker on the power station main switchboard will include the following protection:

50 – Instantaneous overcurrent;

50N – Instantaneous earth fault overcurrent;

The Contractor must advise the Employer of any other protection it requires to be implemented at that circuit breaker.

## Earthing

The earthing must ensure the safety of all personnel and equipment under all normal and abnormal operating conditions and all fault conditions.

General earthing shall be according to the Utility Regulatory Authority (URA) Installation Standards and IEC standards as listed in section Error! Reference source not found., and shall include the following:

DC electrical system;

PCU;

Transformers and Neutral points;

Fencing;

Platforms and handrails and

Buildings/enclosures.

Particular attention shall be given to:

Achieving low-resistance connections that are resistant to degradation at all locations where grounding conductors or rods are bonded together

Achieving the best possible contact with earth

Verifications through tests that all electrical bonding within the grounding system has been properly affected

The design calculations shall include any area of the PV array exposed to step, touch and  transfer potentials induced by earth potential rise, low frequency induction as well as electromagnetic and electric fields for the installation.

The LV/MV transformer earthing design is to use a common LV/MV grid. The design is to take into account:

The touch voltages limits for any local pipes.

The EPR transferred to the power station on an 11 kV earth fault.

## Cabling and cable management

All cabling to be procured as well as the design methodology and considerations must strictly comply with Sections 3 to 5 of the Utility Regulator Authority (URA) Installation Standards.

MV cables must be 3C x Cu/XLPE/SCT/PVC/SWA/PVC , 6.35/11kV to British Standard or IEC 60502.

LV cables must be 4C x CU/XLPE/SWA/PVC, 0.6/1kV to British Standard or IEC 60502.

Additionally:

- Cables shall be labelled at both ends, with permanent labels.

- Above ground cabling shall be placed and protected such that DC clamp meters can be used to confirm no current flow for safety isolation purposes. No tools shall be required to allow such cable access. Service loops shall be placed in all cables external to the combiner box to allow re-termination if required.

- All outdoor enclosure cable entries are to be done from the bottom of the enclosure, to prevent water ingress.

- For underground cables, cable markers shall be installed at each change of direction, road crossing, and every 200 m of straight line length. Cable markers should designate the underground service details, depth, and relevant contact details. Cable markers should be selected to last the design life. Cable markers should be sensitive to the location (for example, flush mounted where they would obstruct other activities) and agreed with the Employer.

- Underground cables shall be protected from damage by vermin. A termite-protection layer shall be included in all underground cables. Water blocking shall be included in all 11 kV cables.

## Fixings and fasteners

Any fixings and fasteners should give consideration to corrosion requirements. Dissimilar metals should be avoided and otherwise separated by nylon washers.

## DC Combiner panels

If combining multiple DC circuits (output from battery racks) in parallel for input to PCUs, combiner panels must be used. DC combiner panels shall meet the Standards and conform to the below specifications at a minimum:

- The equipment and components making up each combiner box shall be housed in an enclosure.

- Outdoor combiner panel enclosures must have the following features:

  - a minimum ingress protection rating of IP65 in accordance with IEC 60529

  - an integral key lock or keyed padlock to prevent access to live terminals

  - UV resistant to suit the environmental conditions and design life of the project

  - drainage devices (with a minimum IP66 rating)

  - adequately sealed to prevent vermin infestation.

  - self-extinguishing and halogen-free

- Readily replaceable Surge Protection Devices (SPD) shall be provided in the combiner boxes.

- Combiner panels and all associated equipment and components shall be rated for the maximum system voltage, and maximum array prospective fault currents as per IEC requirements. Combiner panels inputs and outputs shall each be able to be disconnected by utilising an incorporated disconnect switch.

- Requirement for fuses or other protection for DC circuits shall be assessed for all fault scenarios and demonstrated for the combined fault current. If used, it shall be possible to change DC circuit fuses without use of specialised tools, and without removing touch-proofing or guarding for the other items within the Combiner panel.  It must also be possible to remove power from the fuse, so that it may be changed to a safe and de-energised state. To achieve this, fuses mounted in the combiner panel shall be mounted in fully enclosed pull out or hinged fuse carriers.

- A protective transparent cover (Perspex or similar) shall be used to allow visual inspection without accidental contact with live parts inside the combiner box.

- Combiner Panel shall be labelled. A sign indicating that the main disconnecting device, or individual input devices, does not fully isolate the internal components shall also be provided.

- The installation must include lightning protection.

# Civil and structural works requirements

## Service conditions

### Corrosion protection requirements

Equipment shall incorporate all necessary passive corrosion protection sufficient to achieve the design life in the site environmental conditions. Local environmental conditions shall be assumed to be at least as corrosive as Category 5M of ISO 12944-2.

Corrosion protection shall include all internal systems (taking into account levels of atmospheric moisture, salt, dust, etc). Corrosion protection will not require major maintenance, such as replacement of major components or surface protections (sacrificial materials designed for replacement is acceptable). Electronic equipment should be suitably coated to prevent corrosion.

Use of hermetically sealed compartments to achieve corrosion protection shall demonstrate consideration for operations and maintenance requirements, including the effect of opening compartments for maintenance purposes.

### Inundation

All equipment shall be designed and mounted to avoid inundation, including during cyclonic storm surge. As part of satisfying this requirement, equipment BESS modular units shall be mounted such that their base is a minimum of 1,000 mm above the local natural ground level.

### Geotechnical

Geotechnical and soil resistivity data for the site are not available and the Contractor is expected to make provision for foreseeable circumstances, and carry out necessary testing as part of its design.

### Other

There are existing concealed and underground services on-site that may not be fully mapped. The Contractor shall undertake its own investigations in cooperation with local power station operators to confirm.

The worksite is critical infrastructure for supply of electricity in each island. Any access to the site must not interfere with power station operation unless explicitly agreed with the Employer. The Employer will provide all reasonable access for the Contractor to enter the worksite and undertake work. Contractor will be required to meet minimum training levels, complete permit to work (or similar) procedures and demarcate the worksite. If the Contractor breaches any conditions of this access the access may be revoked until remedied without Contractor recourse.

The Contractor must ensure that the equipment configuration is appropriate for the site. This includes due consideration of impacts to other activities at the site, such as access to other equipment and safety.

## Scope of civil works

Under the project, civil works are expected to include:

- Foundations of the BESS modular units

- Foundations of transformers and switchgear

- Site drainage and erosion control

- Minor works such as improvement of access ways, or surface stabilisation for carnage in order to support installation of the BESS modular units, transformers and switchgear.

## Civil works requirements

Civil works requirements shall comply with local regulations, including the Maldives National Building Code Handbook.

Concrete shall be specified, and comply with ISO standards, including but not limited to:

- ISO 12439:2010 Mixing water for concrete

- ISO 14824:2012 Grout for prestressing tendons

- ISO 16204:2012 Durability — Service life design of concrete structures

- ISO 19595:2017 Natural aggregates for concrete

- ISO 19596:2017 Admixtures for concrete

- ISO 22904:2020 Additions for concrete

- ISO 22965-1:2007 Concrete — Part 1: Methods of specifying and guidance for the specifier

- ISO 22965-2:2007 Concrete — Part 2: Specification of constituent materials, production of concrete and compliance of concrete

- ISO 22966:2009 Execution of concrete structures

## Scope of structural works

Under the project, structural works are expected to include:

- Fencing, for sites where existing site security fencing is inadequate or not available.

- Racking, cabinets and enclosures for EMS

- Cable management systems (cable ladders, trays, etc.)

- Foundations for BESS modular units (e.g. pile type foundations)

- Ancillary structures, such as poles for instrumentation, lightning protection, lighting or security.

## Requirements of structural works

Civil works requirements shall comply with local regulations, including the Maldives National Building Code Handbook.

Wind loadings must consider cyclonic conditions, with wind gusts up to 75 m/s. Earthquake loadings must be considered.

# Engineering studies

The design process will produce the following, minimum set, of detail design reports to support the electrical connection design:

- Power system studies including but not limited to the following:

  - Short-circuit analysis, minim and maximum fault levels and locations;

  - Load flow;

  - System stability (Voltage & Frequency transients);

  - Ramping on/off requirements; and

  - Insulation co-ordination and lightning mitigation

  - Arc fault levels;

  - Harmonic response – injection levels to 50th order

  - Flicker levels

- Protection study that documents:

  - All protection devices and schemes;

  - Protection coordination with upstream devices;

  - CT and VT sizing calculations.

- Earthing study documenting:

  - Reporting site resistivity levels

  - Expected EPR contours at each site

  - Earthing system design methodology

  - Recommend mitigation / grid design

- Cable sizing report documenting:

  - Soil thermal resistivity reports

  - MV and LV AC cable Sizing calculations (capacity, volt drop, fault capacity, design assumptions, losses etc.)

  - DC Cable Sizing calculations (capacity, volt drop, fault capacity, design assumptions, losses etc.)

  - MV and  LV Cable trench design parameters

- Arc flash study:

  - AC and DC panels and cabinets shall be subject to arc flash safety assessment and nomination of appropriate PPE

  - IEEE 1584 is used to establish the incident energy and arc flash boundary for electrical equipment installed.

  - The design shall be such that the arc flash study shows that for operation or any maintenance activities no higher than arc flash PPE category 1 is required for DC circuits as defined in “NFPA70E Table 130.7(C)(15)(b) Arc-Flash PPE Categories for Direct Current (dc) Systems”, and for AC circuits as defined in “NFPA70E Table 130.7(C)(15)(a) Arc-Flash PPE Categories for Alternating Current (ac) Systems”.

Additionally, the design process shall include civil and structural design analysis as required to substantiate the design, comply with local building regulations, and support application for building permits. This must include:

- Applicable standards and evidence of compliance with such standards

- Static, wind, earthquake, and any other design loading considerations

- Corrosion protection, rates of degradation

- Application of above to determine main civil and structural design elements

- Application of above to determine material and equipment specifications

# Quality control

The Contractor shall provide a Quality Management Plan (QMP) that describes the quality control methods for manufacture of all major equipment and equipment installation and testing. The scope of the QMP shall include:

- Full production chain of quality assurance

- Subcontracted works and manufactured components of the project

- Comprehensive matrix of testing planned, including FAT, Manufacturer Data Records, and Inspection Test Plans

- Inclusion of checks, witnessing and auditing required for quality control

- Document management for quality assurance documentation.

## Witness and Hold Points

The Contractor shall provide all test plans including recommended Hold and Witness points. The Employer shall have the option to review and nominate additional Hold or Witness Points if reasonably required.

The Employer’s presence is required at Witness Points. The Contractor may proceed past the point provided the agreed notice of test (written / e-mail / documented notification) is given and the Employer elects not to be present at the time of the test.

### Hold Points

Where Hold Points have been identified by the Employer in the CDRL, no work is to proceed beyond these points prior to the Employer’s inspection, and/or prior to the Employer providing approval. Waiver of the inspection can only be given in writing by the Employer

## Inspection and testing

The Employer shall have the option to witness, or appoint a third party to witness, any testing of the BESS or its components. At least 10 days’ notice of planned testing shall be provided.

Inspection and testing shall be planned with due consideration for the limitations on site testing, including resources and disruption of the grid. All efforts shall be made to rigorously confirm product quality and performance prior to shipment to site.

### Factory acceptance tests (FAT)

The Employer shall have the option to witness, or appoint a third party to witness, any testing Major component FAT. At least 10 days’ notice of planned testing shall be provided.

Major components shall be subject to FAT including:

- BESS

- Transformer

- Switchgear

- EMS

The FAT shall include pre-energisation (cold test) quality control checks including fabrication, installation, connections, electrical safety tests, and subsystem functionality. These shall ensure installation and equipment is as per specification.

The FAT shall include energised (hot) quality control tests to confirm all operational capabilities and to measure equipment performance in accordance with the functional guarantees.

Energised FAT (for Employer witness) shall not proceed until the Contractor has met the following conditions:

- FAT Plan, including detailed ITP has been provided and reviewed.

- No further work is required to complete the build of the equipment, and, excepting packing or other such requirements to make safe the equipment for transport, the equipment is complete and ready for shipment.

- Evidence is submitted to show that all pre-energisation checks are completed satisfactorily, and that the equipment is fully capable of energisation.

- Evidence is submitted to show that all control programming and bench tests of control systems are complete.

The scope of the FAT shall be sufficient to:

- Comprehensively ensure that the equipment operates as agreed in the Employer Requirements

- Ensure that the equipment operates as intended

- Allow the Employer to observe operation characteristics that may impact integration to the power station

Other components and materials shall be subject to end-of-line testing and factory quality control, and be issued with the associated manufacturer data records. This includes:

- Cables (electrical and fibre)

- Metalwork

- Cabinets and enclosures

- PLCs, control, networking and associated equipment

### Inspection and test plans

The Contractor shall prepare an Inspection and Test Plans (ITPs) covering all aspects of the works; these shall be submitted to the Employer for review and approval prior to any Inspection and Testing of the works. The Contractor shall carry out inspection and testing in accordance with the best industry practice and manufacturers recommendations.

Commissioning Management Plan. The Contractor must provide the Employer with a Commissioning Management Plan within the timeframe outlined in the CDRL. The Commissioning Management plan must detail the schedule of ITPs and checklists to be provided and the dates on which they will be provided to the Employer.

The Employer reserves the right to inspect the Works to the extent necessary to satisfy himself that the work conforms to the drawings and specifications and to verify that all the required testing and inspections have been completed to the satisfaction of the Employer and Client Engineers.

The Employer may appoint an Inspection Agency to carry out inspection services and to witness and verify tests. The Contractor shall liaise and co-ordinate fully with the Inspector and take all necessary measures to facilitate testing and verification.

The ITPs shall clearly define the objectives, any pre-requisites and pass / fail criteria. The pass criteria shall be correct operation. Any failed test shall be registered as a defect or non-conformance (as applicable) and rectified by the Contractor. On the identification of a failed test the Employer reserves the right to halt all further testing until satisfactory remedies have been implemented and recorded.

The ITP shall be marked up during testing and each test signed as completed by the Contractor and witnessed by the Employer (at its discretion). A copy of the signed off ITP and related test certificates shall be delivered to the Employer in electronic form at the successful completion of the tests.

No testing shall commence before the ITP has been approved by the Employer.

ITPs and checklists are to be signed off progressively as work progresses. ITPs and checklists are required to be submitted to the Employer progressively throughout construction, with test records, completed ITPs and checklists forming part of the verification records for the work and be compiled into the MDR and As-Built documentation.

### Materials handling

Quality control must include materials handling procedures. This includes procedures for:

- Inspection prior to shipment and on receipt at site

- Transport of equipment, loading and unloading

- Storage requirements

- Tracking of equipment and storage locations

Procedures shall include completion of relevant quality control documentation.

### Pre-Commissioning Tests

#### General

The Contractor shall carry out Pre-Commissioning Tests on-site following completion of installation of the Plant and prior to completion, in accordance with the Contract. The purpose of the Pre-Commissioning Tests is to confirm that the installation of the Plant is complete and correct, and in a safe condition for livening and operation.

#### Electrical Pre-Commissioning Tests

The Contractor shall pre-commission all of the electrical works.

The Electrical Pre-Commissioning Tests shall include all requisite cold checks, high potential testing, meggering, phasing, insulation resistance, continuity, point to point termination checks, polarity, phase rotation, protection testing (including current injection) and functional operation of all devices and controls.

The Contractor shall provide all suitably calibrated test equipment to perform all pre- commissioning and post livening tests and suitably qualified and experienced personnel to provide the testing.

The Contractor shall provide detailed test sheets for the commissioning of each protection and metering type. The Employer test sheets shall be limited to an overall check sheet encompassing all checks suitable for sign off before livening.

No item of plant shall be livened until clearance is obtained from the Employer, at which time the necessary warning notice in accordance with safety procedures shall be attached to the relevant circuit switch or isolator, and where appropriate, to the plant item itself.

In addition to any testing required under local regulations, the Electrical Pre-Commissioning Tests shall include but not be limited to the following:

#### Visual Inspections

Visual inspections shall include:

- Checking plant for conformity with specifications

- Removal of packing or protective materials from instruments, equipment and devices

- Systems complete “component count”

- Switches, fuses and ancillary equipment correctly labelled and set to appropriate current ratings

- Checking all fasteners, fittings, supports, alignments and clearances

- Checking rotation direction of all drives

- Checking of all earthing

- Electrical systems certified for compliance with the relevant standards

##### Switchgear

Tests to be carried out on the switchgear shall include, but not be limited to the following:

- High potential tests on busbars, including metal enclosed bus, and switchgear

- Contact resistance measurements of joints in bus and cable connections

- Mechanical tests

- Point-to-point wiring continuity checks on all low voltage circuits to confirm that the final connections agree with the panel wiring diagrams

- Meggering at the appropriate voltage of all high voltage circuits

- Energizing of all low voltage circuits

- Functional testing of all equipment including interlocks

##### Motors:

Motor tests shall include;

- Insulation resistance measurement

- Phase rotation check

- Vibration

- Shaft Alignment

##### Medium / High Voltage Cables

All high voltage cables shall be tested for:

- Continuity

- Ductor testing of terminations

- Pressure tests (High voltage AC only)

- Correct phasing

- Labelling

- High voltage terminations shall be included in the test circuit.

##### Control and Instrument Cables

Control and instrument cables shall be tested for:

- Continuity

- Labelling

- Terminations against schematics

- Removal against schematics

##### Low Voltage Cables

Low Voltage cables shall be tested for:

- Continuity

- Insulation resistance

- Labelling

- Terminations against schematics

##### Earthing

Conductivity tests of the system and earthing resistance tests shall be performed at points throughout the system before any electrical equipment is energised from the permanent source of power.

The commissioning testing of the earthing system will include performance testing, continuity testing and visual inspection for design compliance. The objectives of the testing will be to:

- Verify the safety performance installed earthing system in accordance with URA Electrical Installation Requirements, IEEE 80 - Guide for Safety in AC Substation Grounding, and other relevant standards codes, guides and legal requirements;

- Establish bench marks for the earthing system performance for future audits by simulated earth fault current injection tests to determine earth grid voltage rise, step and touch voltages and earthing system impedances; and

- Report on the condition of the earthing systems in terms of compliance with the design, standards and to provide a statement of compliance or non-compliance. The intent of the report is to provide a comprehensive assessment of the condition and performance of the earthing systems and provide sufficient information such that remedial action can be arranged based on the recommendations provided in the report.

The performance testing shall use the off-frequency current injection test to perform the following testing:

- Earth grid voltage rise (EGVR)

- Fault current distribution

- Earthing system and earth grid impedances

- Earth potential rise (EPR) voltage profiles

- Prospective touch and step potentials at relevant locations inside and outside the substation

- Transfer potentials around the substation

Physical inspection of the earthing system shall include inspection of the earthing system to determine condition and compliance to design (conductor size, material, connections).

The Contractor shall carry out electrical continuity measurements on the earthing system, to a specific reference point(s), to determine whether plant equipment is adequately earthed in compliance with design and relevant standards.

##### Fibre Cables

Fibre cables shall be tested for:

- Optical Time Domain Reflectometer (OTDR) Tests, all cores in both directions;

- Single Mode Fibres: 1310nm and 1550nm

- Multimode Fibres: 850nm and 1300nm

- Insertion loss tests

- Labelling

- Terminations against schematics

##### Protection Equipment

All protection items shall be checked for the necessary protections associated with the protection of cables/ transformers/ and motor generator sets.

Secondary injection testing of protection relays is required.

##### Instrumentation

All instrument items shall be field calibrated and a calibration certificate shall be provided for each instrument.

Instrumentation shall be tested where applicable for;

- Full loop test using primary signal injection, i.e. temperature, pressure, flow etc.

- Check of the complete measurement/display from instrument to HMI for correct display including value and unit of measure and alarm points

The Contractor shall liaise with the Employer to carry out the above, and provide comprehensive calibration reports and testing check lists for each instrument.

### Mechanical, Civil and Structural pre-commissioning tests

The Contractor shall pre-commission all of the Mechanical, Civil and Structural works.

The Mechanical, Civil and Structural Pre-Commissioning Tests shall include all requisite checks to ensure that the condition of works is sound and in accordance with the design.

##### Visual Inspections

Visual inspections shall include:

- Site survey to confirm installation at correct location and elevation in accordance with design

- Checking plant for conformity with standards and specifications, including materials, finishes, dimensions, connections, compaction

- Checking all fasteners, fittings, supports, alignments and clearances

- Checking for any evident damage, scratches, discolouration, corrosion, burrs, holes or other such defects

- Checking for any safety risks

- Checking that Plant is accessible and operable, and tasks as set out in the Operations and Maintenance plan can be carried out

- Required operating documentation is available on site

- All spares and tools provided and stored

- Any operating procedures, labels and other signage are in place

- Checking for proper function of drainage and erosion controls

- Any revegetation and permanent erosion control measures are in place.

##### Materials tests

All materials tests, including Manufacturer Data Records and site testing for locally acquired materials, shall be compiled and available.

##### Third party Inspections

The Contractor is required to engage an appropriately qualified third party to inspect and certify compliance of Mechanical, Civil and Structural works with local regulations.

### Livening

The Inspections and Tests shall be deemed to have been completed when the Contractor has obtained from the Employer written verification that the said Inspections and Tests have been completed and passed in accordance with the Contract and that the Plant is ready for the commencement of the commissioning and livening.

The Contractor shall provide a detailed plan for livening equipment. This shall be provided in accordance with the network operator’s standard practices, and the following requirements:

- Provided at least two weeks ahead of planned livening

- Planned date, time of commencement

- Expected date, time and duration for any outage

- List of necessary pre-conditions for livening, including pre-commissioning test results submitted

- Detailed steps and schedule for the livening process, including allocations of responsibilities, necessary checks and confirmations prior to each operation

- Required actions from the network operator

- Contingency plans

- Risk assessment appropriate to the task

Checks during livening shall include operation of all essential services and system communications.

All checks during livening shall be accompanied by the necessary check sheets. Documentation shall be provided in accordance with the network operator’s standard procedures.

### Hand Over

Following successful livening, and the Plant operating as specified, and subject to completion of required training and (if relevant), the initial operations and maintenance period where the Contractor has responsibility for operation of the Plant, the Contractor may hand-over the Plant for operation to the Employer. Conduct of functional guarantee testing as required under the contract shall be undertaken by the Contractor in cooperation with the network operator. This may be undertaken prior to hand over, or the Employer will hand back operation of the Plant for the purpose of functional guarantee testing.

The Contractor shall provide to the Employer signed and dated reproducible copies of Reports, Red Lined As Built Drawings / Schedules and Inspection Test Sheets / Plans clearly showing the extent to which Inspections and Tests have been completed and the result of such inspection and testing. The Contractor must sign supplied check lists.

Handover documentation to include all operator and maintenance training, and higher level site engineer training on the equipment supplied.

# Warranty requirements

In addition to the Contractors obligations during defect liability period (DLP) and extended defects liability period (EDLP), the Contractor is also required to offer to assign all OEM warranties to the Employer. Novation of the warranty shall retain all warranty features available to the Contractor.

OEM warranties should apply for the maximum period offered by the OEM, and shall be a minimum of the following:

- The BESS modular units (all components, excluding inverter): 10 years

  - Option to extend BESS warranty to 15 years (subject to operations and maintenance of BESS within specification)

- Inverter: 5 years

  - Option to extend inverter warranty to 10 years (subject to operations and maintenance of inverter within specification)

- Transformer: 5 years

- Switchgear: 5 years

- Cables: 5 years

- EMS hardware: 2 years

- Other equipment: 2 years

Further details are included in Appendix B and D.

Upon placement of orders for the above equipment Contractor must provide a letter from the OEM stating that the OEM has no objection to a novation of the warranty to the Employer after the specified 2-year operations and maintenance period, or at any other time after Completion on request of the Employer.

All manufacturers for the above equipment manufacturer must hold current certification for compliance with ISO 9001, ISO 14001 and ISO 18001.

# Remote commissioning

The Contractor must have procedures available to commission the BESS and EMS (and any other specialty OEM hardware) without limitation on the availability of specialist personnel for physical travel. That is, in the event of border closures (irrespective of change of law) or unavailability of flights, or other such restriction, commissioning of specialist equipment shall be able to continue to schedule using remote commissioning processes.

# Appendix B – Battery Energy Storage System (BESS) requirements

# Relationship to other parts of the Employer Requirements

This part of the Employer Requirements (Appendix B –BESS requirements), provides key technical requirements for the BESS units required under this project. It shall be read in conjunction with other parts of the Employer’s Requirements. All parts of the Employer’s Requirements are applicable to BESS equipment and shall not be read in isolation.

In particular, note:

- Employer Requirements:

  - This document provides the necessary overview information on the project scope and general requirements. It also includes summary information on the island specific capacities and requirements.

- Appendix A –General and Electrical:

  - This document provides details of the electrical standards and equipment requirements that the Plant must meet.

- Appendix C –Energy Management System:

  - This document provides key technical and functional requirements of the Energy Management System (EMS) that must be provided independent of the BESS to provide island wide generation dispatch management.

- Appendix D –Operations and Maintenance requirements:

  - This document provides details of the support that Contractors are required to provide for the electrical standards and equipment requirements that the Plant must meet.

- Appendix E –Project Site Specific Details:

  - This document provides details of the requirements at each site. It includes site descriptions and data, capacity requirements, details on existing equipment and infrastructure, details of the point(s) of connection, and other related information for each island.

- Appendix F – Environmental and Social Requirements:

  - This appendix provides the environmental social safeguards requirements and reference is made to relevant safeguards documents of the project

# Definitions

Unless explicitly stated in this document, or the Employer Requirements, definitions are as per IEC 62933.

| Acronym | Definition |
| --- | --- |
| AC | Alternating current |
| Aux | Auxiliary |
| BESS | Battery energy storage system |
| BS | British standard |
| BMS | Battery management system |
| dBA | Decibels |
| DC | Direct current |
| DHCP | Dynamic Host Configuration Protocol |
| EMS | Energy management system |
| EES | Electrical Energy Storage |
| IEC | International Electrotechnical Commission |
| IP | Internet Protocol |
| IP | Ingress protection |
| ISO | International Standards Organisation |
| ITP | Inspection test plans |
| EMC | Electromagnetic Compatibility |
| GPO | General power outlet |
| FAT | Factory acceptance test |
| HMI | Human-machine interface |
| HV | High voltage |
| HVAC | Heating, ventilation and air conditioning |
| LV | Low voltage |
| MV | Medium voltage |
| O&M | Operation and maintenance |
| OEM | Original equipment manufacturer |
| PC | Personal computer |
| PCU | Power Conversion Unit |
| POC | Point of Connection |
| PQ | Active and reactive power |
| PPC | Power plant controller |
| PV | Photovoltaic |
| SAT | Site acceptance test |
| SCADA | Supervisory Control and Data Acquisition |
| SoC | State of charge |
| UPS | Uninterruptible power supply |
| TCP | Transmission control protocol |
| RMU | Ring Main Unit |

# Standards

All equipment shall be installed and all work shall be carried out in accordance with statutory requirements of the relevant jurisdiction (including amendments).

The Maldives typically adopts the use of International Electrotechnical Commission (IEC) standards, and International Standards Organisation (ISO) standards. All equipment supplied under these specifications shall conform to the latest editions of the IEC or ISO standards, or where no IEC or ISO standards, to British Standard (BS), or equivalent national standards as may be approved by the Employer.

IEC 62933:2018 Electrical Energy Storage (EES) Systems

IEC 62485-5:2020  Safety requirements for secondary batteries and battery installations - Part 5: Safe operation of stationary lithium ion batteries

UL 1973:2018 ANSI/CAN/UL Standard for Batteries for Use in Stationary, Vehicle Auxiliary Power and Light Electric Rail (LER) Applications

UL 1741: Standard for Inverters, Converters, Controllers and Interconnection System Equipment for Use with Distributed Energy Resources

IEC 62619:2017 Secondary cells and batteries containing alkaline or other non-acid electrolytes. Safety requirements for secondary lithium cells and batteries, for use in industrial applications.

IEC 63056:2020 Secondary cells and batteries containing alkaline or other non-acid electrolytes – Safety requirements for secondary lithium cells and batteries for use in electrical energy storage systems.

IEC 62109-1:2010 Safety Of Power Converters For Use In Photovoltaic Power Systems

IEC 62477-1:2012 Safety requirements for power electronic converter systems and equipment - Part 1: General

IEEE 519: 2014 Recommended Practice and Requirements for Harmonic Control in Electric Power Systems

IEEE 80: 2013 Guide for Safety in AC Substation Grounding

IEC 61000 Electromagnetic Compatibility (EMC) all parts as applicable

ISO 7240 Fire detection and alarm systems

ISO 14520 Gaseous fire-extinguishing systems — Physical properties and system design

ISO 5149-1:2014 Refrigerating systems and heat pumps — Safety and environmental requirements

IEC 62281:2019 Safety of primary and secondary lithium cells and batteries during transport

IEC 61936 Power installations exceeding 1 kV a.c. and 1,5 kV d.c.

IEC 60364 Electrical Installations for Buildings

In case the equipment or materials offered from a country where the relevant standards to which the equipment or materials offer better performance or safeguards for the Principal than IEC or BS Specifications, these are acceptable. The Contractor must substantiate any such claims by submitting an independent assessment, by an appropriately qualified person, that identifies differences in the standards and demonstrates the benefit for the Principal.

All listed standards must be complied with unless exception is granted, or noted in these Employer Requirements. If a requirement included in the Employer Requirements exceeds a standard listed, then the requirement within the Employer Requirements shall be adhered to.

Standard(s) referred to shall mean the current Edition / Revision together with Amendments issued.

All installations and materials and cabling shall be in accordance with the IEEE Wiring Regulations. All works shall conform to the requirements of the URA.

# Intended Purpose

This section details the Intended Purpose of the BESS by describing general features and functionality that are required for the BESS to fulfil its role. It summarizes requirements, which are specified in more detail subsequently in this document.

## Key performance requirements

The primary functional requirements for the plant are:

- Output of the BESS conversion units (PCUs) must be at 11 kV (may be via external transformer).

- Continuous power rating: (functional guarantee)

- Energy storage: As per Employer Requirements Section 1.13.

- Round trip efficiency: (functional guarantee)

- Minimum service life: (functional guarantee)

- Availability: (functional guarantee)

- Minimum design life: 15 years

The BESS shall be installed adjacent to the thermal station. The location and battery limits of the BESS is specified in Part E - Project Site Specific Details.

## Functionality

The BESS is required to provide continuous operation to optimise the use of renewable energy generation (primarily solar PV) and enable efficient scheduling of diesel generators in isolated island networks.

To fulfil this functionality, the BESS should have as its primary functionality, the capabilities described for Class A applications in IEC 62933-2, and secondary functionality for Class B applications in IEC 62933-2.

### Active and reactive power capabilities

The BESS must be able to supply and absorb active and reactive power at the rates specified in Section ‎8 of this Appendix. This includes short term overload capacity.

### Energy storage

The BESS must offer a minimum Energy storage as specified in Section ‎8 of this Appendix (indicatively 1 hour of storage).

### Control modes:

The BESS must be able to operate in, and seamlessly transition between the following control modes, to the extent allowed by its performance capabilities:

- Grid forming (voltage source)

  - Configurable frequency and voltage droop control functions

    - must be able to use external setpoint signal to apply bias settings for active and reactive power (PQ), or active power / power factor

  - Isochronous control (The inverter must have the capability to operate in island mode, without an external source of voltage and frequency for reference and no other synchronous generation online)

- Grid following (current source)

  - PQ and PV mode: BESS must be able to follow external active and reactive power commands

- Black start capability is not mandatory, but should be included if it is within the capability of the product offered.

The BESS must be able to be configured to automatically and rapidly transition to Grid forming isochronous mode on detection, or notification by the EMS, of a loss of the synchronous generation (islanding event).

#### Secondary control functions

Additionally, the BESS control must offer functionality to provide active power ramp-rate control in any of the modes in 4.1.2 to smooth solar PV variability, if provided with a solar PV output signal.

### Response time

When operating in Grid forming mode, the BESS must respond instantaneously (<50ms) to changes in network frequency and voltage. Response to external setpoint signals, and in grid following mode, shall be less than 1s for full scale response.

### Operating states

The BESS must have Operating, Stand-by, and Stopped operating states.

Operating: The BESS must respond to any command or change in grid condition in accordance with its performance requirements and Control modes.

Standby: The BESS is connected, but not supplying or absorbing active or reactive power. It must be able to transition to Operating mode within 1s. The BESS may shutdown some systems for the purpose of reducing energy consumption and/or wear during Standby.

Stopped: Grid-disconnected and the accumulation subsystem is disconnected from the inverter. Auxiliary subsystems must still be operational, including HVAC and communications. To transition from Stopped to Standby or Operating may include a state where the accumulation subsystem is connected first, prior to grid-connection. Transition from Stopped to Standby or Operating must be possible within 2 minutes.

### Descriptive

The BESS will be installed at, and connected to the power station of a small remote grid. The power station uses diesel generation as the primary source of electric power to supply network loads. Network loads are primarily residential, small to medium commercial customers, and government buildings. Solar PV is being installed as distributed generators of various sizes in the network, and will contribute to the electric power supply.

The BESS is required primarily to ensure system reliability and power quality is maintained with increasing solar PV penetration. To this end, the BESS will be required to provide a reliable source of instantly available active and reactive power to support the grid through abnormal or fault conditions, or unplanned variation in generation output. The BESS is intended to maximise solar PV generation direct to load, and must therefore allow a reduction in on-line diesel generator capacity during solar PV generation. It is expected that this capability will also allow less diesel generation capacity online even when there is no solar PV operational.

The BESS will typically operate with at least one diesel generator online (two will be required to meet redundancy requirements, but only one may be online after a fault). Diesel generator online capacity may be less than grid load (shortfall made up by solar PV and / or BESS). The BESS will contribute with frequency and voltage control, and to fault currents within its capability, but safe operation of the grid will continue to rely on fault current contributions from online diesel generators when operating in this way.

Diesel off operation with the BESS as the isochronous unit is not planned for MV grids, however, the BESS must have the capability to operate in this mode, as there may be instances where it is advantageous. It is not necessarily expected that the BESS will have fault / short circuit current (SCR) capacity to support all solar generation during such events. For LV grids, diesel off operation is will be required as part of normal operations. When operating diesel off, it is recognised that fault discrimination and provision of SCR for solar may not be possible and BESS contractor shall provide for safe shutdown under fault conditions.

Islanded grids have very low inertia compared to traditional grids and they can become unbalanced in timeframes of tens of milliseconds. The BESS is required to operate robustly to respond to this characteristic.

The BESS is required, where it does not compromise its primary function, to store excess solar PV energy and later release it to the grid. This will reduce solar spill and increase the overall contribution of renewable energy to the grid.

## Duty cycle

The duty cycle of the BESS is heavily dependent on evolving power system conditions. These not only include growing renewable energy generation, but also growing and potentially changing demand profiles and customer equipment. Therefore, this specification requires that the BESS and its warranties robustly achieve the required performance and longevity in a wide range of usage scenarios typical of the intended application.

The following duty cycle shall be used whenever interpretation of the Employer Requirements refers to a duty cycle. Nevertheless, the BESS must be robust to a full range of usage cases including modes of operation, duty cycle, grid support, and grid forming, with seamless transition.

Duty cycle characteristics:

- Constant power factor of pf=0.92 (supply reactive power to the grid)

- Operate grid-forming, in VF mode, with droop control. Active power set points in the duty cycle below are provided as bias to the droop control.

- Two typical daily profiles (repeated daily for the operating life) shall be considered (BESS must satisfy both requirements):

  - The charge rate of the sample solar smoothing charge profile shall be as per the attached ‘charge profile.xlsx’ time series. This time series contains 1-second data points for a single day.

    - Charge or discharge at 60 s overload rate for 60 s may occur at any time in the duty cycle, up to two (2) times per day. Follow by discharge or charge at 20% continuous power to return to previous state of charge.

    - Charge or discharge at 1 s overload rate for 60 s may occur at any time in the duty cycle, up to two (2) times per day. Follow by discharge or charge at 20% continuous power to return to previous state of charge.

  - Total daily discharge is equal to 1 hr x island specific BESS rated power.

- Droop control function to be designed for site characteristics, graded faster than diesel generator response (subject to confirmation during detailed design). However, for the purposes of the Duty Cycle calculation, no additional load associated with frequency control is required.

## Expected service life

The Expected Service Life of the BESS is 10 years, or accumulated energy discharge equal to 3650 x Rated Energy Capacity (whichever occurs first).

The BESS must be designed to fully comply with the specification throughout the Expected Service Life.

There shall be no restriction on use of the BESS by the Employer beyond the Expected Service Life, and within the Design Life, except to the extent that state of health may limit performance, mandate isolation or replacement of battery modules.

## Robustness to failure

The BESS must have a modular and redundant design so that failure of any single component shall not reduce capacity by more than 20% (or the 1/ number of indivisible components of one type, whichever is larger), and so that faulty parts can be replaced through isolation of the local modular component only.

# Scope of work

The Contractor has single responsibility for delivery of the operational BESS. This includes the design, documentation, certification, supply, delivery, installation, testing and commissioning of a BESS, including all associated balance of plant, and meeting the functional requirements of this specification.

The scope shall also include training and capacity building of local staff to operate and maintain the system as well as provide warranties for equipment and workmanship, and performance guarantees and defects liability for the complete system as a whole.

The works shall include but not be limited to the following:

- Design of the BESS

- Supply and installation of BESS including:

  - Battery modules

  - Racking and containers

  - Grid interactive inverters

  - Auxiliary power system

  - Step-up transformers

  - AC and DC switchgear

  - Control and SCADA interface

- Supply and installation of footings for PCUs and other hardware as applicable.

- Installation of drainage, erosion and sediment control measures

- Supply and installation of switchboards

- Supply and installation of AC, DC, control and communications cabling.

- Supply and installation of 11 kV feeder cable to point of connection and termination at the point of connection.

- All system lightning and surge protection as required.

- All system earthing and equipotential bonding as required, including interface to existing earth grids as relevant.

- Interface to conduits, ducting or cableways existing or installed under other works packages.

- Supply and install all cable management equipment, supports, trays, ladder and conduit etc. including trenching, ducting and catenary wires.

- Provision of data and communications network cabling for interface of new data logging, control and monitoring systems into existing networks as well as provision of a new dedicated internet connection.

- Supply, installation and testing of communications cabling, outlets, frames etc.

- Co-ordination with the site owner for access and coordination of activities.

- Co-ordination and liaison with the Employer’s Representative and Owner’s Engineer at the outset and throughout the entirety project.

- Submission of documentation as per the documentation deliverables list.

- Provide training and capacity building of local staff in the operation, maintenance and safety of the system.

- Installation of all required temporary facilities.

- Supply of all required spares expected for the first 5 years of system operation, including storage cabinet or equivalent (Employer workshop may be used for small volumes of spare parts).

- Supply of a full set of tools required for the maintenance and operation of the system.

- Ensuring compatibility with existing equipment and other plant supplied by the Contractor.

# Architecture

The BESS shall use a modular architecture consistent with the IEC 62933-1 description of an “EES system architecture with one POC type” (auxiliary loads to be supplied by the BESS rather than via separate feed from the thermal power station). That is, each modular unit of the BESS must have this architecture with a single POC and single communications interface.

Where multiple modular BESS units are assembled in order to meet the capacity requirements of a single island, the outputs of each modular BESS unit shall be marshalled to either one (1) or two (2) POC (according to the specifications for each site). Communication interfaces shall also be marshalled to provide a functional common interface point. Multiple modular units at a single island location shall be able to be operated as a single integrated BESS using a redundant plant controller, which may be embedded in the BESS modular units.

Figure 1 Examples of connection architecture including where multiple BES modular units are required

## Point of Connection (POC) arrangement

The BESS will connect to the existing network at 11 kV via one (1) or two (2) existing circuit breaker(s) (according to the specifications for each site) on the power station 11 kV bus.

BESS modular units must output LV and should utilise external transformer(s) to step-up to 11 kV with 11kV breaker either as an RMU or integrated kiosk prior to connection to a circuit breaker (existing, or to be installed by the Contractor as per specifications for each site) on the Power Station bus.

Maximum single transformer size is 6 MVA. Three winding transformers may be used.

## Communications interface

To support centralised grid operation and dispatch control, data from the BESS must be available via a router / switch / patch-panel installed with the BESS. The communications connection point must include single mode fibre optic connection to the EMS and Employer SCADA. Communication infrastructure must be installed in a readily accessible panel.

The BESS controller must have a dedicated interface with an external port reserved for communication over third-party networks via static IP or DHCP.

All communications must be Modbus compliant.

All IO modules shall include 25% spare capacity.

The following information shall be provided to the grid at a minimum:

- Operation status of the BESS plant, including status of all subsystems, consolidated warnings and alarms

- Voltage at MV busbar of the BESS

- Active Power, Reactive Power and electric current interchanged at the Metering point

- Status of the MV circuit breaker(s) and isolator switches

- BESS plant controller default data (including but not limited to relevant BMS and Inverter data, status, alarms, warnings, configuration settings, operating mode, SoC, DC and AC power / voltage / current, temperature).

- Heartbeat.

Additional indicative data available from the BESS is shown in IEC 62933-3-1, Table 4.

The BESS shall receive, acknowledge and act on the following dispatch commands, which may be issued at intervals of 1 s or greater:

- Control mode

- Active Power setpoint

- Reactive Power setpoint

- Shutdown, standby and start commands

- Transfer of control commands (local and remote, where allowed by safety protocols)

- Start / stop automatic ramp rate control for solar PV

Indicative communications architecture diagram, including remainder of the grid, is shown below:

Figure 2 Indicative communications architecture

# Physical and installation requirements

## Design life and workmanship

The Design Life of the BESS must be at least 15 years.

O&M procedures must list all items that require replacement to achieve this life, including indicative replacement/repair intervals with consideration of site conditions and Duty Cycle.

The BESS shall be designed and installed such that all components will remain safe, operational, and maintainable for the entire design life using tendered O&M procedures (except where the state of health of battery modules requires their isolation or replacement).

Fits and tolerances shall be given in accordance with ISO Standards. Fits shall be selected for the smooth functioning of the components for the design life.

Any evidence of corrosion, degradation or leakage during defects liability period will be treated as a defect if it has potential to impact expected life or may introduce O&M challenges or additional work.

## Service conditions

The BESS shall be designed for Outdoor operation under Normal Environmental Conditions as per IEC 62933-2 (except that Ambient Air Temperature less than 10oC need not be considered).

The BESS may alternatively be installed outdoors, or indoors within the power station building subject to individual site specifications.

The BESS shall be designed for other service conditions as described in IEC 62933-2 and as per this specification (Noting in particular the requirements described in Appendix A and site specific information in Appendix E).

### Ingress protection

The BESS modular unit enclosures must be rated for ingress protection (IP) class 65 to IEC 60529.

The BESS modular unit enclosures shall prevent entry by vermin including but not limited to mice, wasps, and termites.

### Access and egress

BESS installation must include all necessary structures, fixtures, fittings, and other equipment to ensure safe access and egress for lifecycle operations and maintenance requirements at all times (including in wet weather and at night). This includes, but is not limited to:

- External fencing (where applicable depending on other site use / security)

- Internal and external lighting

- Platforms, stairs, walkways, awnings

- Emergency exit(s)

  - Emergency exits must comply with relevant standards. Safety bars will be provided on doors. Floor surface, step dimensions and handrails must provide safe exit. Aisle widths, protrusions into aisles and panel door clearances must provide unobstructed access. Emergency exit lighting must be provided and sufficient for emergency egress.

- Equipment must be properly designed for arc flash protection, and eliminating exposed live equipment (including within cabinets if they need to be opened without first being isolated). Arc flash study required as per Appendix A – General and Electrical.

- Where possible equipment shall be mounted such that working at heights is not required.

Installation of the BESS must not limit access or egress to existing infrastructure, except as agreed with the Employer.

## Heating, ventilation and air-conditioning

BESS shall include heating, ventilation and air conditioning (HVAC) systems as necessary to allow its operation in satisfaction of the functional requirements.

Contractor’s shall note relatively high humidity, temperature, and saline air content typical of the Maldives. Contractor’s will be expected to demonstrate suitability of all HVAC and passive design to these environmental conditions.

For any BESS equipment other than enclosures containing Battery Modules, the HVAC system may include passive design, and must allow continuous operation at full rating in Site Conditions.

For enclosures containing Battery Modules, the enclosure must be a sealed unit and HVAC shall be designed according to the following requirements:

- In accordance with the functional requirement for robustness to failure of any single component.

- HVAC systems shall be designed to prevent condensation due to internal humidity conditions. In the event of a BESS shutdown where HVAC is deactivated (including for extended periods), design measures shall be included to prevent condensation occurring.

- Maintain warranty:

  - The HVAC system, operating in conjunction with the PPC and BMS, shall not allow any batteries to operate outside the allowed battery room temperature range (temperature range within which batteries can operate at rated power with no warranty reduction) for any site conditions.

  - The passive design of the BESS must consider HVAC failures, and taking into consideration the function of the PPC and BMS to de-rate or shutdown the BESS in any conditions, must ensure that the batteries do not exist in standby or off mode at temperatures outside their warranted temperature range for those states, for any site conditions.

  - In the event of a containerised solution, with split system reverse cycle air-conditioning for the whole container, the air conditioner must be an industrial quality with partial redundancy such that failure of any component will result in de-rating of the heat load capacity for that container by not more than 40%.

  - Any event of any battery experiencing temperature or humidity conditions that reduce OEM Energy Storage warranty by more than 1%, or void the OEM Energy Storage warranty for that battery will require the Contractor to replace that battery module.

- To meet the Availability Guarantee. For the purposes of the Availability Guarantee, any HVAC fault is considered a Failure of the component(s) of the BESS served by that HVAC unit, except in the above case for a containerised solution with split system reverse cycle air-conditioning, in which case the derated power may count toward the Availability Guarantee.

- The HVAC system, in conjunction with the fire management system, must be robust to external smoke so as not to create spurious alarms.

- O&M plan must show compliance with ISO 5149, including consideration of requirements for replacement of coolant while achieving low maintenance costs

- Any working fluids must be shown to be compliant with Ozone Protection and Synthetic Greenhouse Gas Management Regulations 1995

Additionally, as part of its design, the Contractor shall demonstrate the suitability of the HVAC system by:

- Providing comprehensive HVAC design and modelling.

- By reference to an existing system of the same or very similar design, provide test data to demonstrate that actual performance matches with design / modelling, including for extremes of Site Conditions.

- Demonstrate that any failures in the HVAC system can be rectified by site operators, using the provided tools, manuals, and spare parts.

## Miscellaneous requirements

| Item | Requirement |
| --- | --- |
| - Power station access | BESS must not interfere with or reduce access to other nearby equipment or buildings. Refinement of the layout will occur during detailed design. |
| - Security | The BESS will be able to be secured against unauthorised access. Doors shall be lockable using a common key (no padlocks). |
| - Noise | Outdoor noise: < 80 dBA to 2 m. |
| - Materials | Presence of all hazardous material must be clearly documented. The BESS shall be configured to prevent personal contact of hazardous material or environmental contamination due to hazardous materials. The BESS will include appropriate first aid equipment for contact with hazardous materials. All hazardous material shall have a clear documented method of safe disposal. |
| - Fabrication | Designs shall eliminate any requirements for on-site fabrication and welding. |
| - External colour | The external colour of the BESS shall be agreed with the Employer, taking into account that managing solar heat gain in accordance with the BESS design shall be the overriding factor. |
| - Signage | Safety signage shall be installed in accordance with relevant local, IEC or ISO standards. |
| - Branding | Any branding applied to the BESS or its surroundings requires approval by the Employer. Generally, low profile branding only to identify the supplier / manufacturer of the BESS will be acceptable. |
| - Height | The height of the BESS is not to exceed 4.5 m above ground level |
| - Emergency stop | Hard wired and fail-safe emergency stops must be included. |
| - Internet and cloud services | Contractor must provide internet connection for the BESS, in coordination with utility security procedures and access. The BESS must operate with full functionality without any internet connection or cloud based data services. |

## Human machine interface

The BESS shall have a physical HMI located within the BESS envelope in a position where is it safe to use while the BESS is in operation. The HMI shall also be available (remote access) on a supplied PC installed in the power station control room.

The BESS HMI must be configured so that the Employer can operate, control and interrogate the BESS at the BESS location (i.e. locally). This includes:

- Displaying all detailed alarms

- Displaying BESS system data suitable for operation and fault finding

- Locally controlling the BESS, such as providing charge and discharge set points

- Locally enter BESS operation modes, such as charge to a target SOC, charge to a string target voltage and cell state of heath checks.

- Setting configurable parameters, such as adjusting ramp rates

- Providing detailed performance and system data logs

The Contractor will provide remote access to the HMI at a separate PC located in the power station control centre.

## Operation and maintenance

The BESS should be designed to allow for safe and easy maintenance. This should be achieved through adherence to the following principles:

- Major equipment of the BESS must have plug-and-play capability, allowing for replacement of faulty components by following O&M manuals and without requiring onerous removal of other components for access. It is essential that nearly all maintenance tasks are undertaken without complex procedures, reprogramming, specialist skills or high risk activities. Except in rare circumstances, all components must be replaceable through a standard procedure of shut-down, isolation, disconnection, removal, replacement, reconnection, removal of isolation and start-up.

- As much as possible, the requirement for on-site high level technical expertise should be limited. Maintenance processes must designed for completion by local staff with appropriate training.

- The BESS should have the capacity to identify all potential warning and fault events and communicate these to Employer SCADA in a standard format over the communications interface and local HMI.

- Troubleshooting and fault rectification processes must be clearly laid out in system operation and maintenance manuals.

- Complete and comprehensive labelling of all electrical components, wiring, and connections to be provided in English, for ready reference to system schematics and electrical drawings. All labels shall be permanent (not stickers).

- Comprehensively support isolation and ‘lock and tag’ procedures.

- Appropriate lockable isolation points for all sources of energy.

The BESS, including all sub-systems and components, will present relevant information concerning system status, operation mode and fault events in a format that is well labelled, in English, and is clear and easy to read and interpret by local operators. The BESS shall allow sufficient local operator control for O&M works. This is in addition to SCADA interfaces. All HMI will be located so that it is safe to use and sufficiently accessible for its role.

## Spares and tools

Sufficient spare parts shall be supplied for operation of the BESS for the period as required in the Contract.

The Contractor will locally hold a quantity of additional spares during commissioning. These will be selected to prevent long delays during commissioning.

All supplied spare parts shall be of same material / workmanship and interchangeable with the corresponding parts of the executed work, protected against corrosion, have identification labels and marked ‘Approved’. Provision shall be made within the BESS enclosure (or a suitable, separate enclosure provided by the Contractor) to store any spare parts that require a controlled environment for adequate longevity, such as spare cell modules.

Supplied tools shall be of high quality and fit for purpose. The following tools shall be supplied:

- All tools and accessories required for maintenance of the system

- Any customary and special tools, as well as auxiliary devices

- Special tools designed and supplied for the project.

Supplied tools can be used by the Contractor during installation and commissioning, however they must be handed over to the Employer in good working condition with minimal wear and tear.

The Contractor must provide sufficient information so that the Employer can order replacement parts for the BESS as required. Supplied spare parts and tools shall be listed in detail, including, manufacturer, model, part number, stockist, present cost and typical lead time during the design review stage.

The Contractor or equipment OEM shall continually hold, for not less than 10 years, all spares that may be required to repair the BESS.

If spare parts become discontinued then, at that time and to the maximum extent practical, the Contractor shall either inform of a compatible replacement product or freely release the item’s design detail under irrevocable licence to Employer so that Employer can have the item(s) fabricated as needed.

## Fire safety

Fire safety requirements are included in Section 11. Contractor shall consider individual site characteristics as part of its fire safety risk assessment and mitigations.

# Performance requirements

## Metering point

Metering points must be included at the medium and low voltage side of the BESS transformer.

The medium voltage metering point (MV Metering Point) is required to support operation of the BESS, including provision of relevant data to the grid operator.

The low voltage metering point (LV Metering Point) is to be used for measuring and reporting BESS performance against the Performance requirements.

Meter specifications are as specified in Part A – General and Electrical.

## Power

Active, reactive, and apparent power of the BESS must meet the requirements of this section. Requirements are specified for Rated Power (Continuous operation while the BESS is within its SOC limits), 120% overload for a duration of 60 s, and 140% overload for a duration of 1 s. The requirements are shown in the following diagram.

Figure 3 - Power requirements

Table 1- Power requirements

| Duration | Requirement |
| --- | --- |
| Continuous (Rated Power) | Must provide specified Rated Power (as specified per island) as apparent power. That is, the Rated Power (kW) must be available as apparent Power (kVA) for any power factor. |
| 60 s | 1.2 x Continuous capability in all quadrants |
| 1 s | 1.4 x Continuous capability in all quadrants, except that real power need not exceed 60s requirement |

Additionally:

- Continuous power must always be available while the BESS is within SoC limits, even following overloads.

- Overload power must always be available and be maintained for at least the set time limit, unless there has been a separate overload within the previous 10 minutes.

  - Access to intermediate overloads should be offered if supported by the proposed equipment

- Fault current capability must be equal to or greater than the 1 s overload requirement.

### Operation of the frequency droop curve

In Grid Forming – Droop mode, the BESS must implement a frequency droop curve as per the following figure:

Figure 4 Operation of the frequency droop curve

### Operation of the voltage droop curve

In Grid Forming – Droop mode, the BESS must implement a voltage droop curve as per the following figure:

Figure 5 Operation of the voltage droop curve

### Response time

Rate of change of active or reactive power up to +/-100 MW/s and +/-100 MVA/s shall be available.

Step load acceptance response must stabilise within 50 ms.

Response to external set-point change must stabilise within 1 s.

## Power System models

The Contractor must supply a PowerFactory dynamic model of the BESS to the Employer that may be used in future modelling of the power system. Where the Employer has existing network power systems models available, the Contractor shall integrate the BESS model into these network models.

If required, the Contractor must also supply a PSCAD model of the BESS.

Models must be fully documented.

## Energy storage

Rated Energy Storage must meet or exceed the value specified in the Functional Guarantee for Rated Energy Storage

Initial Actual Energy Storage must be at least the Rated Energy Storage.

## Roundtrip efficiency

Shall meet or exceed the value specified in the Functional Guarantee for roundtrip efficiency.

## Transitions

To avoid destabilising the grid, the BESS must implement gradual transitions of active power in relevant situations, which may include:

- Standby command

- Shutdown command

- Loss of communications

Details of the scenarios, transition rate, and final state shall be determined during design in consultation with grid operators. This will also include determination of the state in which to resume operations following a condition causing a transition.

## Frequency withstand capability

Under frequency variations, the BESS must remain connected and fully operational for duration as shown in the following table (minor variations to step points are acceptable).

| Frequency | Duration (s) |
| --- | --- |
| f >55 | Instantaneous disconnection |
| 54< f ≤ 55 | 1 |
| 52 < f ≤ 54 | 20 |
| 51 < f ≤ 52 | 180 |
| 49≤ f ≤ 51 | Continuous |
| 49< f ≤ 47.5 | 180 |
| 47.5< f ≤ 46 | 30 seconds |
| 46< f ≤ 45 | 1 second |
| f < 45 | Instantaneous disconnection |

Ride through settings must be configurable in at least six bands between 45 Hz and 55 Hz.

If default capability of equipment exceeds this requirement, the default capability must be maintained and accessible to the Employer without restriction.

### Voltage withstand capability

For fault events, the BESS must remain connected and fully operational for duration as shown in the following table (minor variations in step points are acceptable):

| Voltage (p.u.) | Duration (s) |
| --- | --- |
| V>1.3 | Instantaneous disconnection |
| 1.15≤ V ≤ 1.2 | 0.2 |
| 1.12≤ V ≤ 1.15 | 70 |
| 0.85≤ V ≤ 1.12 | Continuous |
| 0.75< V ≤ 0.85 | 70 |
| 0.65< V ≤ 0.75 | 15 |
| 0.45< V ≤ 0.65 | 2 |
| 0.25< V ≤ 0.45 | 0.8 |
| V ≤ 0.25 | 0.15 |

If default capability of equipment exceeds this requirement the default capability must be maintained and accessible to the Employer without restriction.

Ride through settings must be configurable within the above requirements.

## Power quality

The BESS shall comply with IEEE Std. 519-2014 limits for current and voltage emissions at the point of connection. In particular, the following limits apply:

| Order Range (odd harmonics) | 3 ≤ h <11 | 11≤ h < 17 | 17 ≤ h < 23 | 23 ≤ h < 35 | 35 ≤ h ≤ 50 | TDD |
| --- | --- | --- | --- | --- | --- | --- |
| Percent of BESS Nominal Current (IL) | 4.00% | 2.00% | 1.50% | 0.60% | 0.30% | 5.00% |

As part of the required power systems studies under Part A – general and electrical, Contractor must ensure that the harmonic characteristics of the inverter are compatible with other generators and site loads.

## Self-discharge

Self-discharge must be a no more than 5 % of storage capacity discharged per month.

# Equipment Requirements

## Compatibility

Contractor must provide written statements of compatibility from both the OEM of the Battery modules and the OEM of the PCU, referencing the proposed design capacities and interface, to confirm compatibility under all proposed operating conditions and functions.

## Battery modules

Battery modules, their racking systems, enclosures must comply with the standards. Certifications must be provided for (at a minimum):

- UL9450A (as part of demonstrating compliance with IEC 62933-5.2)

- IEC 62619

- IEC 61000-6-2 (safety systems to IEC 61000-6-7)

- IEC 62281

## Power conversion units

The power conversion units (PCUs) shall convert DC power from the battery modules array to AC power at the required connection voltage. The PCU shall incorporate central inverter, step-up transformer, and switchgear for protection and isolation.

PCUs shall meet the following requirements:

- Utilise a standard, modular, industrial PCU product with proven track record in the US or Europe.

- Meet the requirements of IEC 61000-6-2 (safety systems to IEC 61000-6-7)

- Be suitable for outdoor operation in the site conditions. Temperature de-rating, if applicable, shall be considered in the Energy Model.

- Include overvoltage AC and DC surge protection devices.

- Include SCADA and communications.

- Include fire detection and alarm systems, integrated with the SCADA.

- Include auxiliary power for all PCU functions, as well as local ancillary loads such as lighting and met station. Auxiliary transformers shall meet the requirement of IEC 60076.1 and rated for maximum design loads.

- IP45 (or better) general power outlet (GPO) for small loads.

- Integrate earthing with the overall plant earth grid

- Include safety inter-tripping and inter-locking to ensure safe operation and access to HV Equipment.

- Include any bunding requirements for transformer(s).

- Contain a UPS backup system to maintain system critical functions for at least 2 hours. Critical functions including:

- All sensors and communications equipment

- Protection and switchgear

### Inverters

Inverters shall convert DC to AC power and provide the required safety and grid support functionality. Inverters shall:

- Meet the requirements of IEC 62477.

- Be rated to IP65 (minimum).

- Include integrated current, voltage and fault monitoring at DC input terminals.

- Include an AC side automatic and remotely operable circuit breaker to protect and isolate the Inverter.

- Include lockable disconnect switch for main DC power to facilitate maintenance.

- Have peak efficiency shall be greater than 96%, and greater than 93% at rated output.

- Be capable of external control and automatic grid support functions as described in this specification.

- Shall use MODBUS TCP communications or similar Ethernet connections compatible with the selected SCADA.

- Have an earthing system compatible with the existing infrastructure earthing design, and integrated into the overall site earth grid design.

### Transformers

Step up transformers for the BESS plant shall be in accordance with Part A – General and Electrical.

### Switchgear

Switchgear for the BESS plant shall be in accordance with Part A – General and Electrical.

# Environmental risk

The Contractor will be required to demonstrate that the BESS has been subject to a lifecycle environmental risk assessment, and mitigations applied to minimise harm to the environment. As a minimum, “Guidelines for issues from the EES system to the environment” under IEC62933-4 shall be addressed.

Additionally, the Contractor will be required to demonstrate readily available disposal and/or recycling facilities for hazardous materials components of the BESS. Such facilities must be certified as fully compliant with international standards for environmental management ISO 14000. The plan must show that multiple disposal facilities are readily accessible and offer certification that they will accept the proposed BESS battery modules.

# Safety and risk mitigation requirements

The BESS must be able to demonstrate substantial conformance with requirements of IEC 62933-5.2.

Under IEC 62933-5.2, the following categorisation shall be used:

- POC voltage: V-H (High: V > 1 kV AC or 1,5 kV DC)

- Energy Capacity: E-L (Not small: E > 20kWh)

- Site Occupancy: S-O (Occupied site)

- Chemistry: C-A (BESS using non-aqueous electrolyte battery (e.g. Li-based)

### Fire and explosion

The BESS will operate in a remote location with very high reliability requirements. Any fire or explosion is likely to have severe consequences for site operations. Best practice mitigation measures must be implemented in respect of these risks.

## Additional requirements

In addition to requirements under IEC 62933-5.2, the following requirements must be met.

| - Faults | The BESS shall detect and isolate all credible faults or hazardous conditions that may affect safety, security or result in asset damage. The BESS shall activate any internal systems that are intended to reduce severity (e.g. fire suppression). |
| --- | --- |
| - Protection response | The BESS must detect and isolate all credible faults or hazardous conditions that may affect safety, security or result in asset damage. The BESS shall activate any internal systems that are intended to reduce severity (e.g. fire suppression). Internal faults should be isolated as close as practical to the affected equipment so that the BESS will still operate without interruption at a reduced capacity if safe to do so (i.e. if a string has a fault, then it is isolated and the BESS continues with the remaining strings). Unpredictable BESS operation will cause power system instability and has considerable potential to cause the entire power system to fail (e.g. black out). |
|  | The BESS must be configured so that if an error with the BESS is developing (e.g. equipment over-temperature) the BESS shall notify the power station controller so that the power station controller can command the BESS to idle (i.e. zero charge and discharge) after it has activated additional equipment to ensure the power system will remain stable. This will typically occur within 60 seconds. |
|  | - If an error occurs that does not have an immediate risk to safety or plant (e.g. power station controller communication loss) then the BESS will: - Send the appropriate fault code to the power station; - Override the power station controller and ramp down in a controlled manner; and - Disconnect, shut down or remain at idle as appropriate. - The ramp rate will be configurable across a wide range. |
|  | - In rare circumstances the BESS may have a fault that requires it to trip immediately for safety or to protect plant (e.g. e-stop). In these cases the BESS shall: - Disconnect or shut down as rapidly as possible; and - Send the appropriate fault code to the power station. |
| - Fail safe | The BESS design must guarantee safe controlled shutdown (or revert to a safe passive mode if agreed with the Employer) if, without warning, communications to the power station is disconnected or becomes unresponsive or there is a major power system fault such as complete power system outage and loss of all electrical supply. The BESS must be capable of automated restart once communications are restored (subject to restart procedures). |
| - Uninterruptable power supply (UPS) | The BESS must be configured and have sufficient UPS to achieve safe and controlled shutdown from when any supply or electrical connection is lost. The UPS size will be sufficient to ensure the BESS can restart in a controlled and safe manner, such that no operator intervention is required, for at least 30 minutes since the major fault if external power is not restored. This includes preventing PLC signals that may unnecessarily trip power system circuit breakers or other undesirable actions. The UPS shall automatically reconnect to the external power supply when the supply is re-activated. This includes when power is solely supplied by the power station backup diesel generator. |
| - Surge arrestor | The BESS must include a surge arrestor between the DC accumulator and inputs of the inverter (unless |
| - Local circuit breaker | The BESS shall include electrical protection in the form of circuit breakers on the low voltage side of the transformer suitable for BESS self-protection and isolation. The BESS shall be capable of remote operation of the local circuit breaker, for both connection and disconnection. Remote operation shall include operation via a command issued from the Employer SCADA, and operation via a manual start / stop button (with e-stop capability) located at the BESS site (but away from the immediate location of the local circuit breaker). |

# Inspection and testing

## Factory acceptance tests (FAT)

The BESS shall be subjected to a comprehensive Factory Acceptance Test (FAT) before it is delivered to site. Dispatch from factory (to site) shall not occur until a FAT is completed, a report is submitted and approved by the Employer, and the Employer is satisfied that the testing demonstrates compliance with this Specification.

Substitution of equipment for testing (such as type testing) may be allowed, but only if the Contractor has adequately demonstrated that the Employer’s intent for FAT is met. If this is offered, the Employer must be satisfied with all FAT departures, the rigor of their justification and the completeness of the tender response. Type testing will be subject to provision of an independent certification for quality assurance. Supplied BESS must be from the same factory and assembly line, and using the same bill of materials as the certified type testing.

Where more than one BESS modular unit is to be grouped together on an island, the FAT must demonstrate parallel operation of two or more BESS modular units under control of a plant controller.

## Site acceptance tests (SAT)

The Employer requires SAT of the complete BESS. Tests may occur during pre-commissioning, commissioning and functional guarantee test period as appropriate and agreed.

The tender response must include a method statement for SAT, including concept inspection test plans (ITP).

The Contractor will provide detailed inspection test plans (ITPs) for the Employer to review during detailed design. ITPs must include consideration of the limitations of the power system and associated risks. The Contractor will perform additional tests that the Employer requests where they are reasonable. The Employer will reject ITPs that do not comprehensively prove the capability of the BESS against the Employer Requirements, or introduce undue risks to the power station or continuity of power supply. SAT must not proceed until all ITPs are agreed.

The scope of the SAT shall be sufficient to:

- Ensure that the equipment was not damaged in transit

- Ensure that the equipment was installed correctly

- Complete tests against the Employer Requirements

- Observe correct BESS operation at the power station for its intended purpose

The Contractor will have sufficient supervision and technical experience on site during SAT to undertake works and to rapidly overcome BESS equipment faults, documentation errors and miscommunications.

The Contractor should demonstrate a plan that addresses the following limitations of the hybrid mini-grids when compiling the SAT ITP:

- BESS charge and discharge rates are limited by the capacity of the power station. High power commands and commands that require rapid changes in power will cause unacceptable power system instability.

- The power station must be specially configured to prevent instability during specific tests. Factors such as renewable energy generation and system load may prevent appropriate configurations from time to time.

- Most BESS operations are large enough to change the dynamics of the power station that can affect the validity of many tests.

- Local manufacturing facilities are limited.

- Delivery of equipment can be time consuming.

- Assembling the required specialised personnel can be difficult at remote sites. Significant delay and cost can be incurred if the equipment does not function as intended in the agreed timeframes.

Interruptions to normal operations of the grid shall be minimised, and not more than 8 hours during connection. Testing shall be planned for times that least disrupt customers.

# Warranty requirements

Warranties for BESS modular units should have the following features:

- Clearly state all usage limitations. These may include:

  - Maximum energy throughput

  - Calendar life

  - Maximum number of power overloads

  - Time at various SOC

- Be immune to any inadequate BESS design (as observed during defects liability period)

- Be robust to the full range of usage profiles that the BESS may be subject to

- Warrant that:

  - Power capability will not reduce

  - Minimum discharge capacity for end of life will be met

  - Fewer than 10 % of cells may be replaced before end of Expected Service Life

- Provide for complete replacement of faulty equipment, such that the BESS can continue to operate as designed for at least the remainder of warranty period

- Include shipping, installation and testing costs, with minimal use of Employer labour.

# Guarantee tests

Each of the BESS Functional Guarantees shall be tested using the relevant method from IEC 62933-2. Continuous Power, Energy Storage, and Round-Trip Efficiency shall be tested as a pre-requisite for Completion.

Service life shall be determined by a repeat of the Energy Storage Test after 1 year of operation, and shall not exceed the BESS battery warranty period. To calculate Service life, ratio of Energy Storage to the energy storage degradation curve provided with the contractor’s bid at completion and after year 1 of operation shall be linearly extrapolated over time. The time at which the product of this ratio and the corresponding energy storage degradation curve provided with the contractor’s bid no longer meets the Functional Guarantee is the expected service life. An example is shown below:

In the event of underperformance of the service life guarantee, Contractor may retest after 2 years operation (at its cost) and recalculate expected service life using the same approach. An example is shown below:

Measurement tolerance for each of the tests is 1% (of the measured parameter).

Availability is calculated as the percentage of time where the BESS is able to meet all Employer Requirements. To allow for short term part performance, the system shall be deemed to be available if, and only if:

- Rate of charge / discharge > 80% required level

- Energy storage > 80% required level

Availability will be determined by BESS self-reporting status, except in cases where this is shown to be inaccurate (either determined through performance tests or operational data) and averaged over each 365 day period following Completion. If compliance with warranty conditions requires idle time for the BESS, the BESS is considered not Available for this period.

Functional guarantee levels and liquidated damages payable per island are as specified in the Employer Requirements.

In the event of underperformance, Contractor may make adjustments and retest (at its cost). Any new result will be applied subsequent to the retest only for the purposes of calculating liquated damages. Retest will not be grounds for extension of time.

# Appendix C – Energy Management System (EMS) requirements

# Relationship to other parts of the Employer Requirements

This part of the Employer Requirements (Appendix C – EMS requirements), provides key technical requirements for the EMS required under this project. It shall be read in conjunction with other parts of the Employer’s Requirements. All parts of the Employer’s Requirements are applicable to EMS equipment and shall not be read in isolation.

In particular, note:

- Employer Requirements:

  - This document provides the necessary overview information on the project scope and general requirements. It also includes summary information on the island specific capacities and requirements.

- Appendix A –General and Electrical:

  - This document provides details of the electrical standards and equipment requirements that the Plant must meet.

- Appendix B –Battery Energy Storage System (BESS):

  - This document provides key technical and functional requirements of the Battery Energy Storage System (BESS).

- Appendix D –Operations and Maintenance requirements:

  - This document provides details of the support that Contractors are required to provide for the electrical standards and equipment requirements that the Plant must meet.

- Appendix E –Project Site Specific Details:

  - This document provides details of the requirements at each site. It includes site descriptions and data, capacity requirements, details on existing equipment and infrastructure, details of the point(s) of connection, and other related information for each island.

- Appendix F – Environmental and Social Requirements:

  - This appendix provides the environmental social safeguards requirements and reference is made to relevant safeguards documents of the project

# Intended Purpose

The purpose of the Energy Management System (EMS) is to issue schedule, dispatch, and operating mode instructions to the electricity generating subsystems (thermal plant, solar PV plant, and BESS). The instructions must ensure that system safety requirements, reliability, and power quality requirements are maintained, while minimising use of fuel (diesel), minimising generator run-time and starts.

The EMS must:

- Operate proven and configurable algorithms demonstrating reliable operation of hybrid energy systems of a similar scale, and providing for optimal dispatch of solar PV, BESS, and diesel generation to minimize cost of energy. Capabilities should include:

  - Capability to adapt BESS SoC limits when load shifting to ensure full grid support functionality at all times

  - Ability to control BESS and solar PV plant under all their intended control modes.

  - Capability to adapt to different configurations of thermal generators (including outages for maintenance) while ensuring redundancy requirements are met.

  - Capability to curtail solar and change solar PV voltage support settings based on grid state

  - Capability to use real-time local irradiance data to estimate capacity of curtailed solar PV and utilize this in dynamically allocating spinning reserve.

  - Provision for accommodating typical response times of connected generators to dispatch commands, including start-up of additional thermal generators

  - User configurable (tuneable) settings for inputs to dynamic spinning reserve calculation, ramp times, delays, limits, and conditions for state transition.

- Be operable as a stand-alone system, even when the BESS or solar PV is off-line for maintenance.

- Be separable, such that the existing thermal power plant can continue to operate if the EMS is off-line.

- Use Modbus TCP communications and fibre optic connections

- Be capable of integrating with Deep Sea diesel generator controllers, which FENAKA currently uses to control the diesel generators

- Be capable of interfacing with solar PV plant with SunSpec protocols, and associated switchgear

- Be capable of interfacing with existing centralized SCADA

- Be capable of interfacing with remote equipment via optic fiber or 4G communications

- Be capable of interfacing with other BESS and micro-grid controllers operating in the network (subject to above expectations on interface and communications, and cooperation of the supplier / operator of that equipment); may require definition of a response profile for management of that other equipment

- Include a HMI, with remote web access capability, also accessible on the power station operator workstation

- Provide expansion capability to add or reconfigure BESS, solar PV, or thermal generators over the EMS life (up to 100% of initial connections as spare)

- The EMS must provide flexibility for future upgrade requirements. Future upgrade requirements may include addition of new generators or configuration changes in the network, or adopting improvements in available EMS software. EMS vendor will be required to offer product support and support for such requirements (which may include remote support and site visits if needed). EMS vendor will be required to provide fully documented open source code on standard industrial hardware, or other provision to ensure the EMS is not stranded / left unsupported under any circumstance.

## Operation

The EMS is intended to be a PLC based dispatch style controller, issuing instructions and updating data input typically on a time scale of 0.2-2s. Response from each sub-system to EMS commands is expected on a similar time scale (except for start of off-line thermal generators, for which approximately 300 s should be allowed). The EMS is not expected to act as a low-level unit controller (operating at millisecond time scale to balance load or respond to system dynamic events) – these functions are expected to be autonomously performed by the subsystems. The EMS and subsystems should be designed and selected accordingly.

For example, following a thermal generator trip event, the BESS autonomous controller would instantly provide frequency support, exporting active power to compensate. Meanwhile, the EMS would register this event, monitor BESS SoC, adjust curtailment limits on solar PV, and ensure another thermal generator is started (or potentially forecast planned load shedding).

The hybrid system is intended to operate primarily as a thermal generation plant supplemented by solar PV energy and BESS grid support. It is intended that the system will not operate without thermal generation, and that the thermal generation will always operate as the isochronous unit. The EMS should be designed on this basis. However:

- The EMS should also support (prevent disruption of) operations that do not require the BESS and solar PV plant, including black start (ensuring compatible setting of solar PV and BESS state, mode, or other requirement, including their respective switchgear, and communicating status with the thermal system)

- The EMS shall be configurable to operate in a zero diesel scenario (100% renewables), despite not being the expected normal operation mode.

## Robustness to failure

The EMS must utilise high quality, industrial standard equipment including PLCs in compliance with IEC 61131 (or similar with higher quality – to be approved by the employer). Power supplies, cabinets, cables, connections, switches etc. must also be specified for low failure rates and continuous operation for the design life.

The EMS is not strictly required to have dual redundancy (2N), unless deemed necessary by the Contractor to meet these specifications. The EMS and subsystem control must, however, implement failsafe actions to ensure controlled and conservative response to all plausible failure modes, including of the EMS.

## Compatibility for future operations

Open source code for all software shall be utilised wherever this option is available. Open source code shall be provided as a deliverable, including documentation.

If proprietary software is utilised, then in the event that an OEM is unable to meet the required commitment to support any proprietary software needed for operations, then this software must be made available to the Employer in a standard, usable, source code form with documentation such software. Provision to meet this requirement through a third party shall be made in advance (prior to Completion) in the event OEM is unavailable to release software.

Contractor shall minimize variation in EMS equipment, software, and configuration across all installations, for ease of operations and maintenance for FENAKA and their staff.

# Scope of work

The Contractor has single responsible for delivery of the operational EMS. This includes the design, documentation, certification, supply, delivery, installation, testing and commissioning of an EMS, including all associated balance of plant, meeting the functional requirements of this specification.

The scope shall also include training and capacity building of local staff to operate and maintain the system as well as provide warranties for equipment and workmanship and performance guarantees and defects liability for the complete system as a whole.

The works shall include but not be limited to the following:

- Design of the EMS

- Supply and installation of EMS including:

  - PLC(s)

  - Software packages to allow plant operators to interrogate (and troubleshoot) the system

  - Racking and cabinets

  - Power supply converters

  - Cables and communications and media converters as required

    - All local communications at the power station, including any supporting infrastructure such as power supplies, cabinets, etc. are the responsibility of the Contractor

    - Communications to remote solar PV plants will be via fibre optic cables, with backup radio communications to a single interface switch and will be provided by others. Contractor is responsible for interfacing to this communications infrastructure.

  - Configuration settings and application backup (in native file format)

- Supply and installation of any required structures, footings, cable management

- All system lightning and surge protection as required.

- All system earthing and equipotential bonding as required, including interface to existing earth grids as relevant.

- Co-ordination with the site owner for access and coordination of activities.

- Co-ordination and liaison with the Employer’s Representative and Owner’s Engineer at the outset and throughout the entirety project.

- Submission of documentation as per the documentation deliverables list.

- Provide training and capacity building of local staff in the operation, maintenance and safety of the system.

- Installation of all required temporary facilities.

- Supply of all required spares as per the contract, including storage cabinet or equivalent.

- Supply of a full set of tools required for the maintenance and operation of the system.

- Ensuring compatibility with existing equipment and other plant supplied by the Contractor – especially ensuring that the existing controllers, meters and subsystems are also compatible with the procured equipment.

- Assess data available from existing plant (diesel generator controller), and ensure that all information required for the effective operation of the EMS is available on the EMS.

# Safety, reliability and power quality requirements

Requirements for safety, reliability and power quality take precedence over requirements to minimise fossil fuel use or thermal generator runtime and starts.

## Safety

The EMS, or associated systems monitored by the EMS, must ensure the following requirements are met for operation of the hybrid power system:

- All sub-system protections and safety systems not compromised or conflicted

- Safety interlock system for switching, operation, or shutdown of subsystems

- Provision for operator initiated controlled and emergency shutdown

- Provision for safe operation of the EMS, remotely or locally, at any time

- Inclusion of failsafe automatic response where required for various fault scenarios.

## Reliability

The required system to remain operational under the following contingency events:

- Loss of any single operational generator (single thermal generator, solar PV plant, BESS)

- Loss of any single feeder

- 80% reduction or increase in solar PV plant output (relative to rated AC capacity) within 10 s

  - Note that if curtailed below rated AC capacity, proportionally less change applies

- 20% variation in load within 10 s

Each event shall be considered in isolation, however:

- System shall be restored and able to respond to a subsequent contingency event within 300 s

- In the 300 s immediately following the loss of any single thermal generator, reliability should be maintained with variation in solar PV output of up to 40% (reduced proportionally if solar PV plant output is constrained) or rated AC capacity and 10% of load

Inter-trip operations are not normally expected as part of the EMS, but may be required to be implemented in conjunction with the EMS if required to meet these requirements (for example, trip of a large solar plant if the BESS trips when charging)

It may be assumed that:

- An offline thermal generator is available at any time and can be started and fully operational within 300 s.

- Minimum load of the thermal generators is 30% rated capacity. Short term lower load may be possible subject to negotiation with Employer and may require subsequent heat run or other mitigation.

- The generators can accept or reject loads (step change) up to 30% of their available capacity each (within the range between minimum load and rated capacity).

- The Employer’s SCADA shall act primarily as a remote data access and monitoring system and shall not be relied on for functionality of the island system.

## Power quality requirements

Power quality requirements are generally met by the subsystem requirements. The EMS will, however, be required to set the operating mode of subsystems (e.g. voltage control by solar PV plant) if required for different operating states or conditions. Preferred operating modes are to be determined by the Contractor as part of the system studies required under Appendix A – General and Electrical.

# System states

The EMS must demonstrate maintenance of the required system safety, reliability and power quality under plausible system states, transitions between system states, and failure modes.

System states shall include (at least):

| State | Diesel generators | Solar PV Plant | BESS | Load | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | ON | ON | ON | ON |  |
| 2 | ON | OFF / NIGHT | ON | ON |  |
| 3 | ON | ON | OFF | ON |  |
| 4 | ON | OFF / NIGHT | OFF | ON |  |
| 5 | OFF | ON / OFF | ON | ON | Selectable options for: A) BESS transitions to isochronous mode and forms grid with diesel generators off B) Support safe shutdown |
| 6 | OFF | ON / OFF | OFF | ON | Support safe shutdown |
| 6 | ON | ON / OFF | ON / OFF | OFF | Support safe shutdown |
| 7 | OFF | OFF | OFF | OFF | Support thermal system to undertake safe black-start (BESS not required for black-start; EMS to ensure no disruption and planned handover). |

Where necessary, sub-states may be used to reflect different load conditions, BESS SoC, or different solar resource conditions / forecast.

Under each system state, additional sub-states for failure modes shall be considered. During a failure mode, the intended purpose shall be adhered to the extent possible. Failure modes shall include:

- Action on loss of communications:

  - Specific actions shall be considered for each communication pathway that may experience a loss of communications.

  - Any associated / required automatic response at the subsystem side experiencing loss of communications must be included in the design of the relevant subsystem and made fail-safe.

- Action on subsystem alarm or partial functionality:

  - Alarm response to be consistent with sub-system design for safe operation.

  - To the extent practical, partial functionality shall be dealt with by proportionally reducing contribution of the hybrid sub-systems to the thermal plant operation. Where this is not practical, shutdown of hybrid subsystems may be required.

Typical action in a failure situation, or in any State other than State 1, may include:

- Increase / decrease online thermal generation (by diesel master controller if thermal plant trip)

- Reduce system variability by curtailing solar PV plant

- Alter operating mode and grid support functionality of part of the system

- Altering the BESS SoC target and normal operating limits

- Controlled shutdown of part / all of the system (note that an under-frequency load shedding scheme is in-place)

Actions on failure modes and state transitions shall be fully described in a cause and effect matrix and/or state diagram.

# Performance requirements

Within the constraints of safety, reliability, and power quality, the EMS must act to minimise:

- the use of fuel within the thermal power station

- the combined run-time of thermal generators

- the number of thermal generator starts

The first two performance requirements are considered to be generally compatible. However, the third requirement is not generally compatible – more starts (and stops) of thermal generators can reduce fuel use and run-time. Therefore the Contractor shall adopt an approach that provides flexibility in setting of parameters to tune the system for optimal site performance according to the Employer’s priorities which may vary from time to time.

Generally, the performance objectives require:

- Maximise solar PV plant generation directly used by the load (without storage)

- Store excess solar PV plant generation

- Utilise curtailed solar PV as part of instantaneous spinning reserve

- Manage BESS SoC within designated target ranges to:

  - Reduce number of diesel  generators on-line

  - Avoid diesel generator stop or start for potentially transient conditions

- Run diesel generators for a minimum time (typically 1 hour) after starting

The EMS should have the capability to adopt situational profiles that reflect different system states or other conditions.

## Ramp rate control

The BESS is required to include the capability for ramp rate control for solar smoothing. Ramp rate control will typically only be required to be used if:

- Thermal generator ramping in response to solar PV ramping introduces maintenance costs to the Employer, which are less than any corresponding wear of the BESS absorbing the ramping.

To allow for this case, the solar PV meter data (active power) shall be available to the BESS to use a signal on which to base its ramp response. The ramp rate limits used by the BESS shall be configurable via the EMS and may only apply in certain conditions (e.g. low number of thermal generators online).

Notably, if solar ramping exceeds thermal generator capacity for compensatory ramping (technical limit rather than financial impact), the BESS frequency droop response should automatically provide the necessary ramp control.

# Interfaces

## Thermal generation

The existing thermal generation system is currently, and shall continue to be fully operational without the EMS. In the thermal generation system, individual generator unit controllers are coordinated by a Deep Sea Electronics parallel generator master controller (model 8610 or 8810). The master controller interfaces with generator unit controllers, protection relays and other ancillary equipment in the thermal power station. The primary responsibility of the generator master controller is to automate the operation of the thermal generation system, coordinating the starting and stopping of thermal generators according to a set of system measurements, namely the system loads and generation supplying power to the points of connection to the 11kV bus. It also ensures parallel operation of the individual generators, such that they operate as a single isochronous generating unit controlling system frequency and voltage.

The EMS is required to communicate with the master controller to indirectly influence the scheduling of thermal generators by managing the solar PV plant and BESS active power in order to minimise the use of fossil fuel. That is, the EMS will not take on the responsibilities of the generator master controller in directly starting, stopping, or parallel operation of thermal generators. Instead, it will monitor the state of the thermal generation system and loads (and solar PV plant and BESS) and will provide indirect inputs to the generator master controller to achieve the optimal outcome in terms of online generators based on the state of the BESS and solar PV plant parameters.

At its cost, the Contractor is required to engage with the generator master controller OEM to determine and design a robust interface approach, endorsed by the OEM.

Any additional control modules, interfaces, or supplementary equipment needed for the generator master controller to accommodate the EMS interface and control strategy shall be provided by the Contractor, and included in their design (including cabinets, power supply, etc.).

## BESS and Solar PV

Interface and operation of the BESS and solar PV shall be determined by the Contractor.

Typically both operating mode and power / voltage set-point bias should be provided for control (along with system commands such as start / stop or operation of breakers). Monitoring should include all subsystem parameters, alarms, metering data, protection status, met data, state of charge, etc. as applicable.

## Data and parameter lists

The Contractor shall provide full parameter lists for:

- Input data parameters from thermal plant, BESS, solar PV plant or other (e.g. time signal)

- Output data parameters to thermal plant, BESS, solar PV plant or other

- Configurable parameters governing EMS operation

All parameters shall specify:

- Data type

- Units

- Allowable range

Configurable parameters shall also include:

- Nominal values

- Recommended values for non-standard operations if applicable (e.g. system test, conservative contingency operation).

The Contractor shall maintain a data archive on an industrial PC with the EMS (see section ‎0). The Contractor shall also provide all required support to the Employer to configure and test data tables in the Employer’s SCADA, and advise on recommended parameters to archive on the Employer’s historian.

Capability to generate standard reports on warnings and alarms, as well as basic generation summary data shall be available thought the operator workstation.

# Physical and installation requirements

## Design life and workmanship

The Design Life of the EMS must be at least 20 years.

O&M procedures must list all items that may require replacement to achieve this life.

The EMS shall be designed and installed such that all components will remain safe during the design life.

## Installation

The EMS shall be installed in a stand-alone cabinet at the power station. It shall use dedicated equipment that does not require replacement should the BESS reach end of life and be replaced. The EMS shall be accessible at any time, independent of the BESS.

## Equipment

### Local server

The EMS must include an industrial PC within the EMS cabinet to provide local data logging and remote access to help support detailed investigation of system events and adjustment of configuration parameters if required.

Remote access to the industrial PC via internet connection is required.

### Communications

All communications must be Modbus TCP compliant.

All IO modules shall include minimum 50% spare capacity.

### Internet connection

A local internet connection shall be provided by the Contractor for remote access. Employer’s security requirements shall be followed.

### Ingress protection

The EMS cabinet shall be rated for ingress protection (IP) class 65 to IEC 60529.

### Access

EMS cabinet shall be accessible to operations and maintenance personnel without need for PPE or other special equipment (EMS shall not be co-located in DC, LV or MV panel or other location with personnel risk).

All weather access must be available, including any required lighting, platforms, stairs, awnings etc.

Location shall not interfere with access to other equipment or buildings.

EMS cabinet shall be lockable using a common key (no padlock).

### Emergency stop

The EMS cabinet must include a hard wired and fail-safe emergency stop, unless in proximity to BESS or power station emergency stop.

## Human machine interface

The EMS shall have a remote access HMI accessible from operator workstation in the power station control room and external web-interface (meeting Employer’s security requirements).

## Operation and maintenance

The EMS should be designed for minimal maintenance, and safe and easy inspection. This should be achieved through adherence to the following principles:

- Industry standard equipment, hardware, fixings and fittings, cable connections etc. Equipment to have plug-and-play capability, allowing for replacement of faulty components by following O&M manuals. Any fault maintenance must be possible without complex procedures, reprogramming, specialist skills or high risk activities. All components must be replaceable through a standard procedure of shut-down, isolation, disconnection, removal, replacement, reconnection, removal of isolation and start-up.

- As much as possible, the requirement for on-site high level technical expertise should be limited. Maintenance processes must designed for completion by local staff with appropriate training.

- The EMS should have the capacity to identify all potential warning and alarm conditions (including conditions where the subsystems themselves have not experienced a fault or alarm, but where the EMS identifies an increased risk it cannot meet reliability requirements in the short term). Such events shall be communicated to Employer SCADA and local HMI.

- Troubleshooting and fault rectification processes must be clearly laid out in system operation and maintenance manuals.

- Complete and comprehensive labelling of all electrical components, wiring, and connections to be provided in English, for ready reference to system schematics and electrical drawings. All labels shall be permanent (not stickers).

## Spares and tools

Unless a dual redundant configuration is implemented (not required), all key parts (that cannot be readily repaired or replaced within 5 days) of the EMS must have spares provided. Where applicable, spares must be pre-programmed with the same program and parameters as the operational equivalent.

All supplied spare parts shall be of same material / workmanship and interchangeable with the corresponding parts of the executed work, protected against corrosion, have identification labels.

Supplied tools shall be of high quality and fit for purpose. The following tools shall be supplied:

- All tools and accessories required for operation and maintenance of the system, including any special leads, cards, keys, programming devices etc.

Supplied tools can be used by the Contractor during installation and commissioning, however they must be handed over to the Employer in good working condition with minimal wear and tear.

The Contractor must provide sufficient information so that the Employer can order replacement parts for the EMS as required. Supplied spare parts and tools shall be listed in detail, including, manufacturer, model, part number, stockist, present cost and typical lead time during the design review stage.

# Quality management

Quality management requirements are as described in Part A – General and Electrical. Specific requirements for quality control of the EMS are addressed here.

## Inspection and testing

During the design phase, the Contractor is required to provide a comprehensive presentation on the operation of the EMS to the Employer. This shall cover all aspects of the EMS functional description and cause and effect matrix. It shall also demonstrate, using a simulated EMS or demonstration EMS typical operating scenarios and contingency scenarios and EMS response.

### Factory acceptance tests (FAT)

The EMS shall be subjected to a comprehensive bench test (Factory Acceptance Test (FAT)) before it is installed. The bench test shall include simulated or actual elements for each subsystem (thermal generators, solar PV plant and BESS). Any simulated elements must be validated.

Previous ‘type testing’ may be substituted for comprehensive FAT, but a bench-test must still be carried out with selected operating parameters / configuration parameters and sub-system elements to prove site specific suitability prior to installation. In particular, the bench-test should demonstrate:

- Communications with the diesel generator master controller and successful selection (start / stop) of diesel generators.

- Adaption of scheduling to reporting of available diesel generators (for instance if a generator is out of service).

- Communications with the BESS, enabling selection of any available operating mode, issuing set-points, and response to self-reporting status of BESS.

- Communication with solar PV plant utilising Sunspec protocols, issuing curtailment and mode setting commands, and adaption to self-reporting status of solar plant.

- Operation of required interlocks (for example, if manual control of the BESS from the HMI is enabled).

- Transition between operating states.

Testing must demonstrate expected operation (cause and effect) for all operating conditions, warnings and alarms under each system state.

### Inspection and test plan (ITP)

The Contractor will provide a detailed ITP for installation and site testing of the EMS. Installation is expected to be verified by the OEM.

The Contractor shall prepare a comprehensive commissioning plan for the EMS. The commissioning plan shall progressively verify and bring-online control of each interface plant (BESS, diesel generators, solar PV, Employer SCADA) in a safe manner.

During installation, the Contractor will provide all necessary support to the Employer to verify system communications and interface to Employer SCADA.

# Performance test

A comprehensive performance test of the EMS in meeting its performance requirements is generally highly complex and not practical without a system model interrogation against operational data. Therefore, performance tests are to be undertaken on a re-analysis basis. The re-analysis requires:

- Selection of 10 random instants with the system operating in State 1, including both day and night and loads covering at least 80% of the normal range.

- For each instant, list:

  - Safety, Reserve and power quality requirements met

  - Solar PV direct to load

  - Solar PV being stored

  - Stored solar PV to load

  - Solar excess energy

  - Number of thermal generators online, and their average runtime since last start

  - Instantaneous fuel consumption

- Estimate, for the same load but without the hybrid plant installed (thermal only system):

  - Number of thermal generators online, and their average runtime since last start

  - Instantaneous fuel consumption

- Test that they hybrid system provides lower instantaneous fuel consumption, less thermal generators online, and average runtime at least half when compared to the thermal only system. This is intended to provide a coarse check of improved performance.

- Test as follows (using spreadsheet analysis):

  - Vary BESS SoC, Solar curtailment set-point, and number of thermal generators online within their possible ranges using monte-carlo style parameter set

  - Eliminate cases that violate safety, reliability, or power quality requirements

  - Calculate the thermal generator load and estimate fuel consumption for each parameter set

  - Verify that there are no instances where fuel consumption or number of online thermal generators is less than the measured values. A tolerance equal to 10% of the difference between measured fuel consumption and estimated thermal only fuel consumption is allowed.

- In the event the second test is not satisfied, this may be due to prior conditions. Further investigation is allowed to provide a reasonable explanation of prior conditions for sub-optimal instantaneous performance.

The Contractor may propose alternative performance test which the Employer must consider reasonable.

In the event that performance testing shows that the EMS is not operating optimally, Contractor is required to work with the Employer to tune EMS parameters to improve performance and reassess.

All performance test analysis will be performed by the Contractor for review by the Employer.

# Appendix D – Battery Energy Storage System (BESS) and Energy Management System (EMS) Operation and Maintenance Requirements

The Appendix D - Battery Energy Storage System (BESS) and Energy Management System (EMS) Operation and Maintenance Requirements provides key technical requirements for the BESS units and EMS required under this project. It shall be read in conjunction with other parts of the Employer’s Requirements. All parts of the Employer’s Requirements are applicable to BESS equipment and shall not be read in isolation.

In particular, note:

- Employer Requirements:

  - This document provides the necessary overview information on the project scope and general requirements. It also includes summary information on the island specific capacities and requirements.

- Appendix A –General and Electrical:

  - This document provides details of the electrical standards and equipment requirements that the Plant must meet.

- Appendix B –Battery Energy Storage System (BESS):

  - This document provides key technical and functional requirements of the Battery Energy Storage System (BESS).

- Appendix C –Energy Management System:

  - This document provides key technical and functional requirements of the Energy Management System (EMS) that must be provided independent of the BESS to provide island wide generation dispatch management.

- Appendix E –Project Site Specific Details:

  - This document provides details of the requirements at each site. It includes site descriptions and data, capacity requirements, details on existing equipment and infrastructure, details of the point(s) of connection, and other related information for each island.

# Standards

All equipment shall be installed and all work shall be carried out in accordance with statutory requirements of the relevant jurisdiction (including amendments). The following standards are listed to inform and guide.

- IEEE Std 2030.2.1-2019 Guide for Design, Operation, and Maintenance of Battery Energy Storage Systems, both Stationary and Mobile, and Applications Integrated with Electric Power Systems

- IEC 60300.3.14-2005 Dependability management - Application guide - Maintenance and maintenance support

- ISO 55000:2014, Asset management—Overview, principles and terminology

- ISO 55001:2014, Asset management— Management systems—Requirements

- ISO 55002:2014, Asset management— Management systems—Guidelines for the application of AS ISO 55001

# Operations and Maintenance

Post Completion, the Contractor will be required to provide operations and maintenance (O&M) support to the Employer, in addition to its Contractual obligations for Defects Liability. A joint responsibility model is proposed. For the specified Duration of Support, Contractor will have full responsibility for specialist operating and maintenance activities of the BESS and EMS. Table 2 below provides Contractor O&M indicative in country support services and duration.

For the Duration of Support, local (Employer) staff will have responsibility for:

- General housekeeping, cleaning and basic site maintenance.

- All O&M activities for balance of plant (external to BESS and EMS, including, for example any cabling, transformer, switchgear, foundations, fencing, signage etc.).

- Transitioning to include all Contractor O&M activities.

The original equipment manufacturer (OEM) will have responsibility for specialist functions of its equipment that cannot reasonably be performed by others due to warranty or proprietary restrictions. OEM costs shall be paid by the Contractor for the Duration of Support. OEM must service the Maldives region, including either ability to send staff to site or train and delegate tasks to Contractor or suitably qualified local staff.

- OEM must be available to provide remote support for local technicians to troubleshoot the system in case of system failures or alarms during the BESS life.

- The OEM must offer to provide a thorough Operations and Maintenance training for the local crew in order to qualify the technicians to do routine inspections, troubleshoot failures and have a sound understanding of the system.

To fulfil its obligations during the specified two year period, Contractor is expected to have at least 1 qualified full-time equivalent staff stationed in the Maldives and able to travel to any of the project islands at short notice.

## Service Level

The Functional Guarantee for availability forms part of the service levels required from the Contractor. That is, the O&M support provided by the Contractor should ensure that the availability guarantee is met. Failure to meet the availability guarantee will result in liquidated damages as specified in the Employer Requirements.

Additionally, the following services levels for preventative and corrective maintenance are required:

- Planned Downtime

  - Proportion of scheduled activities completed within one week of scheduled date >90%

- Unplanned downtime

  - Proportion of critical faults responded to and rectified within 5 hours >70%

  - Proportion of critical faults responded to and rectified within 24 hours >95%

- Other

  - All warranty claims resolved within 3 months

  - Spare parts replaced within 1 month>90%

Contractor must demonstrate that their Asset Management Plan and staffing is capable of delivering the required service level.

Failure to meet required service levels will constitute a defect under the contract.

## Reporting

The Contractor shall provide a monthly report for the first three months of operation, then subsequent three monthly reports with associated summary data sets as an appendix to support reporting metrics indicating O&M performance. These will included and not limited to:

- BESS Availability

- O&M cost actual vs. projected

- Planned Downtime (including availability/lost revenue impact)

  - Proportion of scheduled activities completed within one week of scheduled date >90%

- Unplanned downtime  (including availability/lost revenue impact)

  - Maintenance related shutdown overrun

  - Corrective maintenance summary and Pareto of faults

  - Proportion of critical faults responded to and rectified within 5 hours >70%

  - Proportion of critical faults responded to and rectified within 24 hours >95%

  - Warranty claims

  - Incident reports including lessons learnt

- Reliability summary by subsystem

  - Mean Time Between Failure (MTBF)

  - Mean Time to Repair (MTTR)

## Duration of support

The Contractor shall offer 24 months of Operations and Maintenance. During the first 12 months, the Contractor shall lead all operations and maintenance requirements in this specification, continuously involving and demonstrating requirements to local Employer staff. During the second 12 months, the local Employer staff shall lead activities, working side by side with Contractor staff who will monitor and instruct as required. Over the full period, the Contractor shall have responsibility for Operations and Maintenance, except for deliberate or negligent actions or omissions by Employer staff.

Nominal period:  24 Months

- 12 months contractor led

- 12 months local staff led with contractor support

Contractor shall make available the option to extend the Duration of Support for a further 12 or 24 months, or to reduce the Duration of Support by 12 months, at rates equivalent to the Nominal period indexed to local inflation.

## Indicative support requirements

Indicative support arrangements are shown below. This will vary as needed based on Contractor’s solution and recommended practice, however, should reflect the functions and objectives shown here. Division of tasks between local and remote shall be determined in cooperation with the Employer to achieve the most efficient approach that fully integrates Employer’s local staff for

Table 2 Contractor O&M indicative requirements

| Service Name | Service Description | Service Category | Interval |
| --- | --- | --- | --- |
| Manage Operations | Daily operations and performance monitoring/record data from all sites. | Site Management | Ongoing |
| Manage Operations | Facilitate and execute any required manual changes in configuration or operating mode, including stop/start. | Site Management | Ongoing |
| Manage Operations | Reports analysing performance and degradation of BESS in accordance with AMP: - Average BESS Availability - Total Energy Consumed - Total Energy Exported - Average auxiliary load and losses (% of MW capacity) - Number of charge and discharge cycles (per Battery Operating Agreement definition) - BESS Health and criticality trends i.e. position in service life and operational life | Site Management | Ongoing |
| Manage Alarms | Monitor BESS and EMS alarms and site-specific alert parameters from Supervision of Monitoring, Information Exchange and Control (MIC) systems for deviations from acceptable levels and alarms. | Site Management | As needed |
| Contractor Response | Contractor available by email and phone 24x7x365. Provide first call response service, respond to all breakdowns. | Emergency Response: Blackout of whole island network, disruption to more than 30% of customers/loads, or active safety issue that cannot be isolated (including fire) | As needed: Attend within 30 minutes major failures of the system, especially those that involve the shutdown and outages of the BESS. |
| Contractor Response | Contractor available by email and phone 24x7x365. Respond to all breakdowns. | Breakdown Response: Fault in any subsystem that prevents its operation, and may result in some load reduction (<30%). | As needed: Attend within 8 hours following breakdown of the system, especially those that involve the shutdown and outages of the critical BESS systems. |
| Manage Inventory | Manage inventory of spare parts and consumables as per AMP including restocking and associated activities. | Inventory Management | As needed |
| Manage Inventory | Full inventory stock take and condition inspection. | Inventory Management | Annual |
| Manage Service Package | Monitoring annual service package. | Asset Management | On going |
| Manage Service Package | Manage/supervise/complete the scheduled routine maintenance, repair services and testing activities of the BESS and EMS as per the AMP i.e. test BESS fire suppression system. | Asset Management | On going |
| Manage Preventive services | Update record with preventive maintenance services and track any problems or warranty issues. | Asset Management | Ongoing |
| Manage Service Package | Through the analysis of the maintenance records, organise next interventions to maintain the physical state of the plant. | Asset Management | On going |
| Manage O&M Services | Document all O&M services completed via agreed methodology/within asset management system. | Asset Management | On going |
| Manage O&M Services | Provide O&M report providing asset management data and analysis (as listed earlier), and feedback on O&M activities. Including summary of/feedback on activities led by local staff. | Asset Management | 6 Monthly |
| Manage documentation | Confirm availability and take any measures to secure operating instructions, warranties and performance guarantees, and other project documentation. | Asset Management | Annual |
| Manage O&M agreements | Review O&M agreements and ensure that services are actually provided | Asset Management | Quarterly |
| Meet with site staff | Cooperate with the owner to ensure the operation and maintenance of the BESS. Meet with key site staff to continue awareness, question any issues and report on findings | Site Management | Ongoing |
| Training | Refresher training with local staff (1 day per island) to ensure plant operators are equipped with knowledge and skill necessary for effectively operating the systems and to conduct maintenance of the system and components. | Site Management | Quarterly |
| Insurance | Contractor to maintain property and third-party liability insurance for the BESS during the specified 2 year O&M period. Prior to handover, Contractor to provide any required information on BESS design, certifications, and operation to Employer’s insurers. | Insurance | Ongoing |

# Asset Management Plan

The Asset Management Plan should be authored by the Contractor and shall consider intput from the BESS supplier, in association with the asset owner. If available, it should be aligned with the utility’s Asset Management Policy and Strategic Asset Management Plan (SAMP). The Asset Management Plan (AMP) provides the detail agreed as necessary to achieve the stated organisational business objectives.

The Asset Management Plan should contain detail to fulfil the following outlined sections provided as guidance.

- Executive Summary

  - Overview of levels of service.

  - Growth forecasts.

  - Contribution to total asset base.

  - Key asset management issues/challenges.

  - Financial forecast.

- Definitions/Abbreviations

- Purpose

  - Overview of Asset Management Plan (AMP).

  - Define approach and rationale to managing the life cycle activities for the BESS and EMS. For instance:

    - Contractor provides operations and maintenance (O&M) support for the BESS installation for nominated time period. A joint responsibility model is proposed. Contractor has full responsibility for specialist operating and maintenance activities of the BESS and EMS.

- Scope and objectives

  - Function i.e.:

    - Frequency regulation

    - Emergency back-up/black start

    - Voltage regulation

    - Electric energy time-shift

    - Optimisation of electric capacity

    - Power quality/electric service reliability improvement

  - Objectives - key project outcomes, specific services and capability

    - Meet customer demand

    - Minimise outages and maintain reliability standards

    - Minimise diesel generator runtime

    - Minimise fuel consumption

- Context

  - Standard asset life for how system is to be operated and operational conditions i.e. temperature.

  - Boundaries and applicability.

  - Demands profile and forecast.

  - Compliance.

- Delivery of Service

  - Stakeholders.

  - Performance monitoring/indicators (reporting frequency), for example:

    - Average BESS Availability

    - Total energy consumed

    - Total energy exported

    - Average auxiliary load and losses (% of MW rated capacity)

    - Number of charge and discharge cycles (per Battery Operating Agreement definition)

  - Financial monitoring/indicators (reporting frequency), for example:

    - Reliability (e.g. SAIDI)

    - Fuel savings

    - Generator runtime

  - Health and Safety i.e. non-compliance reporting.

- Lifecycle asset management

  - Operational Requirements

    - Roles and responsibilities i.e. normal operations, facility communications, control systems etc.:

      - Asset owner

      - Asset manager

      - Service providers

    - Responsibility, Accountability, Consulted, Informed (RACI) matrix i.e.:

      - Identifies the person(s) responsible for the performance of the asset(s).

      - Identifies the person(s) responsible for the maintenance of the asset(s), for example:

        - Checks for corrosion or other degradation of individual cells or larger units that could increase fire or hazardous material risks.

      - Contains safety critical roles, for instance:

        - Conduct a periodic inspection of the general protection functions and all special protection functions of the BESS at different intervals to confirm that the system protections are functional.

        - Prestart-up safety and operational inspections.

        - Clear role responsibility for interaction with first responders in the event of a site incident.

        - Define roles for providing, testing and maintaining an alert and fire suppression system.

    - Operation Procedures:

      - Summary of operational procedures provided in appendix.

  - Maintenance Requirements:

    - The maintenance required for a defined anticipated operational mode of the BESS i.e. rate of charging/discharging, amount of energy cycled. Detail of how the maintenance regime should vary if the operation mode varies outside the defined operation mode.

    - Summary of schedule of preventive maintenance activities such as inspections and servicing, and corrective maintenance activities detailed in appendix.

Figure 6 Types of maintenance tasks

    - Associated lifecycle costs - yearly budget estimates.

  - Training:

    - Role description and expected responsibilities.

    - Expected qualifications.

    - Personnel and Training Plan summary, detail in appendix.

  - Renewal Requirements i.e.:

    - Age/Cycles.

    - Condition based.

  - BESS health and criticality profiles.

  - Conditions under which the system will have met end of warranty, service life, and operational life.

  - System additions - storage capacity increase.

  - Disposal Requirements.

- Asset Data

  - Asset Management System

    - Data standards to ensure access to long term usable data.

    - Identification nomenclature - asset, systems, sub systems.

    - Asset major components and attribute data.

    - Asset maintenance history data.

    - Comprehensive historical asset condition data.

  - Spare parts inventory for all assets/components (included and recommended).

    - For instance and not limited to:

      - Inverter

      - Battery interface

      - Panel

      - Container spare parts

      - SCADA system

      - Spare battery modules

      - Climate control

    - Spare Parts strategies i.e. management of battery hot-spares rotation to ensure wear level of the spares is consistent with the active batteries.

    - Spare part identification system, clearly indicate:

      - Assigned unique inventory code.

      - The equipment, assembly or sub-assembly it belongs to.

    - Spare part inventory list associated detail:

      - Associated attributes list for each spare, for instance and not limited too; parts number, manufacturer, supplier, supplier part number, present cost, model and typical name plate data.

      - Minimum and maximum holding levels.

      - Lead Times and any associated logistic limitations if applicable, i.e. sea freight only of battery modules due to safety reasons.

      - Storage conditions such as controlled environment necessary for longevity.

      - Storage location.

  - Inventory of asset associated supplied spares tools including:

    - All tools and accessories required for maintenance of the system.

    - Any customary and special tools, as well as auxiliary devices i.e. lifting devices, ropes, etc. necessary for assembly and disassembly of all parts.

    - Special tools designed and supplied. Assigned unique inventory code and storage location.

- Appendix A - Operational Procedures

  - Include list of all procedures for all tasks applicable to facility. Procedures should include task based risk assessments with controls to mitigate identified unacceptable risks:

    - Typical regular operator duties/routine tasks. For example only, daily operation conditions of BESS and EMS could include tasks such as:

      - Check the communication between Monitoring, Information Exchange and Control (MIC) systems and each sub-system to verify their functioning status.

      - Check the communication between MIC system and the upper-level control system to verify their functioning status.

      - Check the alarm and protection actions.

    - Trouble shooting and fault rectification processes.

    - Comprehensive standard procedures for low frequency tasks i.e. annual maintenance shutdowns, emergency shutdowns, recommissioning plant including isolation, removal of isolation and start-up.

    - Operation monitoring procedures i.e. collection, analysis and inspection/analysis of BESS data.

      - System voltage

      - Energy capacity

      - SOC

      - SOH

    - Inspection for BESS control and regulation functions.

      - Routine tests:

        - Test the monitoring function.

        - Inspect and record the operation conditions of functions of BESS such as rated power and energy capacity, charge and discharge characteristics, response time, energy efficiency, etc. under the actual demand.

    - Actions for abnormal conditions

      - Notifications

      - Checks and tests as per OEM procedures

    - Pre-start-up safety and operational inspections.

    - Instrumentation and control system documentation.

    - Test after overhaul and upgrade, in addition to routine tests, function tests such as:

      - Frequency regulation

      - Emergency back-up/black start

      - Voltage regulation

      - Electric energy time shift

      - Optimisation of electric capacity

      - Power quality/electric service reliability improvement

    - Shift change over arrangement and communications process.

    - Location of hard and electronic versions of procedures.

- Appendix B - Maintenance Schedule forecast (for defined lifecycle)

  - List all maintenance activities that form the maintenance service plan for the BESS and associated assets/components. For example:

    - Inspect the data collection for voltage, current, temperature and other parameters as well as warning and protection functions to verify their proper functioning.

    - Inspect the battery pack parameters i.e. total charge/discharge voltage, charge/discharge current, SOC, temperature etc.

    - Inspect the communication and executive functions of all high voltage electrical equipment including controllers.

    - Check that BMS trip signal promptly stops high voltage electrical equipment so that batteries are not over discharged.

    - Check battery pack cells are clean, intact with no deformation from cells or modules.

    - Inspect discharge protection equipment such as fast acting fuse, dc contactor, relay and switch.

    - Check tripping function of battery packs main circuit to confirm functional in case of conditions such as short circuit fault or overcurrent.

    - Measure insulation resistance of battery packs to ensure resistance meets the applicable standard and no electric leakage exists.

    - Measure and record open-circuit voltage of battery modules/cells. Open circuit voltage deviation is generally less than X%.

    - Measure and record internal resistance of cells in system for reference. Deviation of internal resistance between cells should not be more than X% and should not exceed the factory setting value.

  - Provide recommended best practice for the BESS components, i.e. for the PCS:

    - The set value and device on-line address are not recommended to be changed during operation since this change will cause communication fault between the PCS and other devices.

    - Attention shall be given to the high voltage terminals during the inspection and handling of the components at the back of BESS devices. Appropriate protection measures shall be taken as the voltages of partial terminals could reach several hundred volts.

    - When devices are networked with HMI and a remote computer system, precautions should be taken to protect information safety according to cyber protection related requirements.

    - Inspect the indicator of the surge arrestor for an action record, which indicates abnormal overvoltage.

  - For each maintenance activity within the schedule list all relevant associated information is separated and ordered by the use of columns i.e.:

    - Routine Code.

    - Routine Name.

    - Maintenance Type i.e. preventive, condition based.

    - Class of work i.e. inspection, test, service & clean, replacement, overhaul.

    - System.

    - Asset.

    - Frequency of routine.

    - Commencement date/next due date.

    - Requirement to have asset in service or out of service.

    - Resources required i.e. electrician.

    - Specialist equipment/tools required i.e. scaffold, thermography camera.

    - Spare parts/consumables.

  - Budget estimates

- Appendix C - Maintenance Plans

  - As much as possible, the requirement for on-site high level technical expertise should be limited. Maintenance processes are intended for completion by suitably qualified local staff with appropriate training.

  - Maintenance plans to list steps/detail for completing each scheduled maintenance activity. Plans should include activity task based risk assessments with controls to mitigate identified unacceptable risks. For example purposes only an inverter maintenance plan steps could include the following whereby each task is risk assessed:

    - Clean and replace the filtering materials in all vent filters of cabinet.

    - Clean the radiator of power components inside the cabinet.

    - Inspect the inside of the cabinet for dust accumulation, fouling, humidity, and water seepage from outside. Clean the parts and take appropriate remedial measures as required.

    - Inspect all power cable connections for looseness and fasten them as required.

    - Inspect connectors and insulation for contamination or deterioration, and replace damaged connectors or eroded contacts as required.

    - Inspect the warning signs fixed inside and outside the cabinet, and replace them as required.

    - Inspect all the fuses and disconnectors.

    - Perform functional test for the emergency shutdown switch.

    - Inspect the function of the door handle switch.

  - Maintenance plans to state acceptable conditions/limits/range as applicable and include corrective steps for unacceptable conditions/out of acceptable limits/range when found.

  - Maintenance standard procedures for disconnection, removal, replacement, reconnection of all major equipment having plug-and-play capability.

  - Maintenance procedures for inspections/corrective measures as a result of alarm/protection actions that occur during BESS operation e.g. overvoltage alarm, under voltage alarm, overcurrent alarm, over-temperature alarm.

  - Activity detail should include:

    - Routine Code.

    - Routine Name.

    - Description of routine.

    - Frequency of routine.

    - Maintenance type i.e. preventive, condition based.

    - Class of work i.e. inspection, test, service & clean, replacement, overhaul.

    - Application i.e. system/asset.

    - Resources required i.e. electrician.

    - Specialist equipment/tools required i.e. scaffold, thermography camera.

    - Spare parts/consumables.

    - Activity steps.

- Appendix D - Personnel and Training Plan:

  - Consistent with the system design, maintenance concept support equipment and procedures and the available skill levels of maintenance personnel.

  - Personnel training should include both initial and continued training to cover attrition, replacement of personnel and the impact of item changes and modifications.

  - Should consist of the following major components:

    - A means of analysing the task to identify training needs.

    - Development of specific training objectives.

    - Development of evaluation criteria.

    - Selection of methods of delivery of instructions.

    - Implementation of training.

    - Means of assessment of the results of training/competency measurement.

    - Where elements of maintenance have been delegated to external specialist organisations the training plan should be tailored to address just those elements under the responsibility of the maintainers and any interfaces required with external specialist organisations.

  - Should cover the following:

    - Operator training - course entry requirements, types of training to be covered and course outline.

    - Maintenance training of all applicable types of maintenance activities and associated plans, including course entry requirements and brief course outline.

    - Full list of training documentation developed.

    - Training equipment, devices, aids and data required to support operator and maintenance training activities.

    - Training schedule for initial operator and maintenance training.

  - Proposed approach for further training throughout the system life cycle.

- Appendix E - Vendor O&M Manuals

| Asset | Vendor | O&M Document Number | O&M Document Description |
| --- | --- | --- | --- |

# Appendix E – Project Site Specific Details

This document provides details of the requirements at each site. It includes site descriptions and data, capacity requirements, details on existing equipment and infrastructure, details of the point(s) of connection, and other related information for each island

Supplementary Information Refer: ARISE BESS Bid Data Room

# Appendix F - Environmental and Social Safeguards Requirements

The Employer had undertaken EIA screening for BESS from EPA and Environmental and Social Screening from the World Bank.  The Environmental and Social Screening Report (ESSR) can be downloaded from the link: www.environment.gov.mv/v2/wp-content/files/publications/20220112-pub-essr-bess-installation-phase1-and-2-arise-project.pdf) and also is provided in bidder data room. As per the screening decision, the Contractor is required to comply with the Environmental and Social Code of Practice (ESCP) Battery Energy Storage System Installation Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) project (link: 20220112-pub-escp-battery-energy-storage-system-installation-arise-project.pdf (environment.gov.mv)). The ESCP is also provided in the bidder data room. The ESCP lists several key requirements from the contractor, these are listed below:

- The Contractor is required to revise the ESCP based on Occupational, Health and Safety Management Plan (OHSMP), Hazard and Operability Study (HAZOP), Emergency Response Plan (ERP), Occupation Safety Management Plan (OSMP), Hazardous Material Management Plan (HMMP), Commissioning Plan (CP), Operations and Maintenance Plan (OMP), Decommissioning Plan (DP) and the Code of Conduct of the Construction workforce and submit to review by Employer within 63 days of notification of award.

- Develop a Code of Conduct of Construction workforce as per the Labour Management Procedure (LMP) (link: Labour Management Procedures: Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) Project (P172788) (environment.gov.mv)) of the project and submit to review by Employer.

- The Contractor shall follow all the good practices highlighted in Chapter 3 of ESCP.

- The Contractor shall undertake environmental and social monitoring and report to the Ministry as per the monitoring plan outlines in Chapter 4 of ESCP.

- The Contractor shall implement the project Grievance Redress Mechanism as highlighted in Annex 7 of ESCP.

- The Contractor shall implement Workers Grievance Redress Mechanism as highlighted in Annex 7 of ESCP.

- The Contractor shall undertake all works as per local environmental and social laws and regulations of Maldives. Summary of applicable laws are provided in Annex 6 of ESCP.

In addition, as per Environmental Social Management Framework (ESMF) (www.environment.gov.mv/v2/wp-content/files/2020/downloads/20200311-pub-environmental-and-social-management-framework-arise-project.pdf) of the project the following are required from the Contractor:

- As per ESMF the contractor needs to prepare the following plans and submit for approval of the Employer.

      - Occupational Health and Safety Management Plan

- Should cover specific actions, procedures that will be undertaken to ensure Occupational Health and Safety during the contract period in line with the Labor Management Procedure (LMP) developed for the project and the Guidelines for Occupational Health and Safety Management of Workers, Communities and Visitors during Construction Works provided in Annex 12 of the ESMF.

      - Hazardous materials management plan

  - Safety Data Sheets (SDS) (prepared in accordance with European Chemicals Agency Guidelines, or equivalent international standard) for all potentially hazardous materials included in the BESS or its spares. This shall include but not be limited to: battery cells (including cathode and anode), fire suppression chemicals, and coolants.

  - Any Original Equipment Manufacturer (OEM) specifications on installation or handling requirements (for example, special electrical protections on surge protection or earthing) that are not covered in the SDS.

  - Any OEM advisories pertaining on incidents or incident investigations pertaining to the particular materials supplied.

  - A project and site specific detailed description for materials handling and logistics, demonstrating compliance with the above documentation. For example, showing that battery modules’ shipping is planned for refrigerated containers (if required by the SDS).

      - Emergency Response plan

  - An Emergency Response Plan (ERP) covering safety of equipment on site, medical treatment of workers, response to external events like floods or cyclone, external fires and evacuation procedure should be proposed. This shall cover both construction and operation phase. In addition a detailed Fire Safety Plan (FSP) should be compiled address both construction and operations stages, covering the following:

    - Fire safety equipment requirements

    - Fire safety signage

    - Procedures in the event of a fire initiated at the container, including shutdown actions, safe distances and evacuation plan, immediate notifications, fire suppression actions (if any) and who is responsible.

    - Procedures following fire event (when is it safe to approach, how to make site safe, who to contact for further clean-up and disposal or investigation).

    - Procedures for an external fire event that may impact the BESS (for example, fire in adjacent equipment).

    - Mitigation to minimize damage to neighbouring inhabitants focusing on fire, explosion or toxic gas discharge

    - Mitigations to minimize impacts on health and safety of workers and the public also include electrical, mechanical, chemical, fire, explosion and gas discharge.

    - Considerations made to reduce risk of fire, toxic emissions and explosions to nearby infrastructure, residences and workers determined through a hazard operability study (HAZOP).

      - Commissioning Plan

- The Commissioning plan will document the sequence of steps necessary to transition the BESS from a mechanically and electrically complete state, to a fully operational system. The sequence of operations in the Commissioning plan must be constructed to ensure safe commencement of operation. It must also include the following documentation:

- Verification that all inspection and test plans under pre-commissioning or site acceptance tests are completed, and that all project documentation requirements are in order (including issued for construction (IFC) design documents, any required third party certifications such as building permits or electrical safety compliance certificates, factory acceptance test (FAT) reports and Master document registers (MDRs)). The Contractor must confirm that the plant is mechanically and electrically sound and in a fit state to operate.

- Documentation of completed Control Assurance Plan (CAP). Verification that safety critical control points are within compliance. CAP should include accuracy and delay compliance thresholds, recorded values, and testing interval. Simulated out-of-range inputs should be used to verify appropriate input or signal sanitization. The CAP should also stipulate data recording requirements and how stale data is handled for each point.

- Documentation of completed Measurement Assurance Plan (MAP). Verification that safety critical measurements are within compliance. The MAP should include accuracy and delay compliance thresholds, recorded values, and testing interval. Simulated out-of-range measurements should be used to verify appropriate alarms and warnings before operation. MAP should also stipulate data recording requirements and how stale data is handled for each point.

- Internal or External Communication Loss. If there is a loss of safety critical measurement or control, the system should gracefully shut down (e.g. loss of temperature measurement). If measurement or control is not safety critical (As determined in the Failure Module Effect Analysis (FMEA) and System Safety Analysis) then the system can continue to operate (e.g. loss of connection to off-site data backup).

- OEM verification of installation of BESS modules, or proof that commissioning team is fully trained and authorized by OEM to complete installation to OEM requirements.

- Ensure comprehensive training of power station staff are provided for emergency situations including simulated emergency drills.

      - Operations and Maintenance Plan

- Plans for inspecting, servicing, repair and renovation as well as any addition to the system (e.g. installation of additional storage capacity). Procurement specification should require Energy Storage supplier, developer, or integrator to deliver a complete operation and maintenance manual. This manual should provide instructions for all required operating and maintenance activities, the timing for these activities, and who will perform them. This manual should also include conditions under which the system will have met end of warranty, service life, and operational life. The O&M plan should also detail periodic maintenance checks and scheduled replacement of consumables that local operators should perform including checks for corrosion or other degradation of individual cells or larger units that could increase fire or hazardous material risks.

      - Decommissioning and Disposal plan

- After the system has reached the end of its operational life, system has to be decommissioned, disposed of or materials can be recycled. This plan should explain the procedure for decommissioning, including any hazards that may present, as well as the steps to disconnect the system using external automated control systems. The plan should demonstrate a practical plan for removal of battery modules at end of life (including shipment out of country) and disposal at a facility that meets international standards for environmental management ISO 14000. The plan must show that multiple disposal facilities are readily accessible and offer certification that they will accept the proposed BESS module. It should elaborate what costs this will incur, how articles should be packaged for disposal, and the procedure for shipping the materials to the disposal or recycling site.

- The following standards or equivalent will be used to assess that risks have satisfactorily been addressed:

| Aspect | Requirement | Required standards |
| --- | --- | --- |
| Lithium batteries (cells) | Remain safe (do not release hazardous waste or risk injury) under normal operations of misuse. Standards should ensure battery cells have been subject to testing for a range of normal and adverse conditions without exhibiting runaway thermal behaviour. | IEC 62133, and IEC 62660 (or UL 1642, UL 1973) |
| Inverters | Electrical safety of equipment, and functionality to support rapid shutdown and related system protection measures | IEC 62909-1 (or UL 1741) |
| Fire detection and suppression systems | Effectively detect and issue alarms for fire events that may arise in BESS. Ensure safe operation of fire suppression (if included). | ISO 7240, ISO 14520 |
| Battery energy storage systems | Provide overarching safety and environmental requirements for integrated systems. Address personnel safety, electrical hazards, essential grid protection functions, fire and explosion safety, hazardous materials, stand-off distances, installation and operation requirements. Include provisions for system level risk assessment and testing. | IEC 62933 (or UL 9540) IEC 92902 |
| Transport of battery cells from manufacturer to site | Minimise risk of electrical hazard, fire, or exposure of hazardous material during transport. | IEC 62281 |
| Access, egress and working space | Ensure adequacy of work spaces, including protection from arc flash or exposure to electrical hazards, unrestricted access to emergency exits, and reduce risk of exposure to fire suppression systems. | IEC 61936-1 |

- The Contractor should have ISO14001 certification or equivalent. This certification needs to be submitted at the time of bidding.

- The Contractor shall be responsible to ensure all construction material are sourced from approved sites or licensed commercial vendors. All key environmental parameters such as vibration and noise shall not exceed the limitation imposed by the Environmental Protection agency.

- If the Contractor fails to adhere to the mitigation and monitoring plan to a level acceptable to the Environmental Social Safeguards Specialist or other monitoring Agencies, the Employer will temporarily suspend the work until such time proper mitigation measures and monitoring are implemented.

- The contractor should allocate 2.5 percent of the total contract value as Environmental Social Health Safety (ESHS) Performance Security.

- If any of the defects identified by the Environmental and Social Safeguards Specialist are not remedied by the Contractor within the time given by the Employer, the Employer will consider the Contractor’s work as non-compliance towards environmental safeguards and necessary remedial action will be undertaken by the Employer through a third party. Further the cost of the third party and 12% (twelve percent) for supervision charges will be deducted from the Contractors Payment or from the ESHS Performance Security. Any additional cost or time incurred due to above will be at contractors’ expense and will not be subjected to extension of time or claim.

- The Contractor will be responsible for cleaning up and disposing of all waste materials and rehabilitating (landscaping) all construction sites and work areas so that these can be returned as close as possible to their previous use. This includes the stabilization and landscaping of all of the construction sites. Any borrow pits that were operated by the contractor are to be reshaped and closed. Any contaminated soil must be removed from fuel and oil storage areas. All construction debris is to be removed. Payment will be withheld from the contractor until all of the sites are satisfactorily cleaned, all spoils removed and the sites satisfactorily rehabilitated. The final payment will be released only after confirmation by the Environmental and Social Specialist that the above-mentioned tasks have been completed satisfactorily by the Contractor.

- Any legal penalties in relation to environmental and social non-compliance, imposed by any government agency, related to works undertaken by the contractor due to non-compliance of provisions included in the contract should be borne by the contractor.

In addition, the following should be used as guidance by the contractor:

- “Generic Environmental and Social Management Plan (ESMP) for Management of Environmental and Social Impacts During the Construction/Installation of Solar PV and BESS Systems and Grid Infrastructure” provided in Annex 10 of ESMF (link: https://www.environment.gov.mv/v2/en/download/10026).

- “Standard Guidance on Safety Considerations to be Included in the Implementation of Battery Energy Storage System (BESS) Subprojects as per International Best Practice” provided in Annex 5 of ESMF (link: https://www.environment.gov.mv/v2/en/download/10026).

# Forms and Procedures

Form of Completion Certificate

Date:	_______________

Loan/Credit No:	_______________

RFB No:	_______________

To: _________________________________

Dear Ladies and/or Gentlemen,

Pursuant to GCC Clause 24 (Completion of the Facilities) of the General Conditions of the Contract entered into between yourselves and the Employer dated _____________, relating to the ____________________,  we hereby notify you that the following part(s) of the Facilities was (were) complete on the date specified below, and that, in accordance with the terms of the Contract, the Employer hereby takes over the said part(s) of the Facilities, together with the responsibility for care and custody and the risk of loss thereof on the date mentioned below.

1.	Description of the Facilities or part thereof:  ______________________________

2.	Date of Completion:  __________________

However, you are required to complete the outstanding items listed in the attachment hereto as soon as practicable.

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

Title

(Project Manager) 
Form of Operational Acceptance Certificate

Date:	_______________

Loan/Credit No:	_______________

RFB No:	_______________

To:  ________________________________________

Dear Ladies and/or Gentlemen,

Pursuant to GCC Sub-Clause 25.3 (Operational Acceptance) of the General Conditions of the Contract entered into between yourselves and the Employer dated _______________, relating to the ___________________________________, we hereby notify you that the Functional Guarantees of the following part(s) of the Facilities were satisfactorily attained on the date specified below.

1.	Description of the Facilities or part thereof:  _______________________________

2.	Date of Operational Acceptance:  _______________________

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

Title

(Project Manager)

Change Order Procedure and Forms

Date:	_______________

Loan/Credit No:	_______________

RFB No:	_______________

CONTENTS

1.	General

2.	Change Order Log

3.	References for Changes

ANNEXES

Annex 1	Request for Change Proposal

Annex 2	Estimate for Change Proposal

Annex 3	Acceptance of Estimate

Annex 4	Change Proposal

Annex 5	Change Order

Annex 6	Pending Agreement Change Order

Annex 7	Application for Change Proposal

Change Order Procedure

1.	General

This section provides samples of procedures and forms for implementing changes in the Facilities during the performance of the Contract in accordance with GCC Clause 39 (Change in the Facilities) of the General Conditions.

2.	Change Order Log

The Contractor shall keep an up-to-date Change Order Log to show the current status of Requests for Change and Changes authorized or pending, as Annex 8.  Entries of the Changes in the Change Order Log shall be made to ensure that the log is up-to-date.  The Contractor shall attach a copy of the current Change Order Log in the monthly progress report to be submitted to the Employer.

3.	References for Changes

(1)	Request for Change as referred to in GCC Clause 39 shall be serially numbered CR-X-nnn.

(2)	Estimate for Change Proposal as referred to in GCC Clause 39 shall be serially numbered CN-X-nnn.

(3)	Acceptance of Estimate as referred to in GCC Clause 39 shall be serially numbered CA-X-nnn.

(4)	Change Proposal as referred to in GCC Clause 39 shall be serially numbered CP-X-nnn.

(5)	Change Order as referred to in GCC Clause 39 shall be serially numbered CO-X-nnn.

Note:	(a)	Requests for Change issued from the Employer’s Home Office and the Site representatives of the Employer shall have the following respective references:

Home Office	CR-H-nnn

Site	CR-S-nnn

(b)	The above number “nnn” is the same for Request for Change, Estimate for Change Proposal, Acceptance of Estimate, Change Proposal and Change Order.

Annex 1.  Request for Change Proposal

(Employer’s Letterhead)

To:  ____________________________________	Date:

Attention:  ______________________________________

Contract Name:  _________________________________

Contract Number:  _______________________________

Dear Ladies and/or Gentlemen:

With reference to the captioned Contract, you are requested to prepare and submit a Change Proposal for the Change noted below in accordance with the following instructions within _______________ days of the date of this letter____________________.

1.	Title of Change:  ________________________

2.	Change Request No. __________________

3.	Originator of Change:	Employer:  _______________________________

Contractor (by Application for Change Proposal No. _______:

4.	Brief Description of Change:  _________________________________________________

5.	Facilities and/or Item No. of equipment related to the requested Change:  _____________

6.	Reference drawings and/or technical documents for the request of Change:

Drawing No./Document No.	Description

7.	Detailed conditions or special requirements on the requested Change:  ________________

8.	General Terms and Conditions:

(a)	Please submit your estimate to us showing what effect the requested Change will have on the Contract Price.

(b)	Your estimate shall include your claim for the additional time, if any, for completion of the requested Change.

(c)	If you have any opinion negative to the adoption of the requested Change in connection with the conformability to the other provisions of the Contract or the safety of the Plant or Facilities, please inform us of your opinion in your proposal of revised provisions.

(d)	Any increase or decrease in the work of the Contractor relating to the services of its personnel shall be calculated.

(e)	You shall not proceed with the execution of the work for the requested Change until we have accepted and confirmed the amount and nature in writing.

(Employer’s Name)

(Signature)

(Name of signatory)

(Title of signatory)

Annex 2.  Estimate for Change Proposal

(Contractor’s Letterhead)

To: ______________________________	Date:

Attention:  _______________________________

Contract Name:  _______________________________

Contract Number:  _____________________________

Dear Ladies and/or Gentlemen:

With reference to your Request for Change Proposal, we are pleased to notify you of the approximate cost of preparing the below-referenced Change Proposal in accordance with GCC Sub-Clause 39.2.1 of the General Conditions.  We acknowledge that your agreement to the cost of preparing the Change Proposal, in accordance with GCC Sub-Clause 39.2.2, is required before estimating the cost for change work.

1.	Title of Change:  ________________________

2.	Change Request No./Rev.:  ____________________________

3.	Brief Description of Change:  __________________________

4.	Scheduled Impact of Change:  ___________________________

5.	Cost for Preparation of Change Proposal:  _______________

(a)	Engineering	(Amount)

(i)	Engineer		 hrs x 	 rate/hr =

(ii)	Draftsperson		 hrs x 	 rate/hr =

Sub-total		 hrs

Total Engineering Cost

(b)	Other Cost

Total Cost (a) + (b)

(Contractor’s Name)

(Signature)

(Name of signatory)

(Title of signatory)

Annex 3.  Acceptance of Estimate

(Employer’s Letterhead)

To:  ______________________________	Date:

Attention:  ________________________________

Contract Name:  _____________________________

Contract Number:  ___________________________

Dear Ladies and/or Gentlemen:

We hereby accept your Estimate for Change Proposal and agree that you should proceed with the preparation of the Change Proposal.

1.	Title of Change:  ___________________________

2.	Change Request No./Rev.:  _______________________________

3.	Estimate for Change Proposal No./Rev.:  _______________________________

4.	Acceptance of Estimate No./Rev.:  _______________________________

5.	Brief Description of Change:  _______________________________

6.	Other Terms and Conditions:  In the event that we decide not to order the Change accepted, you shall be entitled to compensation for the cost of preparation of Change Proposal described in your Estimate for Change Proposal mentioned in para. 3 above in accordance with GCC Clause 39 of the General Conditions.

(Employer’s Name)

(Signature)

(Name and Title of signatory)

Annex 4.  Change Proposal

(Contractor’s Letterhead)

To:  _______________________________	Date:

Attention:  _______________________________

Contract Name:  _______________________________

Contract Number:  _______________________________

Dear Ladies and/or Gentlemen:

In response to your Request for Change Proposal No. _______________________________, we hereby submit our proposal as follows:

1.	Title of Change:  _______________________________

2.	Change Proposal No./Rev.:  _______________________________

3.	Originator of Change:	Employer:  [_______________________________

Contractor:  _______________________________

4.	Brief Description of Change:  _______________________________

5.	Reasons for Change:  _______________________________

6.	Facilities and/or Item No. of Equipment related to the requested Change:  _______________________________

7.	Reference drawings and/or technical documents for the requested Change:

Drawing/Document No.	Description

8.	Estimate of increase/decrease to the Contract Price resulting from Change Proposal:

(Amount)

(a)	Direct material

(b)	Major construction equipment

(c)	Direct field labor (Total 	 hrs)

(d)	Subcontracts

(e)	Indirect material and labor

(f)	Site supervision

(g)	Head office technical staff salaries

Process engineer		 hrs @ 	 rate/hr

Project engineer		 hrs @ 	 rate/hr

Equipment engineer		 hrs @ 	 rate/hr

Procurement		 hrs @ 	 rate/hr

Draftsperson		 hrs @ 	 rate/hr

Total		 hrs

(h)	Extraordinary costs (computer, travel, etc.)

(i)	Fee for general administration, 	 % of Items

(j)	Taxes and customs duties

Total lump sum cost of Change Proposal

(Sum of items (a) to (j))

Cost to prepare Estimate for Change Proposal

(Amount payable if Change is not accepted)

9.	Additional time for Completion required due to Change Proposal

10.	Effect on the Functional Guarantees

11.	Effect on the other terms and conditions of the Contract

12.	Validity of this Proposal:  within [Number] days after receipt of this Proposal by the Employer

13.	Other terms and conditions of this Change Proposal:

(a)	You are requested to notify us of your acceptance, comments or rejection of this detailed Change Proposal within ______________ days from your receipt of this Proposal.

(b)	The amount of any increase and/or decrease shall be taken into account in the adjustment of the Contract Price.

(c)	Contractor’s cost for preparation of this Change Proposal:2

(Contractor’s Name)

(Signature)

(Name of signatory)

(Title of signatory)

Annex 5.  Change Order

(Employer’s Letterhead)

To:  _______________________________	Date:

Attention:  _______________________________

Contract Name:  _______________________________

Contract Number:  _______________________________

Dear Ladies and/or Gentlemen:

We approve the Change Order for the work specified in the Change Proposal (No. _______), and agree to adjust the Contract Price, Time for Completion and/or other conditions of the Contract in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  _______________________________

2.	Change Request No./Rev.:  _______________________________

3.	Change Order No./Rev.:  _______________________________

4.	Originator of Change:	Employer:  _______________________________

Contractor:  _______________________________

5.	Authorized Price:

Ref. No.:  _______________________________	Date:  __________________________

Foreign currency portion __________  plus Local currency portion __________

6.	Adjustment of Time for Completion

None	Increase _________ days	Decrease _________ days

7.	Other effects, if any

Authorized by:  		Date:

(Employer)

Accepted by:  		Date:

(Contractor) 
Annex 6.  Pending Agreement Change Order

(Employer’s Letterhead)

To:  _______________________________	Date:

Attention:  _______________________________

Contract Name: _______________________________

Contract Number:  [_______________________________

Dear Ladies and/or Gentlemen:

We instruct you to carry out the work in the Change Order detailed below in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  _______________________________

2.	Employer’s Request for Change Proposal No./Rev.:  _______________________________dated:  __________

3.	Contractor’s Change Proposal No./Rev.:  __________________ dated:  ___

4.	Brief Description of Change:  _______________________________

5.	Facilities and/or Item No. of equipment related to the requested Change:  _______________________________

6.	Reference Drawings and/or technical documents for the requested Change:

Drawing/Document No.	Description

7.	Adjustment of Time for Completion:

8.	Other change in the Contract terms:

9.	Other terms and conditions:

(Employer’s Name)

(Signature)

(Name of signatory)

(Title of signatory)

Annex 7.  Application for Change Proposal

(Contractor’s Letterhead)

To:  _______________________________	Date:

Attention:  _______________________________

Contract Name:  _______________________________

Contract Number:  _______________________________

Dear Ladies and/or Gentlemen:

We hereby propose that the below-mentioned work be treated as a Change in the Facilities.

1.	Title of Change:  _______________________________

2.	Application for Change Proposal No./Rev.: _______________________________	dated:  _______________________________

3.	Brief Description of Change:  _______________________________

4.	Reasons for Change:

5.	Order of Magnitude Estimation (in the currencies of the Contract):

6.	Scheduled Impact of Change:

7.	Effect on Functional Guarantees, if any:

8.	Appendix:

(Contractor’s Name)

(Signature)

(Name of signatory)

(Title of signatory)

PART 3 – Conditions of Contract and Contract Forms

Section VIII - General Conditions of Contract

Table of Clauses

A.	Contract and Interpretation	323

1.	Definitions	323

2.	Contract Documents	326

3.	Interpretation	326

4.	Communications	328

5.	Law and Language	328

6.	Fraud and Corruption	328

B.	Subject Matter of Contract	329

7.	Scope of Facilities	329

8.	Time for Commencement and Completion	330

9.	Contractor’s Responsibilities	330

10.	Employer’s Responsibilities	334

C.	Payment	335

11.	Contract Price	335

12.	Terms of Payment	335

13.	Securities	336

14.	Taxes and Duties	337

D.	Intellectual Property	338

15.	License/Use of Technical Information	338

16.	Confidential Information	338

E.	Execution of the Facilities	339

17.	Representatives	339

18.	Work Program	341

19.	Subcontracting	343

20.	Design and Engineering	344

21.	Procurement	346

22.	Installation	348

23.	Test and Inspection	360

24.	Completion of the Facilities	362

25. 	Commissioning and Operational Acceptance	363

F.	Guarantees and Liabilities	366

26.	Completion Time Guarantee	366

27.	Defect Liability	367

28.	Functional Guarantees	369

29.	Patent Indemnity	370

30.	Limitation of Liability	371

G.	Risk Distribution	371

31.	Transfer of Ownership	371

32.	Care of Facilities	372

33.	Loss of or Damage to Property; Accident or Injury to Workers; Indemnification	373

34.	Insurance	374

35.	Unforeseen Conditions	376

36.	Change in Laws and Regulations	377

37.	Force Majeure	378

38.	War Risks	379

H.	Change in Contract Elements	380

39.	Change in the Facilities	381

40.	Extension of Time for Completion	384

41.	Suspension	385

42.	Termination	387

43.	Assignment	393

44. 	Export Restrictions	393

I.	Claims, Disputes and Arbitration	393

45.	Contractor’s Claims	393

46. 	Disputes and Arbitration	395

# General Conditions of Contract

- Contract and Interpretation

| 1. Definitions | 1.1 The following words and expressions shall have the meanings hereby assigned to them: “Contract” means the Contract Agreement entered into between the Employer and the Contractor, together with the Contract Documents referred to therein; they shall constitute the Contract, and the term “the Contract” shall in all such documents be construed accordingly. “Contract Documents” means the documents listed in Article 1.1 (Contract Documents) of the Contract Agreement (including any amendments thereto). “GCC” means the General Conditions of Contract hereof. “PCC” means the Particular Conditions of Contract. “day” means calendar day. “year” means 365 days. “month” means calendar month. “Party” means the Employer or the Contractor, as the context requires, and “Parties” means both of them. “Employer” means the person named as such in the PCC and includes the legal successors or permitted assigns of the Employer. “Project Manager” means the person appointed by the Employer in the manner provided in GCC Sub-Clause 17.1 (Project Manager) hereof and named as such in the PCC to perform the duties delegated by the Employer. “Contractor” means the person(s) whose Bid to perform the Contract has been accepted by the Employer and is named as Contractor in the Contract Agreement, and includes the legal successors or permitted assigns of the Contractor. “Contractor’s Representative” means any person nominated by the Contractor and approved by the Employer in the manner provided in GCC Sub-Clause 17.2 (Contractor’s Representative and Construction Manager) hereof to perform the duties delegated by the Contractor. “Construction Manager” means the person appointed by the Contractor’s Representative in the manner provided in GCC Sub-Clause 17.2.4. “Subcontractor,” including manufacturers, means any person to whom execution of any part of the Facilities, including preparation of any design or supply of any Plant, is sub-contracted directly or indirectly by the Contractor, and includes its legal successors or permitted assigns. “Dispute Board” (DB) means the person or persons named as such in the PCC appointed by agreement between the Employer and the Contractor to make a decision with respect to any dispute or difference between the Employer and the Contractor referred to him or her by the Parties pursuant to GCC Sub-Clause 46.1 (Dispute Board) hereof. “The Bank” means the financing institution named in the PCC. “Contract Price” means the sum specified in Article 2.1 (Contract Price) of the Contract Agreement, subject to such additions and adjustments thereto or deductions therefrom, as may be made pursuant to the Contract. “Facilities” means the Plant to be supplied and installed, as well as all the Installation Services to be carried out by the Contractor under the Contract. “Plant” means permanent plant, equipment, machinery, apparatus, materials, articles and things of all kinds to be provided and incorporated in the Facilities by the Contractor under the Contract (including the spare parts to be supplied by the Contractor under GCC Sub-Clause 7.3 hereof), but does not include Contractor’s Equipment. “Installation Services” means all those services ancillary to the supply of the Plant for the Facilities, to be provided by the Contractor under the Contract, such as transportation and provision of marine or other similar insurance, inspection, expediting, site preparation works (including the provision and use of Contractor’s Equipment and the supply of all construction materials required), installation, testing, precommissioning, commissioning, operations, maintenance, the provision of operations and maintenance manuals, training, etc… as the case may require. “Contractor’s Equipment” means all facilities, equipment, machinery, tools, apparatus, appliances or things of every kind required in or for installation, completion and maintenance of Facilities that are to be provided by the Contractor, but does not include Plant, or other things intended to form or forming part of the Facilities. “Country of Origin” means the countries and territories eligible under the rules of the Bank as further elaborated in the PCC. “Site” means the land and other places upon which the Facilities are to be installed, and such other land or places as may be specified in the Contract as forming part of the Site. “Effective Date” means the date of fulfillment of all conditions stated in Article 3 (Effective Date) of the Contract Agreement, from which the Time for Completion shall be counted. “Time for Completion” means the time within which Completion of the Facilities as a whole (or of a part of the Facilities where a separate Time for Completion of such part has been prescribed) is to be attained, as referred to in GCC Clause 8 and in accordance with the relevant provisions of the Contract. “Completion” means that the Facilities (or a specific part thereof where specific parts are specified in the Contract) have been completed operationally and structurally and put in a tight and clean condition, that all work in respect of Precommissioning of the Facilities or such specific part thereof has been completed, and that the Facilities or specific part thereof are ready for Commissioning as provided in GCC Clause 24 (Completion) hereof. “Precommissioning” means the testing, checking and other requirements specified in the Employer’s Requirements that are to be carried out by the Contractor in preparation for Commissioning as provided in GCC Clause 24 (Completion) hereof. “Commissioning” means operation of the Facilities or any part thereof by the Contractor following Completion, which operation is to be carried out by the Contractor as provided in GCC Sub-Clause 25.1 (Commissioning) hereof, for the purpose of carrying out Guarantee Test(s). “Guarantee Test(s)” means the test(s) specified in the Employer’s Requirements to be carried out to ascertain whether the Facilities or a specified part thereof is able to attain the Functional Guarantees specified in the Appendix to the Contract Agreement titled Functional Guarantees, in accordance with the provisions of GCC Sub-Clause 25.2 (Guarantee Test) hereof. “Operational Acceptance” means the acceptance by the Employer of the Facilities (or any part of the Facilities where the Contract provides for acceptance of the Facilities in parts), which certifies the Contractor’s fulfillment of the Contract in respect of Functional Guarantees of the Facilities (or the relevant part thereof) in accordance with the provisions of GCC Clause 28 (Functional Guarantees) hereof and shall include deemed acceptance in accordance with GCC Clause 25 (Commissioning and Operational Acceptance) hereof. “Defect Liability Period” means the period of validity of the warranties given by the Contractor commencing at Completion of the Facilities or a part thereof, during which the Contractor is responsible for defects with respect to the Facilities (or the relevant part thereof) as provided in GCC Clause 27 (Defect Liability) hereof. “ES” means Environmental and Social (including Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH)). “Sexual Exploitation and Abuse” “(SEA)” means the following: Sexual Exploitation is defined as any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another. Sexual Abuse is defined as the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions; “Sexual Harassment” “(SH)” is defined as unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature by the Contractor’s Personnel with other Contractor’s Personnel or Employer’s Personnel. “Contractor’s Personnel” means all personnel whom the Contractor utilizes in the execution of the Contract, including the staff, labor and other employees of the Contractor and each Subcontractor; and any other personnel assisting the Contractor in the execution of the Contract; and “Employer’s Personnel” means all staff, labor and other employees of the Project Manager and of the Employer engaged in fulfilling the Employer’s obligations under the Contract; and any other personnel identified as Employer’s Personnel, by a notice from the Employer to the Contractor. |
| --- | --- |
| 2. Contract Documents | 2.1 Subject to Article 1.2 (Order of Precedence) of the Contract Agreement, all documents forming part of the Contract (and all parts thereof) are intended to be correlative, complementary and mutually explanatory. The Contract shall be read as a whole. |
| 3. Interpretation | 3.1 In the Contract, except where the context requires otherwise: - words indicating one gender include all genders; - words indicating the singular also include the plural and words indicating the plural also include the singular; - provisions including the word “agree,” “agreed,” or “agreement” require the agreement to be recorded in writing; - the word “tender” is synonymous with “Bid,” “tenderer,” with “Bidder,” and “tender documents” with “Bidding Document,” and - “written” or “in writing” means hand-written, type-written, printed or electronically made, and resulting in a permanent record. The marginal words and other headings shall not be taken into consideration in the interpretation of these Conditions. 3.2 Incoterms Unless inconsistent with any provision of the Contract, the meaning of any trade term and the rights and obligations of Parties thereunder shall be as prescribed by Incoterms. Incoterms means international rules for interpreting trade terms published by the International Chamber of Commerce (latest edition), 38 Cours Albert 1er, 75008 Paris, France. 3.3 Entire Agreement Subject to GCC Sub-Clause 16.4 hereof, the Contract constitutes the entire agreement between the Employer and Contractor with respect to the subject matter of Contract and supersedes all communications, negotiations and agreements (whether written or oral) of Parties with respect thereto made prior to the date of Contract. 3.4 Amendment No amendment or other variation of the Contract shall be effective unless it is in writing, is dated, expressly refers to the Contract, and is signed by a duly authorized representative of each Party hereto. 3.5 Independent Contractor The Contractor shall be an independent contractor performing the Contract. The Contract does not create any agency, partnership, joint venture or other joint relationship between the Parties hereto. Subject to the provisions of the Contract, the Contractor shall be solely responsible for the manner in which the Contract is performed. All employees, representatives or Subcontractors engaged by the Contractor in connection with the performance of the Contract shall be under the complete control of the Contractor and shall not be deemed to be employees of the Employer, and nothing contained in the Contract or in any subcontract awarded by the Contractor shall be construed to create any contractual relationship between any such employees, representatives or Subcontractors and the Employer. 3.6 Non-Waiver 3.6.1 Subject to GCC Sub-Clause 3.6.2 below, no relaxation, forbearance, delay or indulgence by either Party in enforcing any of the terms and conditions of the Contract or the granting of time by either Party to the other shall prejudice, affect or restrict the rights of that Party under the Contract, nor shall any waiver by either Party of any breach of Contract operate as waiver of any subsequent or continuing breach of Contract. 3.6.2 Any waiver of a Party’s rights, powers or remedies under the Contract must be in writing, must be dated and signed by an authorized representative of the Party granting such waiver, and must specify the right and the extent to which it is being waived. 3.7 Severability If any provision or condition of the Contract is prohibited or rendered invalid or unenforceable, such prohibition, invalidity or unenforceability shall not affect the validity or enforceability of any other provisions and conditions of the Contract. 3.8 Country of Origin “Origin” means the place where the plant and component parts thereof are mined, grown, produced or manufactured, and from which the services are provided. Plant components are produced when, through manufacturing, processing, or substantial or major assembling of components, a commercially recognized product results that is substantially different in its basic characteristics or in purpose or utility from its components. |
| 4. Communications | 4.1 Wherever these Conditions provide for the giving or issuing of approvals, certificates, consents, determinations, notices, requests and discharges, these communications shall be: - in writing and delivered against receipt; and - delivered, sent or transmitted to the address for the recipient’s communications as stated in the Contract Agreement. When a certificate is issued to a Party, the certifier shall send a copy to the other Party. When a notice is issued to a Party, by the other Party or the Project Manager, a copy shall be sent to the Project Manager or the other Party, as the case may be. |
| 5. Law and Language | 5.1 The Contract shall be governed by and interpreted in accordance with laws of the country specified in the PCC. - The ruling language of the Contract shall be that stated in the PCC. - The language for communications shall be the ruling language unless otherwise stated in the PCC. |
| 6. Fraud and Corruption | - The Bank requires compliance with the Bank’s Anti-Corruption Guidelines and its prevailing sanctions policies and procedures as set forth in the WBG’s Sanctions Framework, as set forth in Appendix B to the GCC. - The Employer requires the Contractor to disclose any commissions or fees that may have been paid or are to be paid to agents or any other party with respect to the Bidding process or execution of the Contract. The information disclosed must include at least the name and address of the agent or other party, the amount and currency, and the purpose of the commission, gratuity or fee. |

| - Subject Matter of Contract |  |  |
| --- | --- | --- |
| 7. Scope of Facilities | 7.1 Unless otherwise expressly limited in the Employer’s Requirements, the Contractor’s obligations cover the provision of all Plant and the performance of all Installation Services required for the design, and the manufacture (including procurement, quality assurance, construction, installation, associated civil works, Precommissioning and delivery) of the Plant, and the installation, completion and commissioning of the Facilities in accordance with the plans, procedures, specifications, drawings, codes and any other documents as specified in the Section, Employer’s Requirements. Such specifications include, but are not limited to, the provision of supervision and engineering services; the supply of labor, materials, equipment, spare parts (as specified in GCC Sub-Clause 7.3 below) and accessories; Contractor’s Equipment; construction utilities and supplies; temporary materials, structures and facilities; transportation (including, without limitation, unloading and hauling to, from and at the Site); and storage, except for those supplies, works and services that will be provided or performed by the Employer, as set forth in the Appendix to the Contract Agreement titled Scope of Works and Supply by the Employer. 7.2 The Contractor shall, unless specifically excluded in the Contract, perform all such work and/or supply all such items and materials not specifically mentioned in the Contract but that can be reasonably inferred from the Contract as being required for attaining Completion of the Facilities as if such work and/or items and materials were expressly mentioned in the Contract. 7.3 In addition to the supply of Mandatory Spare Parts included in the Contract, the Contractor agrees to supply spare parts required for the operation and maintenance of the Facilities for the period specified in the PCC and the provisions, if any, specified in the PCC. However, the identity, specifications and quantities of such spare parts and the terms and conditions relating to the supply thereof are to be agreed between the Employer and the Contractor, and the price of such spare parts shall be that given in Price Schedule No. 6, which shall be added to the Contract Price. The price of such spare parts shall include the purchase price therefor and other costs and expenses (including the Contractor’s fees) relating to the supply of spare parts. |
| 8. Time for Commencement and Completion | 8.1 The Contractor shall commence work on the Facilities within the period specified in the PCC and without prejudice to GCC Sub-Clauses 9.9 and 26.2 hereof, the Contractor shall thereafter proceed with the Facilities in accordance with the time schedule specified in the Appendix to the Contract Agreement titled Time Schedule. 8.2 The Contractor shall attain Completion of the Facilities or of a part where a separate time for Completion of such part is specified in the Contract, within the time stated in the PCC or within such extended time to which the Contractor shall be entitled under GCC Clause 40 hereof. |
| 9. Contractor’s Responsibilities | 9.1 The Contractor shall design, manufacture including associated purchases and/or subcontracting, install and complete the Facilities in accordance with the Contract. When completed, the Facilities should be fit for the purposes for which they are intended as defined in the Contract. 9.2 The Contractor confirms that it has entered into this Contract on the basis of a proper examination of the data relating to the Facilities including any data as to boring tests provided by the Employer, and on the basis of information that the Contractor could have obtained from a visual inspection of the Site if access thereto was available and of other data readily available to it relating to the Facilities as of the date twenty-eight (28) days prior to Bid submission. The Contractor acknowledges that any failure to acquaint itself with all such data and information shall not relieve its responsibility for properly estimating the difficulty or cost of successfully performing the Facilities. 9.3 The Contractor shall acquire and pay for all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located which such authorities or undertakings require the Contractor to obtain in its name and which are necessary for the performance of the Contract, including, without limitation, visas for the Contractor’s Personnel and entry permits for all imported Contractor’s Equipment. The Contractor shall acquire all other permits, approvals and/or licenses that are not the responsibility of the Employer under GCC Sub-Clause 10.3 hereof and that are necessary for the performance of the Contract. 9.4 The Contractor shall comply with all laws in force in the country where the Facilities are to be implemented. The laws will include all local, state, national or other laws that affect the performance of the Contract and bind upon the Contractor. The Contractor shall indemnify and hold harmless the Employer from and against any and all liabilities, damages, claims, fines, penalties and expenses of whatever nature arising or resulting from the violation of such laws by the Contractor or its personnel, including the Subcontractors and their personnel, but without prejudice to GCC Sub-Clause 10.1 hereof. 9.5 Any Plant and Installation Services that will be incorporated in or be required for the Facilities and other supplies shall have their origin as specified under GCC Clause 1 (Country of Origin). Any subcontractors retained by the Contractor shall be from a country as specified in GCC Clause 1 (Country of Origin). 9.6 If the Contractor is a joint venture, or association (JV) of two or more persons, all such persons shall be jointly and severally bound to the Employer for the fulfillment of the provisions of the Contract, and shall designate one of such persons to act as a leader with authority to bind the JV. The composition or the constitution of the JV shall not be altered without the prior consent of the Employer. 9.7 Pursuant to paragraph 2.2 e. of Appendix B to the General Conditions the Contractor shall permit and shall cause its agents (where declared or not), subcontractors, subconsultants, service providers, suppliers, and personnel, to permit, the Bank and/or persons appointed by the Bank to inspect the site and/or the accounts, records and other documents relating to the procurement process, selection and/or contract execution, and to have such accounts, records and other documents audited by auditors appointed by the Bank. The Contractor’s and its Subcontractors’ and subconsultants’ attention is drawn to Sub-Clause 6.1 (Fraud and Corruption) which provides, inter alia, that acts intended to materially impede the exercise of the Bank’s inspection and audit rights constitute a prohibited practice subject to contract termination (as well as to a determination of ineligibility pursuant to the Bank’s prevailing sanctions procedures). 9.8 The Contractor shall conform to the sustainable procurement contractual provisions, if and as specified in the PCC. 9.9 Contractor’s Environmental and Social Management Plan (C-ESMP) The Contractor shall not carry out mobilization to Site unless the Project Manager gives approval, an approval that shall not be unreasonably delayed, to the measures the Contractor proposes to address environmental and social risks and impacts including the code of conduct, in accordance with GCC Sub-Clause 22.4. The Contractor shall submit, to the Project Manager for Review, any additional Management Strategies and Implementation Plans as are necessary to manage the ES risks and impacts of the Facilities. These Management Strategies and Implementation Plans collectively comprise the Contractor’s Environmental and Social Management Plan (C-ESMP). The Contractor shall review the C-ESMP, periodically (but not less than every six (6) months), and update it as required to ensure that it contains measures appropriate to the Facilities. The updated C-ESMP shall be submitted to the Project Manager for its approval. 9.10 Training of Contractor’s Personnel The Contractor shall provide appropriate training to relevant Contractor’s Personnel on ES aspects of the Contract, including appropriate sensitization on prohibition of SEA and health and safety training referred to in GCC Sub-Clause 22.2.7. As stated in the Employer’s Requirements or as instructed by the Project Manager, the Contractor shall also allow appropriate opportunities for the relevant Contractor’s Personnel to be trained on ES aspects of the Contract by the Employer’s personnel and/or other personnel assigned by the Employer. 9.11 Stakeholder engagements The Contractor shall provide relevant contract- related information, as the Employer and/or Project Manager may reasonably request to conduct contract stakeholder engagement. “Stakeholder” refers to individuals or groups who: - are affected or likely to be affected by the Contract; and - may have an interest in the Contract. The Contractor may also directly participate in contract stakeholder engagements, as the Employer and/or Project Manager may reasonably request. 9.12 Forced Labor The Contractor, including its Subcontractors, shall not employ or engage forced labour. Forced labour consists of any work or service, not voluntarily performed, that is exacted from an individual under threat of force or penalty, and includes any kind of involuntary or compulsory labour, such as indentured labour, bonded labour or similar labour-contracting arrangements. No persons shall be employed or engaged who have been subject to trafficking. Trafficking in persons is defined as the recruitment, transportation, transfer, harbouring or receipt of persons by means of the threat or use of force or other forms of coercion, abduction, fraud, deception, abuse of power, or of a position of vulnerability, or of the giving or receiving of payments or benefits to achieve the consent of a person having control over another person, for the purposes of exploitation. The Contractor shall also take measures to require its suppliers (other than Subcontractors) not to employ or engage forced labour including trafficked persons. If forced labour/trafficking cases are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 9.13 Child Labor The Contractor, including its Subcontractors, shall not employ or engage a child under the age of 14 unless the national law specifies a higher age (the minimum age). The Contractor, including its Subcontractors, shall not employ or engage a child between the minimum age and the age of 18 in a manner that is likely to be hazardous, or to interfere with, the child’s education, or to be harmful to the child’s health or physical, mental, spiritual, moral, or social development. The Contractor including its Subcontractors, shall only employ or engage children between the minimum age and the age of 18 after an appropriate risk assessment has been conducted by the Contractor with the Engineer’s consent. The Contractor shall be subject to regular monitoring by the Project Manager that includes monitoring of health, working conditions and hours of work. Work considered hazardous for children is work that, by its nature or the circumstances in which it is carried out, is likely to jeopardize the health, safety, or morals of children. Such work activities prohibited for children include work: - with exposure to physical, psychological or sexual abuse; - underground, underwater, working at heights or in confined spaces; - with dangerous machinery, equipment or tools, or involving handling or transport of heavy loads; - in unhealthy environments exposing children to hazardous substances, agents, or processes, or to temperatures, noise or vibration damaging to health; or - under difficult conditions such as work for long hours, during the night or in confinement on the premises of the employer. The Contractor shall also take measures to require its suppliers (other than Subcontractors) not to employ or engage child labor. If child labor cases are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 9.14 Serious Safety Issues The Contractor, including its Subcontractors, shall comply with all applicable safety obligations. The Contractor shall also take measures to require its suppliers (other than Subcontractors) to adopt procedures and mitigation measures adequate to address safety issues related to their personnel. If serious safety issues are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 9.15 Obtaining natural resource materials The Contractor shall obtain natural resource materials from suppliers that can demonstrate, through compliance with the applicable verification and/ or certification requirements, that obtaining such materials is not contributing to the risk of significant conversion or significant degradation of natural or critical habitats such as unsustainably harvested wood products, gravel or sand extraction from river beds or beaches. If a supplier cannot continue to demonstrate that obtaining such materials is not contributing to the risk of significant conversion or significant degradation of natural or critical habitats, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to demonstrate that they are not significantly adversely impacting the habitats. |
| 10. Employer’s Responsibilities | 10.1 All information and/or data to be supplied by the Employer as described in the Appendix to the Contract Agreement titled Scope of Works and Supply by the Employer, shall be deemed to be accurate, except when the Employer expressly states otherwise. 10.2 The Employer shall be responsible for acquiring and providing legal and physical possession of the Site and access thereto, and for providing possession of and access to all other areas reasonably required for the proper execution of the Contract, including all requisite rights of way, as specified in the Appendix to the Contract Agreement titled Scope of Works and Supply by the Employer. The Employer shall give full possession of and accord all rights of access thereto on or before the date(s) specified in that Appendix. 10.3 The Employer shall acquire and pay for all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located which (a) such authorities or undertakings require the Employer to obtain in the Employer’s name, (b) are necessary for the execution of the Contract, including those required for the performance by both the Contractor and the Employer of their respective obligations under the Contract, and (c) are specified in the Appendix (Scope of Works and Supply by the Employer). 10.4 If requested by the Contractor, the Employer shall use its best endeavors to assist the Contractor in obtaining in a timely and expeditious manner all permits, approvals and/or licenses necessary for the execution of the Contract from all local, state or national government authorities or public service undertakings that such authorities or undertakings require the Contractor or Subcontractors or the personnel of the Contractor or Subcontractors, as the case may be, to obtain. 10.5 Unless otherwise specified in the Contract or agreed upon by the Employer and the Contractor, the Employer shall provide sufficient, properly qualified operating and maintenance personnel; shall supply and make available all raw materials, utilities, lubricants, chemicals, catalysts, other materials and facilities; and shall perform all work and services of whatsoever nature, including those required by the Contractor to properly carry out Precommissioning, Commissioning and Guarantee Tests, all in accordance with the provisions of the Appendix to the Contract Agreement titled Scope of Works and Supply by the Employer, at or before the time specified in the program furnished by the Contractor under GCC Sub-Clause 18.2 hereof and in the manner thereupon specified or as otherwise agreed upon by the Employer and the Contractor. 10.6 The Employer shall be responsible for the continued operation of the Facilities after Completion, in accordance with GCC Sub-Clause 24.8, and shall be responsible for facilitating the Guarantee Test(s) for the Facilities, in accordance with GCC Sub-Clause 25.2. 10.7 All costs and expenses involved in the performance of the obligations under this GCC Clause 10 shall be the responsibility of the Employer, save those to be incurred by the Contractor with respect to the performance of Guarantee Tests, in accordance with GCC Sub-Clause 25.2. 10.8 In the event that the Employer shall be in breach of any of his obligations under this Clause, the additional cost incurred by the Contractor in consequence thereof shall be determined by the Project Manager and added to the Contract Price. |

- Payment

| 11. Contract Price | 11.1 The Contract Price shall be as specified in Article 2 (Contract Price and Terms of Payment) of the Contract Agreement. 11.2 Unless an adjustment clause is provided for in the PCC, the Contract Price shall be a firm lump sum not subject to any alteration, except in the event of a Change in the Facilities or as otherwise provided in the Contract. 11.3 Subject to GCC Sub-Clauses 9.2, 10.1 and 35 hereof, the Contractor shall be deemed to have satisfied itself as to the correctness and sufficiency of the Contract Price, which shall, except as otherwise provided for in the Contract, cover all its obligations under the Contract. |
| --- | --- |
| 12. Terms of Payment | 12.1 The Contract Price shall be paid as specified in Article 2 (Contract Price and Terms of Payment) of the Contract Agreement and in the Appendix to the Contract Agreement titled Terms and Procedures of Payment, which also outlines the procedures to be followed in making application for and processing payments. 12.2 No payment made by the Employer herein shall be deemed to constitute acceptance by the Employer of the Facilities or any part(s) thereof. 12.3 In the event that the Employer fails to make any payment by its respective due date or within the period set forth in the Contract, the Employer shall pay to the Contractor interest on the amount of such delayed payment at the rate(s) shown in the Appendix to the Contract Agreement titled Terms and Procedures of Payment, for the period of delay until payment has been made in full, whether before or after judgment or arbitrage award. 12.4 The currency or currencies in which payments are made to the Contractor under this Contract shall be specified in the Appendix to the Contract Agreement titled Terms and Procedures of Payment, subject to the general principle that payments will be made in the currency or currencies in which the Contract Price has been stated in the Contractor’s Bid. |
| 13. Securities | 13.1 Issuance of Securities The Contractor shall provide the securities specified below in favor of the Employer at the times, and in the amount, manner and form specified below. 13.2 Advance Payment Security 13.2.1 The Contractor shall, within twenty-eight (28) days of the notification of contract award, provide a security in an amount equal to the advance payment calculated in accordance with the Appendix to the Contract Agreement titled Terms and Procedures of Payment, and in the same currency or currencies. 13.2.2 The security shall be in the form provided in the Bidding documents or in another form acceptable to the Employer. The amount of the security shall be reduced in proportion to the value of the Facilities executed by and paid to the Contractor from time to time, and shall automatically become null and void when the full amount of the advance payment has been recovered by the Employer. The security shall be returned to the Contractor immediately after its expiration. 13.3 Performance Security 13.3.1 The Contractor shall, within twenty-eight (28) days of the notification of contract award, provide a security for the due performance of the Contract in the amount specified in the PCC. 13.3.2 The Performance Security shall be denominated in the currency or currencies of the Contract, or in a freely convertible currency acceptable to the Employer, and shall be in the form provided in Section X, Contract Forms, corresponding to the type of bank guarantee stipulated by the Employer in the PCC, or in another form acceptable to the Employer. 13.3.3 Unless otherwise specified in the PCC, the security shall be reduced by half on the date of the Operational Acceptance. The Security shall become null and void, or shall be reduced pro rata to the Contract Price of a part of the Facilities for which a separate Time for Completion is provided, five hundred and forty (540) days after Completion of the Facilities or three hundred and sixty five (365) days after Operational Acceptance of the Facilities, whichever occurs first; provided, however, that if the Defects Liability Period has been extended on any part of the Facilities pursuant to GCC Sub-Clause 27.8 hereof, the Contractor shall issue an additional security in an amount proportionate to the Contract Price of that part. The security shall be returned to the Contractor immediately after its expiration, provided, however, that if the Contractor, pursuant to GCC Sub-Clause 27.10, is liable for an extended defect liability obligation, the Performance Security shall be extended for the period specified in the PCC pursuant to GCC Sub-Clause 27.10 and up to the amount specified in the PCC. 13.3.4 The Employer shall not make a claim under the Performance Security, except for amounts to which the Employer is entitled under the Contract. The Employer shall indemnify and hold the Contractor harmless against and from all damages, losses and expenses (including legal fees and expenses) resulting from a claim under the Performance Security to the extent to which the Employer was not entitled to make the claim. |
| 14. Taxes and Duties | 14.1 Except as otherwise specifically provided in the Contract, the Contractor shall bear and pay all taxes, duties, levies and charges assessed on the Contractor, its Subcontractors or their employees by all municipal, state or national government authorities in connection with the Facilities in and outside of the country where the Site is located. 14.2 Notwithstanding GCC Sub-Clause 14.1 above, the Employer shall bear and promptly pay (a) all customs and import duties for the Plant specified in Price Schedule No. 1; and (b) other domestic taxes such as, sales tax and value added tax (VAT) on the Plant specified in Price Schedules No. 1 and No. 2 and that is to be incorporated into the Facilities, and on the finished goods, imposed by the law of the country where the Site is located. 14.3 If any tax exemptions, reductions, allowances or privileges may be available to the Contractor in the country where the Site is located, the Employer shall use its best endeavors to enable the Contractor to benefit from any such tax savings to the maximum allowable extent. 14.4 For the purpose of the Contract, it is agreed that the Contract Price specified in Article 2 (Contract Price and Terms of Payment) of the Contract Agreement is based on the taxes, duties, levies and charges prevailing at the date twenty-eight (28) days prior to the date of Bid submission in the country where the Site is located (hereinafter called “Tax” in this GCC Sub-Clause 14.4). If any rates of Tax are increased or decreased, a new Tax is introduced, an existing Tax is abolished, or any change in interpretation or application of any Tax occurs in the course of the performance of Contract, which was or will be assessed on the Contractor, Subcontractors or their employees in connection with performance of the Contract, an equitable adjustment of the Contract Price shall be made to fully take into account any such change by addition to the Contract Price or deduction therefrom, as the case may be, in accordance with GCC Clause 36 hereof. |

- Intellectual Property

| 15. License/Use of Technical Information | - 15.1 For the operation and maintenance of the Plant, the Contractor hereby grants a non-exclusive and non-transferable license (without the right to sub-license) to the Employer under the patents, utility models or other industrial property rights owned by the Contractor or by a third Party from whom the Contractor has received the right to grant licenses thereunder, and shall also grant to the Employer a non-exclusive and non-transferable right (without the right to sub-license) to use the know-how and other technical information disclosed to the Employer under the Contract. Nothing contained herein shall be construed as transferring ownership of any patent, utility model, trademark, design, copyright, know-how or other intellectual property right from the Contractor or any third Party to the Employer. 15.2 The copyright in all drawings, documents and other materials containing data and information furnished to the Employer by the Contractor herein shall remain vested in the Contractor or, if they are furnished to the Employer directly or through the Contractor by any third Party, including suppliers of materials, the copyright in such materials shall remain vested in such third Party. |
| --- | --- |
| 16. Confidential Information | 16.1 The Employer and the Contractor shall keep confidential and shall not, without the written consent of the other Party hereto, divulge to any third Party any documents, data or other information furnished directly or indirectly by the other Party hereto in connection with the Contract, whether such information has been furnished prior to, during or following termination of the Contract. Notwithstanding the above, the Contractor may furnish to its Subcontractor(s) such documents, data and other information it receives from the Employer to the extent required for the Subcontractor(s) to perform its work under the Contract, in which event the Contractor shall obtain from such Subcontractor(s) an undertaking of confidentiality similar to that imposed on the Contractor under this GCC Clause 16. 16.2 The Employer shall not use such documents, data and other information received from the Contractor for any purpose other than the operation and maintenance of the Facilities. Similarly, the Contractor shall not use such documents, data and other information received from the Employer for any purpose other than the design, procurement of Plant, construction or such other work and services as are required for the performance of the Contract. 16.3 The obligation of a Party under GCC Sub-Clauses 16.1 and 16.2 above, however, shall not apply to that information which (a) now or hereafter enters the public domain through no fault of that Party (b) can be proven to have been possessed by that Party at the time of disclosure and which was not previously obtained, directly or indirectly, from the other Party hereto (c) otherwise lawfully becomes available to that Party from a third Party that has no obligation of confidentiality (d) is being provided to the Bank. 16.4 The above provisions of this GCC Clause 16 shall not in any way modify any undertaking of confidentiality given by either of the Parties hereto prior to the date of the Contract in respect of the Facilities or any part thereof. 16.5 The provisions of this GCC Clause 16 shall survive termination, for whatever reason, of the Contract. |

- Execution of the Facilities

| 17. Representatives | 17.1 Project Manager If the Project Manager is not named in the Contract, then within fourteen (14) days of the Effective Date, the Employer shall appoint and notify the Contractor in writing of the name of the Project Manager. The Employer may from time to time appoint some other person as the Project Manager in place of the person previously so appointed, and shall give a notice of the name of such other person to the Contractor without delay. No such appointment shall be made at such a time or in such a manner as to impede the progress of work on the Facilities. Such appointment shall only take effect upon receipt of such notice by the Contractor. The Project Manager shall represent and act for the Employer at all times during the performance of the Contract. All notices, instructions, orders, certificates, approvals and all other communications under the Contract shall be given by the Project Manager, except as herein otherwise provided. All notices, instructions, information and other communications given by the Contractor to the Employer under the Contract shall be given to the Project Manager, except as herein otherwise provided. 17.2 Contractor’s Representative & Construction Manager 17.2.1 If the Contractor’s Representative is not named in the Contract, then within fourteen (14) days of the Effective Date, the Contractor shall appoint the Contractor’s Representative and shall request the Employer in writing to approve the person so appointed. If the Employer makes no objection to the appointment within fourteen (14) days, the Contractor’s Representative shall be deemed to have been approved. If the Employer objects to the appointment within fourteen (14) days giving the reason therefor, then the Contractor shall appoint a replacement within fourteen (14) days of such objection, and the foregoing provisions of this GCC Sub-Clause 17.2.1 shall apply thereto. 17.2.2 The Contractor’s Representative shall represent and act for the Contractor at all times during the performance of the Contract and shall give to the Project Manager all the Contractor’s notices, instructions, information and all other communications under the Contract. All notices, instructions, information and all other communications given by the Employer or the Project Manager to the Contractor under the Contract shall be given to the Contractor’s Representative or, in its absence, its deputy, except as herein otherwise provided. The Contractor shall not revoke the appointment of the Contractor’s Representative without the Employer’s prior written consent, which shall not be unreasonably withheld. If the Employer consents thereto, the Contractor shall appoint some other person as the Contractor’s Representative, pursuant to the procedure set out in GCC Sub-Clause 17.2.1. 17.2.3 The Contractor’s Representative may, subject to the approval of the Employer which shall not be unreasonably withheld, at any time delegate to any person any of the powers, functions and authorities vested in him or her. Any such delegation may be revoked at any time. Any such delegation or revocation shall be subject to a prior notice signed by the Contractor’s Representative, and shall specify the powers, functions and authorities thereby delegated or revoked. No such delegation or revocation shall take effect unless and until a copy thereof has been delivered to the Employer and the Project Manager. Any act or exercise by any person of powers, functions and authorities so delegated to him or her in accordance with this GCC Sub-Clause 17.2.3 shall be deemed to be an act or exercise by the Contractor’s Representative. 17.2.4 From the commencement of installation of the Facilities at the Site until Completion, the Contractor’s Representative shall appoint a suitable person as the Construction Manager. The Construction Manager shall supervise all work done at the Site by the Contractor and shall be present at the Site throughout normal working hours except when on leave, sick or absent for reasons connected with the proper performance of the Contract. Whenever the Construction Manager is absent from the Site, a suitable person shall be appointed to act as the Construction Manager’s deputy. 17.2.5 The Project Manager may require the Contractor to remove (or cause to be removed) the Contractor’s Representative or any other person employed by the Contractor in the execution of the Contract, who: - persists in any misconduct or lack of care; - carries out duties incompetently or negligently; - fails to comply with any provision of the Contract; - persists in any conduct which is prejudicial to safety, health, or the protection of the environment; - based on reasonable evidence, is determined to have engaged in Fraud and Corruption during the execution of the Contract; - has been recruited from the Employer’s Personnel in breach of GCC Sub-Clause 22.2.2; - undertakes behaviour which breaches the Code of Conduct (ES), as applicable; If appropriate, the Contractor shall then promptly appoint (or cause to be appointed) a suitable replacement with equivalent skills and experience. Notwithstanding any requirement from the Project Manager to remove or cause to remove any person, the Contractor shall take immediate action as appropriate in response to any violation of (a) through (g) above. Such immediate action shall include removing (or causing to be removed) from the Site or other places where the Contract is being executed, any Contractor’s Personnel who engages in (a), (b), (c), (d), (e) or (g) above or has been recruited as stated in (f) above.. 17.2.6 If any representative or person employed by the Contractor is removed in accordance with GCC Sub-Clause 17.2.5, the Contractor shall, where required, promptly appoint a suitable replacement with equivalent skills and experience. |
| --- | --- |
| 18. Work Program | 18.1 Contractor’s Organization The Contractor shall supply to the Employer and the Project Manager a chart showing the proposed organization to be established by the Contractor for carrying out work on the Facilities within twenty-one (21) days of the Effective Date. The chart shall include the identities of the key personnel and the curricula vitae of such key personnel to be employed shall be supplied together with the chart. The Contractor shall promptly inform the Employer and the Project Manager in writing of any revision or alteration of such an organization chart. 18.2 Program of Performance Within twenty-eight (28) days after the Effective Date, the Contractor shall submit to the Project Manager a detailed program of performance of the Contract, made in a form acceptable to the Project Manager and showing the sequence in which it proposes to design, manufacture, transport, assemble, install and precommission the Facilities, as well as the date by which the Contractor reasonably requires that the Employer shall have fulfilled its obligations under the Contract so as to enable the Contractor to execute the Contract in accordance with the program and to achieve Completion, Commissioning and Acceptance of the Facilities in accordance with the Contract. The program so submitted by the Contractor shall accord with the Time Schedule included in the Appendix to the Contract Agreement titled Time Schedule, and any other dates and periods specified in the Contract. The Contractor shall update and revise the program as and when appropriate or when required by the Project Manager, but without modification in the Times for Completion specified in the PCC pursuant to Sub-Clause 8.2 and any extension granted in accordance with GCC Clause 40, and shall submit all such revisions to the Project Manager. 18.3 Progress Report The Contractor shall monitor progress of all the activities specified in the program referred to in GCC Sub-Clause 18.2 above, and supply a progress report to the Project Manager every month. The progress report shall be in a form acceptable to the Project Manager and shall indicate: (a) percentage completion achieved compared with the planned percentage completion for each activity; and (b) where any activity is behind the program, giving comments and likely consequences and stating the corrective action being taken. Unless otherwise stated in the Employer’s Requirements, each progress report shall include the Environmental and Social (ES) metrics set out in Appendix C. In addition to the progress reports, the Contractor shall inform the Project Manager immediately of any allegation, incident or accident in the Site, which has or is likely to have a significant adverse effect on the environment, the affected communities, the public, Employer’s Personnel or Contractor’s Personnel. This includes, but is not limited to, any incident or accident causing fatality or serious injury; significant adverse effects or damage to private property; or any allegation of SEA and/or SH. In case of SEA and/or SH, while maintaining confidentiality as appropriate, the type of allegation (sexual exploitation, sexual abuse or sexual harassment), gender and age of the person who experienced the alleged incident should be included in the information. The Contractor, upon becoming aware of the allegation, incident or accident, shall also immediately inform the Project Manager of any such incident or accident on the Subcontractors’ or suppliers’ premises relating to the Facilities which has or is likely to have a significant adverse effect on the environment, the affected communities, the public, Employer’s Personnel, or Contractor’s, its Subcontractors’ and suppliers’ personnel. The notification shall provide sufficient detail regarding such incidents or accidents. The Contractor shall provide full details of such incidents or accidents to the Project Manager within the timeframe agreed with the Project Manager. The Contractor shall require its Subcontractors and suppliers to immediately notify the Contractor of any incidents or accidents referred to in this Subclause. 18.4 Progress of Performance If at any time the Contractor’s actual progress falls behind the program referred to in GCC Sub-Clause 18.2, or it becomes apparent that it will so fall behind, the Contractor shall, at the request of the Employer or the Project Manager, prepare and submit to the Project Manager a revised program, taking into account the prevailing circumstances, and shall notify the Project Manager of the steps being taken to expedite progress so as to attain Completion of the Facilities within the Time for Completion under GCC Sub-Clause 8.2, any extension thereof entitled under GCC Sub-Clause 40.1, or any extended period as may otherwise be agreed upon between the Employer and the Contractor. 18.5 Procedures The Contract shall be executed in accordance with the Contract Documents including the procedures given in the Forms and Procedures of the Employer’s Requirements. The Contractor may execute the Contract in accordance with its own standard project execution plans and procedures to the extent that they do not conflict with the provisions contained in the Contract. |
| 19. Subcontracting | 19.1 The Appendix to the Contract Agreement titled List of Major Items of Plant and Installation Services and List of Approved Subcontractors, specifies major items of supply or services and a list of approved Subcontractors against each item, including manufacturers. Insofar as no Subcontractors are listed against any such item, the Contractor shall prepare a list of Subcontractors for such item for inclusion in such list. The Contractor may from time to time propose any addition to or deletion from any such list. The Contractor shall submit any such list or any modification thereto to the Employer for its approval in sufficient time so as not to impede the progress of work on the Facilities. Submission by the Contractor, for addition of any Subcontractor not named in the Contract, shall also include the Subcontractor’s declaration in accordance with Appendix D- Sexual exploitation and Abuse (SEA) and/or Sexual Harassment (SH) Performance Declaration. Approval by the Employer for any of the Subcontractors shall not relieve the Contractor from any of its obligations, duties or responsibilities under the Contract. 19.2 The Contractor shall select and employ its Subcontractors for such major items from those listed in the lists referred to in GCC Sub-Clause 19.1. 19.3 For items or parts of the Facilities not specified in the Appendix to the Contract Agreement titled List of Major Items of Plant and Installation Services and List of Approved Subcontractors, the Contractor may employ such Subcontractors as it may select, at its discretion. 19.4 Each sub-contract shall include provisions which would entitle the Employer to require the sub-contract to be assigned to the Employer under GCC 19.5 (if and when applicable), or in event of termination by the Employer under GCC 42.2. 19.5 If a Subcontractor's obligations extend beyond the expiry date of the relevant Defects Liability Period and the Project Manager, prior to that date, instructs the Contractor to assign the benefits of such obligations to the Employer, then the Contractor shall do so. 19.6 The Contractor shall ensure that its Subcontractors execute the Facilities in accordance with the Contract, including complying with the relevant ES requirements and the obligations set out in GCC Sub-Clause 22.4. |
| 20. Design and Engineering | 20.1 Specifications and Drawings 20.1.1 The Contractor shall execute the basic and detailed design and the engineering work in compliance with the provisions of the Contract, or where not so specified, in accordance with good engineering practice. The Contractor shall be responsible for any discrepancies, errors or omissions in the specifications, drawings and other technical documents that it has prepared, whether such specifications, drawings and other documents have been approved by the Project Manager or not, provided that such discrepancies, errors or omissions are not because of inaccurate information furnished in writing to the Contractor by or on behalf of the Employer. 20.1.2 The Contractor shall be entitled to disclaim responsibility for any design, data, drawing, specification or other document, or any modification thereof provided or designated by or on behalf of the Employer, by giving a notice of such disclaimer to the Project Manager. 20.2 Codes and Standards Wherever references are made in the Contract to codes and standards in accordance with which the Contract shall be executed, the edition or the revised version of such codes and standards current at the date twenty-eight (28) days prior to date of Bid submission shall apply unless otherwise specified. During Contract execution, any changes in such codes and standards shall be applied subject to approval by the Employer and shall be treated in accordance with GCC Clause 39. 20.3 Approval/Review of Technical Documents by Project Manager 20.3.1 The Contractor shall prepare or cause its Subcontractors to prepare, and furnish to the Project Manager the documents listed in the Appendix to the Contract Agreement titled List of Documents for Approval or Review, for its approval or review as specified and in accordance with the requirements of GCC Sub-Clause 18.2 (Program of Performance). Any part of the Facilities covered by or related to the documents to be approved by the Project Manager shall be executed only after the Project Manager’s approval thereof. GCC Sub-Clauses 20.3.2 through 20.3.7 shall apply to those documents requiring the Project Manager’s approval, but not to those furnished to the Project Manager for its review only. 20.3.2 Within fourteen (14) days after receipt by the Project Manager of any document requiring the Project Manager’s approval in accordance with GCC Sub-Clause 20.3.1, the Project Manager shall either return one copy thereof to the Contractor with its approval endorsed thereon or shall notify the Contractor in writing of its disapproval thereof and the reasons therefor and the modifications that the Project Manager proposes. If the Project Manager fails to take such action within the said fourteen (14) days, then the said document shall be deemed to have been approved by the Project Manager. 20.3.3 The Project Manager shall not disapprove any document, except on the grounds that the document does not comply with the Contract or that it is contrary to good engineering practice. 20.3.4 If the Project Manager disapproves the document, the Contractor shall modify the document and resubmit it for the Project Manager’s approval in accordance with GCC Sub-Clause 20.3.2. If the Project Manager approves the document subject to modification(s), the Contractor shall make the required modification(s), whereupon the document shall be deemed to have been approved. 20.3.5 If any dispute or difference occurs between the Employer and the Contractor in connection with or arising out of the disapproval by the Project Manager of any document and/or any modification(s) thereto that cannot be settled between the Parties within a reasonable period, then such dispute or difference may be referred to a Dispute Board for determination in accordance with GCC Sub-Clause 46.1 hereof. If such dispute or difference is referred to a Dispute Board, the Project Manager shall give instructions as to whether and if so, how, performance of the Contract is to proceed. The Contractor shall proceed with the Contract in accordance with the Project Manager’s instructions, provided that if the Dispute Board upholds the Contractor’s view on the dispute and if the Employer has not given notice under GCC Sub-Clause 46.3 hereof, then the Contractor shall be reimbursed by the Employer for any additional costs incurred by reason of such instructions and shall be relieved of such responsibility or liability in connection with the dispute and the execution of the instructions as the Dispute Board shall decide, and the Time for Completion shall be extended accordingly. 20.3.6 The Project Manager’s approval, with or without modification of the document furnished by the Contractor, shall not relieve the Contractor of any responsibility or liability imposed upon it by any provisions of the Contract except to the extent that any subsequent failure results from modifications required by the Project Manager. 20.3.7 The Contractor shall not depart from any approved document unless the Contractor has first submitted to the Project Manager an amended document and obtained the Project Manager’s approval thereof, pursuant to the provisions of this GCC Sub-Clause 20.3. If the Project Manager requests any change in any already approved document and/or in any document based thereon, the provisions of GCC Clause 39 shall apply to such request. |
| 21. Procurement | 21.1 Plant Subject to GCC Sub-Clause 14.2, the Contractor shall procure and transport all Plant in an expeditious and orderly manner to the Site. 21.2 Employer-Supplied Plant If the Appendix to the Contract Agreement titled Scope of Works and Supply by the Employer, provides that the Employer shall furnish any specific items to the Contractor, the following provisions shall apply: 21.2.1 The Employer shall, at its own risk and expense, transport each item to the place on or near the Site as agreed upon by the Parties and make such item available to the Contractor at the time specified in the program furnished by the Contractor, pursuant to GCC Sub-Clause 18.2, unless otherwise mutually agreed. 21.2.2 Upon receipt of such item, the Contractor shall inspect the same visually and notify the Project Manager of any detected shortage, defect or default. The Employer shall immediately remedy any shortage, defect or default, or the Contractor shall, if practicable and possible, at the request of the Employer, remedy such shortage, defect or default at the Employer’s cost and expense. After inspection, such item shall fall under the care, custody and control of the Contractor. The provision of this GCC Sub-Clause 21.2.2 shall apply to any item supplied to remedy any such shortage or default or to substitute for any defective item, or shall apply to defective items that have been repaired. 21.2.3 The foregoing responsibilities of the Contractor and its obligations of care, custody and control shall not relieve the Employer of liability for any undetected shortage, defect or default, nor place the Contractor under any liability for any such shortage, defect or default whether under GCC Clause 27 or under any other provision of Contract. 21.3 Transportation 21.3.1 The Contractor shall at its own risk and expense transport all the materials and the Contractor’s Equipment to the Site by the mode of transport that the Contractor judges most suitable under all the circumstances. 21.3.2 Unless otherwise provided in the Contract, the Contractor shall be entitled to select any safe mode of transport operated by any person to carry the materials and the Contractor’s Equipment. 21.3.3 Upon dispatch of each shipment of materials and the Contractor’s Equipment, the Contractor shall notify the Employer by telex, cable, facsimile or electronic means, of the description of the materials and of the Contractor’s Equipment, the point and means of dispatch, and the estimated time and point of arrival in the country where the Site is located, if applicable, and at the Site. The Contractor shall furnish the Employer with relevant shipping documents to be agreed upon between the Parties. 21.3.4 The Contractor shall be responsible for obtaining, if necessary, approvals from the authorities for transportation of the materials and the Contractor’s Equipment to the Site. The Employer shall use its best endeavors in a timely and expeditious manner to assist the Contractor in obtaining such approvals, if requested by the Contractor. The Contractor shall indemnify and hold harmless the Employer from and against any claim for damage to roads, bridges or any other traffic facilities that may be caused by the transport of the materials and the Contractor’s Equipment to the Site. 21.4 Customs Clearance The Contractor shall, at its own expense, handle all imported materials and Contractor’s Equipment at the point(s) of import and shall handle any formalities for customs clearance, subject to the Employer’s obligations under GCC Sub-Clause 14.2, provided that if applicable laws or regulations require any application or act to be made by or in the name of the Employer, the Employer shall take all necessary steps to comply with such laws or regulations. In the event of delays in customs clearance that are not the fault of the Contractor, the Contractor shall be entitled to an extension in the Time for Completion, pursuant to GCC Clause 40. |
| 22. Installation | 22.1 Setting Out/Supervision 22.1.1 Bench Mark: The Contractor shall be responsible for the true and proper setting-out of the Facilities in relation to bench marks, reference marks and lines provided to it in writing by or on behalf of the Employer. If, at any time during the progress of installation of the Facilities, any error shall appear in the position, level or alignment of the Facilities, the Contractor shall forthwith notify the Project Manager of such error and, at its own expense, immediately rectify such error to the reasonable satisfaction of the Project Manager. If such error is based on incorrect data provided in writing by or on behalf of the Employer, the expense of rectifying the same shall be borne by the Employer. 22.1.2 Contractor’s Supervision: The Contractor shall give or provide all necessary superintendence during the installation of the Facilities, and the Construction Manager or its deputy shall be constantly on the Site to provide full-time superintendence of the installation. The Contractor shall provide and employ only technical personnel who are skilled and experienced in their respective callings and supervisory staff who are competent to adequately supervise the work at hand. 22.2 Labor: 22.2.1 Engagement of Staff and Labor Except as otherwise stated in the Employer’s Requirements, the Contractor shall make arrangements for the engagement of all staff and labor, local or otherwise, and for their payment, housing, feeding and transport. The Contractor shall provide and employ on the Site in the installation of the Facilities such skilled, semi-skilled and unskilled labor as is necessary for the proper and timely execution of the Contract. The Contractor is encouraged to use local labor that has the necessary skills. The Contractor shall be responsible for obtaining all necessary permit(s) and/or visa(s) from the appropriate authorities for the entry of all labor and personnel to be employed on the Site into the country where the Site is located. The Employer will, if requested by the Contractor, use his best endeavors in a timely and expeditious manner to assist the Contractor in obtaining any local, state, national or government permission required for bringing in the Contractor’s Personnel. The Contractor shall at its own expense provide the means of repatriation to all of its Contractor’s Personnel employed for the excution of the Contract at the Site or other places where the Installation Services are carried out to the place where they were recruited or to their domicile. It shall also provide suitable temporary maintenance of all such persons from the cessation of their employment on the Contract to the date programmed for their departure. In the event that the Contractor defaults in providing such means of transportation and temporary maintenance, the Employer may provide the same to such personnel and recover the cost of doing so from the Contractor. The Contractor shall provide Contractor’s Personnel employed for the execution of the Contract at the Site or other places where the Installation Services are carried out, relevant information and documentation that are clear and understandable regarding their terms and conditions of employment. The information and documentation shall set out their rights under relevant labor laws applicable to the Contractor’s Personnel (which will include any applicable collective agreements), including their rights related to hours of work, wages, overtime, compensation and benefits, as well as those arising from any requirements in the Employer’s Requirements. The Contractor’s Personnel shall be informed when any material changes to their terms or conditions of employment occur. 22.2.2 Persons in the Service of Employer The Contractor shall not recruit, or attempt to recruit, staff and labor from amongst the Employer’s Personnel. 22.2.3 Labor Laws The Contractor shall comply with all the relevant labor laws applicable to the Contractor’s Personnel, including laws relating to their employment, health, safety, welfare, immigration and emigration, and shall allow them all their legal rights. The Contractor shall at all times during the progress of the Contract use its best endeavors to prevent any unlawful, riotous or disorderly conduct or behavior by or amongst its employees and the labor of its Subcontractors. The Contractor shall, in all dealings with its labor and the labor of its Subcontractors currently employed on or connected with the Contract, pay due regard to all recognized festivals, official holidays, religious or other customs and all local laws and regulations pertaining to the employment of labor. 22.2.4 Rates of Wages and Conditions of Labor The Contractor shall pay rates of wages, and observe conditions of labor, which are not lower than those established for the trade or industry where the work is carried out. If no established rates or conditions are applicable, the Contractor shall pay rates of wages and observe conditions which are not lower than the general level of wages and conditions observed locally by employers whose trade or industry is similar to that of the Contractor. The Contractor shall inform the Contractor’s Personnel about: - any deduction to their payment and the conditions of such deductions in accordance with the applicable laws or as stated in the Employer’s Requirements; and - their liability to pay personal income taxes in the Country in respect of such of their salaries, wages, allowances and any benefits as are subject to tax under the laws of the Country for the time being in force. The Contractor shall perform such duties in regard to such deductions thereof as may be imposed on him by such laws. Where required by applicable Laws or as stated in the Employer’s Requirements, the Contractor and its Subcontarctors shall provide their personnel written notice of termination of employment and details of severance payments in a timely manner. The Contractor and its Subcontractors shall have paid their personnel (either directly or where appropriate for their benefit) all due wages and entitlements including, as applicable, social security benefits and pension contributions, on or before the end of their engagement/ employment. 22.2.5 Working Hours No work shall be carried out on the Site on locally recognized days of rest, or outside the normal working hours stated in the PCC, unless: (a) otherwise stated in the Contract, (b) the Project Manager gives consent, or (c) the work is unavoidable, or necessary for the protection of life or property or for the safety of the Facilities, in which case the Contractor shall immediately advise the Project Manager. If and when the Contractor considers it necessary to carry out work at night or on public holidays so as to meet the Time for Completion and requests the Project Manager’s consent thereto, the Project Manager shall not unreasonably withhold such consent. This Sub-Clause shall not apply to any work which is customarily carried out by rotary or double-shifts. 22.2.6 Facilities for Staff and Labor Except as otherwise stated in the Employer’s Requirements, the Contractor shall provide and maintain all necessary accommodation and welfare facilities for the Contractor’s Personnel employed for the execution of the Contract at the Site or other places where the Installation Services are carried out. The Contractor shall also provide facilities for the Employer’s Personnel as stated in the Employer’s Requirements. If stated in the Employer’s Requirements, the Contractor shall give access to or provide services that accommodate the physical, social and cultural needs of the Contractor’s Personnel. The Contractor shall also provide similar facilities for the Employer’s Personnel as stated in the Employer’s Requirements. The Contractor shall not permit any of the Contractor’s Personnel to maintain any temporary or permanent living quarters within the structures forming part of the Facilities. 22.2.7 Health and Safety The Contractor shall at all times take all reasonable precautions to maintain the health and safety of the Contractor’s Personnel employed for the execution of Installation Services at the Site (or other places in the country where the Site is located). Subject to GCC Sub-Clause 9.9, the Contractor shall submit to the Project Manager for its approval a health and safety manual which sets out all the health and safety requirements under the Contract. The health and safety manual shall be in addition to any other similar document required under applicable health and safety regulations and Laws. The Contractor shall: - comply with all applicable health and safety regulations and laws; - comply with all applicable health and safety obligations specified in the Contract; - develop and implement procedures to establish and maintain a safe working environment without risk to health at all workplaces, machinery, equipment and processes under the control of the Contractor, including control measures for chemical, physical and biological substances and agents; - provide health and safety training of the Contractor’s Personnel as appropriate and maintain training records; - actively engage the Contractor’s Personnel in promoting understanding, and methods for, implementation of health and safety requirements, as well as in providing information to such personnel, and provision of personal protective equipment without expense to the personnel; - put in place workplace processes for the Contractor’s Personnel to report work situations that they believe are not safe or healthy, and to remove themselves from a work situation which they have reasonable justification to believe presents an imminent and serious danger to their life or health; Contractor’s Personnel who remove themselves from such work situations shall not be required to return to work until necessary remedial action to correct the situation has been taken. Such personnel shall not be retaliated against or otherwise subject to reprisal or negative action for such reporting or removal; - in collaboration with local health authorities, ensure that medical staff, first aid facilities, sick bay and ambulance service are available at all times at the Site and at any accommodation for Contractor’s and Employer’s Personnel; - appoint an accident prevention officer at the Site, responsible for maintaining safety and protection against accidents. This person shall be qualified for this responsibility, and shall have the authority to issue instructions and take protective measures to prevent accidents. Throughout the performance of the Contract, the Contractor shall provide whatever is required by this person to exercise this responsibility and authority; - put in place measures to avoid or minimize the potential for community exposure to water-borne, water-based, water-related, and vector-borne diseases; - put in place measures to be implemented to avoid or minimize the spread of communicable diseases (including transfer of Sexually Transmitted Diseases or Infections (STDs), such as HIV virus) and non-communicable diseases associated with the Installation Services, taking into consideration differentiated exposure to and higher sensitivity of vulnerable groups. This includes taking measures to avoid or minimize the transmission of communicable diseases that may be associated with the influx of temporary or permanent Contract-related labor; - have in place procedures for prevention, preparedness and response activities to be implemented in the case of an emergency event (i.e. an unanticipated incident, arising from both natural and man-made hazards, typically in the form of fire, explosions, leaks or spills, which may occur for a variety of different reasons including failure to implement operating procedures that are designed to prevent their occurrence, extreme weather or lack of early warning); - collaborate, as applicable, with the Employer’s Personnel, any other contractors employed by the Employer, and/or personnel of any legally constituted public authorities and private utility companies that are employed in carrying out, on or near the site, of any work not included in the Contract, in applying the health and safety requirements. This is without prejudice to the responsibility of the relevant entities for the health and safety of their own personnel; and - put in place a system for regular review of health and safety performance and the working environment. 22.2.8 Funeral Arrangements In the event of the death of any of the Contractor’s Personnel or accompanying members of their families, the Contractor shall be responsible for making the appropriate arrangements for their return or burial, unless otherwise specified in the PCC. 22.2.9 Records of Contractor’s Personnel The Contractor shall keep accurate records of the Contractor’s Personnel, including the number of each class of Contractor’s personnel on the Site and the names, ages, genders, hours worked and wages paid to all workers. These records shall be summarized on a monthly basis in a form approved by the Project Manager and shall be available for inspection by the Project Manager until the Contractor has completed all work. 22.2.10 Supply of Foodstuffs The Contractor shall arrange for the provision of a sufficient supply of suitable food as may be stated in the Employer’s Requirements at reasonable prices for the Contractor’s personnel for the purposes of or in connection with the Contract. 22.2.11 Supply of Water The Contractor shall, having regard to local conditions, provide on the Site an adequate supply of drinking and other water for the use of the Contractor’s personnel. 22.2.12 Measures against Insect and Pest Nuisance The Contractor shall at all times take the necessary precautions to protect the Contractor’s Personnel employed on the Site from insect and pest nuisance, and to reduce their danger to health. The Contractor shall comply with all the regulations of the local health authorities, including use of appropriate insecticide. 22.2.13 Alcoholic Liquor or Drugs The Contractor shall not, otherwise than in accordance with the laws of the Country, import, sell, give barter or otherwise dispose of any alcoholic liquor or drugs, or permit or allow importation, sale, gift barter or disposal by Contractor's Personnel. 22.2.14 Arms and Ammunition The Contractor shall not give, barter, or otherwise dispose of, to any person, any arms or ammunition of any kind, or allow Contractor's Personnel to do so. 22.2.15 Workers’ Organizations In countries where the relevant labor laws recognize workers’ rights to form and to join workers’ organizations of their choosing and to bargain collectively without interference, the Contractor shall comply with such laws. In such circumstances, the role of legally established workers’ organizations and legitimate workers’ representatives will be respected, and they will be provided with information needed for meaningful negotiation in a timely manner. Where the relevant labor laws substantially restrict workers’ organizations, the Contractor shall enable alternative means for the Contractor’s Personnel to express their grievances and protect their rights regarding working conditions and terms of employment. The Contractor shall not seek to influence or control these alternative means. The Contractor shall not discriminate or retaliate against the Contractor’s Personnel who participate, or seek to participate, in such organizations and collective bargaining or alternative mechanisms. Workers’ organizations are expected to fairly represent the workers in the workforce. 22.2.16 Non-Discrimination and Equal Opportunity The Contractor shall not make decisions relating to the employment or treatment of Contractor’s Personnel on the basis of personal characteristics unrelated to inherent job requirements. The Contractor shall base the employment of Contractor’s Personnel on the principle of equal opportunity and fair treatment, and shall not discriminate with respect to any aspects of the employment relationship, including recruitment and hiring, compensation (including wages and benefits), working conditions and terms of employment, access to training, job assignment, promotion, termination of employment or retirement, and disciplinary practices. Special measures of protection or assistance to remedy past discrimination or selection for a particular job based on the inherent requirements of the job shall not be deemed discrimination. The Contractor shall provide protection and assistance as necessary to ensure non-discrimination and equal opportunity, including for specific groups such as women, people with disabilities, migrant workers and children (of working age in accordance with GCC Sub-Clause 9.13). 22.2.17 Contractor’s Personnel Grievance Mechanism The Contractor shall have a grievance mechanism for the Contractor’s Personnel, and where relevant the workers’ organizations stated in subclause 22.2.15, to raise workplace concerns. The grievance mechanism shall be proportionate to the nature, scale, risks and impacts of the Contract. The mechanism shall address concerns promptly, using an understandable and transparent process that provides timely feedback to those concerned in a language they understand, without any retribution, and shall operate in an independent and objective manner. The Contractor’s Personnel shall be informed of the grievance mechanism at the time of engagement for the Contract, and the measures put in place to protect them against any reprisal for its use. Measures will be put in place to make the grievance mechanism easily accessible to all Contractor’s Personnel. The grievance mechanism shall not impede access to other judicial or administrative remedies that might be available, or substitute for grievance mechanisms provided through collective agreements. The grievance mechanism may utilize existing grievance mechanisms, providing that they are properly designed and implemented, address concerns promptly, and are readily accessible to such project workers. Existing grievance mechanisms may be supplemented as needed with Contract-specific arrangements. 22.3 Contractor’s Equipment 22.3.1 All Contractor’s Equipment brought by the Contractor onto the Site shall be deemed to be intended to be used exclusively for the execution of the Contract. The Contractor shall not remove the same from the Site without the Project Manager’s consent that such Contractor’s Equipment is no longer required for the execution of the Contract. 22.3.2 Unless otherwise specified in the Contract, upon completion of the Facilities, the Contractor shall remove from the Site all Equipment brought by the Contractor onto the Site and any surplus materials remaining thereon. 22.3.3 The Employer will, if requested, use its best endeavors to assist the Contractor in obtaining any local, state or national government permission required by the Contractor for the export of the Contractor’s Equipment imported by the Contractor for use in the execution of the Contract that is no longer required for the execution of the Contract. 22.4 Site Regulations The Employer and the Contractor shall establish Site regulations setting out the rules to be observed in the execution of the Contract at the Site and shall comply therewith. The Contractor shall prepare and submit to the Project Manager with a copy to the Employer, proposed Site regulations for the Project Manager’s approval, which approval shall not be unreasonably withheld. Such Site regulations shall include, but shall not be limited to, Code of Conduct for environmental and social aspectssubmitted as part of the Bid and agreed to by the Employer, , security arrangements in accordance with GCC Sub-Clause 22.8, safety of the Facilities, gate control, sanitation, medical care, and fire prevention. The Contractor shall take all necessary measures to ensure that each Contractor’s Personnel, employed for the execution of the Contract at the Site or other places where the Installation Services are carried out, is made aware of the Code of Conduct including specific behaviors that are prohibited, and understands the consequences of engaging in such prohibited behaviors. These measures include providing instructions and documentation that can be understood by the Contractor’s Personnel and seeking to obtain that person’s signature acknowledging receipt of such instructions and/or documentation, as appropriate. The Contractor shall also ensure that the Code of Conduct is visibly displayed in multiple locations on the Site and any other place where the Installation Services will be carried out, as well as in areas outside the Site accessible to the local community and project affected people. The posted Code of Conduct shall be provided in languages comprehensible to Contractor’s Personnel, Employer’s Personnel and the local community. The Contractor’s Management Strategy and Implementation Plans shall include appropriate processes for the Contractor to verify compliance with these obligations. 22.5 Opportunities for Other Contractors 22.5.1 The Contractor shall, upon written request from the Employer or the Project Manager, give all reasonable opportunities for carrying out the work to any other contractors employed by the Employer on or near the Site. 22.5.2 If the Contractor, upon written request from the Employer or the Project Manager, makes available to other contractors any roads or ways the maintenance for which the Contractor is responsible, permits the use by such other contractors of the Contractor’s Equipment, or provides any other service of whatsoever nature for such other contractors, the Employer shall fully compensate the Contractor for any loss or damage caused or occasioned by such other contractors in respect of any such use or service, and shall pay to the Contractor reasonable remuneration for the use of such equipment or the provision of such services. 22.5.3 The Contractor shall also so arrange to perform its work as to minimize, to the extent possible, interference with the work of other contractors. The Project Manager shall determine the resolution of any difference or conflict that may arise between the Contractor and other contractors and the workers of the Employer in regard to their work. 22.5.4 The Contractor shall notify the Project Manager promptly of any defects in the other contractors’ work that come to its notice, and that could affect the Contractor’s work. The Project Manager shall determine the corrective measures, if any, required to rectify the situation after inspection of the Facilities. Decisions made by the Project Manager shall be binding on the Contractor. 22.6 Emergency Work If, by reason of an emergency arising in connection with and during the execution of the Contract, any protective or remedial work is necessary as a matter of urgency to prevent damage to the Facilities, the Contractor shall immediately carry out such work. If the Contractor is unable or unwilling to do such work immediately, the Employer may do or cause such work to be done as the Employer may determine is necessary in order to prevent damage to the Facilities. In such event the Employer shall, as soon as practicable after the occurrence of any such emergency, notify the Contractor in writing of such emergency, the work done and the reasons therefor. If the work done or caused to be done by the Employer is work that the Contractor was liable to do at its own expense under the Contract, the reasonable costs incurred by the Employer in connection therewith shall be paid by the Contractor to the Employer. Otherwise, the cost of such remedial work shall be borne by the Employer. 22.7 Site Clearance 22.7.1 Site Clearance in Course of Performance: In the course of carrying out the Contract, the Contractor shall keep the Site reasonably free from all unnecessary obstruction, store or remove any surplus materials, clear away any wreckage, rubbish or temporary works from the Site, and remove any Contractor’s Equipment no longer required for execution of the Contract. 22.7.2 Clearance of Site after Completion: After Completion of all parts of the Facilities, the Contractor shall clear away and remove all wreckage, rubbish and debris of any kind from the Site, and shall leave the Site and Facilities in a clean and safe condition. 22.8 Security of the Site The Contractor shall be responsible for the security of the Site including providing and maintaining at its own expense all lighting, fencing, and watching when and where necessary for the proper execution and the protection of the Facilities, or for the safety of the owners and occupiers of adjacent property and for the safety of the public. If required in the Employer’s Requirements, the Contractor shall submit for the Project Manager’s No-objection a security management plan that sets the security arrangements for the Site. In making security arrangements, the Contractor shall be guided by applicable laws and any other requirements stated in the Employer’s Requirements. The Contractor shall (i) conduct appropriate background checks on any personnel retained to provide security; (ii) train the security personnel adequately (or determine that they are properly trained) in the use of force (and where applicable, firearms), and appropriate conduct towards Contractor’s Personnel, Employer’s personnel and affected communities; and (iii) require the security personnel to act within the applicable Laws and any requirements set out in the Employer’s Reqquirements. The Contractor shall not permit any use of force by security personnel in providing security except when used for preventive and defensive purposes in proportion to the nature and extent of the threat. 22.9 Protection of the Environment The Contractor shall take all necessary measures to: - protect the environment (both on and off the Site); and - limit damage and nuisance to people and property resulting from pollution, noise and other results of the Contractor’s operations and/ or activities. The Contractor shall ensure that emissions, surface discharges, effluent and any other pollutants from the Contractor’s activities shall exceed neither the values indicated in the Employer’s Requirements, nor those prescribed by applicable laws. In the event of damage to the environment, property and/or nuisance to people, on or off Site as a result of the Contractor’s operations, the Contractor shall agree with the Project Manager the appropriate actions and time scale to remedy, as practicable, the damaged environment to its former condition. The Contractor shall implement such remedies at its cost to the satisfaction of the Project Manager. 22.10 Traffic and Road Safety The Contractor shall take all necessary safety measures to avoid the occurrence of incidents and injuries to any third party associated with the use of Contractor’s Equipment on public roads or other public infrastructure. The Contractor shall monitor and use road safety incidents and accidents reports to identify negative safety issues, and establish and implement necessary measures to resolve them. 22.11 – Cultural Heritage Findings All fossils, coins, articles of value or antiquity, structures, groups of structures, and other remains or items of geological, archaeological, paleontological, historical, architectural, religious interest found on the Site shall be placed under the care and custody of the Employer. The Contractor shall: - take all reasonable precautions, including fencing-off the area or site of the finding, to avoid further disturbance and prevent Contractor’s Personnel or other persons from removing or damaging any of these findings; - as soon as practicable after discovery of any such finding, give a notice to the Project Manager, to give the Project Manager the opportunity to promptly inspect and/or investigate the finding before it is disturbed and to issue instructions for dealing with it; - train relevant Contractor’s Personnel on the procedures for handling such findings; and - implement any other action consistent with the requirements of the Employer’s Requirements and relevant laws. If the Contractor suffers delay and/or incurs extra costs from complying with the Project Manager instructions, the Contractor shall be entitled to an extension of time under GCC Sub-Clause 40.1, and the amount of such extra costs shall be added to the Contract Price. |
| 23. Test and Inspection | 23.1 The Contractor shall at its own expense carry out at the place of manufacture and/or on the Site all such tests and/or inspections of the Plant and any part of the Facilities as are specified in the Contract. 23.2 The Employer and the Project Manager or their designated representatives shall be entitled to attend the aforesaid test and/or inspection, provided that the Employer shall bear all costs and expenses incurred in connection with such attendance including, but not limited to, all traveling and board and lodging expenses. 23.3 Whenever the Contractor is ready to carry out any such test and/or inspection, the Contractor shall give a reasonable advance notice of such test and/or inspection and of the place and time thereof to the Project Manager. The Contractor shall obtain from any relevant third Party or manufacturer any necessary permission or consent to enable the Employer and the Project Manager or their designated representatives to attend the test and/or inspection. 23.4 The Contractor shall provide the Project Manager with a certified report of the results of any such test and/or inspection. If the Employer or Project Manager or their designated representatives fails to attend the test and/or inspection, or if it is agreed between the Parties that such persons shall not do so, then the Contractor may proceed with the test and/or inspection in the absence of such persons, and may provide the Project Manager with a certified report of the results thereof. 23.5 The Project Manager may require the Contractor to carry out any test and/or inspection not required by the Contract, provided that the Contractor’s reasonable costs and expenses incurred in the carrying out of such test and/or inspection shall be added to the Contract Price. Further, if such test and/or inspection impede the progress of work on the Facilities and/or the Contractor’s performance of its other obligations under the Contract, due allowance will be made in respect of the Time for Completion and the other obligations so affected. 23.6 If any Plant or any part of the Facilities fails to pass any test and/or inspection, the Contractor shall either rectify or replace such Plant or part of the Facilities and shall repeat the test and/or inspection upon giving a notice under GCC Sub-Clause 23.3. 23.7 If any dispute or difference of opinion shall arise between the Parties in connection with or arising out of the test and/or inspection of the Plant or part of the Facilities that cannot be settled between the Parties within a reasonable period of time, it may be referred to an Dispute Board for determination in accordance with GCC Sub-Clause 46.3. 23.8 The Contractor shall afford the Employer and the Project Manager, at the Employer’s expense, access at any reasonable time to any place where the Plant are being manufactured or the Facilities are being installed, in order to inspect the progress and the manner of manufacture or installation, provided that the Project Manager shall give the Contractor a reasonable prior notice. Without prejudice to GCC Sub-Clause 9.7, as instructed by the Project Manager, the Contractor shall also afford other relevant entities (at the Employer’s or their respective entities’ expense, as appropriate) access to the Facilities, to inspect progress and the manner of the execution of the Facilities, carry out environmental and social audit, as appropriate, or carry out any other duty as stated in the Employer’s Requirements or as instructed by the Project Manager. 23.9 The Contractor agrees that neither the execution of a test and/or inspection of Plant or any part of the Facilities, nor the attendance by the Employer or the Project Manager, nor the issue of any test certificate pursuant to GCC Sub-Clause 23.4, shall release the Contractor from any other responsibilities under the Contract. 23.10 No part of the Facilities or foundations shall be covered up on the Site without the Contractor carrying out any test and/or inspection required under the Contract. The Contractor shall give a reasonable notice to the Project Manager whenever any such parts of the Facilities or foundations are ready or about to be ready for test and/or inspection; such test and/or inspection and notice thereof shall be subject to the requirements of the Contract. 23.11 The Contractor shall uncover any part of the Facilities or foundations, or shall make openings in or through the same as the Project Manager may from time to time require at the Site, and shall reinstate and make good such part or parts. If any parts of the Facilities or foundations have been covered up at the Site after compliance with the requirement of GCC Sub-Clause 23.10 and are found to be executed in accordance with the Contract, the expenses of uncovering, making openings in or through, reinstating, and making good the same shall be borne by the Employer, and the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been delayed or impeded in the performance of any of its obligations under the Contract. |
| 24. Completion of the Facilities | 24.1 As soon as the Facilities or any part thereof has, in the opinion of the Contractor, been completed operationally and structurally and put in a tight and clean condition as specified in the Employer’s Requirements, excluding minor items not materially affecting the operation or safety of the Facilities, the Contractor shall so notify the Employer in writing. 24.2 Within seven (7) days after receipt of the notice from the Contractor under GCC Sub-Clause 24.1, the Employer shall supply the operating and maintenance personnel specified in the Appendix to the Contract Agreement titled Scope of Works and Supply by the Employer for Precommissioning of the Facilities or any part thereof. Pursuant to the Appendix to the Contract Agreement titled Scope of Works and Supply by the Employer, the Employer shall also provide, within the said seven (7) day period, the raw materials, utilities, lubricants, chemicals, catalysts, facilities, services and other matters required for Precommissioning of the Facilities or any part thereof. 24.3 As soon as reasonably practicable after the operating and maintenance personnel have been supplied by the Employer and the raw materials, utilities, lubricants, chemicals, catalysts, facilities, services and other matters have been provided by the Employer in accordance with GCC Sub-Clause 24.2, the Contractor shall commence Precommissioning of the Facilities or the relevant part thereof in preparation for Commissioning, subject to GCC Sub-Clause 25.5. 24.4 As soon as all works in respect of Precommissioning are completed and, in the opinion of the Contractor, the Facilities or any part thereof is ready for Commissioning, the Contractor shall so notify the Project Manager in writing. 24.5 The Project Manager shall, within fourteen (14) days after receipt of the Contractor’s notice under GCC Sub-Clause 24.4, either issue a Completion Certificate in the form specified in the Employer’s Requirements (Forms and Procedures), stating that the Facilities or that part thereof have reached Completion as of the date of the Contractor’s notice under GCC Sub-Clause 24.4, or notify the Contractor in writing of any defects and/or deficiencies. If the Project Manager notifies the Contractor of any defects and/or deficiencies, the Contractor shall then correct such defects and/or deficiencies, and shall repeat the procedure described in GCC Sub-Clause 24.4. If the Project Manager is satisfied that the Facilities or that part thereof have reached Completion, the Project Manager shall, within seven (7) days after receipt of the Contractor’s repeated notice, issue a Completion Certificate stating that the Facilities or that part thereof have reached Completion as of the date of the Contractor’s repeated notice. If the Project Manager is not so satisfied, then it shall notify the Contractor in writing of any defects and/or deficiencies within seven (7) days after receipt of the Contractor’s repeated notice, and the above procedure shall be repeated. 24.6 If the Project Manager fails to issue the Completion Certificate and fails to inform the Contractor of any defects and/or deficiencies within fourteen (14) days after receipt of the Contractor’s notice under GCC Sub-Clause 24.4 or within seven (7) days after receipt of the Contractor’s repeated notice under GCC Sub-Clause 24.5, or if the Employer makes use of the Facilities or part thereof, then the Facilities or that part thereof shall be deemed to have reached Completion as of the date of the Contractor’s notice or repeated notice, or as of the Employer’s use of the Facilities, as the case may be. 24.7 As soon as possible after Completion, the Contractor shall complete all outstanding minor items so that the Facilities are fully in accordance with the requirements of the Contract, failing which the Employer will undertake such completion and deduct the costs thereof from any monies owing to the Contractor. 24.8 Upon Completion, the Employer shall be responsible for the care and custody of the Facilities or the relevant part thereof, together with the risk of loss or damage thereto, and shall thereafter take over the Facilities or the relevant part thereof. |
| 25. Commissioning and Operational Acceptance | 25.1 Commissioning 25.1.1 Commissioning of the Facilities or any part thereof shall be commenced by the Contractor immediately after issue of the Completion Certificate by the Project Manager, pursuant to GCC Sub-Clause 24.5, or immediately after the date of the deemed Completion, under GCC Sub-Clause 24.6. 25.1.2 The Employer shall supply the operating and maintenance personnel and all raw materials, utilities, lubricants, chemicals, catalysts, facilities, services and other matters required for Commissioning. 25.1.3 In accordance with the requirements of the Contract, the Contractor’s and Project Manager’s advisory personnel shall attend the Commissioning, including the Guarantee Test, and shall advise and assist the Employer. 25.2 Guarantee Test 25.2.1 Subject to GCC Sub-Clause 25.5, the Guarantee Test and repeats thereof shall be conducted by the Contractor during Commissioning of the Facilities or the relevant part thereof to ascertain whether the Facilities or the relevant part can attain the Functional Guarantees specified in the Appendix to the Contract Agreement titled Functional Guarantees. The Employer shall promptly provide the Contractor with such information as the Contractor may reasonably require in relation to the conduct and results of the Guarantee Test and any repeats thereof. 25.2.2 If for reasons not attributable to the Contractor, the Guarantee Test of the Facilities or the relevant part thereof cannot be successfully completed within the period from the date of Completion specified in the PCC or any other period agreed upon by the Employer and the Contractor, the Contractor shall be deemed to have fulfilled its obligations with respect to the Functional Guarantees, and GCC Sub-Clauses 28.2 and 28.3 shall not apply. 25.3 Operational Acceptance 25.3.1 Subject to GCC Sub-Clause 25.4 below, Operational Acceptance shall occur in respect of the Facilities or any part thereof when (a) the Guarantee Test has been successfully completed and the Functional Guarantees are met; or (b) the Guarantee Test has not been successfully completed or has not been carried out for reasons not attributable to the Contractor within the period from the date of Completion specified in the PCC pursuant to GCC Sub-Clause 25.2.2 above or any other period agreed upon by the Employer and the Contractor; or (c) the Contractor has paid the liquidated damages specified in GCC Sub-Clause 28.3 hereof; and (d) any minor items mentioned in GCC Sub-Clause 24.7 hereof relevant to the Facilities or that part thereof have been completed. 25.3.2 At any time after any of the events set out in GCC Sub-Clause 25.3.1 have occurred, the Contractor may give a notice to the Project Manager requesting the issue of an Operational Acceptance Certificate in the form provided in the Employer’s Requirements (Forms and Procedures) in respect of the Facilities or the part thereof specified in such notice as of the date of such notice. 25.3.3 The Project Manager shall, after consultation with the Employer, and within seven (7) days after receipt of the Contractor’s notice, issue an Operational Acceptance Certificate. 25.3.4 If within seven (7) days after receipt of the Contractor’s notice, the Project Manager fails to issue the Operational Acceptance Certificate or fails to inform the Contractor in writing of the justifiable reasons why the Project Manager has not issued the Operational Acceptance Certificate, the Facilities or the relevant part thereof shall be deemed to have been accepted as of the date of the Contractor’s said notice. 25.4 Partial Acceptance 25.4.1 If the Contract specifies that Completion and Commissioning shall be carried out in respect of parts of the Facilities, the provisions relating to Completion and Commissioning including the Guarantee Test shall apply to each such part of the Facilities individually, and the Operational Acceptance Certificate shall be issued accordingly for each such part of the Facilities. 25.4.2 If a part of the Facilities comprises facilities such as buildings, for which no Commissioning or Guarantee Test is required, then the Project Manager shall issue the Operational Acceptance Certificate for such facility when it attains Completion, provided that the Contractor shall thereafter complete any outstanding minor items that are listed in the Operational Acceptance Certificate. 25.5 Delayed Precommissioning and/or Guarantee Test 25.5.1 In the event that the Contractor is unable to proceed with the Precommissioning of the Facilities pursuant to Sub-Clause 24.3, or with the Guarantee Test pursuant to Sub-Clause 25.2, for reasons attributable to the Employer either on account of non availability of other facilities under the responsibilities of other contractor(s), or for reasons beyond the Contractor’s control, the provisions leading to “deemed” completion of activities such as Completion, pursuant to GCC Sub-Clause 24.6, and Operational Acceptance, pursuant to GCC Sub-Clause 25.3.4, and Contractor’s obligations regarding Defect Liability Period, pursuant to GCC Sub-Clause 27.2, Functional Guarantee, pursuant to GCC Clause 28, and Care of Facilities, pursuant to GCC Clause 32, and GCC Clause 41.1, Suspension, shall not apply. In this case, the following provisions shall apply. 25.5.2 When the Contractor is notified by the Project Manager that he will be unable to proceed with the activities and obligations pursuant to above Sub-Clause 25.5.1, the Contractor shall be entitled to the following: (a) the Time of Completion shall be extended for the period of suspension without imposition of liquidated damages pursuant to GCC Sub-Clause 26.2; (b) payments due to the Contractor in accordance with the provision specified in the Appendix to the Contract Agreement titled Terms and Procedures of Payment, which would not have been payable in normal circumstances due to non-completion of the subject activities, shall be released to the Contractor against submission of a security in the form of a bank guarantee of equivalent amount acceptable to the Employer, and which shall become null and void when the Contractor will have complied with its obligations regarding those payments, subject to the provision of Sub-Clause 25.5.3 below; (c) the expenses towards the above security and extension of other securities under the contract, of which validity needs to be extended, shall be reimbursed to the Contractor by the Employer; (d) the additional charges towards the care of the Facilities pursuant to GCC Sub-Clause 32.1 shall be reimbursed to the Contractor by the Employer for the period between the notification mentioned above and the notification mentioned in Sub-Clause 25.5.4 below. The provision of GCC Sub-Clause 33.2 shall apply to the Facilities during the same period. 25.5.3 In the event that the period of suspension under above Sub-Clause 25.5.1 actually exceeds one hundred eighty (180) days, the Employer and Contractor shall mutually agree to any additional compensation payable to the Contractor. 25.5.4 When the Contractor is notified by the Project Manager that the Plant is ready for Precommissioning, the Contractor shall proceed without delay in performing Precommissioning in accordance with Clause 24. |

- Guarantees and Liabilities

| 26. Completion Time Guarantee | 26.1 The Contractor guarantees that it shall attain Completion of the Facilities (or a part for which a separate time for completion is specified) within the Time for Completion specified in the PCC pursuant to GCC Sub-Clause 8.2, or within such extended time to which the Contractor shall be entitled under GCC Clause 40 hereof. 26.2 If the Contractor fails to attain Completion of the Facilities or any part thereof within the Time for Completion or any extension thereof under GCC Clause 40, the Contractor shall pay to the Employer liquidated damages in the amount specified in the PCC as a percentage rate of the Contract Price or the relevant part thereof. The aggregate amount of such liquidated damages shall in no event exceed the amount specified as “Maximum” in the PCC as a percentage rate of the Contract Price. Once the “Maximum” is reached, the Employer may consider termination of the Contract, pursuant to GCC Sub-Clause 42.2.2. Such payment shall completely satisfy the Contractor’s obligation to attain Completion of the Facilities or the relevant part thereof within the Time for Completion or any extension thereof under GCC Clause 40. The Contractor shall have no further liability whatsoever to the Employer in respect thereof. However, the payment of liquidated damages shall not in any way relieve the Contractor from any of its obligations to complete the Facilities or from any other obligations and liabilities of the Contractor under the Contract. Save for liquidated damages payable under this GCC Sub-Clause 26.2, the failure by the Contractor to attain any milestone or other act, matter or thing by any date specified in the Appendix to the Contract Agreement titled Time Schedule, and/or other program of work prepared pursuant to GCC Sub-Clause 18.2 shall not render the Contractor liable for any loss or damage thereby suffered by the Employer. 26.3 If the Contractor attains Completion of the Facilities or any part thereof before the Time for Completion or any extension thereof under GCC Clause 40, the Employer shall pay to the Contractor a bonus in the amount specified in the PCC. The aggregate amount of such bonus shall in no event exceed the amount specified as “Maximum” in the PCC. |
| --- | --- |
| 27. Defect Liability | 27.1 The Contractor warrants that the Facilities or any part thereof shall be free from defects in the design, engineering, materials and workmanship of the Plant supplied and of the work executed. 27.2 The Defect Liability Period shall be five hundred and forty (540) days from the date of Completion of the Facilities (or any part thereof) or one year from the date of Operational Acceptance of the Facilities (or any part thereof), whichever first occurs, unless specified otherwise in the PCC pursuant to GCC Sub-Clause 27.10. If during the Defect Liability Period any defect should be found in the design, engineering, materials and workmanship of the Plant supplied or of the work executed by the Contractor, the Contractor shall promptly, in consultation and agreement with the Employer regarding appropriate remedying of the defects, and at its cost, repair, replace or otherwise make good as the Contractor shall determine at its discretion, such defect as well as any damage to the Facilities caused by such defect. The Contractor shall not be responsible for the repair, replacement or making good of any defect or of any damage to the Facilities arising out of or resulting from any of the following causes: (a) improper operation or maintenance of the Facilities by the Employer; (b) operation of the Facilities outside specifications provided in the Contract; or (c) normal wear and tear. 27.3 The Contractor’s obligations under this GCC Clause 27 shall not apply to: (a) any materials that are supplied by the Employer under GCC Sub-Clause 21.2, are normally consumed in operation, or have a normal life shorter than the Defect Liability Period stated herein; (b) any designs, specifications or other data designed, supplied or specified by or on behalf of the Employer or any matters for which the Contractor has disclaimed responsibility herein; or (c) any other materials supplied or any other work executed by or on behalf of the Employer, except for the work executed by the Employer under GCC Sub-Clause 27.7. 27.4 The Employer shall give the Contractor a notice stating the nature of any such defect together with all available evidence thereof, promptly following the discovery thereof. The Employer shall afford all reasonable opportunity for the Contractor to inspect any such defect. 27.5 The Employer shall afford the Contractor all necessary access to the Facilities and the Site to enable the Contractor to perform its obligations under this GCC Clause 27. The Contractor may, with the consent of the Employer, remove from the Site any Plant or any part of the Facilities that are defective if the nature of the defect, and/or any damage to the Facilities caused by the defect, is such that repairs cannot be expeditiously carried out at the Site. 27.6 If the repair, replacement or making good is of such a character that it may affect the efficiency of the Facilities or any part thereof, the Employer may give to the Contractor a notice requiring that tests of the defective part of the Facilities shall be made by the Contractor immediately upon completion of such remedial work, whereupon the Contractor shall carry out such tests. If such part fails the tests, the Contractor shall carry out further repair, replacement or making good, as the case may be, until that part of the Facilities passes such tests. The tests shall be agreed upon by the Employer and the Contractor. 27.7 If the Contractor fails to commence the work necessary to remedy such defect or any damage to the Facilities caused by such defect within a reasonable time (which shall in no event be considered to be less than fifteen (15) days), the Employer may, following notice to the Contractor, proceed to do such work, and the reasonable costs incurred by the Employer in connection therewith shall be paid to the Employer by the Contractor or may be deducted by the Employer from any monies due the Contractor or claimed under the Performance Security. 27.8 If the Facilities or any part thereof cannot be used by reason of such defect and/or making good of such defect, the Defect Liability Period of the Facilities or such part, as the case may be, shall be extended by a period equal to the period during which the Facilities or such part cannot be used by the Employer because of any of the aforesaid reasons. 27.9 Except as provided in GCC Clauses 27 and 33, the Contractor shall be under no liability whatsoever and howsoever arising, and whether under the Contract or at law, in respect of defects in the Facilities or any part thereof, the Plant, design or engineering or work executed that appear after Completion of the Facilities or any part thereof, except where such defects are the result of the gross negligence, fraud, or criminal or willful action of the Contractor. 27.10 In addition, any such component of the Facilities, and during the period of time as may be specified in the PCC, shall be subject to an extended defect liability period. Such obligation of the Contractor shall be in addition to the defect liability period specified under GCC Sub-Clause 27.2. |
| 28. Functional Guarantees | 28.1 The Contractor guarantees that during the Guarantee Test, the Facilities and all parts thereof shall attain the Functional Guarantees specified in the Appendix to the Contract Agreement titled Functional Guarantees, subject to and upon the conditions therein specified. 28.2 If, for reasons attributable to the Contractor, the minimum level of the Functional Guarantees specified in the Appendix to the Contract Agreement titled Functional Guarantees, are not met either in whole or in part, the Contractor shall at its cost and expense make such changes, modifications and/or additions to the Plant or any part thereof as may be necessary to meet at least the minimum level of such Guarantees. The Contractor shall notify the Employer upon completion of the necessary changes, modifications and/or additions, and shall request the Employer to repeat the Guarantee Test until the minimum level of the Guarantees has been met. If the Contractor eventually fails to meet the minimum level of Functional Guarantees, the Employer may consider termination of the Contract, pursuant to GCC Sub-Clause 42.2.2. 28.3 If, for reasons attributable to the Contractor, the Functional Guarantees specified in the Appendix to the Contract Agreement titled Functional Guarantees, are not attained either in whole or in part, but the minimum level of the Functional Guarantees specified in the said Appendix to the Contract Agreement is met, the Contractor shall, at the Contractor’s option, either (a) make such changes, modifications and/or additions to the Facilities or any part thereof that are necessary to attain the Functional Guarantees at its cost and expense, and shall request the Employer to repeat the Guarantee Test or (b) pay liquidated damages to the Employer in respect of the failure to meet the Functional Guarantees in accordance with the provisions in the Appendix to the Contract Agreement titled Functional Guarantees. 28.4 The payment of liquidated damages under GCC Sub-Clause 28.3, up to the limitation of liability specified in the Appendix to the Contract Agreement titled Functional Guarantees, shall completely satisfy the Contractor’s guarantees under GCC Sub-Clause 28.3, and the Contractor shall have no further liability whatsoever to the Employer in respect thereof. Upon the payment of such liquidated damages by the Contractor, the Project Manager shall issue the Operational Acceptance Certificate for the Facilities or any part thereof in respect of which the liquidated damages have been so paid. |
| 29. Patent Indemnity | 29.1 The Contractor shall, subject to the Employer’s compliance with GCC Sub-Clause 29.2, indemnify and hold harmless the Employer and its employees and officers from and against any and all suits, actions or administrative proceedings, claims, demands, losses, damages, costs, and expenses of whatsoever nature, including attorney’s fees and expenses, which the Employer may suffer as a result of any infringement or alleged infringement of any patent, utility model, registered design, trademark, copyright or other intellectual property right registered or otherwise existing at the date of the Contract by reason of: (a) the installation of the Facilities by the Contractor or the use of the Facilities in the country where the Site is located; and (b) the sale of the products produced by the Facilities in any country. Such indemnity shall not cover any use of the Facilities or any part thereof other than for the purpose indicated by or to be reasonably inferred from the Contract, any infringement resulting from the use of the Facilities or any part thereof, or any products produced thereby in association or combination with any other equipment, Plant or materials not supplied by the Contractor, pursuant to the Contract Agreement. 29.2 If any proceedings are brought or any claim is made against the Employer arising out of the matters referred to in GCC Sub-Clause 29.1, the Employer shall promptly give the Contractor a notice thereof, and the Contractor may at its own expense and in the Employer’s name conduct such proceedings or claim and any negotiations for the settlement of any such proceedings or claim. If the Contractor fails to notify the Employer within twenty-eight (28) days after receipt of such notice that it intends to conduct any such proceedings or claim, then the Employer shall be free to conduct the same on its own behalf. Unless the Contractor has so failed to notify the Employer within the twenty-eight (28) day period, the Employer shall make no admission that may be prejudicial to the defense of any such proceedings or claim. The Employer shall, at the Contractor’s request, afford all available assistance to the Contractor in conducting such proceedings or claim, and shall be reimbursed by the Contractor for all reasonable expenses incurred in so doing. 29.3 The Employer shall indemnify and hold harmless the Contractor and its employees, officers and Subcontractors from and against any and all suits, actions or administrative proceedings, claims, demands, losses, damages, costs, and expenses of whatsoever nature, including attorney’s fees and expenses, which the Contractor may suffer as a result of any infringement or alleged infringement of any patent, utility model, registered design, trademark, copyright or other intellectual property right registered or otherwise existing at the date of the Contract arising out of or in connection with any design, data, drawing, specification, or other documents or materials provided or designed by or on behalf of the Employer. |
| 30. Limitation of Liability | 30.1 Except in cases of criminal negligence or willful misconduct, (a) neither Party shall be liable to the other Party, whether in contract, tort, or otherwise, for any indirect or consequential loss or damage, loss of use, loss of production, or loss of profits or interest costs, which may be suffered by the other Party in connection with the Contract, other than specifically provided as any obligation of the Party in the Contract, and (b) the aggregate liability of the Contractor to the Employer, whether under the Contract, in tort or otherwise, shall not exceed the amount resulting from the application of the multiplier specified in the PCC, to the Contract Price or, if a multiplier is not so specified, the total Contract Price, provided that this limitation shall not apply to the cost of repairing or replacing defective equipment, or to any obligation of the Contractor to indemnify the Employer with respect to patent infringement. |

- Risk Distribution

| 31. Transfer of Ownership | 31.1 Ownership of the Plant (including spare parts) to be imported into the country where the Site is located shall be transferred to the Employer upon loading on to the mode of transport to be used to convey the Plant from the country of origin to that country. 31.2 Ownership of the Plant (including spare parts) procured in the country where the Site is located shall be transferred to the Employer when the Plant are brought on to the Site. 31.3 Ownership of the Contractor’s Equipment used by the Contractor and its Subcontractors in connection with the Contract shall remain with the Contractor or its Subcontractors. 31.4 Ownership of any Plant in excess of the requirements for the Facilities shall revert to the Contractor upon Completion of the Facilities or at such earlier time when the Employer and the Contractor agree that the Plant in question are no longer required for the Facilities. 31.5 Notwithstanding the transfer of ownership of the Plant, the responsibility for care and custody thereof together with the risk of loss or damage thereto shall remain with the Contractor pursuant to GCC Clause 32 (Care of Facilities) hereof until Completion of the Facilities or the part thereof in which such Plant are incorporated. |
| --- | --- |
| 32. Care of Facilities | 32.1 The Contractor shall be responsible for the care and custody of the Facilities or any part thereof until the date of Completion of the Facilities pursuant to GCC Clause 24 or, where the Contract provides for Completion of the Facilities in parts, until the date of Completion of the relevant part, and shall make good at its own cost any loss or damage that may occur to the Facilities or the relevant part thereof from any cause whatsoever during such period. The Contractor shall also be responsible for any loss or damage to the Facilities caused by the Contractor or its Subcontractors in the course of any work carried out, pursuant to GCC Clause 27. Notwithstanding the foregoing, the Contractor shall not be liable for any loss or damage to the Facilities or that part thereof caused by reason of any of the matters specified or referred to in paragraphs (a), (b) and (c) of GCC Sub-Clauses 32.2 and 38.1. 32.2 If any loss or damage occurs to the Facilities or any part thereof or to the Contractor’s temporary facilities by reason of (a) insofar as they relate to the country where the Site is located, nuclear reaction, nuclear radiation, radioactive contamination, pressure wave caused by aircraft or other aerial objects, or any other occurrences that an experienced contractor could not reasonably foresee, or if reasonably foreseeable could not reasonably make provision for or insure against, insofar as such risks are not normally insurable on the insurance market and are mentioned in the general exclusions of the policy of insurance, including War Risks and Political Risks, taken out under GCC Clause 34 hereof; or (b) any use or occupation by the Employer or any third Party other than a Subcontractor, authorized by the Employer of any part of the Facilities; or (c) any use of or reliance upon any design, data or specification provided or designated by or on behalf of the Employer, or any such matter for which the Contractor has disclaimed responsibility herein, the Employer shall pay to the Contractor all sums payable in respect of the Facilities executed, notwithstanding that the same be lost, destroyed or damaged, and will pay to the Contractor the replacement value of all temporary facilities and all parts thereof lost, destroyed or damaged. If the Employer requests the Contractor in writing to make good any loss or damage to the Facilities thereby occasioned, the Contractor shall make good the same at the cost of the Employer in accordance with GCC Clause 39. If the Employer does not request the Contractor in writing to make good any loss or damage to the Facilities thereby occasioned, the Employer shall either request a change in accordance with GCC Clause 39, excluding the performance of that part of the Facilities thereby lost, destroyed or damaged, or, where the loss or damage affects a substantial part of the Facilities, the Employer shall terminate the Contract pursuant to GCC Sub-Clause 42.1 hereof. 32.3 The Contractor shall be liable for any loss of or damage to any Contractor’s Equipment, or any other property of the Contractor used or intended to be used for purposes of the Facilities, except (i) as mentioned in GCC Sub-Clause 32.2 with respect to the Contractor’s temporary facilities, and (ii) where such loss or damage arises by reason of any of the matters specified in GCC Sub-Clauses 32.2 (b) and (c) and 38.1. 32.4 With respect to any loss or damage caused to the Facilities or any part thereof or to the Contractor’s Equipment by reason of any of the matters specified in GCC Sub-Clause 38.1, the provisions of GCC Sub-Clause 38.3 shall apply. |
| 33. Loss of or Damage to Property; Accident or Injury to Workers; Indemnification | 33.1 Subject to GCC Sub-Clause 33.3, the Contractor shall indemnify and hold harmless the Employer and its employees and officers from and against any and all suits, actions or administrative proceedings, claims, demands, losses, damages, costs, and expenses of whatsoever nature, including attorney’s fees and expenses, in respect of the death or injury of any person or loss of or damage to any property other than the Facilities whether accepted or not, arising in connection with the supply and installation of the Facilities and by reason of the negligence of the Contractor or its Subcontractors, or their employees, officers or agents, except any injury, death or property damage caused by the negligence of the Employer, its contractors, employees, officers or agents. 33.2 If any proceedings are brought or any claim is made against the Employer that might subject the Contractor to liability under GCC Sub-Clause 33.1, the Employer shall promptly give the Contractor a notice thereof and the Contractor may at its own expense and in the Employer’s name conduct such proceedings or claim and any negotiations for the settlement of any such proceedings or claim. If the Contractor fails to notify the Employer within twenty-eight (28) days after receipt of such notice that it intends to conduct any such proceedings or claim, then the Employer shall be free to conduct the same on its own behalf. Unless the Contractor has so failed to notify the Employer within the twenty-eight (28) day period, the Employer shall make no admission that may be prejudicial to the defense of any such proceedings or claim. The Employer shall, at the Contractor’s request, afford all available assistance to the Contractor in conducting such proceedings or claim, and shall be reimbursed by the Contractor for all reasonable expenses incurred in so doing. 33.3 The Employer shall indemnify and hold harmless the Contractor and its employees, officers and Subcontractors from any liability for loss of or damage to property of the Employer, other than the Facilities not yet taken over, that is caused by fire, explosion or any other perils, in excess of the amount recoverable from insurances procured under GCC Clause 34, provided that such fire, explosion or other perils were not caused by any act or failure of the Contractor. 33.4 The Party entitled to the benefit of an indemnity under this GCC Clause 33 shall take all reasonable measures to mitigate any loss or damage which has occurred. If the Party fails to take such measures, the other Party’s liabilities shall be correspondingly reduced. |
| 34. Insurance | 34.1 To the extent specified in the Appendix to the Contract Agreement titled Insurance Requirements, the Contractor shall at its expense take out and maintain in effect, or cause to be taken out and maintained in effect, during the performance of the Contract, the insurances set forth below in the sums and with the deductibles and other conditions specified in the said Appendix. The identity of the insurers and the form of the policies shall be subject to the approval of the Employer, who should not unreasonably withhold such approval. (a) Cargo Insurance During Transport Covering loss or damage occurring while in transit from the Contractor’s or Subcontractor’s works or stores until arrival at the Site, to the Plant (including spare parts therefor) and to the Contractor’s Equipment. (b) Installation All Risks Insurance Covering physical loss or damage to the Facilities at the Site, occurring prior to Completion of the Facilities, with an extended maintenance coverage for the Contractor’s liability in respect of any loss or damage occurring during the Defect Liability Period while the Contractor is on the Site for the purpose of performing its obligations during the Defect Liability Period. (c) Third Party Liability Insurance Covering bodily injury or death suffered by third Parties including the Employer’s personnel, and loss of or damage to property occurring in connection with the supply and installation of the Facilities. (d) Automobile Liability Insurance Covering use of all vehicles used by the Contractor or its Subcontractors, whether or not owned by them, in connection with the execution of the Contract. (e) Workers’ Compensation In accordance with the statutory requirements applicable in any country where the Contract or any part thereof is executed. (f) Employer’s Liability In accordance with the statutory requirements applicable in any country where the Contract or any part thereof is executed. (g) Other Insurances Such other insurances as may be specifically agreed upon by the Parties hereto as listed in the Appendix to the Contract Agreement titled Insurance Requirements. 34.2 The Employer shall be named as co-insured under all insurance policies taken out by the Contractor pursuant to GCC Sub-Clause 34.1, except for the Third Party Liability, Workers’ Compensation and Employer’s Liability Insurances, and the Contractor’s Subcontractors shall be named as co-insureds under all insurance policies taken out by the Contractor pursuant to GCC Sub-Clause 34.1 except for the Cargo Insurance During Transport, Workers’ Compensation and Employer’s Liability Insurances. All insurer’s rights of subrogation against such co-insureds for losses or claims arising out of the performance of the Contract shall be waived under such policies. 34.3 The Contractor shall, in accordance with the provisions of the Appendix to the Contract Agreement titled Insurance Requirements, deliver to the Employer certificates of insurance or copies of the insurance policies as evidence that the required policies are in full force and effect. The certificates shall provide that no less than twenty-one (21) days’ notice shall be given to the Employer by insurers prior to cancellation or material modification of a policy. 34.4 The Contractor shall ensure that, where applicable, its Subcontractor(s) shall take out and maintain in effect adequate insurance policies for their personnel and vehicles and for work executed by them under the Contract, unless such Subcontractors are covered by the policies taken out by the Contractor. 34.5 The Employer shall at its expense take out and maintain in effect during the performance of the Contract those insurances specified in the Appendix to the Contract Agreement titled Insurance Requirements, in the sums and with the deductibles and other conditions specified in the said Appendix. The Contractor and the Contractor’s Subcontractors shall be named as co-insureds under all such policies. All insurers’ rights of subrogation against such co-insureds for losses or claims arising out of the performance of the Contract shall be waived under such policies. The Employer shall deliver to the Contractor satisfactory evidence that the required insurances are in full force and effect. The policies shall provide that not less than twenty-one (21) days’ notice shall be given to the Contractor by all insurers prior to any cancellation or material modification of the policies. If so requested by the Contractor, the Employer shall provide copies of the policies taken out by the Employer under this GCC Sub-Clause 34.5. 34.6 If the Contractor fails to take out and/or maintain in effect the insurances referred to in GCC Sub-Clause 34.1, the Employer may take out and maintain in effect any such insurances and may from time to time deduct from any amount due the Contractor under the Contract any premium that the Employer shall have paid to the insurer, or may otherwise recover such amount as a debt due from the Contractor. If the Employer fails to take out and/or maintain in effect the insurances referred to in GCC 34.5, the Contractor may take out and maintain in effect any such insurances and may from time to time deduct from any amount due the Employer under the Contract any premium that the Contractor shall have paid to the insurer, or may otherwise recover such amount as a debt due from the Employer. If the Contractor fails to or is unable to take out and maintain in effect any such insurances, the Contractor shall nevertheless have no liability or responsibility towards the Employer, and the Contractor shall have full recourse against the Employer for any and all liabilities of the Employer herein. 34.7 Unless otherwise provided in the Contract, the Contractor shall prepare and conduct all and any claims made under the policies effected by it pursuant to this GCC Clause 34, and all monies payable by any insurers shall be paid to the Contractor. The Employer shall give to the Contractor all such reasonable assistance as may be required by the Contractor. With respect to insurance claims in which the Employer’s interest is involved, the Contractor shall not give any release or make any compromise with the insurer without the prior written consent of the Employer. With respect to insurance claims in which the Contractor’s interest is involved, the Employer shall not give any release or make any compromise with the insurer without the prior written consent of the Contractor. |
| 35. Unforeseen Conditions | 35.1 If, during the execution of the Contract, the Contractor shall encounter on the Site any physical conditions other than climatic conditions, or artificial obstructions that could not have been reasonably foreseen prior to the date of the Contract Agreement by an experienced contractor on the basis of reasonable examination of the data relating to the Facilities including any data as to boring tests, provided by the Employer, and on the basis of information that it could have obtained from a visual inspection of the Site if access thereto was available, or other data readily available to it relating to the Facilities, and if the Contractor determines that it will in consequence of such conditions or obstructions incur additional cost and expense or require additional time to perform its obligations under the Contract that would not have been required if such physical conditions or artificial obstructions had not been encountered, the Contractor shall promptly, and before performing additional work or using additional Plant or Contractor’s Equipment, notify the Project Manager in writing of (a) the physical conditions or artificial obstructions on the Site that could not have been reasonably foreseen; (b) the additional work and/or Plant and/or Contractor’s Equipment required, including the steps which the Contractor will or proposes to take to overcome such conditions or obstructions; (c) the extent of the anticipated delay; and (d) the additional cost and expense that the Contractor is likely to incur. On receiving any notice from the Contractor under this GCC Sub-Clause 35.1, the Project Manager shall promptly consult with the Employer and Contractor and decide upon the actions to be taken to overcome the physical conditions or artificial obstructions encountered. Following such consultations, the Project Manager shall instruct the Contractor, with a copy to the Employer, of the actions to be taken. 35.2 Any reasonable additional cost and expense incurred by the Contractor in following the instructions from the Project Manager to overcome such physical conditions or artificial obstructions referred to in GCC Sub-Clause 35.1 shall be paid by the Employer to the Contractor as an addition to the Contract Price. If the Contractor is delayed or impeded in the performance of the Contract because of any such physical conditions or artificial obstructions referred to in GCC Sub-Clause 35.1, the Time for Completion shall be extended in accordance with GCC Clause 40. |
| 36. Change in Laws and Regulations | 36.1 If, after the date twenty-eight (28) days prior to the date of Bid submission, in the country where the Site is located, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated or changed which shall be deemed to include any change in interpretation or application by the competent authorities, that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the performance of any of its obligations under the Contract. Notwithstanding the foregoing, such additional or reduced costs shall not be separately paid or credited if the same has already been accounted for in the price adjustment provisions where applicable, in accordance with the PCC pursuant to GCC Sub-Clause 11.2. |
| 37. Force Majeure | 37.1 “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the Party affected, and shall include, without limitation, the following: (a) war, hostilities or warlike operations whether a state of war be declared or not, invasion, act of foreign enemy and civil war (b) rebellion, revolution, insurrection, mutiny, usurpation of civil or military government, conspiracy, riot, civil commotion and terrorist acts (c) confiscation, nationalization, mobilization, commandeering or requisition by or under the order of any government or de jure or de facto authority or ruler or any other act or failure to act of any local state or national government authority (d) strike, sabotage, lockout, embargo, import restriction, port congestion, lack of usual means of public transportation and communication, industrial dispute, shipwreck, shortage or restriction of power supply, epidemics, quarantine and plague (e) earthquake, landslide, volcanic activity, fire, flood or inundation, tidal wave, typhoon or cyclone, hurricane, storm, lightning, or other inclement weather condition, nuclear and pressure waves or other natural or physical disaster (f) shortage of labor, materials or utilities where caused by circumstances that are themselves Force Majeure. 37.2 If either Party is prevented, hindered or delayed from or in performing any of its obligations under the Contract by an event of Force Majeure, then it shall notify the other in writing of the occurrence of such event and the circumstances thereof within fourteen (14) days after the occurrence of such event. 37.3 The Party who has given such notice shall be excused from the performance or punctual performance of its obligations under the Contract for so long as the relevant event of Force Majeure continues and to the extent that such Party’s performance is prevented, hindered or delayed. The Time for Completion shall be extended in accordance with GCC Clause 40. 37.4 The Party or Parties affected by the event of Force Majeure shall use reasonable efforts to mitigate the effect thereof upon its or their performance of the Contract and to fulfill its or their obligations under the Contract, but without prejudice to either Party’s right to terminate the Contract under GCC Sub-Clauses 37.6 and 38.5. 37.5 No delay or nonperformance by either Party hereto caused by the occurrence of any event of Force Majeure shall (a) constitute a default or breach of the Contract, or (b) give rise to any claim for damages or additional cost or expense occasioned thereby, subject to GCC Sub-Clauses 32.2, 38.3 and 38.4 if and to the extent that such delay or nonperformance is caused by the occurrence of an event of Force Majeure. 37.6 If the performance of the Contract is substantially prevented, hindered or delayed for a single period of more than sixty (60) days or an aggregate period of more than one hundred and twenty (120) days on account of one or more events of Force Majeure during the currency of the Contract, the Parties will attempt to develop a mutually satisfactory solution, failing which either Party may terminate the Contract by giving a notice to the other, but without prejudice to either Party’s right to terminate the Contract under GCC Sub-Clause 38.5. 37.7 In the event of termination pursuant to GCC Sub-Clause 37.6, the rights and obligations of the Employer and the Contractor shall be as specified in GCC Sub-Clauses 42.1.2 and 42.1.3. 37.8 Notwithstanding GCC Sub-Clause 37.5, Force Majeure shall not apply to any obligation of the Employer to make payments to the Contractor herein. |
| 38. War Risks | 38.1 “War Risks” shall mean any event specified in paragraphs (a) and (b) of GCC Sub-Clause 37.1 and any explosion or impact of any mine, bomb, shell, grenade or other projectile, missile, munitions or explosive of war, occurring or existing in or near the country (or countries) where the Site is located. 38.2 Notwithstanding anything contained in the Contract, the Contractor shall have no liability whatsoever for or with respect to (a) destruction of or damage to Facilities, Plant, or any part thereof; (b) destruction of or damage to property of the Employer or any third Party; or (c) injury or loss of life if such destruction, damage, injury or loss of life is caused by any War Risks, and the Employer shall indemnify and hold the Contractor harmless from and against any and all claims, liabilities, actions, lawsuits, damages, costs, charges or expenses arising in consequence of or in connection with the same. 38.3 If the Facilities or any Plant or Contractor’s Equipment or any other property of the Contractor used or intended to be used for the purposes of the Facilities shall sustain destruction or damage by reason of any War Risks, the Employer shall pay the Contractor for (a) any part of the Facilities or the Plant so destroyed or damaged to the extent not already paid for by the Employer and so far as may be required by the Employer, and as may be necessary for completion of the Facilities (b) replacing or making good any Contractor’s Equipment or other property of the Contractor so destroyed or damaged (c) replacing or making good any such destruction or damage to the Facilities or the Plant or any part thereof . If the Employer does not require the Contractor to replace or make good any such destruction or damage to the Facilities, the Employer shall either request a change in accordance with GCC Clause 39, excluding the performance of that part of the Facilities thereby destroyed or damaged or, where the loss, destruction or damage affects a substantial part of the Facilities, shall terminate the Contract, pursuant to GCC Sub-Clause 42.1. If the Employer requires the Contractor to replace or make good on any such destruction or damage to the Facilities, the Time for Completion shall be extended in accordance with GCC 40. 38.4 Notwithstanding anything contained in the Contract, the Employer shall pay the Contractor for any increased costs or incidentals to the execution of the Contract that are in any way attributable to, consequent on, resulting from, or in any way connected with any War Risks, provided that the Contractor shall as soon as practicable notify the Employer in writing of any such increased cost. 38.5 If during the performance of the Contract any War Risks shall occur that financially or otherwise materially affect the execution of the Contract by the Contractor, the Contractor shall use its reasonable efforts to execute the Contract with due and proper consideration given to the safety of its and its Subcontractors’ personnel engaged in the work on the Facilities, provided, however, that if the execution of the work on the Facilities becomes impossible or is substantially prevented for a single period of more than sixty (60) days or an aggregate period of more than one hundred and twenty (120) days on account of any War Risks, the Parties will attempt to develop a mutually satisfactory solution, failing which either Party may terminate the Contract by giving a notice to the other. 38.6 In the event of termination pursuant to GCC Sub-Clauses 38.3 or 38.5, the rights and obligations of the Employer and the Contractor shall be specified in GCC Sub-Clauses 42.1.2 and 42.1.3. |

- Change in Contract Elements

| 39. Change in the Facilities | 39.1 Introducing a Change 39.1.1 Subject to GCC Sub-Clauses 39.2.5 and 39.2.7, the Employer shall have the right to propose, and subsequently require, that the Project Manager order the Contractor from time to time during the performance of the Contract to make any change, modification, addition or deletion to, in or from the Facilities hereinafter called “Change”, provided that such Change falls within the general scope of the Facilities and does not constitute unrelated work and that it is technically practicable, taking into account both the state of advancement of the Facilities and the technical compatibility of the Change envisaged with the nature of the Facilities as specified in the Contract. 39.1.2 Value Engineering: The Contractor may prepare, at its own cost, a value engineering proposal at any time during the performance of the contract. The value engineering proposal shall, at a minimum, include the following; - the proposed change(s), and a description of the difference to the existing contract requirements; - a full cost/benefit analysis of the proposed change(s) including a description and estimate of costs (including life cycle costs) the Employer may incur in implementing the value engineering proposal; and - a description of any effect(s) of the change on performance/functionality. The Employer may accept the value engineering proposal if the proposal demonstrates benefits that: - accelerates the delivery period; or - reduces the Contract Price or the life cycle costs to the Employer; or - improves the quality, efficiency, safety or sustainability of the Facilities; or - yields any other benefits to the Employer, without compromising the necessary functions of the Facilities. If the value engineering proposal is approved by the Employer and results in: - a reduction of the Contract Price; the amount to be paid to the Contractor shall be the percentage specified in the PCC of the reduction in the Contract Price; or - an increase in the Contract Price; but results in a reduction in life cycle costs due to any benefit described in (a) to (d) above, the amount to be paid to the Contractor shall be the full increase in the Contract Price. 39.1.3 Notwithstanding GCC Sub-Clauses 39.1.1 and 39.1.2, no change made necessary because of any default of the Contractor in the performance of its obligations under the Contract shall be deemed to be a Change, and such change shall not result in any adjustment of the Contract Price or the Time for Completion. 39.1.4 The procedure on how to proceed with and execute Changes is specified in GCC Sub-Clauses 39.2 and 39.3, and further details and forms are provided in the Employer’s Requirements (Forms and Procedures). 39.2 Changes Originating from Employer 39.2.1 If the Employer proposes a Change pursuant to GCC Sub-Clause 39.1.1, it shall send to the Contractor a “Request for Change Proposal,” requiring the Contractor to prepare and furnish to the Project Manager as soon as reasonably practicable a “Change Proposal,” which shall include the following: (a) brief description of the Change (b) effect on the Time for Completion (c) estimated cost of the Change (d) effect on Functional Guarantees (if any) (e) effect on the Facilities (f) effect on any other provisions of the Contract. 39.2.2 Prior to preparing and submitting the “Change Proposal,” the Contractor shall submit to the Project Manager an “Estimate for Change Proposal,” which shall be an estimate of the cost of preparing and submitting the Change Proposal. Upon receipt of the Contractor’s Estimate for Change Proposal, the Employer shall do one of the following: (a) accept the Contractor’s estimate with instructions to the Contractor to proceed with the preparation of the Change Proposal (b) advise the Contractor of any part of its Estimate for Change Proposal that is unacceptable and request the Contractor to review its estimate (c) advise the Contractor that the Employer does not intend to proceed with the Change. 39.2.3 Upon receipt of the Employer’s instruction to proceed under GCC Sub-Clause 39.2.2 (a), the Contractor shall, with proper expedition, proceed with the preparation of the Change Proposal, in accordance with GCC Sub-Clause 39.2.1. 39.2.4 The pricing of any Change shall, as far as practicable, be calculated in accordance with the rates and prices included in the Contract. If such rates and prices are inequitable, the Parties thereto shall agree on specific rates for the valuation of the Change. 39.2.5 If before or during the preparation of the Change Proposal it becomes apparent that the aggregate effect of compliance therewith and with all other Change Orders that have already become binding upon the Contractor under this GCC Clause 39 would be to increase or decrease the Contract Price as originally set forth in Article 2 (Contract Price) of the Contract Agreement by more than fifteen percent (15%), the Contractor may give a written notice of objection thereto prior to furnishing the Change Proposal as aforesaid. If the Employer accepts the Contractor’s objection, the Employer shall withdraw the proposed Change and shall notify the Contractor in writing thereof. The Contractor’s failure to so object shall neither affect its right to object to any subsequent requested Changes or Change Orders herein, nor affect its right to take into account, when making such subsequent objection, the percentage increase or decrease in the Contract Price that any Change not objected to by the Contractor represents. 39.2.6 Upon receipt of the Change Proposal, the Employer and the Contractor shall mutually agree upon all matters therein contained. Within fourteen (14) days after such agreement, the Employer shall, if it intends to proceed with the Change, issue the Contractor with a Change Order. If the Employer is unable to reach a decision within fourteen (14) days, it shall notify the Contractor with details of when the Contractor can expect a decision. If the Employer decides not to proceed with the Change for whatever reason, it shall, within the said period of fourteen (14) days, notify the Contractor accordingly. Under such circumstances, the Contractor shall be entitled to reimbursement of all costs reasonably incurred by it in the preparation of the Change Proposal, provided that these do not exceed the amount given by the Contractor in its Estimate for Change Proposal submitted in accordance with GCC Sub-Clause 39.2.2. 39.2.7 If the Employer and the Contractor cannot reach agreement on the price for the Change, an equitable adjustment to the Time for Completion, or any other matters identified in the Change Proposal, the Employer may nevertheless instruct the Contractor to proceed with the Change by issue of a “Pending Agreement Change Order.” Upon receipt of a Pending Agreement Change Order, the Contractor shall immediately proceed with effecting the Changes covered by such Order. The Parties shall thereafter attempt to reach agreement on the outstanding issues under the Change Proposal. If the Parties cannot reach agreement within sixty (60) days from the date of issue of the Pending Agreement Change Order, then the matter may be referred to the Dispute Board in accordance with the provisions of GCC Sub-Clause 46.1. 39.3 Changes Originating from Contractor 39.3.1 If the Contractor proposes a Change pursuant to GCC Sub-Clause 39.1.2, the Contractor shall submit to the Project Manager a written “Application for Change Proposal,” giving reasons for the proposed Change and including the information specified in GCC Sub-Clause 39.1.2. Upon receipt of the Application for Change Proposal, the Parties shall follow the procedures outlined in GCC Sub-Clauses 39.2.6 and 39.2.7. However, the Contractor shall not be entitled to recover the costs of preparing the Application for Change Proposal. |
| --- | --- |
| 40. Extension of Time for Completion | 40.1 The Time(s) for Completion specified in the PCC pursuant to GCC Sub-Clause 8.2 shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 39 (b) any occurrence of Force Majeure as provided in GCC Clause 37, unforeseen conditions as provided in GCC Clause 35, or other occurrence of any of the matters specified or referred to in paragraphs (a), (b) and (c) of GCC Sub-Clause 32.2 (c) any suspension order given by the Employer under GCC Clause 41 hereof or reduction in the rate of progress pursuant to GCC Sub-Clause 41.2 or (d) any changes in laws and regulations as provided in GCC Clause 36 or (e) any default or breach of the Contract by the Employer, Appendix to the Contract Agreement titled ,or any activity, act or omission of the Employer, or the Project Manager, or any other contractors employed by the Employer, or - any delay on the part of a Subcontractor, provided such delay is due to a cause for which the Contractor himself would have been entitled to an extension of time under this sub-clause, or - delays attributable to the Employer or caused by customs, or - any other matter specifically mentioned in the Contract by such period as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. 40.2 Except where otherwise specifically provided in the Contract, the Contractor shall submit to the Project Manager a notice of a claim for an extension of the Time for Completion, together with particulars of the event or circumstance justifying such extension as soon as reasonably practicable after the commencement of such event or circumstance. As soon as reasonably practicable after receipt of such notice and supporting particulars of the claim, the Employer and the Contractor shall agree upon the period of such extension. In the event that the Contractor does not accept the Employer’s estimate of a fair and reasonable time extension, the Contractor shall be entitled to refer the matter to a Dispute Board, pursuant to GCC Sub-Clause 46.1. 40.3 The Contractor shall at all times use its reasonable efforts to minimize any delay in the performance of its obligations under the Contract. 40.4 In all cases where the Contractor has given a notice of a claim for an extension of time under GCC 40.2, the Contractor shall consult with the Project Manager in order to determine the steps (if any) which can be taken to overcome or minimize the actual or anticipated delay. The Contractor shall there after comply with all reasonable instructions which the Project Manager shall give in order to minimize such delay. If compliance with such instructions shall cause the Contractor to incur extra costs and the Contractor is entitled to an extension of time under GCC 40.1, the amount of such extra costs shall be added to the Contract Price. |
| 41. Suspension | 41.1 The Employer may request the Project Manager, by notice to the Contractor, to order the Contractor to suspend performance of any or all of its obligations under the Contract. Such notice shall specify the obligation of which performance is to be suspended, the effective date of the suspension and the reasons therefor. The Contractor shall thereupon suspend performance of such obligation, except those obligations necessary for the care or preservation of the Facilities, until ordered in writing to resume such performance by the Project Manager. If, by virtue of a suspension order given by the Project Manager, other than by reason of the Contractor’s default or breach of the Contract, the Contractor’s performance of any of its obligations is suspended for an aggregate period of more than ninety (90) days, then at any time thereafter and provided that at that time such performance is still suspended, the Contractor may give a notice to the Project Manager requiring that the Employer shall, within twenty-eight (28) days of receipt of the notice, order the resumption of such performance or request and subsequently order a change in accordance with GCC Clause 39, excluding the performance of the suspended obligations from the Contract. If the Employer fails to do so within such period, the Contractor may, by a further notice to the Project Manager, elect to treat the suspension, where it affects a part only of the Facilities, as a deletion of such part in accordance with GCC Clause 39 or, where it affects the whole of the Facilities, as termination of the Contract under GCC Sub-Clause 42.1. 41.2 If (a) the Employer has failed to pay the Contractor any sum due under the Contract within the specified period, has failed to approve any invoice or supporting documents without just cause pursuant to the Appendix to the Contract Agreement titled Terms and Procedures of Payment, or commits a substantial breach of the Contract, the Contractor may give a notice to the Employer that requires payment of such sum, with interest thereon as stipulated in GCC Sub-Clause 12.3, requires approval of such invoice or supporting documents, or specifies the breach and requires the Employer to remedy the same, as the case may be. If the Employer fails to pay such sum together with such interest, fails to approve such invoice or supporting documents or give its reasons for withholding such approval, or fails to remedy the breach or take steps to remedy the breach within fourteen (14) days after receipt of the Contractor’s notice or (b) the Contractor is unable to carry out any of its obligations under the Contract for any reason attributable to the Employer, including but not limited to the Employer’s failure to provide possession of or access to the Site or other areas in accordance with GCC Sub-Clause 10.2, or failure to obtain any governmental permit necessary for the execution and/or completion of the Facilities, then the Contractor may by fourteen (14) days’ notice to the Employer suspend performance of all or any of its obligations under the Contract, or reduce the rate of progress. 41.3 If the Contractor’s performance of its obligations is suspended or the rate of progress is reduced pursuant to this GCC Clause 41, then the Time for Completion shall be extended in accordance with GCC Sub-Clause 40.1, and any and all additional costs or expenses incurred by the Contractor as a result of such suspension or reduction shall be paid by the Employer to the Contractor in addition to the Contract Price, except in the case of suspension order or reduction in the rate of progress by reason of the Contractor’s default or breach of the Contract. 41.4 During the period of suspension, the Contractor shall not remove from the Site any Plant, any part of the Facilities or any Contractor’s Equipment, without the prior written consent of the Employer. |
| 42. Termination | 42.1 Termination for Employer’s Convenience 42.1.1 The Employer may at any time terminate the Contract for any reason by giving the Contractor a notice of termination that refers to this GCC Sub-Clause 42.1. 42.1.2 Upon receipt of the notice of termination under GCC Sub-Clause 42.1.1, the Contractor shall either immediately or upon the date specified in the notice of termination (a) cease all further work, except for such work as the Employer may specify in the notice of termination for the sole purpose of protecting that part of the Facilities already executed, or any work required to leave the Site in a clean and safe condition (b) terminate all subcontracts, except those to be assigned to the Employer pursuant to paragraph (d) (ii) below (c) remove all Contractor’s Equipment from the Site, repatriate the Contractor’s Personnel from the Site, remove from the Site any wreckage, rubbish and debris of any kind, and leave the whole of the Site in a clean and safe condition, and (d) subject to the payment specified in GCC Sub-Clause 42.1.3, (i) deliver to the Employer the parts of the Facilities executed by the Contractor up to the date of termination (ii) to the extent legally possible, assign to the Employer all right, title and benefit of the Contractor to the Facilities and to the Plant as of the date of termination, and, as may be required by the Employer, in any subcontracts concluded between the Contractor and its Subcontractors; and (iii) deliver to the Employer all non-proprietary drawings, specifications and other documents prepared by the Contractor or its Subcontractors as at the date of termination in connection with the Facilities. 42.1.3 In the event of termination of the Contract under GCC Sub-Clause 42.1.1, the Employer shall pay to the Contractor the following amounts: (a) the Contract Price, properly attributable to the parts of the Facilities executed by the Contractor as of the date of termination (b) the costs reasonably incurred by the Contractor in the removal of the Contractor’s Equipment from the Site and in the repatriation of the Contractor’s Personnel (c) any amounts to be paid by the Contractor to its Subcontractors in connection with the termination of any subcontracts, including any cancellation charges (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition pursuant to paragraph (a) of GCC Sub-Clause 42.1.2 (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third Parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. 42.2 Termination for Contractor’s Default 42.2.1 The Employer, without prejudice to any other rights or remedies it may possess, may terminate the Contract forthwith in the following circumstances by giving a notice of termination and its reasons therefor to the Contractor, referring to this GCC Sub-Clause 42.2: (a) if the Contractor becomes bankrupt or insolvent, has a receiving order issued against it, compounds with its creditors, or, if the Contractor is a corporation, a resolution is passed or order is made for its winding up, other than a voluntary liquidation for the purposes of amalgamation or reconstruction, a receiver is appointed over any part of its undertaking or assets, or if the Contractor takes or suffers any other analogous action in consequence of debt (b) if the Contractor assigns or transfers the Contract or any right or interest therein in violation of the provision of GCC Clause 43. (c) if the Contractor, in the judgment of the Employer has engaged in Fraud and Corruption, as defined in paragrpah 2.2 a. of Appendix B to the GCC, in competing for or in executing the Contract. 42.2.2 If the Contractor (a) has abandoned or repudiated the Contract (b) has without valid reason failed to commence work on the Facilities promptly or has suspended, other than pursuant to GCC Sub-Clause 41.2, the progress of Contract performance for more than twenty-eight (28) days after receiving a written instruction from the Employer to proceed (c) persistently fails to execute the Contract in accordance with the Contract or persistently neglects to carry out its obligations under the Contract without just cause (d) refuses or is unable to provide sufficient materials, services or labor to execute and complete the Facilities in the manner specified in the program furnished under GCC Sub-Clause 18.2 at rates of progress that give reasonable assurance to the Employer that the Contractor can attain Completion of the Facilities by the Time for Completion as extended, then the Employer may, without prejudice to any other rights it may possess under the Contract, give a notice to the Contractor stating the nature of the default and requiring the Contractor to remedy the same. If the Contractor fails to remedy or to take steps to remedy the same within fourteen (14) days of its receipt of such notice, then the Employer may terminate the Contract forthwith by giving a notice of termination to the Contractor that refers to this GCC Sub-Clause 42.2. 42.2.3 Upon receipt of the notice of termination under GCC Sub-Clauses 42.2.1 or 42.2.2, the Contractor shall, either immediately or upon such date as is specified in the notice of termination, (a) cease all further work, except for such work as the Employer may specify in the notice of termination for the sole purpose of protecting that part of the Facilities already executed, or any work required to leave the Site in a clean and safe condition (b) terminate all subcontracts, except those to be assigned to the Employer pursuant to paragraph (d) below (c) deliver to the Employer the parts of the Facilities executed by the Contractor up to the date of termination (d) to the extent legally possible, assign to the Employer all right, title and benefit of the Contractor to the Facilities and to the Plant as of the date of termination, and, as may be required by the Employer, in any subcontracts concluded between the Contractor and its Subcontractors (e) deliver to the Employer all drawings, specifications and other documents prepared by the Contractor or its Subcontractors as of the date of termination in connection with the Facilities. 42.2.4 The Employer may enter upon the Site, expel the Contractor, and complete the Facilities itself or by employing any third Party. The Employer may, to the exclusion of any right of the Contractor over the same, take over and use with the payment of a fair rental rate to the Contractor, with all the maintenance costs to the account of the Employer and with an indemnification by the Employer for all liability including damage or injury to persons arising out of the Employer’s use of such equipment, any Contractor’s Equipment owned by the Contractor and on the Site in connection with the Facilities for such reasonable period as the Employer considers expedient for the supply and installation of the Facilities. Upon completion of the Facilities or at such earlier date as the Employer thinks appropriate, the Employer shall give notice to the Contractor that such Contractor’s Equipment will be returned to the Contractor at or near the Site and shall return such Contractor’s Equipment to the Contractor in accordance with such notice. The Contractor shall thereafter without delay and at its cost remove or arrange removal of the same from the Site. 42.2.5 Subject to GCC Sub-Clause 42.2.6, the Contractor shall be entitled to be paid the Contract Price attributable to the Facilities executed as of the date of termination, the value of any unused or partially used Plant on the Site, and the costs, if any, incurred in protecting the Facilities and in leaving the Site in a clean and safe condition pursuant to paragraph (a) of GCC Sub-Clause 42.2.3. Any sums due the Employer from the Contractor accruing prior to the date of termination shall be deducted from the amount to be paid to the Contractor under this Contract. 42.2.6 If the Employer completes the Facilities, the cost of completing the Facilities by the Employer shall be determined. If the sum that the Contractor is entitled to be paid, pursuant to GCC Sub-Clause 42.2.5, plus the reasonable costs incurred by the Employer in completing the Facilities, exceeds the Contract Price, the Contractor shall be liable for such excess. If such excess is greater than the sums due the Contractor under GCC Sub-Clause 42.2.5, the Contractor shall pay the balance to the Employer, and if such excess is less than the sums due the Contractor under GCC Sub-Clause 42.2.5, the Employer shall pay the balance to the Contractor. The Employer and the Contractor shall agree, in writing, on the computation described above and the manner in which any sums shall be paid. 42.3 Termination by the Contractor 42.3.1 If (a) the Employer has failed to pay the Contractor any sum due under the Contract within the specified period, has failed to approve any invoice or supporting documents without just cause pursuant to the Appendix to the Contract Agreement titled Terms and Procedures of Payment, or commits a substantial breach of the Contract, the Contractor may give a notice to the Employer that requires payment of such sum, with interest thereon as stipulated in GCC Sub-Clause 12.3, requires approval of such invoice or supporting documents, or specifies the breach and requires the Employer to remedy the same, as the case may be. If the Employer fails to pay such sum together with such interest, fails to approve such invoice or supporting documents or give its reasons for withholding such approval, fails to remedy the breach or take steps to remedy the breach within fourteen (14) days after receipt of the Contractor’s notice, or (b) the Contractor is unable to carry out any of its obligations under the Contract for any reason attributable to the Employer, including but not limited to the Employer’s failure to provide possession of or access to the Site or other areas or failure to obtain any governmental permit necessary for the execution and/or completion of the Facilities, then the Contractor may give a notice to the Employer thereof, and if the Employer has failed to pay the outstanding sum, to approve the invoice or supporting documents, to give its reasons for withholding such approval, or to remedy the breach within twenty-eight (28) days of such notice, or if the Contractor is still unable to carry out any of its obligations under the Contract for any reason attributable to the Employer within twenty-eight (28) days of the said notice, the Contractor may by a further notice to the Employer referring to this GCC Sub-Clause 42.3.1, forthwith terminate the Contract. 42.3.2 The Contractor may terminate the Contract forthwith by giving a notice to the Employer to that effect, referring to this GCC Sub-Clause 42.3.2, if the Employer becomes bankrupt or insolvent, has a receiving order issued against it, compounds with its creditors, or, being a corporation, if a resolution is passed or order is made for its winding up (other than a voluntary liquidation for the purposes of amalgamation or reconstruction), a receiver is appointed over any part of its undertaking or assets, or if the Employer takes or suffers any other analogous action in consequence of debt. 42.3.3 If the Contract is terminated under GCC Sub-Clauses 42.3.1 or 42.3.2, then the Contractor shall immediately (a) cease all further work, except for such work as may be necessary for the purpose of protecting that part of the Facilities already executed, or any work required to leave the Site in a clean and safe condition (b) terminate all subcontracts, except those to be assigned to the Employer pursuant to paragraph (d) (ii) (c) remove all Contractor’s Equipment from the Site and repatriate the Contractor’s Personnel from the Site, and (d) subject to the payment specified in GCC Sub-Clause 42.3.4, (i) deliver to the Employer the parts of the Facilities executed by the Contractor up to the date of termination (ii) to the extent legally possible, assign to the Employer all right, title and benefit of the Contractor to the Facilities and to the Plant as of the date of termination, and, as may be required by the Employer, in any subcontracts concluded between the Contractor and its Subcontractors, and (iii) deliver to the Employer all drawings, specifications and other documents prepared by the Contractor or its Subcontractors as of the date of termination in connection with the Facilities. 42.3.4 If the Contract is terminated under GCC Sub-Clauses 42.3.1 or 42.3.2, the Employer shall pay to the Contractor all payments specified in GCC Sub-Clause 42.1.3, and reasonable compensation for all loss, except for loss of profit, or damage sustained by the Contractor arising out of, in connection with or in consequence of such termination. 42.3.5 Termination by the Contractor pursuant to this GCC Sub-Clause 42.3 is without prejudice to any other rights or remedies of the Contractor that may be exercised in lieu of or in addition to rights conferred by GCC Sub-Clause 42.3. 42.4 In this GCC Clause 42, the expression “Facilities executed” shall include all work executed, Installation Services provided, and all Plant acquired, or subject to a legally binding obligation to purchase, by the Contractor and used or intended to be used for the purpose of the Facilities, up to and including the date of termination. 42.5 In this GCC Clause 42, in calculating any monies due from the Employer to the Contractor, account shall be taken of any sum previously paid by the Employer to the Contractor under the Contract, including any advance payment paid pursuant to the Appendix to the Contract Agreement titled Terms and Procedures of Payment. |
| 43. Assignment | 43.1 Neither the Employer nor the Contractor shall, without the express prior written consent of the other Party, which consent shall not be unreasonably withheld, assign to any third Party the Contract or any part thereof, or any right, benefit, obligation or interest therein or thereunder, except that the Contractor shall be entitled to assign either absolutely or by way of charge any monies due and payable to it or that may become due and payable to it under the Contract. |
| 44. Export Restrictions | 44.1 Notwithstanding any obligation under the Contract to complete all export formalities, any export restrictions attributable to the Employer, to the country of the Employer or to the use of the Plant and Installation Services to be supplied which arise from trade regulations from a country supplying those Plant and Installation Services, and which substantially impede the Contractor from meeting its obligations under the Contract, shall release the Contractor from the obligation to provide deliveries or services, always provided, however, that the Contractor can demonstrate to the satisfaction of the Employer and of the Bank that it has completed all formalities in a timely manner, including applying for permits, authorizations and licenses necessary for the export of the Plant and Installation Services under the terms of the Contract. Termination of the Contract on this basis shall be for the Employer’s convenience pursuant to Sub-Clause 42.1. |

- Claims, Disputes and Arbitration

| 45. Contractor’s Claims | 45.1 If the Contractor considers himself to be entitled to any extension of the Time for Completion and/or any additional payment, under any Clause of these Conditions or otherwise in connection with the Contract, the Contractor shall submit a notice to the Project Manager, describing the event or circumstance giving rise to the claim. The notice shall be given as soon as practicable, and not later than 28 days after the Contractor became aware, or should have become aware, of the event or circumstance. If the Contractor fails to give notice of a claim within such period of 28 days, the Time for Completion shall not be extended, the Contractor shall not be entitled to additional payment, and the Employer shall be discharged from all liability in connection with the claim. Otherwise, the following provisions of this Sub-Clause shall apply. The Contractor shall also submit any other notices which are required by the Contract, and supporting particulars for the claim, all as relevant to such event or circumstance. The Contractor shall keep such contemporary records as may be necessary to substantiate any claim, either on the Site or at another location acceptable to the Project Manager. Without admitting the Employer’s liability, the Project Manager may, after receiving any notice under this Sub-Clause, monitor the record-keeping and/or instruct the Contractor to keep further contemporary records. The Contractor shall permit the Project Manager to inspect all these records, and shall (if instructed) submit copies to the Project Manager. Within 42 days after the Contractor became aware (or should have become aware) of the event or circumstance giving rise to the claim, or within such other period as may be proposed by the Contractor and approved by the Project Manager, the Contractor shall send to the Project Manager a fully detailed claim which includes full supporting particulars of the basis of the claim and of the extension of time and/or additional payment claimed. If the event or circumstance giving rise to the claim has a continuing effect: - this fully detailed claim shall be considered as interim; - the Contractor shall send further interim claims at monthly intervals, giving the accumulated delay and/or amount claimed, and such further particulars as the Project Manager may reasonably require; and - the Contractor shall send a final claim within 28 days after the end of the effects resulting from the event or circumstance, or within such other period as may be proposed by the Contractor and approved by the Project Manager. Within 42 days after receiving a claim or any further particulars supporting a previous claim, or within such other period as may be proposed by the Project Manager and approved by the Contractor, the Project Manager shall respond with approval, or with disapproval and detailed comments. He may also request any necessary further particulars, but shall nevertheless give his response on the principles of the claim within such time. Each Payment Certificate shall include such amounts for any claim as have been reasonably substantiated as due under the relevant provision of the Contract. Unless and until the particulars supplied are sufficient to substantiate the whole of the claim, the Contractor shall only be entitled to payment for such part of the claim as he has been able to substantiate. The Project Manager shall agree with the Contractor or estimate: (i) the extension (if any) of the Time for Completion (before or after its expiry) in accordance with GCC Clause 40, and/or (ii) the additional payment (if any) to which the Contractor is entitled under the Contract. The requirements of this Sub-Clause are in addition to those of any other Sub-Clause which may apply to a claim. If the Contractor fails to comply with this or another Sub-Clause in relation to any claim, any extension of time and/or additional payment shall take account of the extent (if any) to which the failure has prevented or prejudiced proper investigation of the claim, unless the claim is excluded under the second paragraph of this Sub-Clause. In the event that the Contractor and the Employer cannot agree on any matter relating to a claim, either Party may refer the matter to the Dispute Board pursuant to GCC 46 hereof. |
| --- | --- |
| 46. Disputes and Arbitration | ### 46.1 Appointment of the Dispute Board Disputes shall be referred to a DB for decision in accordance with GCC Sub-Clause 46.3. The Parties shall appoint a DB by the date stated in the PCC. The DB shall comprise, as stated in the PCC, either one or three suitably qualified persons (“the members”), each of whom shall meet the criteria set forth in Sub-Clause 3 of Appendix A- General Conditions of Dispute Board Agreement. If the number is not so stated and the Parties do not agree otherwise, the DB shall comprise three persons, one of whom shall serve as chairman. If the Contract is with a foreign Contractor, the DB members shall not have the same nationality as the Employer or the Contractor. If the Parties have not jointly appointed the DB 21 days before the date stated in the PCC and the DB is to comprise three persons, each Party shall nominate one member for the approval of the other Party. The first two members shall recommend and the Parties shall agree upon the third member, who shall act as chairman. However, if a list of potential members is included in the PCC, the members shall be selected from those on the list, other than anyone who is unable or unwilling to accept appointment to the DB. The agreement between the Parties and either the sole member or each of the three members shall incorporate by reference the General Conditions of Dispute Board Agreement contained in the Appendix to these General Conditions, with such amendments as are agreed between them. The DB shall be deemed to be constituted on the date the Parties and the sole member or the three members (as the case may be) of the DB have all signed a DB agreement. The terms of the remuneration of either the sole member or each of the three members, including the remuneration of any expert whom the DB consults, shall be mutually agreed upon by the Parties when agreeing the terms of appointment of the member or such expert (as the case may be). Each Party shall be responsible for paying one-half of this remuneration. If a member declines to act or is unable to act as a result of death, disability, resignation or termination of appointment, a replacement shall be appointed in the same manner as the replaced person was required to have been nominated or agreed upon, as described in this Sub-Clause. The appointment of any member may be terminated by mutual agreement of both Parties, but not by the Employer or the Contractor acting alone. Unless otherwise agreed by both Parties, the appointment of the DB (including each member) shall expire when the Operational Acceptance Certificate has been issued in accordance with GCC Sub-Clause 25.3. |
|  | ### 46.2 Failure to Agree on the Composition of the Dispute Board If any of the following conditions apply, namely: - the Parties fail to agree upon the appointment of the sole member of the DB by the date stated in the first paragraph of GCC Sub-Clause 46.1, - either Party fails to nominate a member (for approval by the other Party) of a DB of three persons by such date, - the Parties fail to agree upon the appointment of the third member (to act as chairman) of the DB by such date, or - the Parties fail to agree upon the appointment of a replacement person within 42 days after the date on which the sole member or one of the three members declines to act or is unable to act as a result of death, disability, resignation or termination of appointment, then the appointing entity or official named in the PCC shall, upon the request of either or both of the Parties and after due consultation with both Parties, appoint this member of the DB. This appointment shall be final and conclusive. Each Party shall be responsible for paying one-half of the remuneration of the appointing entity or official. |
|  | ### 46.3 Obtaining Dispute Board’s Decision If a dispute (of any kind whatsoever) arises between the Parties in connection with the performance of the Contract, including any dispute as to any certificate, determination, instruction, opinion or valuation of the Project Manager, either Party may refer the dispute in writing to the DB for its decision, with copies to the other Party and the Project Manager. Such reference shall state that it is given under this Sub-Clause. For a DB of three persons, the DB shall be deemed to have received such reference on the date when it is received by the chairman of the DB. Both Parties shall promptly make available to the DB all such additional information, further access to the Site, and appropriate facilities, as the DB may require for the purposes of making a decision on such dispute. The DB shall be deemed to be not acting as arbitrator(s). Within 84 days after receiving such reference, or within such other period as may be proposed by the DB and approved by both Parties, the DB shall give its decision, which shall be reasoned and shall state that it is given under this Sub-Clause. The decision shall be binding on both Parties, who shall promptly give effect to it unless and until it shall be revised in an amicable settlement or an arbitral award as described below. Unless the Contract has already been abandoned, repudiated or terminated, the Contractor shall continue with the performance of the Facilities in accordance with the Contract. If either Party is dissatisfied with the DB’s decision, then either Party may, within 28 days after receiving the decision, give notice to the other Party of its dissatisfaction and intention to commence arbitration. If the DB fails to give its decision within the period of 84 days (or as otherwise approved) after receiving such reference, then either Party may, within 28 days after this period has expired, give notice to the other Party of its dissatisfaction and intention to commence arbitration. In either event, this notice of dissatisfaction shall state that it is given under this Sub-Clause, and shall set out the matter in dispute and the reason(s) for dissatisfaction. Except as stated in GCC Sub-Clauses 46.6 and 46.7, neither Party shall be entitled to commence arbitration of a dispute unless a notice of dissatisfaction has been given in accordance with this Sub-Clause. If the DB has given its decision as to a matter in dispute to both Parties, and no notice of dissatisfaction has been given by either Party within 28 days after it received the DB’s decision, then the decision shall become final and binding upon both Parties. |
|  | ### 46.4 Amicable Settlement Where notice of dissatisfaction has been given under GCC Sub-Clause 46.3 above, both Parties shall attempt to settle the dispute amicably before the commencement of arbitration. However, unless both Parties agree otherwise, arbitration may be commenced on or after the fifty-sixth day after the day on which notice of dissatisfaction and intention to commence arbitration was given, even if no attempt at amicable settlement has been made. |
|  | ### 46.5 Arbitration Unless indicated otherwise in the PCC, any dispute not settled amicably and in respect of which the DB’s decision (if any) has not become final and binding shall be finally settled by arbitration. Unless otherwise agreed by both Parties, arbitration shall be conducted as follows: (a) For contracts with foreign contractors: unless otherwise specified in the PCC; the dispute shall be finally settled under the Rules of Arbitration of the International Chamber of Commerce; by one or three arbitrators appointed in accordance with these Rules. The place of arbitration shall be the neutral location stated in the PCC; and the arbitration shall be conducted in the ruling language stated in the PCC; and (b) For contracts with domestic contractors, arbitration with proceedings conducted in accordance with the laws of the Employer’s Country. The arbitrator(s) shall have full power to open up, review and revise any certificate, determination, instruction, opinion or valuation of the Project Manager, and any decision of the DB, relevant to the dispute. Nothing shall disqualify the Project Manager from being called as a witness and giving evidence before the arbitrator(s) on any matter whatsoever relevant to the dispute. Neither Party shall be limited in the proceedings before the arbitrator(s) to the evidence or arguments previously put before the DB to obtain its decision, or to the reasons for dissatisfaction given in its notice of dissatisfaction. Any decision of the DB shall be admissible in evidence in the arbitration. Arbitration may be commenced prior to or after completion of the Facilities. The obligations of the Parties, the Project Manager and the DB shall not be altered by reason of any arbitration being conducted during the progress of the execution of the Facilities. |
|  | ### 46.6 Failure to Comply with Dispute Board’s Decision In the event that a Party fails to comply with a DB decision which has become final and binding, then the other Party may, without prejudice to any other rights it may have, refer the failure itself to arbitration under GCC Sub-Clause 46.5. GCC Sub-Clauses 46.3 and 46.4 shall not apply to this reference. |
|  | ### 46.7 Expiry of Dispute Board’s Appointment If a dispute arises between the Parties in connection with the performance of the Contract, and there is no DB in place, whether by reason of the expiry of the DB’s appointment or otherwise: (a) GCC Sub-Clauses 46.3 and 46.4 shall not apply, and ### (b) the dispute may be referred directly to arbitration under GCC Sub-Clause 46.5 |

APPENDIX A

General Conditions of Dispute Board Agreement

1.	Definitions

Each “Dispute Board Agreement” is a tripartite agreement by and between:

the “Employer”;

the “Contractor”; and

the “Member” who is defined in the Dispute Board Agreement as being:

(i) 	the sole member of the “DB” and, where this is the case, all references to the “Other Members” do not apply, or

(ii) 	one of the three persons who are jointly called the “DB” (or “dispute board”) and, where this is the case, the other two persons are called the “Other Members”.

The Employer and the Contractor have entered (or intend to enter) into a contract, which is called the “Contract” and is defined in the Dispute Board Agreement, which incorporates this Appendix. In the Dispute Board Agreement, words and expressions which are not otherwise defined shall have the meanings assigned to them in the Contract.

2.	General Provisions

Unless otherwise stated in the Dispute Board Agreement, it shall take effect on the latest of the following dates:

(a)	the Commencement Date defined in the Contract,

(b)  	when the Employer, the Contractor and the Member have each signed the Dispute Board Agreement, or

(c) 	when the Employer, the Contractor and each of the Other Members (if any) have respectively each signed a dispute board agreement.

This employment of the Member is a personal appointment. At any time, the Member may give not less than 70 days’ notice of resignation to the Employer and to the Contractor, and the Dispute Board Agreement shall terminate upon the expiry of this period.

3.	Warranties

The Member warrants and agrees that he/she is and shall be impartial and independent of the Employer, the Contractor and the Project Manager. The Member shall promptly disclose, to each of them and to the Other Members (if any), any fact or circumstance which might appear inconsistent with his/her warranty and agreement of impartiality and independence.

- When appointing the Member, the Employer and the Contractor relied upon the Member’s representations that he/she is:has at least a bachelor’s degree in relevant disciplines such as law, engineering, construction management or contract management;

- has at least ten years of experience in contract administration/management and dispute resolution, out of which at least five years of experience as an arbitrator or adjudicator in construction-related disputes;

- has received formal training as an adjudicator from an internationally recognized organization;

- has experience and/or is knowledgeable in the type of work which the Contractor is to carry out under the Contract;

- has experience in the interpretation of construction and/or engineering contract documents; and

- is fluent in the language for communications defined in GCC Sub-Clause 5.3  (or the language as agreed between the Parties and the DB).

4.	General Obligations of the Member

The Member shall:

(a) 	have no interest financial or otherwise in the Employer, the Contractor or the Project Manager, nor any financial interest in the Contract except for payment under the Dispute Board Agreement;

(b) 	not previously have been employed as a consultant or otherwise by the Employer, the Contractor or the Project Manager, except in such circumstances as were disclosed in writing to the Employer and the Contractor before they signed the Dispute Board Agreement;

(c) 	have disclosed in writing to the Employer, the Contractor and the Other Members (if any), before entering into the Dispute Board Agreement and to his/her best knowledge and recollection, any professional or personal relationships with any director, officer or employee of the Employer, the Contractor or the Project Manager, and any previous involvement in the overall project of which the Contract forms part;

(d)  	not, for the duration of the Dispute Board Agreement, be employed as a consultant or otherwise by the Employer, the Contractor or the Project Manager, except as may be agreed in writing by the Employer, the Contractor and the Other Members (if any);

(e)	comply with the annexed procedural rules and with GCC Sub-Clause 46.3;

(f)	not give advice to the Employer, the Contractor, the Employer’s Personnel or the Contractor’s  Personnel concerning the conduct of the Contract, other than in accordance with the annexed procedural rules;

(g)	not while a Member enter into discussions or make any agreement with the Employer, the Contractor or the Project Manager regarding employment by any of them, whether as a consultant or otherwise, after ceasing to act under the Dispute Board Agreement;

(h)	ensure his/her availability for all site visits and hearings as are necessary;

(i)	become conversant with the Contract and with the progress of the Facilities (and of any other parts of the project of which the Contract forms part) by studying all documents received which shall be maintained in a current working file;

(j)	treat the details of the Contract and all the DB’s activities and hearings as private and confidential, and not publish or disclose them without the prior written consent of the Employer, the Contractor and the Other Members (if any); and

(k)	be available to give advice and opinions, on any matter relevant to the Contract when requested by both the Employer and the Contractor, subject to the agreement of the Other Members (if any).

5.	General Obligations of the Employer and the Contractor

The Employer, the Contractor, the Employer’s Personnel and the Contractor’s Personnel shall not request advice from or consultation with the Member regarding the Contract, otherwise than in the normal course of the DB’s activities under the Contract and the Dispute Board Agreement. The Employer and the Contractor shall be responsible for compliance with this provision, by the Employer’s Personnel and the Contractor’s  Personnel respectively.

The Employer and the Contractor undertake to each other and to the Member that the Member shall not, except as otherwise agreed in writing by the Employer, the Contractor, the Member and the Other Members (if any):

(a)	be appointed as an arbitrator in any arbitration under the Contract;

(b)	be called as a witness to give evidence concerning any dispute before arbitrator(s) appointed for any arbitration under the Contract; or

(c)	be liable for any claims for anything done or omitted in the discharge or purported discharge of the Member’s functions, unless the act or omission is shown to have been in bad faith.

The Employer and the Contractor hereby jointly and severally indemnify and hold the Member harmless against and from claims from which he is relieved from liability under the preceding paragraph.

Whenever the Employer or the Contractor refers a dispute to the DB under GCC Sub-Clause 46.3, which will require the Member to make a site visit and attend a hearing, the Employer or the Contractor shall provide appropriate security for a sum equivalent to the reasonable expenses to be incurred by the Member. No account shall be taken of any other payments due or paid to the Member.

6.	Payment

The Member shall be paid as follows, in the currency named in the Dispute Board Agreement:

(a)	a retainer fee per calendar month, which shall be considered as payment in full for:

(i)	being available on 28 days’ notice for all site visits and hearings;

(ii)	becoming and remaining conversant with all project developments and maintaining relevant files;

(iii) 	all office and overhead expenses including secretarial services, photocopying and office supplies incurred in connection with his duties; and

(iv) 	all services performed hereunder except those referred to in sub-paragraphs (b) and (c) of this Clause.

The retainer fee shall be paid with effect from the last day of the calendar month in which the Dispute Board Agreement becomes effective; until the last day of the calendar month in which the Taking-Over Certificate is issued for the whole of the Facilities.

With effect from the first day of the calendar month following the month in which Taking-Over Certificate is issued for the whole of the Facilities, the retainer fee shall be reduced by one third This reduced fee shall be paid until the first day of the calendar month in which the Member resigns or the Dispute Board Agreement is otherwise terminated.

(b) 	a daily fee which shall be considered as payment in full for:

(i) 	each day or part of a day up to a maximum of two days’ travel time in each direction for the journey between the Member’s home and the site, or another location of a meeting with the Other Members (if any);

(ii) 	each working day on site visits, hearings or preparing decisions; and

(iii) 	each day spent reading submissions in preparation for a hearing.

(c)  	all reasonable expenses including necessary travel expenses (air fare in less than first class, hotel and subsistence and other direct travel expenses) incurred in connection with the Member’s duties, as well as the cost of telephone calls, courier charges, faxes and telexes: a receipt shall be required for each item in excess of five percent of the daily fee referred to in sub-paragraph (b) of this Clause;

(d)	any taxes properly levied in the Country on payments made to the Member (unless a national or permanent resident of the Country) under this Clause 6.

The retainer and daily fees shall be as specified in the Dispute Board Agreement. Unless it specifies otherwise, these fees shall remain fixed for the first 24 calendar months, and shall thereafter be adjusted by agreement between the Employer, the Contractor and the Member, at each anniversary of the date on which the Dispute Board Agreement became effective.

If the Parties fail to agree on the retainer fee or the daily fee the appointing entity or official named in the PCC shall determine the amount of the fees to be used.

The Member shall submit invoices for payment of the monthly retainer and air fares quarterly in advance. Invoices for other expenses and for daily fees shall be submitted following the conclusion of a site visit or hearing. All invoices shall be accompanied by a brief description of activities performed during the relevant period and shall be addressed to the Contractor.

The Contractor shall pay each of the Member’s invoices in full within 56 calendar days after receiving each invoice and shall apply to the Employer (in the Statements under the Contract) for reimbursement of one-half of the amounts of these invoices. The Employer shall then pay the Contractor in accordance with the Contract.

If the Contractor fails to pay to the Member the amount to which he/she is entitled under the Dispute Board Agreement, the Employer shall pay the amount due to the Member and any other amount which may be required to maintain the operation of the DB; and without prejudice to the Employer’s rights or remedies. In addition to all other rights arising from this default, the Employer shall be entitled to reimbursement of all sums paid in excess of one-half of these payments, plus all costs of recovering these sums and financing charges calculated at the rate specified in accordance with GCC Sub-Clause 12.3.

If the Member does not receive payment of the amount due within 70 days after submitting a valid invoice, the Member may (i) suspend his/her services (without notice) until the payment is received, and/or (ii) resign his/her appointment by giving notice under Clause 7.

7.	Termination

At any time: (i) the Employer and the Contractor may jointly terminate the Dispute Board Agreement by giving 42 days’ notice to the Member; or (ii) the Member may resign as provided for in Clause 2.

If the Member fails to comply with the Dispute Board Agreement, the Employer and the Contractor may, without prejudice to their other rights, terminate it by notice to the Member. The notice shall take effect when received by the Member.

If the Employer or the Contractor fails to comply with the Dispute Board Agreement, the Member may, without prejudice to his other rights, terminate it by notice to the Employer and the Contractor. The notice shall take effect when received by them both.

Any such notice, resignation and termination shall be final and binding on the Employer, the Contractor and the Member. However, a notice by the Employer or the Contractor, but not by both, shall be of no effect.

8.	Default of the Member

If the Member fails to comply with any of his obligations under Clause 4 concerning his impartiality or independence in relation to the Employer or the Contractor, he/she shall not be entitled to any fees or expenses hereunder and shall, without prejudice to their other rights, reimburse each of the Employer and the Contractor for any fees and expenses received by the Member and the Other Members (if any), for proceedings or decisions (if any) of the DB which are rendered void or ineffective by the said failure to comply.

9.	Disputes

Any dispute or claim arising out of or in connection with this Dispute Board Agreement, or the breach, termination or invalidity thereof, shall be finally settled by institutional arbitration. If no other arbitration institute is agreed, the arbitration shall be conducted under the Rules of Arbitration of the International Chamber of Commerce by one arbitrator appointed in accordance with these Rules of Arbitration.

Appendix A

DISPUTE BOARD GUIDELINES

1. 	Unless otherwise agreed by the Employer and the Contractor, the DB shall visit the site at intervals of not more than 140 days, including times of critical construction events, at the request of either the Employer or the Contractor. Unless otherwise agreed by the Employer, the Contractor and the DB, the period between consecutive visits shall not be less than 70 days, except as required to convene a hearing as described below.

2. 	The timing of and agenda for each site visit shall be as agreed jointly by the DB, the Employer and the Contractor, or in the absence of agreement, shall be decided by the DB. The purpose of site visits is to enable the DB to become and remain acquainted with the progress of the execution of the Contract and of any actual or potential problems or claims, and, as far as reasonable, to prevent potential problems or claims from becoming disputes.

3.  	Site visits shall be attended by the Employer, the Contractor and the Project Manager and shall be coordinated by the Employer in co-operation with the Contractor. The Employer shall ensure the provision of appropriate conference facilities and secretarial and copying services. At the conclusion of each site visit and before leaving the site, the DB shall prepare a report on its activities during the visit and shall send copies to the Employer and the Contractor.

4.  	The Employer and the Contractor shall furnish to the DB one copy of all documents which the DB may request, including Contract documents, progress reports, variation instructions, certificates and other documents pertinent to the performance of the Contract. All communications between the DB and the Employer or the Contractor shall be copied to the other Party. If the DB comprises three persons, the Employer and the Contractor shall send copies of these requested documents and these communications to each of these persons.

5.  	If any dispute is referred to the DB in accordance with GCC Sub-Clause 46.3, the DB shall proceed in accordance with GCC Sub-Clause 46.3 and these Guidelines. Subject to the time allowed to give notice of a decision and other relevant factors, the DB shall:

(a)  	act fairly and impartially as between the Employer and the Contractor, giving each of them a reasonable opportunity of putting his case and responding to the other’s case, and

(b)  	adopt procedures suitable to the dispute, avoiding unnecessary delay or expense.

6.  	The DB may conduct a hearing on the dispute, in which event it will decide on the date and place for the hearing and may request that written documentation and arguments from the Employer and the Contractor be presented to it prior to or at the hearing.

7. 	 Except as otherwise agreed in writing by the Employer and the Contractor, the DB shall have power to adopt an inquisitorial procedure, to refuse admission to hearings or audience at hearings to any persons other than representatives of the Employer, the Contractor and the Project Manager, and to proceed in the absence of any Party who the DB is satisfied received notice of the hearing; but shall have discretion to decide whether and to what extent this power may be exercised.

8.  	The Employer and the Contractor empower the DB, among other things, to:

(a) 	establish the procedure to be applied in deciding a dispute,

(b) 	decide upon the DB’s own jurisdiction, and as to the scope of any dispute referred to it,

(c) 	conduct any hearing as it thinks fit, not being bound by any rules or procedures other than those contained in the Contract and these Guidelines,

(d) 	take the initiative in ascertaining the facts and matters required for a decision,

(e)	make use of its own specialist knowledge, if any,

(f) 	decide upon the payment of financing charges in accordance with the Contract,

(g) 	decide upon any provisional relief such as interim or conservatory measures,

(h) 	open up, review and revise any certificate, decision, determination, instruction, opinion or valuation of the Project Manager, relevant to the dispute, and

(i)  	appoint, should the DB so consider necessary and the Parties agree, a suitable expert/s  (including legal and technical expert(s)) at the cost of the Parties to give advice on a specific matter/s relevant to the dispute.

9.  	The DB shall not express any opinions during any hearing concerning the merits of any arguments advanced by the Parties. Thereafter, the DB shall make and give its decision in accordance with GCC Sub-Clause 46.3, or as otherwise agreed by the Employer and the Contractor in writing. If the DB comprises three persons:

(a)  	it shall convene in private after a hearing, in order to have discussions and prepare its decision;

(b)  	it shall endeavor to reach a unanimous decision: if this proves impossible the applicable decision shall be made by a majority of the Members, who may require the minority Member to prepare a written report for submission to the Employer and the Contractor; and

(c) 	 if a Member fails to attend a meeting or hearing, or to fulfil any required function, the other two Members may nevertheless proceed to make a decision, unless:

(i)	either the Employer or the Contractor does not agree that they do so, or

(ii) 	the absent Member is the chairman and he/she instructs the other Members to not make a decision.

APPENDIX B

Fraud and Corruption

(Text in this Appendix shall not be modified)

- Purpose

  - The Bank’s Anti-Corruption Guidelines and this annex apply with respect to procurement under Bank Investment Project Financing operations.

- Requirements

- The Bank requires that Borrowers (including beneficiaries of Bank financing); bidders (applicants/proposers), consultants, contractors and suppliers; any sub-contractors, sub-consultants, service providers or suppliers; any agents (whether declared or not); and any of their personnel, observe the highest standard of ethics during the procurement process, selection and contract execution of Bank-financed contracts, and refrain from Fraud and Corruption.

- To this end, the Bank:

- Defines, for the purposes of this provision, the terms set forth below as follows:

- “corrupt practice” is the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party;

- “fraudulent practice” is any act or omission, including misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain financial or other benefit or to avoid an obligation;

- “collusive practice” is an arrangement between two or more parties designed to achieve an improper purpose, including to influence improperly the actions of another party;

- “coercive practice” is impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party;

- “obstructive practice” is:

- deliberately destroying, falsifying, altering, or concealing of evidence material to the investigation or making false statements to investigators in order to materially impede a Bank investigation into allegations of a corrupt, fraudulent, coercive, or collusive practice; and/or threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or

- acts intended to materially impede the exercise of the Bank’s inspection and audit rights provided for under paragraph 2.2 e. below.

- Rejects a proposal for award if the Bank determines that the firm or individual recommended for award, any of its personnel, or its agents, or its sub-consultants, sub-contractors, service providers, suppliers and/ or their employees, has, directly or indirectly, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices in competing for the contract in question;

- In addition to the legal remedies set out in the relevant Legal Agreement, may take other appropriate actions, including declaring misprocurement, if the Bank determines at any time that representatives of the Borrower or of a recipient of any part of the proceeds of the loan engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices during the procurement process, selection and/or execution of the contract in question, without the Borrower having taken timely and appropriate action satisfactory to the Bank to address such practices when they occur, including by failing to inform the Bank in a timely manner at the time  they knew of the practices;

- Pursuant to the Bank’s Anti- Corruption Guidelines and in accordance with the Bank’s prevailing sanctions policies and procedures, may sanction a firm or individual, either indefinitely or for a stated period of time, including by publicly declaring such firm or individual ineligible (i) to be awarded or otherwise benefit from a Bank-financed contract, financially or in any other manner; (ii) to be a nominated sub-contractor, consultant, manufacturer or supplier, or service provider of an otherwise eligible firm being awarded a Bank-financed contract; and (iii) to receive the proceeds of any loan made by the Bank or otherwise to participate further in the preparation or implementation of any Bank-financed project;

- Requires that a clause be included in bidding/request for proposals documents and in contracts financed by a Bank loan, requiring (i) bidders (applicants/proposers), consultants, contractors, and suppliers, and their sub-contractors, sub-consultants, service providers, suppliers, agents personnel, permit the Bank to inspect all accounts, records and other documents relating to the procurement process, selection and/or contract execution, and to have them audited by auditors appointed by the Bank.

APPENDIX C

Metrics for Progress Reports- Environmental and Social (ES)

[Note to Employer: the following metrics is taken from large Work’s Standard Procurement Documents (SPDs). This should be suitably amended to reflect the specifics of the Contract. The Employer shall ensure that the metrics provided are appropriate for Plant and impacts/key issues identified in the environmental and social assessment].

Metrics for regular reporting:

        - environmental incidents or non-compliances with contract requirements, including contamination, pollution or damage to ground or water supplies;

        - health and safety incidents, accidents, injuries that require treatment and all fatalities;

        - interactions with regulators:  identify agency, dates, subjects, outcomes (report the negative if none);

        - status of all permits and agreements:

- work permits: number required, number received, actions taken for those not received;

- status of permits and consents:

- temporary Construction site permit.

        - health and safety supervision:

- number of workers, work hours, metric of PPE use (percentage of workers with full personal protection equipment (PPE), partial, etc.), worker violations observed (by type of violation, PPE or otherwise), warnings given, repeat warnings given, follow-up actions taken (if any);

        - worker accommodations:

- number of expats housed in accommodations, number of locals;

- date of last inspection, and highlights of inspection including status of accommodations’ compliance with national and local law and good practice, including sanitation, space, etc.;

- actions taken to recommend/require improved conditions, or to improve conditions.

        - gender (for expats and locals separately): number of female workers, percentage of workforce, gender issues raised and dealt with (cross-reference grievances or other sections as needed);

        - training:

- number of new workers, number receiving induction training, dates of induction training;

- number and dates of toolbox talks, number of workers receiving Occupational Health and Safety (OHS), environmental and social training;

- number and dates of communicable diseases (including STDs) sensitization and/or training, no. workers receiving training (in the reporting period and in the past); same questions for gender sensitization, flag person training.

- number and date of SEA prevention and SH sensitization and/or training events, including number of workers receiving training on Code of Conduct for Contractor’s Personnel (in the reporting period and in the past), etc.

        - environmental and social supervision:

- environmental and Social Safeguards Officer: days worked, areas inspected and numbers of inspections, highlights of activities/findings (including violations of environmental and/or social best practices, compliance with ESCP and actions taken), reports to environmental and/or social specialist/construction/site management;

        - Grievances: list new grievances (e.g. number of allegations of SEA and SH) received in the reporting period and number of unresolved past grievances by date received, complainant’s age and sex, how received, to whom referred to for action, resolution and date (if completed), data resolution reported to complainant, any required follow-up (Cross-reference other sections as needed):

- Worker grievances;

- Community grievances

        - Traffic, road safety and vehicles/equipment:

- traffic and road safety incidents and accidents involving project vehicles & equipment: provide date, location, damage, cause, follow-up;

- traffic and road safety incidents and accidents involving non-project vehicles or property (also reported under immediate metrics): provide date, location, damage, cause, follow-up;

- overall condition of vehicles/equipment (subjective judgment by environmentalist); non-routine repairs and maintenance needed to improve safety and/or environmental performance (to control smoke, etc.).

        - Environmental mitigations and issues (what has been done):

- compliance status for conditions of all relevant consents/permits, for the Work, including quarries, etc.): statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance;

- compliance status of ESCP (Appendix F) requirements: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- compliance status of SEA and SH prevention and response action plan: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- compliance status of Health and Safety Management Plan re: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- other unresolved issues from previous reporting periods related to environmental and social: continued violations, continued failure of equipment, continued lack of vehicle covers, spills not dealt with, continued compensation or blasting issues, etc.  Cross-reference other sections as needed.

APPENDIX D

Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment (SH) Performance Declaration for Subcontractors

[The following table shall be filled in by each subcontractor proposed by the Contractor, that was not named in the Contract]

Subcontractor’s Name: [insert full name]
Date: [insert day, month, year]
Contract reference [insert contract reference]
Page [insert page number] of [insert total number] pages

SEA and/or SH Declaration

We:  (a) have not been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.  (b) are subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.  (c) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations. An arbitral award on the disqualification case has been made in our favor.

[If (c) above is applicable, attach evidence of an arbitral award reversing the findings on the issues underlying the disqualification.]

Name of the Subcontractor

Name of the person duly authorized to sign on behalf of the Subcontractor	_______

Title of the person signing on behalf of the Subcontractor	______________________

Signature of the person named above	______________________

Date signed ________________________________ day of ___________________, _____

Countersignature of authorized representative of the Contractor:

Signature: ________________________________________________________

Date signed ________________________________ day of ___________________, _____

Section IX - Particular Conditions of Contract

The following Particular Conditions of Contract shall supplement the General Conditions of Contract in Section VIII. Whenever there is a conflict, the provisions herein shall prevail over those in the General Conditions.

Particular Conditions of Contract (PCC)

The following Particular Conditions (PCC) shall supplement the General Conditions (GCC).  Whenever there is a conflict, the provisions herein shall prevail over those in the GCC.  The clause number of the PCC is the corresponding clause number of the GCC.

| PCC 1. Definitions | The Employer is: Ministry of Environment, Climate Change and Environment The Project Manager is: _____________________ The Bank is: The World Bank Country of Origin: all countries and territories as indicated in Section V of the bidding document, Eligible Countries. |
| --- | --- |
| PCC 5. Law and Language | PCC 5.1 The Contract shall be interpreted in accordance with the laws of: The Republic of Maldives. PCC 5.2 The ruling language is: English PCC 5.3 The language for communications is: English |
| PCC 7. Scope of Facilities [Spare Parts] (GCC Clause 7) | PCC 7.3 The Contractor agrees to supply spare parts for a period of years: Five (5) Years Sample Addition to PCC 7.3 The Contractor shall carry sufficient inventories to ensure an ex-stock supply of consumable spares for the Plant. Other spare parts and components shall be supplied as promptly as possible, but at the most within three (3) months of placing the order and opening the letter of credit. In addition, in the event of termination of the production of spare parts, advance notification will be made to the Employer of the pending termination, with sufficient time to permit the Employer to procure the needed requirement. Following such termination, the Contractor will furnish to the extent possible and at no cost to the Employer the blueprints, drawings and specifications of the spare parts, if requested. |
| PCC 8. Time for Commencement and Completion | PCC 8.1 The Contractor shall commence work on the Facilities within from the Effective Date for determining Time for Completion as specified in the Contract Agreement. PCC 8.2 The Time for Completion of the whole of the Facilities shall be 12 months from the Effective Date as described in the Contract Agreement. |
| PCC 11. Contract Price | PCC 11.2 The Contract Price shall be adjusted in accordance with the provisions of the Appendix to the Contract Agreement titled Adjustment Clause. (NOT APPLICABLE) |
| PCC 13. Securities | PCC 13.3.1 The amount of Performance Security, as a percentage of the Contract Price for the Facility or for the part of the Facility for which a separate Time for Completion is provided, shall be: Five percent (5%). PCC 13.3.2 The Performance Security shall be in the form of the Bank Guarantee attached hereto in Section X, Contract Forms. PCC 13.3.3 The Performance Security shall not be reduced on the date of the Operational Acceptance. PCC 13.3.3 The Performance Security shall be reduced to Ten percent (10%) of the value of the component covered by the extended defect liability to cover the Contractor’s extended defect liability in accordance with the provision in the PCC, pursuant to GCC Sub-Clause 27.10. |
| PCC 22 Installation | PCC22.2.5 Working Hours Normal working hours are: 8 Hours a Day 6 Days a Week |
| PCC 25. Commissioning and Operational Acceptance | PCC 25.2.2 The Guarantee Test of the Facilities shall be successfully completed within One (1) Month from the date of Completion. |
| PCC 26. Completion Time Guarantee | PCC 26.2 Applicable rate for liquidated damages: Zero Point Zero One percent (0.01%) of Contract Price per Day. The above rate applies to the price of the part of the Facilities, as quoted in the Price Schedule, for that part for which the Contractor fails to achieve Completion within the particular Time for Completion. Maximum deduction for liquidated damages: Ten percent (10%) of Contract Price PCC 26.3 No bonus will be given for earlier Completion of the Facilities or part thereof. |
| PCC 27. Defect Liability | PCC 27.10 The critical components covered under the extended defect liability are: - Battery Inverters - Battery Modules and the period shall be 12 Months from the installation and acceptance of the respective component(s). |
| PCC 30. Limitation of Liability | PCC 30.1 (b) The multiplier of the Contract Price is: One Point One (1.1) times. |
| PCC 39. Value Engineering | NOT APPLICABLE |
| PCC46. Disputes and Arbitration | PCC 46.1 The DB shall be appointed within Sixty 60 Days after signature by both parties of the Contract Agreement PCC 46.1 The DB shall be: One (1) member. PCC 46.1 List of potential DB members: Proposed by Employer [Attach CVs to the bidding document and the Contract] 1._____________________ Proposed by Contractor [Attach CVs to the Contract] 1.________________________ PCC 46.2 Appointment (if not agreed) to be made by: Ministry of Finance. Rules of arbitration GCC Sub-Clause 46.5 (a) shall apply in the case of a Contract with a foreign Contractor. GCC Sub-Clause 46.5 (b): shall apply in the case of a Contract with a Domestic Contractor. Place of arbitration if GCC Sub-Clause 46.5 (a) applies is Singapore. |

Section X - Contract Forms

## Table of Forms

Notification of Intention to Award	420

Beneficial Ownership Disclosure Form	424

Letter of Acceptance	426

Contract Agreement	427

Appendix 1.  Terms and Procedures of Payment	431

Appendix 2.  Price Adjustment	433

Not Applicable	433

Appendix 3.  Insurance Requirements	434

Appendix 4.  Time Schedule	438

Appendix 5.  List of Major Items of Plant and Installation Services and List of Approved Subcontractors	439

Appendix 6.  Scope of Works and Supply by the Employer	440

Appendix 7.  List of Documents for Approval or Review	441

Appendix 8.  Functional Guarantees	442

Performance Security Form– Bank Guarantee	444

Advance Payment Security	446

Notification of Intention to Award

[This Notification of Intention to Award shall be sent to each Bidder that submitted a Bid.]

[Send this Notification to the Bidder’s Authorized Representative named in the Bidder Information Form]

For the attention of Bidder’s Authorized Representative

Name: [insert Authorized Representative’s name]

Address: [insert Authorized Representative’s Address]

Telephone/Fax numbers: [insert Authorized Representative’s telephone/fax numbers]

Email Address: [insert Authorized Representative’s email address]

[IMPORTANT: insert the date that this Notification is transmitted to Bidders. The Notification must be sent to all Bidders simultaneously. This means on the same date and as close to the same time as possible.]

DATE OF TRANSMISSION: This Notification is sent by: [email/fax] on [date] (local time)

Notification of Intention to Award

Employer: [insert the name of the Employer]

Project: [insert name of project]

Contract title: [insert the name of the contract]

Country: [insert country where RFB is issued]

Loan No. /Credit No. / Grant No.: [insert reference number for loan/credit/grant]

RFB No: [insert RFB reference number from Procurement Plan]

This Notification of Intention to Award (Notification) notifies you of our decision to award the above contract. The transmission of this Notification begins the Standstill Period. During the Standstill Period, you may:

- request a debriefing in relation to the evaluation of your Bid, and/or

- submit a Procurement-related Complaint in relation to the decision to award the contract.

- The successful Bidder

| Name: | [insert name of successful Bidder] |
| --- | --- |
| Address: | [insert address of the successful Bidder] |
| Contract price: | [insert contract price of the successful Bid] |

- Other Bidders [INSTRUCTIONS: insert names of all Bidders that submitted a Bid. If the Bid’s price was evaluated include the evaluated price as well as the Bid price as read out.]

| Name of Bidder | Bid price | Evaluated Bid Cost |
| --- | --- | --- |
| [insert name] | [insert Bid price] | [insert evaluated cost] |
| [insert name] | [insert Bid price] | [insert evaluated cost] |
| [insert name] | [insert Bid price] | [insert evaluated cost] |
| [insert name] | [insert Bid price] | [insert evaluated cost] |
| [insert name] | [insert Bid price] | [insert evaluated cost] |

- Reason/s why your Bid was unsuccessful

[INSTRUCTIONS: State the reason/s why this Bidder’s Bid was unsuccessful. Do NOT include: (a) a point by point comparison with another Bidder’s Bid or (b) information that is marked confidential by the Bidder in its Bid.]

- How to request a debriefing

DEADLINE: The deadline to request a debriefing expires at midnight on [insert date] (local time). You may request a debriefing in relation to the results of the evaluation of your Bid. If you decide to request a debriefing, your written request must be made within three (3) Business Days of receipt of this Notification of Intention to Award. Provide the contract name, reference number, name of the Bidder, contact details; and address the request for debriefing as follows: Attention: [insert full name of person, if applicable] Title/position: [insert title/position] Agency: [insert name of Employer] Email address: [insert email address] Fax number: [insert fax number] delete if not used If your request for a debriefing is received within the 3 Business Days deadline, we will provide the debriefing within five (5) Business Days of receipt of your request. If we are unable to provide the debriefing within this period, the Standstill Period shall be extended by five (5) Business Days after the date that the debriefing is provided. If this happens, we will notify you and confirm the date that the extended Standstill Period will end. The debriefing may be in writing, by phone, video conference call or in person. We shall promptly advise you in writing how the debriefing will take place and confirm the date and time. If the deadline to request a debriefing has expired, you may still request a debriefing. In this case, we will provide the debriefing as soon as practicable, and normally no later than fifteen (15) Business Days from the date of publication of the Contract Award Notice.

- How to make a complaint

Period: Procurement-related Complaint challenging the decision to award shall be submitted by midnight, [insert date] (local time). Provide the contract name, reference number, name of the Bidder, contact details; and address the Procurement-related Complaint as follows: Attention: [insert full name of person, if applicable] Title/position: [insert title/position] Agency: [insert name of Employer] Email address: [insert email address] Fax number: [insert fax number] delete if not used At this point in the procurement process, you may submit a Procurement-related Complaint challenging the decision to award the contract. You do not need to have requested, or received, a debriefing before making this complaint. Your complaint must be submitted within the Standstill Period and received by us before the Standstill Period ends. Further information: For more information see the Procurement Regulations for IPF Borrowers (Procurement Regulations)[https://policies.worldbank.org/sites/ppf3/PPFDocuments/Forms/DispPage.aspx?docid=4005] (Annex III). You should read these provisions before preparing and submitting your complaint. In addition, the World Bank’s Guidance “How to make a Procurement-related Complaint” [http://www.worldbank.org/en/projects-operations/products-and-services/brief/procurement-new-framework#framework] provides a useful explanation of the process, as well as a sample letter of complaint. In summary, there are four essential requirements: - You must be an ‘interested party’. In this case, that means a Bidder who submitted a Bid in this bidding process, and is the recipient of a Notification of Intention to Award. - The complaint can only challenge the decision to award the contract. - You must submit the complaint within the period stated above. - You must include, in your complaint, all of the information required by the Procurement Regulations (as described in Annex III).

- Standstill Period

DEADLINE: The Standstill Period is due to end at midnight on [insert date] (local time). The Standstill Period lasts ten (10) Business Days after the date of transmission of this Notification of Intention to Award. The Standstill Period may be extended as stated in Section 4 above.

If you have any questions regarding this Notification please do not hesitate to contact us.

On behalf of the Employer:

Signature: 	______________________________________________

Name:	______________________________________________

Title/position:	______________________________________________

Telephone:	______________________________________________

Email:	______________________________________________

Beneficial Ownership Disclosure Form

INSTRUCTIONS TO BIDDERS: DELETE THIS BOX ONCE YOU HAVE COMPLETED THE FORM

This Beneficial Ownership Disclosure Form (“Form”) is to be completed by the successful Bidder.  In case of joint venture, the Bidder must submit a separate Form for each member.  The beneficial ownership information to be submitted in this Form shall be current as of the date of its submission.

For the purposes of this Form, a Beneficial Owner of a Bidder is any natural person who ultimately owns or controls the Bidder by meeting one or more of the following conditions:

- directly or indirectly holding 25% or more of the shares

- directly or indirectly holding 25% or more of the voting rights

- directly or indirectly having the right to appoint a majority of the board of directors or equivalent governing body of the Bidder

RFB No.: [insert number of RFB process]

Request for Bid No.: [insert identification]

To: [insert complete name of Employer]

In response to your request in the Letter of Acceptance dated [insert date of letter of Acceptance] to furnish additional information on beneficial ownership: [select one option as applicable and delete the options that are not applicable]

(i) we hereby provide the following beneficial ownership information.

Details of beneficial ownership

| Identity of Beneficial Owner | Directly or indirectly holding 25% or more of the shares (Yes / No) | Directly or indirectly holding 25 % or more of the Voting Rights (Yes / No) | Directly or indirectly having the right to appoint a majority of the board of the directors or an equivalent governing body of the Bidder (Yes / No) |
| --- | --- | --- | --- |
| [include full name (last, middle, first), nationality, country of residence] |  |  |  |

OR

(ii) We declare that there is no Beneficial Owner meeting one or more of the following conditions:

- directly or indirectly holding 25% or more of the shares

- directly or indirectly holding 25% or more of the voting rights

- directly or indirectly having the right to appoint a majority of the board of directors or equivalent governing body of the Bidder

OR

(iii) We declare that we are unable to identify any Beneficial Owner meeting one or more of the following conditions. [If this option is selected, the Bidder shall provide explanation on why it is unable to identify any Beneficial Owner]

- directly or indirectly holding 25% or more of the shares

- directly or indirectly holding 25% or more of the voting rights

- directly or indirectly having the right to appoint a majority of the board of directors or equivalent governing body of the Bidder]”

Name of the Bidder: *[insert complete name of the Bidder]_________

Name of the person duly authorized to sign the Bid on behalf of the Bidder: **[insert complete name of person duly authorized to sign the Bid]___________

Title of the person signing the Bid: [insert complete title of the person signing the Bid]______

Signature of the person named above: [insert signature of person whose name and capacity are shown above]_____

Date signed [insert date of signing] day of [insert month], [insert year]_____

* In the case of the Bid submitted by a Joint Venture specify the name of the Joint Venture as Bidder. In the event that the Bidder is a joint venture, each reference to “Bidder” in the Beneficial Ownership Disclosure Form (including this Introduction thereto) shall be read to refer to the joint venture member.

** Person signing the Bid shall have the power of attorney given by the Bidder. The power of attorney shall be attached with the Bid Schedules.

Letter of Acceptance

______________________

To:  ____________________________

This is to notify you that your Bid dated ____________ for execution of the _________________ for the Contract Price in the aggregate of _____________________ ________________, as corrected and modified in accordance with the Instructions to Bidders is hereby accepted by our Agency.

You are requested to furnish (i) the Performance Security within 28 days in accordance with the Conditions of Contract, using for that purpose one of the Performance Security Forms and (ii) the additional information on beneficial ownership in accordance with BDS ITB 46.1, within eight (8) Business days using the Beneficial Ownership Disclosure Form, included in Section X, - Contract Forms, of the bidding document.

Authorized Signature:

Name and Title of Signatory:

Name of Agency:

Attachment:  Contract Agreement

Contract Agreement

THIS AGREEMENT is made the ________ day of ________________________, _____,

BETWEEN

(1) ______________________, a corporation incorporated under the laws of ___________ and having its principal place of business at ___________________ (hereinafter called “the Employer”), and (2) ______________________, a corporation incorporated under the laws of ________________________ and having its principal place of business at ________________________ (hereinafter called “the Contractor”).

WHEREAS the Employer desires to engage the Contractor to design, manufacture, test, deliver, install, complete and commission certain Facilities, viz. _________________ (“the Facilities”), and the Contractor has agreed to such engagement upon and subject to the terms and conditions hereinafter appearing.

NOW IT IS HEREBY AGREED as follows:

| Article 1. Contract Documents | 1.1 Contract Documents (Reference GCC Clause 2) The following documents shall constitute the Contract between the Employer and the Contractor, and each shall be read and construed as an integral part of the Contract: (a) This Contract Agreement and the Appendices hereto (b) Letter of Bid and Price Schedules submitted by the Contractor (c) Particular Conditions (d) General Conditions (e) Specification (f) Drawings (g) Other completed Bidding forms submitted with the Bid (h) Any other documents forming part of the Employer’s Requirements (i) Any other documents forming part of the contract, including, but not limited to: - the ES Management Strategies and Implementation Plans; and ii. Code of Conduct for Contractor’s Personnel (ES). [Any other documents shall be added here.] 1.2 Order of Precedence (Reference GCC Clause 2) In the event of any ambiguity or conflict between the Contract Documents listed above, the order of precedence shall be the order in which the Contract Documents are listed in Article 1.1 (Contract Documents) above. 1.3 Definitions (Reference GCC Clause 1) Capitalized words and phrases used herein shall have the same meanings as are ascribed to them in the General Conditions. |
| --- | --- |
| Article 2. Contract Price and Terms of Payment | 2.1 Contract Price (Reference GCC Clause 11) The Employer hereby agrees to pay to the Contractor the Contract Price in consideration of the performance by the Contractor of its obligations hereunder. The Contract Price shall be the aggregate of: __________________, _______________ as specified in Price Schedule No. 5 (Grand Summary), and_______________, _________________, or such other sums as may be determined in accordance with the terms and conditions of the Contract. 2.2 Terms of Payment (Reference GCC Clause 12) The terms and procedures of payment according to which the Employer will reimburse the Contractor are given in the Appendix (Terms and Procedures of Payment) hereto. The Employer may instruct its bank to issue an irrevocable confirmed documentary credit made available to the Contractor in a bank in the country of the Contractor. The credit shall be for an amount of ________________________; and shall be subject to the Uniform Customs and Practice for Documentary Credits 2007 Revision, ICC Publication No. 600. In the event that the amount payable under Schedule No. 1 is adjusted in accordance with GCC 11.2 or with any of the other terms of the Contract, the Employer shall arrange for the documentary credit to be amended accordingly. |
| Article 3. Effective Date | 3.1 Effective Date (Reference GCC Clause 1) The Effective Date from which the Time for Completion of the Facilities shall be counted is the date when all of the following conditions have been fulfilled: (a) This Contract Agreement has been duly executed for and on behalf of the Employer and the Contractor; (b) The Contractor has submitted to the Employer the Performance Security and the advance payment guarantee; (c) The Employer has paid the Contractor the advance payment; (d) The Contractor has been advised that the documentary credit referred to in Article 2.2 above has been issued in its favor; (e ) constitution of the DB. Each party shall use its best efforts to fulfill the above conditions for which it is responsible as soon as practicable. 3.2 If the conditions listed under 3.1 are not fulfilled within two (2) months from the date of this Contract notification because of reasons not attributable to the Contractor, the Parties shall discuss and agree on an equitable adjustment to the Contract Price and the Time for Completion and/or other relevant conditions of the Contract. |
| Article 4. Communications | 4.1 The address of the Employer for notice purposes, pursuant to GCC 4.1 is: ______________________. - The address of the Contractor for notice purposes, pursuant to GCC 4.1 is: ________________________. |
| Article 5. Appendices | 5.1 The Appendices listed in the attached List of Appendices shall be deemed to form an integral part of this Contract Agreement. - Reference in the Contract to any Appendix shall mean the Appendices attached hereto, and the Contract shall be read and construed accordingly. |

IN WITNESS WHEREOF the Employer and the Contractor have caused this Agreement to be duly executed by their duly authorized representatives the day and year first above written.

Signed by, for and on behalf of the Employer

[Signature]

[Title]

in the presence of

Signed by, for and on behalf of the Contractor

[Signature]

[Title]

in the presence of

APPENDICES

Appendix 1	Terms and Procedures of Payment

Appendix 2	Price Adjustment

Appendix 3	Insurance Requirements

Appendix 4	Time Schedule

Appendix 5	List of Major Items of Plant and Installation Services and List of Approved Subcontractors

Appendix 6	Scope of Works and Supply by the Employer

Appendix 7	List of Documents for Approval or Review

Appendix 8	Functional Guarantees

Appendix 1.  Terms and Procedures of Payment

In accordance with the provisions of GCC Clause 12 (Terms of Payment), the Employer shall pay the Contractor in the following manner and at the following times, on the basis of the Price Breakdown given in the section on Price Schedules.  Payments will be made in the currencies quoted by the Bidder unless otherwise agreed between the Parties.  Applications for payment in respect of part deliveries may be made by the Contractor as work proceeds.

Schedule No. 1.  Plant and Equipment Supplied from Abroad

In respect of plant and equipment supplied from abroad, the following payments shall be made:

Ten percent (10%) of the total CIP amount as an advance payment against receipt of invoice and an irrevocable advance payment security for the equivalent amount made out in favor of the Employer.  The advance payment security may be reduced in proportion to the value of the plant and equipment delivered to the site, as evidenced by shipping and delivery documents.

Fifty percent (50%) of the total or pro rata CIP amount upon Incoterm “CIP”, upon delivery to the carrier within forty-five (45) days after receipt of documents.

The documents to be submitted:

1. Invoice

2. Packing list

3. Bill of Lading

4. Insurance certificate to the named place of destination

5. Customs declaration issued by the customs authorities of the Employer's country

6. Certificate of origin

7. Test report

Thirty percent (30%) of the total or pro rata CIP amount upon issue of the Completion Certificate, within forty-five (45) days after receipt of invoice.

Ten percent (10%) of the total or pro rata CIP amount upon issue of the Operational Acceptance Certificate, within forty-five (45) days after receipt of invoice.

Schedule No. 2.  Design Services

In respect of design services for both the foreign currency and the local currency portions, the following payments shall be made:

Ten percent (10%) of the total design services amount as an advance payment against receipt of invoice, and an irrevocable advance payment security for the equivalent amount made out in favor of the Employer.

Ninety percent (90%) of the total or pro rata design services amount upon acceptance of design in accordance with GCC Clause 20 by the Project Manager within forty-five (45) days after receipt of invoice.

Schedule No. 3.  Installation Services

In respect of installation services for both the foreign and local currency portions, the following payments shall be made:

Ten percent (10%) of the total installation services amount as an advance payment against receipt of invoice, and an irrevocable advance payment security for the equivalent amount made out in favor of the Employer.  The advance payment security may be reduced in proportion to the value of work performed by the Contractor as evidenced by the invoices for installation services.

Seventy percent (70%) of the measured value of work performed by the Contractor, as identified in the said Program of Performance, during the preceding month, as evidenced by the Employer’s authorization of the Contractor’s application, will be made monthly within forty-five (45) days after receipt of invoice.

Five percent (5%) of the total or pro rata value of installation services performed by the Contractor as evidenced by the Employer’s authorization of the Contractor’s monthly applications, upon issue of the Completion Certificate, within forty-five (45) days after receipt of invoice.

Five percent (5%) of the total or pro rata value of installation services performed by the Contractor as evidenced by the Employer’s authorization of the Contractor’s monthly applications, upon issue of the Operational Acceptance Certificate, within forty-five (45) days after receipt of invoice.

Five percent (5%) of the total installation services performed by the Contractor as evidenced by the Employer’s authorization of the Contractor’s monthly applications, upon issue of the Operational Acceptance Certificate and for the following 12 months of operations and maintenance services performed by the contractor, within forty-five (45) days after receipt of invoice.

Five percent (5%) of the total Accepted Contract Amount upon completion of the retention period and within forty-five (45) days after receipt of invoice.

In the event that the Employer fails to make any payment on its respective due date, the Employer shall pay to the Contractor interest on the amount of such delayed payment at the annual rate of two percent (2%) above SOFR per month for period of delay until payment has been made in full.

PAYMENT PROCEDURES

The procedures to be followed in applying for certification and making payments shall be as follows:

As described in Schedule 1. 2. & 3 above.

Appendix 2.  Price Adjustment

Not Applicable

Appendix 3.  Insurance Requirements

Insurances to be Taken Out by the Contractor

In accordance with the provisions of GCC Clause 34, the Contractor shall at its expense take out and maintain in effect, or cause to be taken out and maintained in effect, during the performance of the Contract, the insurances set forth below in the sums and with the deductibles and other conditions specified.  The identity of the insurers and the form of the policies shall be subject to the approval of the Employer, such approval not to be unreasonably withheld.

(a)	Cargo Insurance

Covering loss or damage occurring, while in transit from the supplier’s or manufacturer’s works or stores until arrival at the Site, to the Facilities (including spare parts therefor) and to the construction equipment to be provided by the Contractor or its Subcontractors.

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| 110% of the contract price | 5% of the total contract value | Contractor / Subcontractor and Employer | Contractor's / Subcontractor's, Supplier's or Manufacturer's works or stores | Site |

(b)	Installation All Risks Insurance

Covering physical loss or damage to the Facilities at the Site, occurring prior to completion of the Facilities, with an extended maintenance coverage for the Contractor’s liability in respect of any loss or damage occurring during the defect liability period while the Contractor is on the Site for the purpose of performing its obligations during the defect liability period.

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| Total contract value | 5% of the total contract value | Contractor, Subcontractor and Employer | 28 days from effective date On the site and in temporary storage anywhere in Maldives | Provisional Acceptance Certificate |

(c)	Third Party Liability Insurance

Covering bodily injury or death suffered by third parties (including the Employer’s personnel) and loss of or damage to property (including the Employer’s property and any parts of the Facilities that have been accepted by the Employer) occurring in connection with the supply and installation of the Facilities.

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| USD 2 Million value | Maximum USD 5,000 for property damage only | Contractor, Subcontractor and Employer | Duration of contract On the site and in temporary storage anywhere in Maldives | Provisional Acceptance Certificate |

(d)	Automobile Liability Insurance

Covering use of all vehicles used by the Contractor or its Subcontractors (whether or not owned by them) in connection with the supply and installation of the Facilities.  Comprehensive insurance in accordance with statutory requirements.

(e)	Workers’ Compensation

In accordance with the statutory requirements applicable in any country where the Facilities or any part thereof is executed.

(f)	Employer’s Liability

In accordance with the statutory requirements applicable in any country where the Facilities or any part thereof is executed.

(g)	Other Insurances

The Contractor is also required to take out and maintain at its own cost the following insurances:

Details:

Amount	Deductible limits	Parties insured	From	To

The Employer shall be named as co-insured under all insurance policies taken out by the Contractor pursuant to GCC Sub-Clause 34.1, except for the Third Party Liability, Workers’ Compensation and Employer’s Liability Insurances, and the Contractor’s Subcontractors shall be named as co-insureds under all insurance policies taken out by the Contractor pursuant to GCC Sub-Clause 34.1, except for the Cargo, Workers’ Compensation and Employer’s Liability Insurances.  All insurer’s rights of subrogation against such co-insureds for losses or claims arising out of the performance of the Contract shall be waived under such policies.

Insurances To Be Taken Out By The Employer

Not Applicable

Appendix 4.  Time Schedule

Appendix 5.  List of Major Items of Plant and Installation Services and List of Approved Subcontractors

Not Applicable

Appendix 6.  Scope of Works and Supply by the Employer

Refer Section VII. Employer’s Requirement

Appendix 7.  List of Documents for Approval or Review

Refer Section VII. Employer’s Requirement

Appendix 8.  Functional Guarantees

1.	General

This Appendix sets out

(a)	the functional guarantees referred to in GCC Clause 28 (Functional Guarantees)

(b)	the preconditions to the validity of the functional guarantees, either in production and/or consumption, set forth below

(c)	the minimum level of the functional guarantees

(d)	the formula for calculation of liquidated damages for failure to attain the functional guarantees.

2.	Preconditions

The Contractor gives the functional guarantees (specified herein) for the facilities, subject to the following preconditions being fully satisfied:

____________________________________________________________________________________

3.	Functional Guarantees

Subject to compliance with the foregoing preconditions, the Contractor guarantees as follows:

3.1	Production Capacity

_____________________________________________________________________________

and/or

3.2	Raw Materials and Utilities Consumption

____________________________________________________________________________

4.	Failure in Guarantees and Liquidated Damages

4.1	Failure to Attain Guaranteed Production Capacity

If the production capacity of the facilities attained in the guarantee test, pursuant to GCC Sub-Clause 25.2, is less than the guaranteed figure specified in para. 3.1 above, but the actual production capacity attained in the guarantee test is not less than the minimum level specified in para. 4.3 below, and the Contractor elects to pay liquidated damages to the Employer in lieu of making changes, modifications and/or additions to the Facilities, pursuant to GCC Sub-Clause 28.3, then the Contractor shall pay liquidated damages at the rate of ___________________ for every complete one percent (1%) of the deficiency in the production capacity of the Facilities, or at a proportionately reduced rate for any deficiency, or part thereof, of less than a complete one percent (1%).

4.2	Raw Materials and Utilities Consumption in Excess of Guaranteed Level

__________________________________________________________________

If the actual measured figure of specified raw materials and utilities consumed per unit (or their average total cost of consumption) exceeds the guaranteed figure specified in para. 3.2 above (or their specified average total cost of consumption), but the actual consumption attained in the guarantee test, pursuant to GCC Sub-Clause 25.2, is not more than the maximum level specified in para. 4.3 below, and the Contractor elects to pay liquidated damages to the Employer in lieu of making changes, modifications and/or additions to the Facilities pursuant to GCC Sub-Clause 28.3, then the Contractor shall pay liquidated damages at the rate of [amount in the contract currency] for every complete one percent (1%) of the excess consumption of the Facilities, or part thereof, of less than a complete one percent (1%).

4.3	Minimum Levels

Notwithstanding the provisions of this paragraph, if as a result of the guarantee test(s), the following minimum levels of performance guarantees (and consumption guarantees) are not attained by the Contractor, the Contractor shall at its own cost make good any deficiencies until the Facilities reach any of such minimum performance levels, pursuant to GCC Sub-Clause 28.2:

(a)	production capacity of the Facilities attained in the guarantee test:  ninety-five percent (95%) of the guaranteed production capacity (the values offered by the Contractor in its Bid for functional guarantees represents 100%).

and/or

(b)	average total cost of consumption of all the raw materials and utilities of the Facilities:  one hundred and five percent (105%) of the guaranteed figures (the figures offered by the Contractor in its Bid for functional guarantees represents 100%).

4.4	Limitation of Liability

Subject to para. 4.3 above, the Contractor’s aggregate liability to pay liquidated damages for failure to attain the functional guarantees shall not exceed ______ percent ( ___ %) of the Contract price.

Performance Security Form– Bank Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	[insert name and Address of Employer]

Date:	_ [Insert date of issue]

PERFORMANCE GUARANTEE No.: ____[Insert guarantee reference number]

Guarantor:  [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ____________________ (hereinafter called “the Applicant”) has entered into Contract No. ________________dated ____________ with the Beneficiary, for the execution of ____________________________ (hereinafter called “the Contract”).

Furthermore, we understand that, according to the conditions of the Contract, a performance guarantee is required.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of _________________(___),such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating that the Applicant is in breach of its obligation(s) under the Contract, without the Beneficiary needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall be reduced by half upon our receipt of:

(a) 	a copy of the Operational Acceptance Certificate; or

(b) 	a registered letter from the Applicant (i) attaching a copy of its notice requesting issuance of the Operational Acceptance Certificate and (ii) stating that the Project Manager has failed to issue such Certificate within the time required or provide in writing justifiable reasons why such Certificate has not been issued, so that Operational Acceptance is deemed to have occurred.

This guarantee shall expire no later than the earlier of:

(a) 	twelve months after our receipt of either (a) or (b) above; or

(b) 	eighteen months after our receipt of:

(i) 	a copy of the Completion Certificate; or

(ii) 	a registered letter from the Applicant, attaching a copy of the notice to the Project Manager that the Facilities are ready for commissioning, and stating that fourteen days have elapsed from receipt of such notice (or seven days have elapsed if the notice was a repeated notice) and the Project Manager has failed to issue a Completion Certificate or inform the Applicant in writing of any defects or deficiencies; or

(iii) 	a registered letter from the Applicant stating that no Completion Certificate has been issued but the Employer is making use of the Facilities; or

(c) 	the ____ day of _____, 2___.

Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

_____________________ 
[signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

Advance Payment Security

Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary: 	Name and Address of Employer

Date:[Insert date of issue]

Advance Payment Guarantee No.:[Insert guarantee reference number]

Guarantor:  [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that . . . . .. . . . .  (hereinafter called “the Applicant”) has entered into Contract No. . . . . .. . . . . dated . . . . . . ..with the Beneficiary, for the execution of, . . . . . .. . . . .  (hereinafter called “the Contract”).

Furthermore, we understand that, according to the Conditions of the Contract, an advance payment in the sum  . . . . .. . . . . . (. . . . .. . . . .  ) is to be made against an advance payment guarantee.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of . 
(. . . . .. . . . .  )  upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating either that the applicant:

    - has used the advance payment for purposes other than the costs of mobilization in respect of the Facilities; or

    - has failed to repay the advance payment in accordance with the Contract conditions, specifying the amount which the Applicant has failed to repay.

A demand under this guarantee may be presented as from the presentation to the Guarantor of a certificate from the Beneficiary’s bank stating that the advance payment referred to above has been credited to the Applicant on its account number ___________ at _________________..

The maximum amount of this guarantee shall be progressively reduced by the amount of the advance payment repaid by the Applicant as indicated in copies of interim statements or payment certificates which shall be presented to us.  This guarantee shall expire, at the latest, upon our receipt of documentation indicating full repayment by the Applicant of the amount of the advance payment, or on the . . . day of . . . . . . . , . . . . ., whichever is earlier.  Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

____________________ [signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

Nonperformance, as decided by the Employer, shall include all contracts where (a) nonperformance was not challenged by the contractor, including through referral to the dispute resolution mechanism under the respective contract, and (b) contracts that were so challenged but fully settled against the contractor. Nonperformance shall not include contracts where Employers decision was overruled by the dispute resolution mechanism. Nonperformance must be based on all information on fully settled disputes or litigation, i.e. dispute or litigation that has been resolved in accordance with the dispute resolution mechanism under the respective contract and where all appeal instances available to the Bidder have been exhausted.

This requirement also applies to contracts executed by the Bidder as JV member.

The Bidder shall provide accurate information on the related Letter of Bid about any litigation or arbitration resulting from contracts completed or ongoing under its execution over the last five years. A consistent history of awards against the Bidder or any member of a joint venture may result in failure of the Bid.

The Employer may use this information to seek further information or clarifications in carrying out its due diligence.

Line of Credit (LOC) shall be specific to the Bid/Lot or if a general LOC is presented it shall include up to date details such as remaining balance one month prior to date of bid submission.

For contracts under which the Bidder participated as a joint venture member or sub-contractor, only the Bidder’s share, by value, shall be considered to meet this requirement

Substantial completion shall be based on 80% or more Plant and installation completed under the contract.

In the case of JV, the value of contracts completed by its members shall not be aggregated to determine whether the requirement of the minimum value of a single contract has been met. Instead, each contract performed by each member shall satisfy the minimum value of a single contract as required for single entity. In determining whether the JV meets the requirement of total number of contracts, only the number of contracts completed by all members each of value equal or more than the minimum value required shall be aggregated.

In the case of JV, the value of contracts completed by its members shall not be aggregated to determine whether the requirement of the minimum value of a single contract has been met. Instead, each contract performed by each member shall satisfy the minimum value of a single contract as required for single entity. In determining whether the JV meets the requirement of total number of contracts, only the number of contracts completed by all members each of value equal or more than the minimum value required shall be aggregated.

For contracts under which the Applicant participated as a joint venture member or sub-contractor, only the Applicant’s share, by value, and role and responsibilities shall be considered to meet this requirement.

In the case of JV, the value of contracts completed by its members shall not be aggregated to determine whether the requirement of the minimum value of a single contract has been met. Instead, each contract performed by each member shall satisfy the minimum value of a single contract as required for single entity. In determining whether the JV meets the requirement of total number of contracts, only the number of contracts completed by all members each of value equal or more than the minimum value required shall be aggregated.

Substantial completion shall be based on 80% or more Plant and installation completed under the contract.

Bidder shall submit a supporting document stating the scope of ESIA/ESMP/ESCP specific works undertaken.

For the avoidance of doubt, a sanctioned party’s ineligibility to be awarded a contract shall include, without limitation, (i) applying for pre-qualification, expressing interest in a consultancy, and bidding, either directly or as a nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider, in respect of such contract, and (ii) entering into an addendum or amendment introducing a material modification to any existing contract.

A nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider (different names are used depending on the particular bidding document) is one which has been: (i) included by the bidder in its pre-qualification application or bid because it brings specific and critical experience and know-how that allow the bidder to meet the qualification requirements for the particular bid; or (ii) appointed by the Borrower.

Inspections in this context usually are investigative (i.e., forensic) in nature.  They involve fact-finding activities undertaken by the Bank or persons appointed by the Bank to address specific matters related to investigations/audits, such as evaluating the veracity of an allegation of possible Fraud and Corruption, through the appropriate mechanisms.  Such activity includes but is not limited to: accessing and examining a firm's or individual's financial records and information, and making copies thereof as relevant; accessing and examining any other documents, data and information (whether in hard copy or electronic format) deemed relevant for the investigation/audit, and making copies thereof as relevant; interviewing staff and other relevant individuals; performing physical inspections and site visits; and obtaining third party verification of information.

The bus bar and isolators must withstand the system power flow since they may be installed in series with the existing lines

Witness may include in-person, or remote via video conference. Contractor must be able to provide for either option. Employer witness may include Employer nominated representative.

For example, SOC limits may be applied for storage of excess solar PV that are less than the actual SOC limits, ensuring residual capacity for full grid support functionality.

Standard operating power factor is 0.9 – 0.95 (except during start-up)

For example, if there is a single transformer, the capacity may reduce by 100% on transformer failure; if there are two inverters, capacity may reduce by 50% on inverter failure; if there are 30 battery modules, performance may reduce by 20% on failure of one battery module.

Excludes HVAC

Where applicable, separate states for each separate solar PV system should be considered.

These may constitute separate system states if inverters are powered on at night for reactive power support.

IEE Std. 2030.2.1, Section 7.1.4 Inspection of BESS Protections p.34

IEC60300.3.14.2005 R2016 - Figure 3, p.11

IEE Std. 2030.2.1, Section 7.1.1 Inspection for daily operation conditions, p.33.

IEE Std. 2030.2.1, Section 7.1.2 Collection, analysis and inspection of BESS data p.33

IEE Std. 2030.2.1, Section 7.1.3 Inspection for BESS control and regulation functions, p.33

IEE Std. 2030.2.1, Section 7.1.3 Inspection for BESS control and regulation functions, p.33

IEE Std. 2030.2.1, Section 7.3.1 Routine maintenance, p.35

IEE Std. 2030.2.1, Section 7.2.1 Scheduled inspection and maintenance of PCS, p.34

IEE Std. 2030.2.1, Section 7.2.1 Scheduled inspection and maintenance of PCS p.34.

IEC60300.3.14.2005 R2016 - Training plan, p.20

Costs shall be in the currencies of the Contract.

Costs shall be in the currencies of the Contract.

2 Specify where necessary.

For the avoidance of doubt, a sanctioned party’s ineligibility to be awarded a contract shall include, without limitation, (i) applying for pre-qualification, expressing interest in a consultancy, and bidding, either directly or as a nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider, in respect of such contract, and (ii) entering into an addendum or amendment introducing a material modification to any existing contract.

A nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider (different names are used depending on the particular bidding document) is one which has been: (i) included by the bidder in its pre-qualification application or bid because it brings specific and critical experience and know-how that allow the bidder to meet the qualification requirements for the particular bid; or (ii) appointed by the Borrower.

Inspections in this context usually are investigative (i.e., forensic) in nature.  They involve fact-finding activities undertaken by the Bank or persons appointed by the Bank to address specific matters related to investigations/audits, such as evaluating the veracity of an allegation of possible Fraud and Corruption, through the appropriate mechanisms.  Such activity includes but is not limited to: accessing and examining a firm's or individual's financial records and information, and making copies thereof as relevant; accessing and examining any other documents, data and information (whether in hard copy or electronic format) deemed relevant for the investigation/audit, and making copies thereof as relevant; interviewing staff and other relevant individuals; performing physical inspections and site visits; and obtaining third party verification of information.

The Guarantor shall insert an amount representing the percentage of the Contract Price specified in the Contract and denominated either in the currency(ies) of the Contract or a freely convertible currency acceptable to the Employer.

This text shall be revised as and where necessary to take into account (i) partial acceptance of the Facilities in accordance with Sub-Clause 25.4 of the GCC; and (ii) extension of the Performance Security when the Contractor is liable for an extended warranty obligation pursuant to Sub-Clause 27.10 of the GCC (although in this latter case the Employer might want to consider an extended warranty security in lieu of the extension of the Performance Security).

Insert the date twenty-eight days after the expected expiration date of the Defect Liability Period. The Employer should note that in the event of an extension of the time for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor. Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph: “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months][one year], in response to the Employer’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”

The Guarantor shall insert an amount representing the amount of the advance payment and denominated either in the currency(ies) of the advance payment as specified in the Contract, or in a freely convertible currency acceptable to the Employer.

Insert the expected expiration date of the Time for Completion.  The Employer should note that in the event of an extension of the time for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor.  Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph:  “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months][one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”