## Cover Page
BILL OF QUANTITIES
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
CLIENT : MINISTRY OF NATIONAL PLANNING, HOUSING & INFRASTRUCTURE

## Grand Summary
SUMMARY OF BILLS OF QUANTITIES
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
| DESCRIPTION | AMOUNT (MRF) | %
| Bill №: 01 - GENERAL WORKS | 0
| Bill №: 02 - GRAVITY SEWARAGE SYSTEM | 0
| Bill №: 03 - WATER SUPPLY SYSTEM | 0
| Bill №: 04 - ADMIN BUILDING | #REF!
| GST 6% | #REF!
| TOTAL AMOUNT | #REF!

## 01 General BoQ Summary
SUMMARY OF BILLS OF QUANTITIES
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
01 GENERAL WORKS
| DESCRIPTION | AMOUNT (MRF) | %
| BILL NO. 01 - GENERAL AND PRELIMINARIES | 0
| BILL NO. 02 - SITE PREPARATION | 0
| BILL NO. 03 - DECOMISSIONING | 0
| BILL NO. 04 - TRAIL OPERATION AND TRAINNING | 0
| BILL NO. 05 - ADDITIONS AND OMMISSIONS | 0
| TOTAL AMOUNT | 0

## 01 General BOQ
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
01 GENERAL WORKS
Male', Republic of Maldives
BILL OF QUANTITIES
ITEM | DESCRIPTION | QTY | UNIT | MATERIAL RATE | LABOUR RATE | AMOUNT
BILL NO. 01 - GENERAL AND PRELIMINARIES
1.1.00 | Project Management cost
1.1.01 | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings & similar. | 1 | Item |  |  | 0
1.1.02 | Provision of Contractor's Office | 18 | months |  |  | 0
1.1.03 | Provision of Contractor's Staff Accommodation | 18 | months |  |  | 0
1.1.04 | Maintaining Contractor's Office | 18 | months |  |  | 0
1.1.05 | Maintaining Contractor's Staff Accommodation | 18 | months |  |  | 0
1.2.00 | Contractual Requirements
1.2.01 | Provide & Maintain all necessary Insurances, Guarantees and Securities. | 1 | Item |  |  | 0
1.3.00 | Specified Requirements
1.3.01 | Provision and Erection of Notice Boards 3m x 4m size as per drawing and specification, including complete cost and conveyanceof materials, labour charges, & etc. | 1 | Item |  |  | 0
1.3.02 | Provision of photographs of important activities of the work during the progress of work as directed by the Engineer. | 1 | Item |  |  | 0
1.3.03 | Provision of videograph of the progress of works, one video tape not more than 30 minutes duration showing the progress during evey month. | 1 | Item |  |  | 0
1.3.04 | Submission of detailed shop drawings and submittals for approval by the Engineer prior to commencement of work | 1 | Item |  |  | 0
1.3.05 | Provision and maintaining of adequately equipped Laboratory services as required for site control on the quality of materials and the works as required by the engineer; | 1 | Item |  |  | 0
1.4.00 | Temporary Works
1.4.01 | Mobilize to site and maintain water bowsers to meet the drinking water needs of the households affected by dewatering of trenches. | 1 | Item |  |  | 0
1.4.02 | Provision of temporary sewerage connections by septic tanks or diversion of existing lines for household that are affected by the construction activities such as pipelaying | 1 | Item |  |  | 0
1.5.00 | Dewatering
1.5.01 | Dewatering as required as per EPA regulation 2013/R-1697 | 1 | Item |  |  | 0
1.5.02 | Arrange during dewatering of trenches, for pumping ground water of salinity greater than 2500 microsiemens to be pumped out to sea. | 1 | Item |  |  | 0
1.6.00 | Environmental Monitoring and Reporting | 1 | Item
Undertake Environmental Monitoring & Reporing as per the requirements set in the Specifications.
1.7.00 | TOTAL OF BILL №: 01 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 02 - SITE PREPARATION
2.1.00 | In survey
2.1.01 | Detailed house connection survey of each plot and prepare site layout and identify household catchpit and water supply connection meter location and obtain Homeowner & Contractor agreement for each house | 1 | Item |  |  | 0
2.1.02 | Detailed setting out survey for each facility location and preperation of shopdrawings based on detail drawings and specifications | 1 | Item |  |  | 0
2.1.02 | Detailed level survey of each Manhole/cleanout location and submission of surveys as per specification to engineers approval | 1 | Item |  |  | 0
2.2.00 | Clearing grass, bushes, shrubs, saplings, uprooting rank vegetation all along the pipeline route and removal & disposal of rubbish to approved tips anywhere in the island as directed by the Engineer-in-charge | 1 | Item |  |  | 0
2.3.00 | Cutting of trees, including trunks, branching and removal of stumps, roots, stacking of serviceable materials with all lifts and up to all lead within project area and earthfilling in the depression/pit, including excavation & backfilling
2.3.01 | Girth size up to 300mm | 1 | item |  |  | 0
2.3.02 | Girth size from 300mm to 600mm | 1 | item |  |  | 0
2.3.03 | Girth size from 600mm to above | 1 | item |  |  | 0
2.4.00 | Dismantling of existing structures like pillars, walls, slabs and any other structure constructed of Brick or coral stone masonry, cement concrete, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material within the project area and facilty locations | 1 | item |  |  | 0
2.5.00 | Road Clearance (Provisional Item)
2.5.01 | Clearing of roads to enable laying of pipes within the vegetation zones in the island to facilitate connections for future plots or connection to facility locations | 330 | m |  |  | 0
2.6.0 | TOTAL OF BILL №: 02 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 03 - DECOMISSIONING
3.1.00 | Decomissioning of existing septic tanks and small bore gravity sewers upon completion and testing and comissioning of new system. Rates shall include for removal of all the existing sludge from the septic tanks and soak wells using proper equiment such as sucker truck; and transfer the contents to STP/Discharge sites. Once all the content has been thoroughly removed the septic tanks should be backfilled with adequate material and compacted | 1 | item |  |  | 0
3.2.00 | TOTAL OF BILL №: 03 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 04 - TRAIL OPERATION AND TRAINNING
4.1.00 | Operation of the entire system after commissioning the system inluding, power and consumables, daily operation, house connection works etc | 3 | months |  |  | 0
4.2.00 | Training of employer's nominees in specialist skills required for pipelaying, pipe welding house connections, pump and electroc mechnical installations and all other works neccesary to complete the system | 18 | months |  |  | 0
4.3.00 | Training of employer's nominees in operation and maintenance | 3 | months |  |  | 0
4.4.00 | TOTAL OF BILL №: 04 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 05 - ADDITIONS AND OMMISSIONS
5.1.00 | ADDITIONS
5.1.01 | BILL NO. 01 - GENERAL AND PRELIMINARIES
5.1.02 | BILL NO. 02 - SITE PREPARATION
5.1.03 | BILL NO. 03 - DECOMISSIONING
5.1.04 | BILL NO. 04 - TRAIL OPERATION AND TRAINNING
5.2.00 | OMMISSIONS
5.2.01 | BILL NO. 01 - GENERAL AND PRELIMINARIES
5.2.02 | BILL NO. 02 - SITE PREPARATION
5.2.03 | BILL NO. 03 - DECOMISSIONING
5.2.04 | BILL NO. 04 - TRAIL OPERATION AND TRAINNING
5.3.00 | TOTAL OF BILL №: 06 - Carried Over To Summary |  |  |  |  | 0

## 02 Sewerage System summary
SUMMARY OF BILLS OF QUANTITIES
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
02 GRAVITY SEWARAGE SYSTEM
| DESCRIPTION | AMOUNT (MRF) | %
| BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (2 nos.) | 0
| BILL NO. 02 - GRAVITY SEWER SYSTEM AND PRESSURE MAINS | 0
| BILL NO. 03 - DPS | 0
| BILL NO. 04 - SEA OUTFALL | 0
| BILL NO. 05 - SUPPLY AND INSTALLATION OF PUMPS | 0
| BILL NO. 06 - MECHANICAL AND ELECTRICAL WORKS | 0
| BILL NO. 07 - SUPPLY OF O&M EQUIPMENT AND SPARES | 0
| BILL NO. 08 - TESTING AND COMMISSIONING | 0
| BILL NO. 09 - ADDITIONS AND OMMISSIONS | 0
| TOTAL AMOUNT | 0

## 02 sewarage system
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
02 GRAVITY SEWARAGE SYSTEM
Male', Republic of Maldives
BILL OF QUANTITIES
ITEM | DESCRIPTION | QTY | UNIT | MATERIAL RATE | LABOUR RATE | AMOUNT
BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (2 nos.)
1.1.00 | General Notes
(a) Cement for all structural works shall be Sulphate resistant portland cement to BS4027:1996 unless specified otherwise
(b) All structural reinforcement steel shall be epoxy coated reinforcement to ASTM A775 / A775M
(c) The required soil bearing pressure for the foundation is 150kn/m². The contractor shall carryout geotechnical testing to ensure that this is achieved and necessary ground improvements and piling shall be done if required
d) rates shall include the pump sump, valve chamber, control panel cabinet and valves, fittings inside the valve chamber and vent structures
(e) All internal concrete surfaces shall be protected with epoxy coating of thickness 500 microns
(f) Bituminous coating shall be provided to all external surfaces of concrete works below ground
(g) Rates should include reinforcements as per sepecifications and drawings, formworks , damp proof membranes, and all other ancillaries to make the work complete
1.2.00 | Excavation Works
1.2.01 | Excavation for PS1 & VC | 34.89 | m3 |  |  | 0
1.2.02 | Excavation for PS2 & VC | 36.4 | m3 |  |  | 0
1.2.03 | Excavation for Vent Stack & Light Post | 2.42 | m3 |  |  | 0
1.2.04 | Excavation for Control Panel | 1.26 | m3 |  |  | 0
1.3.00 | Concrete Works
Lean Concrete
1.3.01 | Lean concrete for PS1 & VC | 5.88 | m3 |  |  | 0
1.3.02 | Lean concrete for PS2 & VC | 5.88 | m3
1.3.03 | Lean concrete for Vent Stack & Light Post | 0.24 | m3 |  |  | 0
1.3.04 | Lean concrete for Control Panel | 0.2 | m3 |  |  | 0
Reinforced Concrete
1.3.05 | Reinforced concrete for PS1 & VC | 17.74 | m3 |  |  | 0
1.3.06 | Reinforced concrete for PS2 & VC | 18.27 | m3 |  |  | 0
1.3.07 | Reinforced concrete for Vent Stack & Light Post | 2.06 | m3 |  |  | 0
1.3.08 | Reinforced concrete for Control Panel | 2.36 | m3 |  |  | 0
1.4.00 | Plastering works
1.4.01 | Plastering works for PS1 & VC | 13.87 | m2 |  |  | 0
1.4.02 | Plastering works for PS2 & VC | 13.87 | m2 |  |  | 0
1.4.03 | Plastering works for Vent Stack & Light Post | 4.32 | m2 |  |  | 0
1.4.04 | Plastering works for Control Panel | 39.44 | m2 |  |  | 0
1.5.00 | Internal coating (500 Micron Epoxy coating )
1.5.01 | Coating for PS1 & VC | 55.24 | m2 |  |  | 0
1.5.02 | Coating for PS2 & VC | 56.81 | m2 |  |  | 0
1.6.00 | Bituminous External coating
1.6.01 | External coating for PS1 & VC | 49 | m2 |  |  | 0
1.6.02 | External coating for PS2 & VC | 50.95 | m2 |  |  | 0
1.6.03 | External coating for Vent Stack & Light Post | 5.84 | m2 |  |  | 0
1.6.04 | External coating for Control Panel | 9.66 | m2 |  |  | 0
1.7.00 | Boundary wall
Rates shall include for lean and reinforced concrete works, formworks, masonry wall, plastering, steel works, painting,finishing works, steel gates and all accesaries as per drawings and technical spoecification
1.7.01 | PS1 | 22 | m |  |  | 0
1.7.02 | PS2 | 22 | m |  |  | 0
1.8.00 | Vent structures
1.8.01 | Supply and installation of vent structure with carbon filters and other ancilliaries as per the drawing and specificattions | 2 | nos. |  |  | 0
1.9.00 | Valves
1.9.01 | Gate Valves | 4 | nos. |  |  | 0
1.9.02 | Check Valves | 2 | nos. |  |  | 0
1.10.00 | Others
1.10.01 | Provision of internal piping, light posts, fittings, guide rails, lifting chain, duckfoot bends,flanges, dismantling joints, DI covers and all other ancillaries as per drawaings and specifications | 1 | Item |  |  | 0
1.11.00 | TOTAL OF BILL №: 01 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 02 - GRAVITY SEWER SYSTEM AND PRESSURE MAINS
2.1.00 | General Notes
(a) The rate for pipe laying shall comprise excavation of trenches, backfilling after laying and testing, jointing pipes, installing house connection wyes on the main line, providing granular bedding for pipe laying, including dismantling of road layers and reinstatement after works
(b) all gravity sewer pipes shall be UPVC to BS EN1401-1:2009.
(c) All gravity sewer mains shall be 160mm dia UPVC of wall thickness & stiffness rated to SN4 & SDR41.
(d) All gravity house laterals shall be 110mm dia UPVC of wall thickness & stiffness rated to SN4 & SDR41.
(e) All gravity sewer mains shall have minimum 0.4% slope.
(f) All gravity sewer pipes shall be jointed using rubber ring push fit jointing method & rubber rings comply with bs 2494 (type2)
(h) All sewer pipes shall be buried under earth cover of minimum 0.6 meters.
(h) All pressure main should be of HDPE PE100 PN16 SDR11 BS EN 12201: 2011 or Equivalent
(I) All Pumping mains should be installed using electrofusion technologies
2.2.00 | Pipe laying
All pipes are measured in linear meters on plan veiw. Contractor shall adjust for slopes
2.2.01 | 160mm dia, uPVC gravity sewer main (SN4, SDR41) | 3023 | m |  |  | 0
2.3.00 | Pumping Main
2.3.01 | Pumping main 110mm dia. HDPE PE100 SDR11 PN16 pipe | 768 | m |  |  | 0
2.3.02 | Pumping main 160mm dia. HDPE PE100 SDR11 PN16 pipe | 0 | m |  |  | 0
2.3.03 | Pumping main 200mm dia. HDPE PE100 SDR11 PN16 pipe | 0 | m |  |  | 0
2.4.00 | Maintenance shaft
(a) Rates shall include for all connections, concrete protections and necessary ancillary items, as per drawing and technical specifications
2.4.01 | 600mm dia. PE/PP Maintenance shaft with concrete protection | 53 | nos. |  |  | 0
2.5.00 | Clean out
(a) Rates shall include for all connections, concrete protections and necessary ancillary items, as per drawing and technical specifications
2.5.01 | 160mm dia. uPVC clean out | 34 | nos. |  |  | 0
2.6.00 | House Connection
2.6.01 | Lateral house connection to main network, not exceeding maximum distance of 8m, using 110mm uPVC pipes, including provision and installation of 315mm dia , uPVC House inspection chamber and ancillaries as per detail drawing and specifications | 66 | nos. |  |  | 0
2.7.00 | TOTAL OF BILL №: 02 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 03 - DPS
3.1.00 | General Notes
(a) Cement for all structural works shall be Sulphate resistant portland cement to BS4027:1996 unless specified otherwise
(b) All structural reinforcement steel shall be epoxy coated reinforcement to ASTM A775 / A775M
(c) The required soil bearing pressure for the foundation is 150kn/m². The contractor shall carryout geotechnical testing to ensure that this is achieved and necessary ground improvements and piling shall be done if required
d) rates shall include the pump sump, valve chamber, control panel cabinet and valves, fittings inside the valve chamber and vent structures
(e) All internal concrete surfaces shall be protected with epoxy coating of thickness 500 microns
(f) Bituminous coating shall be provided to all external surfaces of concrete works below ground
(g) Rates should include reinforcements as per sepecifications and drawings, formworks , damp proof membranes, and all other ancillaries to make the work complete
3.2.00 | Excavation Works
3.2.01 | Excavation for DPS & VC | 34.89 | m3 |  |  | 0
3.2.02 | Excavation for Vent Stack & Light Post | 1.21 | m3 |  |  | 0
3.2.03 | Excavation for Control Panel | 0.63 | m3 |  |  | 0
3.3.00 | Concrete Works
Lean Concrete
3.3.01 | Lean concrete for DPS & VC | 5.88 | m3 |  |  | 0
3.3.02 | Lean concrete for Vent Stack & Light Post | 0.12 | m3 |  |  | 0
3.3.03 | Lean concrete for Control Panel | 0.1 | m3 |  |  | 0
Reinforced Concrete
3.3.04 | Reinforced concrete for DPS & VC | 17.74 | m3 |  |  | 0
3.3.05 | Reinforced concrete for Vent Stack & Light Post | 1.03 | m3 |  |  | 0
3.3.06 | Reinforced concrete for Control Panel | 1.18 | m3 |  |  | 0
3.4.00 | Plastering works
3.4.01 | Plastering works for DPS & VC | 13.87 | m2 |  |  | 0
3.4.02 | Plastering works for Vent Stack & Light Post | 2.16 | m2 |  |  | 0
3.4.03 | Plastering works for Control Panel | 19.8 | m2 |  |  | 0
3.5.00 | Internal coating (500 Micron Epoxy coating )
3.5.01 | Coating for DPS & VC | 55.24 | m2 |  |  | 0
3.6.00 | Bituminous External coating
3.6.01 | External coating for DPS & VC | 49 | m2 |  |  | 0
3.6.02 | External coating for Vent Stack & Light Post | 2.92 | m2 |  |  | 0
3.6.03 | External coating for Control Panel | 4.83 | m2 |  |  | 0
3.7.00 | Boundary wall
Rates shall include for lean and reinforced concrete works, formworks, masonry wall, plastering, steel works, painting,finishing works, steel gates and all accesaries as per drawings and technical spoecification
3.7.01 | boundary wall DPS | 127 | m |  |  | 0
3.8.00 | Vent structures
3.8.01 | Supply and installation of vent structure with carbon filters and other ancilliaries as per the drawing and specificattions | 1 | nos. |  |  | 0
3.9.00 | Valves
3.9.01 | Gate Valves | 2 | nos. |  |  | 0
3.9.02 | Check Valves | 1 | nos. |  |  | 0
3.10.00 | Others
3.10.01 | Provision of internal piping, light posts, fittings, guide rails, lifting chain, duckfoot bends,flanges, dismantling joints, DI covers and all other ancillaries as per drawaings and specifications | 1 | Item |  |  | 0
3.11.00 | TOTAL OF BILL №: 03 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 04 - SEA OUTFALL
4.1.00 | General Notes
(a) Cement for all structural works shall be Sulphate resistant portland cement to BS4027:1996 unless specified otherwise
(b) All structural reinforcement steel shall be epoxy coated reinforcement to ASTM A775 / A775M
c) Rates shall include concrete ballast blocks, diffusers, anchoring necessary concrete protections, fittings , flanges and ancillaries as per drawings and specifications
d) All pipes are measured in linear meters on plan veiw and contractor shall adjust for slopes and actual profile
(e) All pressure mains should be installed using electrofusion technologies
4.2.00 | Construction of outfall
4.2.01 | 160mm dia, HDPE(PE100, PN16, SDR11) sea outfall pipe on land | 156 | m |  |  | 0
4.2.02 | 160mm dia, HDPE(PE100, PN16, SDR11) sea outfall pipe offshore | 1445 | m |  |  | 0
4.3.00 | TOTAL OF BILL №: 04 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 05 - SUPPLY AND INSTALLATION OF PUMPS
5.1.00 | General Notes
(a) Rates shall include for supply and installation as per approved drawings, specifications and approved manufacturers details
b) rates shall include costs for power cables, level control switches, other ancillaries as per drawing and specifications.
5.2.00 | Pumps
5.2.01 | Submersible Pumps (Pump Station 01) - Pump Capacity, Qdp= 0.8 l/s, Head= 10.7 m each | 2 | nos. |  |  | 0
5.2.02 | Submersible Pumps (Pump Station 02) -Pump Capacity, Qdp=1.2 l/s, Head= 9.8 m each | 2 | nos. |  |  | 0
5.2.03 | Submersible Pumps (DPS) -Pump Capacity, Qdp= 2 l/s, Head= 37.6 m each | 2 | nos. |  |  | 0
5.3.00 | Air Blowers
5.3.01 | Air blowers Q= 14m3/min | 3 | Nos |  |  | 0
5.4.00 | TOTAL OF BILL №: 05 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 06 - MECHANICAL AND ELECTRICAL WORKS
6.1.00 | General Notes
(a) The rate shall include for any necessary excavation of trenches, backfilling after laying and testing, jointing, installing house connection wyes on the main line, dewatering if absolutely necessarry, and any other required accessories, including dismantling of road layers and reinstatement after works
(b) The rate shall include for making good any areas affected by below works
6.2.00 | Preparation and updation of electrical panel drawings based on the MEA approved SLD drawings provided and material approvals for specific electromechnical items and obtaining approval from MEA | 1 | Item |  |  | 0
6.3.00 | Main feeder cable from island grid( distribiution boxes) /power house to PS/DPS
6.3.01 | 25 mm2 4-Core armoured cable (feeder to PS) | 180 | m |  |  | 0
6.3.02 | 70 mm2 4-Core armoured cable ( Power House to STP/DPS) | 200 | m |  |  | 0
6.4.00 | Control panels with necessary cabling, control wiring, PLC and other ancillaries as per approved details
6.4.01 | Control Panel for PS1 | 1 | Item |  |  | 0
6.4.02 | Control Panel for PS2 | 1 | Item |  |  | 0
6.4.03 | Control Panel for DPS | 1 | Item |  |  | 0
6.5.00 | Monitoring system
6.5.01 | Monitoring system for Pump stations and DPS including all necessary cabling, wiring or GSM modules, ancilliaries as per sepcifications and approved materials . | 1 | Item |  |  | 0
6.6.00 | Testing and Commissioning of the complete electrical system. | 1 | Item |  |  | 0
6.7.00 | TOTAL OF BILL №: 06 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 07 - SUPPLY OF O&M EQUIPMENT AND SPARES
7.1.00 | Safety Tools
Supply and Delivery of the following safety equipments and tools:
7.1.01 | First Aid Box | 1 | nos. |  |  | 0
7.1.02 | Rubber mat of 1.1kV grade of size 6mm thick. | 1 | nos. |  |  | 0
7.1.03 | Fire Safety Rules chart. | 3 | nos. |  |  | 0
7.1.04 | Shock Treatment Chart | 3 | nos. |  |  | 0
7.2.00 | General Maintenance Tools
Supply and Delivery of standard maintenance tools / equipments to Engineer's approval.
7.2.01 | Hand Wrench (8-32mm) | 1 | nos. |  |  | 0
7.2.02 | Adjustable Wrench 12mm | 1 | nos. |  |  | 0
7.2.03 | Socket Set 8-32 | 1 | nos. |  |  | 0
7.2.04 | Allen Key Set 6-14mm | 1 | nos. |  |  | 0
7.2.05 | Hammer (wood) | 1 | nos. |  |  | 0
7.2.06 | Screw Driver Set | 1 | nos. |  |  | 0
7.2.07 | Grease Gun | 1 | nos. |  |  | 0
7.2.08 | Utility Knife | 1 | nos. |  |  | 0
7.2.09 | Combination pliers | 1 | nos. |  |  | 0
7.2.10 | Long Nose Pliers 180mm | 1 | nos. |  |  | 0
7.2.11 | Cable Cutter | 1 | nos. |  |  | 0
7.2.12 | Halogen Light (LED light) | 2 | nos. |  |  | 0
7.2.13 | Electric Cable 2.5mm2, 3core | 25 | m |  |  | 0
7.2.14 | Hand Saw | 1 | nos. |  |  | 0
7.2.15 | Flat Chisel | 1 | nos. |  |  | 0
7.2.16 | NT Cutter | 1 | nos. |  |  | 0
7.2.17 | Multimeter | 1 | nos. |  |  | 0
7.2.18 | Tester | 1 | nos. |  |  | 0
7.3.00 | Network Maintenance Tools
Supply and Delivery of standard maintenance tools / equipments to Engineer's approval.
7.3.01 | Sewer Cleaning Rods (locking, pvc rods) 2 m each | 35 | nos. |  |  | 0
7.3.02 | 160mm Hole saw/Cutter | 1 | nos. |  |  | 0
7.3.03 | Respiratory Mask | 5 | nos. |  |  | 0
7.3.04 | Gloves | 5 | Set |  |  | 0
7.4.00 | Pump Spares
Supply and Delivery of pump spares based on Approved pumps and to Engineer's approval.
7.4.01 | Pump Cable | 15 | m |  |  | 0
7.4.02 | Basic Repair kit for pump | 3 | set |  |  | 0
7.4.03 | Grip eye (for Pump chain) | 3 | Set |  |  | 0
7.4.04 | Floats | 3 | nos |  |  | 0
7.5.00 | Network and House Connection Spares
Supply and Delivery of standard spare parts as per the approved manafactureres for networks and house connection components and to Engineer's approval.
7.5.01 | 160/110mm UPVC “y” Branch | 10 | nos. |  |  | 0
7.5.02 | 160mm uPVC Pipe | 60 | m |  |  | 0
7.5.03 | 160mm uPVC Pipe | 60 | m |  |  | 0
7.5.04 | 110mm UPVC Bend 45 degree, (spigot ended) | 10 | nos. |  |  | 0
7.5.05 | 160mm Repair Coupler UPVC | 10 | set |  |  | 0
7.5.06 | 110mm Repair Coupler UPVC | 10 | set |  |  | 0
7.5.07 | 110mm UPVC Insitu Adapter | 10 | nos. |  |  | 0
7.5.08 | 160mm UPVC Insitu Adapter | 10 | nos. |  |  | 0
7.5.09 | 315mm PE/ HDPE Catch pit Base | 10 | nos. |  |  | 0
7.5.10 | 315mm Corrugated shafts | 10 | m |  |  | 0
7.5.11 | Ring and Cover for 315 Catch pit | 10 | nos. |  |  | 0
7.6.00 | Sewer jetting
7.6.01 | Supply of vehicle mounted sewer jetting machine with suction and jetting incorporated as per the specifications and engineers approval ( 1500 litre tank) | 1 | item |  |  | 0
7.7.00 | TOTAL OF BILL №: 07 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 08 - TESTING AND COMMISSIONING
8.1.00 | Preparation ofall O&M manuals, training documents and as-built drawings | 1 | item |  |  | 0
8.2.00 | Training of employeer's nominnes in operation and maintainance | 1 | Item |  |  | 0
8.3.00 | Testing and comissioning of system | 1 | item |  |  | 0
8.4.00 | TOTAL OF BILL №: 08 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 09 - ADDITIONS AND OMMISSIONS
9.1.00 | ADDITIONS
9.1.01 | BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (2 nos.)
9.1.02 | BILL NO. 02 - GRAVITY SEWER SYSTEM AND PRESSURE MAINS
9.1.03 | BILL NO. 03 - DPS
9.1.04 | BILL NO. 04 - SEA OUTFALL
9.1.05 | BILL NO. 05 - SUPPLY AND INSTALLATION OF PUMPS
9.1.06 | BILL NO. 06 - MECHANICAL AND ELECTRICAL WORKS
9.1.07 | BILL NO. 07 - SUPPLY OF O&M EQUIPMENT AND SPARES
9.1.08 | BILL NO. 08 - TESTING AND COMMISSIONING
9.2.00 | OMMISSIONS
9.2.01 | BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (2 nos.)
9.2.02 | BILL NO. 02 - GRAVITY SEWER SYSTEM AND PRESSURE MAINS
9.2.03 | BILL NO. 03 - DPS
9.2.04 | BILL NO. 04 - SEA OUTFALL
9.2.05 | BILL NO. 05 - SUPPLY AND INSTALLATION OF PUMPS
9.2.06 | BILL NO. 06 - MECHANICAL AND ELECTRICAL WORKS
9.2.07 | BILL NO. 07 - SUPPLY OF O&M EQUIPMENT AND SPARES
9.2.08 | BILL NO. 08 - TESTING AND COMMISSIONING
9.3.00 | TOTAL OF BILL №: 09- Carried Over To Summary |  |  |  |  | 0

## 03 Water Supply System summary
SUMMARY OF BILLS OF QUANTITIES
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
03 WATER SUPPLY SYSTEM
| DESCRIPTION | AMOUNT (MRF) | %
| BILL NO. 01 - WATER DISTRIBUTION NETWORK - PIPES AND FITTINGS | 0
| BILL NO. 02 - RAIN WATER INTEGRATION | 0
| BILL NO. 03 - CUSTOMER CONNECTIONS | 0
| BILL NO. 04 - WATER TREATMENT PLANT (WTP) FACILITY WORKS | 0
| BILL NO. 05 - BRINE OUTFALL | 0
| BILL NO. 06 - SUPPLY AND INSTALLATION OF PLANTS | 0
| BILL NO. 07 - SUPPLY AND INSTALLATION OF PUMPS | 0
| BILL NO. 08 - MECHANICAL AND ELECTRICAL WORKS | 0
| BILL NO. 09 - PHOTOVOLTAIC GRID CONNECTION | 0
| BILL NO. 10 - SUPPLY OF O&M EQUIPMENT AND SPARES | 0
| BILL NO. 11 - TESTING AND COMMISSIONING | 0
| BILL NO. 12 - ADDITIONS AND OMMISSIONS | 0
| TOTAL AMOUNT | 0

## 03 Water Supply system
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
03 WATER SUPPLY SYSTEM
Male', Republic of Maldives
ITEM | DESCRIPTION | UNIT | QTY | MATERIAL RATE | LABOUR RATE | AMOUNT
BILL NO. 01 - WATER DISTRIBUTION NETWORK - PIPES AND FITTINGS
1.1.00 | General
(a) All work items mentioned here in after for all project facilities and units shall include supply, delivery, transportation, storage, installation, adjustment, testing, commissioning. and other required materials. Equipment and workmanship to execute the items of construction in accordance with the specifications, drawings, and Supervising Engineer's instructions, complete in place and ready for handing over.
(b) The rate for pipe laying shall comprise excavation of trenches, backfilling after laying and testing, jointing pipes, amrker tapes , dewatering if absolutely necessarry, providing granular bedding for pipe laying, including dismantling of road layers and reinstatement after works
c) All pipes are measured in linear meters on plan view. Contractor shall adjust for slopes
1.2.00 | Water Supply Pipes and Fittings
Supply, Installation and Testing of PE Water Supply Pipes, including all fittings, and accessories for connection, laying and fixing Including excavation, and back filling including compaction as required and filling materials as required. Including a 20cm wide warning tape with aluminum strip conductor, shoring, dewatering, disinfection, thrust blocks, plain concrete and reinforced concrete for pipe encasements, as per drawings, specifications
1.2.01 | 250mm dia, HDPE water main distribution pipe (PE100, PN10, SDR17) | 0 | m |  |  | 0
1.2.02 | 200mm dia, HDPE water main distribution pipe (PE100, PN10, SDR17) | 0 | m |  |  | 0
1.2.03 | 160mm dia, HDPE water main distribution pipe (PE100, PN10, SDR17) | 0 | m |  |  | 0
1.2.04 | 110mm dia, HDPE water main distribution pipe (PE100, PN10, SDR17) | 622 | m |  |  | 0
1.2.05 | 90mm dia, HDPE water main distribution pipe (PE100, PN10, SDR17) | 0 | m |  |  | 0
1.2.06 | 75mm dia, HDPE water main distribution pipe (PE100, PN10, SDR17) | 1104 | m |  |  | 0
1.2.07 | 63mm dia, HDPE water main distribution pipe (PE100, PN10, SDR17) | 1361 | m |  |  | 0
1.3.00 | Gate Valves & Fittings with all Accessories
(a) Rates shall include for protection of isolation valves in concrete chambers or similar, including all connections and necessary ancillary items, as per drawings and technical specifications
1.3.01 | Gate Valve, 250mm | 0 | No. |  |  | 0
1.3.02 | Gate Valve, 200mm | 0 | No. |  |  | 0
1.3.03 | Gate Valve, 160mm | 0 | No. |  |  | 0
1.3.04 | Gate Valve, 110mm | 1 | No. |  |  | 0
1.3.05 | Gate Valve, 90mm | 0 | No. |  |  | 0
1.3.05 | Gate Valve, 75mm | 3 | No. |  |  | 0
1.3.06 | Gate Valve, 63mm | 1 | No. |  |  | 0
1.4.00 | Washout
(a) Rates shall include for protection of isolation valves in concrete chambers or similar, including all connections and necessary ancillary items, as per typical drawings and technical specifications
1.4.01 | 50mm | 2 | No. |  |  | 0
1.5.00 | TOTAL OF BILL №: 01 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 02 - RAIN WATER INTEGRATION
2.1.00 | General
(a) All work items mentioned here in after for all project facilities and units shall include supply, delivery, transportation, storage, installation, adjustment, testing, commissioning. and other required materials. Equipment and workmanship to execute the items of construction in accordance with the specifications, drawings, and Supervising Engineer's instructions, complete in place and ready for handing over.
(b) The rate for pipe laying shall comprise excavation of trenches, backfilling after laying and testing, jointing pipes, , dewatering if absolutely necessarry, providing granular bedding for pipe laying, including dismantling of road layers and reinstatement after works
2.2.00 | Pipelaying works for rainwater dirversion line from exisitng rainwater harvesting facility to Water treatment plot and connection to degassifier | 1 | Item |  |  | 0
2.3.00 | TOTAL OF BILL №: 02 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 03 - CUSTOMER CONNECTIONS
3.1.00 | supply and installation of house laterals including, electrofusion saddle, NRV, control valve, meter kit, MT adaptar, lockable tap, and all accesorries and GI pipe protection, as per drawing and specifications. | 55 | Nos. |  |  | 0
3.2.00 | Supply and Installation of materials for installation of Comercial / Institutional Customer connections Icluding, electrofusion saddle, NRV, control valve, meter kit, MT adaptar, lockable tap, and all accesorries and GI pipe protection, as per drawing and specifications. | 15 | Nos. |  |  | 0
3.3.00 | Main Water Meters
Supply and installation of water meters class C or better including all accessories
3.1.01 | 15mm | 55 | No. |  |  | 0
3.1.02 | 40mm | 15 | No. |  |  | 0
3.4.00 | TOTAL OF BILL №: 03 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 04 - WATER TREATMENT PLANT (WTP) FACILITY WORKS
4.1.00 | Desalination Feed Water Borehole
4.1.01 | Construction and installation of Desalination Plant Feed Water Borehole 250mm dia x 35-40m deep and associated structures as described and shown in drawings and specifications. Rates shall include for all excavation and other earth works, machineries, equipments, pipes and fittings, materials and accessories required for complete works | 2 | nos. |  |  | 0
4.2.00 | Brine Tank
Rates shall include for excavation works, lean concrete , reinforced concrete, all piping,connection works, valves, float switch, etc as per drawings and technical specification
4.2.01 | RC brine tank with heavy duty access cover), epoxy coating of thickness 500 microns, RC valve chamber, manhole cover as per drawings and technical specification | 1 | Item |  |  | 0
4.3.00 | Storage Tanks
Rates shall include for all piping and connection works.
4.3.01 | Supply and installation of Product Storage tanks 85 m3 modular RTP Fussion Bonded Epoxy or Glass Lined. Including base plate, anchor bolts, ladder, coatings and all ancillaries as described in drawings and technical specification | 2 | nos |  |  | 0
4.3.02 | Foundation works for product water tanks , including excavations, lean concrete, reincforced concrete and all other ancillaries as per drawings and specifications | 1 | Item |  |  | 0
4.4.00 | Pipework
4.4.01 | Supply and installation of all associated yard pipings, including valves, valce chambers and all other ancillaries as per drawings and specifications | 1 | item |  |  | 0
4.5.00 | Pump Shed
4.5.01 | Construction of Brine pump and rainwater liftwell pump shed including as per typical shed drawings and specifcations | 1 | item |  |  | 0
4.6.00 | TOTAL OF BILL №: 04 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 05 - BRINE OUTFALL
5.1.00 | General Notes
(a) Cement for all structural works shall be Sulphate resistant portland cement to BS4027:1996 unless specified otherwise
(b) All structural reinforcement steel shall be epoxy coated reinforcement to ASTM A775 / A775M
c) Rates shall include concrete ballast blocks, diffusers, anchoring necessary concrete protections, fittings , flanges and ancillaries as per drawings and specifications
d) All pipes are measured in linear meters on plan veiw and contractor shall adjust for slopes and actual profile
5.2.00 | Construction of outfall
5.2.01 | 110mm dia, HDPE(PE100, PN16, SDR11) outfall pipe on land | 152 | m |  |  | 0
5.2.02 | 110mm dia, HDPE(PE100, PN16, SDR11) outfall pipe offshore | 1518 | m |  |  | 0
5.3.00 | TOTAL OF BILL №: 05 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 06 - SUPPLY AND INSTALLATION OF PLANTS
6.1.00 | RO plant system
6.1.01 | Supply and Installation of RO Plant 15 m3/day (18 hours per day) with all pre filters, RO membrane, Higher pressure pumps, dosing systems, valves , piping, control and monotring systems and all other ancillaries as per typical P&I drawings and technical specification | 2 | nos. |  |  | 0
6.2.00 | CIP System
6.2.01 | Supply and Installation of skid mounted movable CIP system including all tanks, pumps, valves , piping, and all other ancillaries as per typical P&I drawings and technical specification | 1 | Item |  |  | 0
6.3.00 | De-gasefication Unit
6.3.01 | Supply and installation of de-gasefication unit including concrete foundations,blowers and all accessories required for complete works | 1 | item |  |  | 0
6.4.00 | TOTAL OF BILL №: 06 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 07 - SUPPLY AND INSTALLATION OF PUMPS
7.1.00 | GENERAL
(a) Rates shall include for supply and installation as per approved manufacturers details
(b) Rates shall include for all internal piping, valves connections and ancillaries
7.2.00 | Distribiution Pumps
7.2.01 | Supply and install of Water Distribution System Pumps including VFD, Pressure tank, valves, pipe work, and other accessories
| Pump Capacity,Q= 3.1 m3/hr and Head = 35 m each | 2 | nos. |  |  | 0
7.3.00 | Borehole Pumps
7.3.01 | Supply and installation, including VFDs and and other ancillaries
| Capacity, Q= 5.56 m3/hr and Head = 50m each | 2 | nos. |  |  | 0
7.3.00 | Transfer Pumps
7.3.01 | Supply and installation, including all neccesary ancillaries
| Capacity, Q= 4.2 m3/hr and Head = 10 m each | 2 | nos. |  |  | 0
7.4.00 | Brine Discharge Pumps
7.4.01 | Supply and installation, including all neccesary ancillaries
| Capacity, Q= 3.9 m3/hr and Head = 17 m each | 2 | nos. |  |  | 0
7.5.00 | Rainwater Transfer Pump
7.5.01 | Supply and installation, including all neccesary ancillaries
| Capacity, Q= 2.7 m3/hr and Head = 30 m each | 2 | nos. |  |  | 0
7.6.00 | TOTAL OF BILL №: 07 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 08 - MECHANICAL AND ELECTRICAL WORKS
8.1.00 | General Notes
(a) The rate shall include for any necessary excavation of trenches, backfilling after laying and testing, jointing, installing house connection wyes on the main line, dewatering if absolutely necessarry, and any other required accessories, including dismantling of road layers and reinstatement after works
(b) The rate shall include for making good any areas affected by below works
8.2.00 | Preparation and updation of electrical panel drawings based on the MEA approved SLD drawings provided and material approvals given for specific electromechnical items and obtaining approval from MEA | 1 | Item |  |  | 0
8.3.00 | Main feeder cable from island grid( distribiution boxes) /power house to WTP
8.3.01 | 95 mm2 4-Core armoured cable ( Power House to WTP) | 315 | m |  |  | 0
8.4.00 | Control panels with necessary cabling, control wiring, PLC and other ancillaries as per approved details
8.4.01 | RO plant | 1 | Item |  |  | 0
8.4.02 | UF plant | 1 | Item |  |  | 0
8.5.00 | Monitoring system
8.5.01 | Monitoring system for water treatment system including all necessary cabling, wiring or GSM modules, ancilliaries as per sepcifications and approved materials . | 1 | Item |  |  | 0
8.6.00 | Testing and Commissioning of the complete electrical system. | 1 | Item |  |  | 0
8.7.00 | TOTAL OF BILL №: 08 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 09 - PHOTOVOLTAIC GRID CONNECTION
9.1.00 | General Notes
(a) The rate shall include all electrical and wiring works neccesary to provide a grid connection as per MEA regulations including DC Isolator box for arrays, Inverter, AC interconnection box, provision for AC Disconnect, provision for Service Panel Connection .
9.2.00 | Installation of 20.7 KW solar system on admin building roof
9.2.01 | 370W Solar panel (1970x1000) | 56 | nos |  |  | 0
9.3.00 | Installation of 6.7 KW solar system on parking shed roof
9.3.01 | 370W Solar panel (1970x1000) | 18 | nos |  |  | 0
9.4.00 | TOTAL OF BILL №: 09 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 10 - SUPPLY OF O&M EQUIPMENT AND SPARES
10.1.00 | Safety Tools
Supply and Delivery of the following safety equipments and tools:
10.1.01 | First Aid Box | 1 | nos. |  |  | 0
10.1.02 | Rubber mat of 1.1kV grade of size 6mm thick. | 1 | nos. |  |  | 0
10.1.03 | Fire Safety Rules chart. | 3 | nos. |  |  | 0
10.1.04 | Shock Treatment Chart | 3 | nos. |  |  | 0
10.2.00 | General Maintenance Tools
Supply and Delivery of standard maintenance tools / equipments to Engineer's approval.
10.2.01 | Hand Wrench (8-32mm) | 1 | nos. |  |  | 0
10.2.02 | Adjustable Wrench 12mm | 1 | nos. |  |  | 0
10.2.03 | Socket Set 8-32 | 1 | nos. |  |  | 0
10.2.04 | Allen Key Set 6-14mm | 1 | nos. |  |  | 0
10.2.05 | Hammer (wood) | 1 | nos. |  |  | 0
10.2.06 | Screw Driver Set | 1 | nos. |  |  | 0
10.2.07 | Grease Gun | 1 | nos. |  |  | 0
10.2.08 | Utility Knife | 1 | nos. |  |  | 0
10.2.09 | Combination pliers | 1 | nos. |  |  | 0
10.2.10 | Long Nose Pliers 180mm | 1 | nos. |  |  | 0
10.2.11 | Cable Cutter | 1 | nos. |  |  | 0
10.2.12 | Halogen Light (LED light) | 2 | nos. |  |  | 0
10.2.13 | Electric Cable 2.5mm2, 3core | 25 | m |  |  | 0
10.2.14 | Hand Saw | 1 | nos. |  |  | 0
10.2.15 | Flat Chisel | 1 | nos. |  |  | 0
10.2.16 | NT Cutter | 1 | nos. |  |  | 0
10.2.17 | Multimeter | 1 | nos. |  |  | 0
10.2.18 | Tester | 1 | nos. |  |  | 0
10.3.00 | RO plant Spares
Supply and Delivery of standard maintenance tools / equipments to Engineer's approval.
10.3.01 | 5 Micron Bag filters | 5 | nos. |  |  | 0
10.3.02 | 10 Micron Bag filters | 5 | nos. |  |  | 0
10.3.03 | High pressure pump basic repair kit | 1 | set |  |  | 0
10.4.00 | Pump Spares
Supply and Delivery of pump spares based on Approved pumps and to Engineer's approval.
10.4.01 | Pump Cable | 18 | m |  |  | 0
10.4.02 | Basic Repair kit for pump ( 1 set per each type of pump) | 8 | set |  |  | 0
10.5.00 | Network and House Connection Spares
Supply and Delivery of standard spare parts as per the approved manafactureres for networks and house connection components and to Engineer's approval.
10.5.01 | PE pipe OD 160mm | 0 | m |  |  | 0
10.5.02 | PE pipe OD 110mm | 18 | m |  |  | 0
10.5.03 | PE pipe OD 90mm | 0 | m |  |  | 0
10.5.04 | PE pipe OD 63mm | 60 | m |  |  | 0
10.5.05 | PE pipe OD 32mm | 60 | m |  |  | 0
10.5.06 | PE pipe OD 25mm | 60 | m |  |  | 0
10.5.07 | EF Coupler OD 160mm | 3 | nos. |  |  | 0
10.5.08 | EF Coupler OD 110mm | 3 | nos. |  |  | 0
10.5.09 | EF Coupler OD 90mm | 6 | nos. |  |  | 0
10.5.10 | EF Coupler OD 63mm | 5 | nos. |  |  | 0
10.5.11 | EF Saddle (63/32) | 5 | nos. |  |  | 0
10.5.12 | EF Saddle (63/50) | 5 | nos. |  |  | 0
10.5.13 | EF reducer 32/25 | 5 | nos |  |  | 0
10.5.14 | House Connection Kit including water meters and ancillaries | 5 | set |  |  | 0
10.5.15 | Commercial Connection Kit including water meters and ancillaries | 5 | set |  |  | 0
10.5.16 | Gate Valve Key | 2 | nos |  |  | 0
10.5.17 | Electrofusion Machine- OD 20mm -125mm | 1 | Nos |  |  | 0
10.6.00 | Laboratory Equipment
10.6.01 | Supply,delivery and installation of laboratory equipments and related consumables, as per specification and to engineer's approval. | 1 | item |  |  | 0
10.7.00 | TOTAL OF BILL №: 10 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 11 - TESTING AND COMMISSIONING
11.1.00 | Preparation ofall O&M manuals, training documents and as-built drawings | 1 | item |  |  | 0
11.2.00 | Training of employeer's nominnes in operation and maintainance | 1 | item |  |  | 0
11.3.00 | Testing and Commissioning of the overall Water System | 1 | item |  |  | 0
11.4.00 | TOTAL OF BILL №: 11 - Carried Over To Summary |  |  |  |  | 0
BILL NO. 12 - ADDITIONS AND OMMISSIONS
12.1.00 | ADDITIONS
12.1.01 | BILL NO. 01 - WATER DISTRIBUTION NETWORK - PIPES AND FITTINGS
12.1.02 | BILL NO. 02 - RAIN WATER INTEGRATION
12.1.03 | BILL NO. 03 - CUSTOMER CONNECTIONS
12.1.04 | BILL NO. 04 - WATER TREATMENT PLANT (WTP) FACILITY WORKS
12.1.05 | BILL NO. 05 - BRINE OUTFALL
12.1.06 | BILL NO. 06 - SUPPLY AND INSTALLATION OF PLANTS
12.1.07 | BILL NO. 07 - SUPPLY AND INSTALLATION OF PUMPS
12.1.08 | BILL NO. 08 - MECHANICAL AND ELECTRICAL WORKS
12.1.09 | BILL NO. 09 - PHOTOVOLTAIC GRID CONNECTION
12.1.10 | BILL NO. 10 - SUPPLY OF O&M EQUIPMENT AND SPARES
12.1.11 | BILL NO. 11 - TESTING AND COMMISSIONING
12.2.00 | OMMISSIONS
12.2.01 | BILL NO. 01 - WATER DISTRIBUTION NETWORK - PIPES AND FITTINGS
12.2.02 | BILL NO. 02 - RAIN WATER INTEGRATION
12.2.03 | BILL NO. 03 - CUSTOMER CONNECTIONS
12.2.04 | BILL NO. 04 - WATER TREATMENT PLANT (WTP) FACILITY WORKS
12.2.05 | BILL NO. 05 - BRINE OUTFALL
12.2.06 | BILL NO. 06 - SUPPLY AND INSTALLATION OF PLANTS
12.2.07 | BILL NO. 07 - SUPPLY AND INSTALLATION OF PUMPS
12.2.08 | BILL NO. 08 - MECHANICAL AND ELECTRICAL WORKS
12.2.09 | BILL NO. 09 - PHOTOVOLTAIC GRID CONNECTION
12.2.10 | BILL NO. 10 - SUPPLY OF O&M EQUIPMENT AND SPARES
12.2.11 | BILL NO. 11 - TESTING AND COMMISSIONING
12.3.00 | TOTAL OF BILL №: 12- Carried Over To Summary |  |  |  |  | 0

## 04 Admin Building Summary
SUMMARY OF BILLS OF QUANTITIES
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
04 ADMINISTRATION BUILDING
| DESCRIPTION | AMOUNT (MRF) | %
| BILL NO. 01 - PRELIMINARIES | #REF!
| BILL NO. 02 - WORKS BELOW GROUND | 0
| BILL NO. 03 - CONCRETE WORKS | 0
| BILL NO. 04 - METAL AND CARPENTRY WORKS | 0
| BILL NO. 05 - MASONRY AND PLASTERING | 0
| BILL NO. 06 - DOOR AND WINDOW SCHEDULE | 0
| BILL NO. 07 - PAINTING | 0
| BILL NO. 08 - FLOOR FINISHES | 0
| BILL NO. 09 - HYDRAULICS AND DRAINAGE | 0
| BILL NO. 10 - ELECTRICAL INSTALLATIONS | 0
| BILL NO. 11 - FIRE DETECTION AND PROTECTION | 0
| BILL NO. 12 - MECHANICAL SYSTEMS | 0
| BILL NO. 13 - PARKING SHED WORKS | 0
| BILL NO. 14 - COMPOUND AND BOUNDARY WALL | 0
| BILL NO. 15 - ADDITIONS | 0
| BILL NO. 16- OMISSIONS | 0
| TOTAL AMOUNT | #REF!

## 04 Administration Building
WATER SUPPLY & SEWARAGE SYSTEM IN M.RAIYMANDHOO
04 ADMINISTRATION BUILDING
Male', Republic of Maldives
NO | DESCRIPTION | UNIT | QTY | MATERIAL RATE | LABOUR RATE | TOTAL
1 | BILL NO. 01 - PRELIMINARIES
1 | General Notes
m - meter
No - Numbers
m³ - cubic meter
m² - square meter
Lm - linear meter
t - tonnes
incl - including
mm - millimeter
dia - diameter
SS - stainless steel
GI - galvanized iron
thk - thick
END OF BILL NO 01: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | #REF!
2 | BILL NO. 02 - WORKS BELOW GROUND
2 | General
a | Rates shall include for: levelling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating and disposing surplus soil
WORKS BELOW GROUND
2.1 | Excavation, upto 0.75m
| Excavation, upto 1.15m for pad footing | m3 | 0.97175 |  |  | 0
| Excavation, upto 0.375m for foundation beam | m3 | 16.275 |  |  | 0
| Disposal of Excess Sand | m3 | 6.78 |  |  | 0
2.2 | Dewatering
| Allow for clean-up of completed works and site upon completion. | item | 1 |  |  | 0
2.3 | Backfilling
| Backfilling and compacting after concrete curing | m3 | 10.4667 |  |  | 0
END OF BILL NO 02: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
3 | BILL NO. 03 - CONCRETE WORKS
3.1 | GENERAL |  |  |  |  | 0
a | Rates shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
b | Concrete quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
c | Formwork rates shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork.
d | Reinforcement rates shall include for: cleaning, fabrication, placing, the provision for all necessary temporary fixings, and supports including tie wire and chair supports, laps, distribution bars, spacer bar and wastage.
e | All reinforcing bars shall be high strength bars and over lap should be 45 x diameter.
f | Install slurry type water proofing to top surfaces of balcony slabs and external surfaces of underground concrete work.
g | Mix ratio for concrete shall be 1:2:3; unless stated otherwise
h | Concrete shall be castes using non-ageed structural steel and cement and such shall be newly puchased for this project and all concrete materials shall be subjected to inspection by the client
1) | Allow for concrete testing | item | 1 |  |  | 0
3.2 | WORKS BELOW GROUND |  |  |  |  | 0
1) | Lean concrete
| 50mm thick Lean concrete | m3 | 2.3 |  |  | 0
2) | RO Plant Base
| Concrete | m3 | 7.92 |  |  | 0
Reinforcement
| Steel deformed bars, 12 mm dia | kg | 313.28 |  |  | 0
| Water proofing | item | 1 |  |  | 0
3) | Formwork
| Plywood, Nuts Bolts, Screws, Mould oil, and Supports, pvc through beam for threadded bars included in price for formwork | m2 | 10.32 |  |  | 0
4) | Foundation Beam FB
| Concrete | m3 | 7.525 |  |  | 0
Reinforcement
| Steel ring bars 6mm dia | kg | 152.736 |  |  | 0
| Steel deformed bars, 12mm dia | kg | 459.24 |  |  | 0
| Binding Wire | Item | 1 |  |  | 0
5) | Formwork
| Plywood, Nuts Bolts, Screws, Mould oil, and Supports, pvc through beam for threadded bars included in price for formwork | m2 | 43 |  |  | 0
3.3 | GROUND FLOOR |  |  |  |  | 0
1) | Ground slab, 100mm thickness
| Concrete | m3 | 13.375 |  |  | 0
Reinforcement
| Steel deformed bars, 10mm dia @ 200 | kg | 829.25 |  |  | 0
| Polythene sheet | m2 | 151 |  |  | 0
2) | Column C1
| Concrete | m3 | 2.52 |  |  | 0
Reinforcement
| Steel ring bars 6mm dia | kg | 74.592 |  |  | 0
| Steel deformed bars, 12 mm dia | kg | 256.32 |  |  | 0
| Binding Wire | Item | 1 |  |  | 0
3) | Formwork
| Plywood, Nuts Bolts, Screws, Mould oil, and Supports, pvc through beam for threadded bars included in price for formwork | m2 | 50.4 |  |  | 0
3.4 | ROOF |  |  |  |  | 0
1) | Roof Beam RB
| Concrete | m3 | 5.16 |  |  | 0
Reinforcement
| Steel ring bars 6mm dia | kg | 106.9152 |  |  | 0
| Steel deformed bars, 12mm dia | kg | 382.7 |  |  | 0
| Binding Wire | Item | 1 |  |  | 0
2) | Formwork
| Plywood, Nuts Bolts, Screws, Mould oil, and Supports, pvc through beam for threadded bars included in price for formwork | m2 | 68.8 |  |  | 0
3) | Sloping Roof Beam SRB
| Concrete | m3 | 2.76 |  |  | 0
Reinforcement
| Steel ring bars 6mm dia | kg | 57.1872 |  |  | 0
| Steel deformed bars, 12mm dia | kg | 240.7932 |  |  | 0
| Binding Wire | Item | 1 |  |  | 0
4) | Formwork
| Plywood, Nuts Bolts, Screws, Mould oil, and Supports, pvc through beam for threadded bars included in price for formwork | m2 | 27.6 |  |  | 0
END OF BILL NO 03: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
4 | BILL NO. 04 - METAL AND CARPENTRY WORKS
4.0 | GENERAL
a | Rates shall include for: all fabrication work, welding, marking, drilling for bolts including those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
b | contractor shall submit for approval shop draings for all ceiling works for apartments including ceilings for bedrooms, sitting rooms and toilets. The ceilings shall be as specified by the dlient and are subjected to written spproval by the client
c | Rates shall include for all painting and finishing as specified in the specification.
d | Rates shall include for fabrication and erection and temporary supports and fixing into position.
e | Stair Case, Balcony and parapet railing shall be made as shown in the drawing
f | Lift Machine room stars shall be incl. in the lift supply and installation
4.1 | GROUND FLOOR |  |  |  |  | 0
| Cement Board False Ceiling [200mm below beam bottom] | m2 | 3 |  |  | 0
| Plaster Board False Ceiling [200mm below beam bottom] | m2 | 18 |  |  | 0
| Plaster Board False Ceiling [at roof beam top level] | m2 | 18 |  |  | 0
4.2 | ROOF |  |  |  |  | 0
| Roofing Covering as per given drawing Including the Mineral Wool Insulation | m2 | 184.44 |  |  | 0
| TR1 Truss works (10.7m) | item | 1 |  |  | 0
| 50x150x2.5 GI 'C' channel purlins @1000 C/C | item | 1 |  |  | 0
END OF BILL NO 04: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
5 | BILL NO. 05 - MASONRY AND PLASTERING
5 | GENERAL
a | Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding, frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good
b | Cement solid block, laid on and incl. mortar tie rods, compression joint gap filler, nylon/plastic mesh as specified
c | Cement plastering on walls and concrete surfaces as specified incl. wire mesh at the joints of concrete surfaces and walls
d | Masonry brick should be salt free PWS / Municipalty solid bricks.
5.1 | GROUND FLOOR |  |  |  |  | 0
1) | Masonry
| External Blockwork | m2 | 186.855 |  |  | 0
| Internal Blockwork | m2 | 105.447 |  |  | 0
2) | Plastering & Screeding
| External Plastering of wall surfaces | m2 | 186.855 |  |  | 0
| Internal Plastering of wall surfaces | m2 | 397.749 |  |  | 0
| Floor screed | m2 | 150.5 |  |  | 0
END OF BILL NO 05: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
6 | BILL NO. 06 - DOOR AND WINDOW SCHEDULE
6 | GENERAL
a | Rates shall include for: Locks (mortise double Locks), Latches, Closers, Bolts, Puch Plates, Pull Handles, Kick Plates, Hinges and all door and window hardware.
b | Locks (mortise double Locks), Latches, Closers, Bolts, Puch Plates and all Doors and windows shall be as specified in drawings and subjected to written approval by the client
c | The contractor shall take delivery and complete installation
6.1 | GROUND FLOOR |  |  |  |  | 0
| D1 | nos | 2 |  |  | 0
| D2 | nos | 1 |  |  | 0
| D3 | nos | 3 |  |  | 0
| V1 | nos | 1 |  |  | 0
| DW1 | nos | 1 |  |  | 0
| DW2 | nos | 1 |  |  | 0
| W3 | nos | 2 |  |  | 0
| GD1 | nos | 1 |  |  | 0
END OF BILL NO 06: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
7 | BILL NO. 07 - PAINTING
7 | GENERAL
a | Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window
b | All painting work shall be carried in accordance with the Specifications
c | Paint system shall be approved paint from client and consultant.
7.1 | GROUND FLOOR |  |  |  |  | 0
| Paint on External Walls | m2 | 186.855 |  |  | 0
| Paint on Internal Walls | m2 | 397.749 |  |  | 0
| Paint on Ceilings and exposed slab | m2 | 41 |  |  | 0
| Industrial grade paint on plant room floor | m2 | 92 |  |  | 0
END OF BILL NO 07: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
8 | BILL NO. 08 - FLOOR FINISHES
8 | GENERAL
a | Rates shall include for:motar, fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing.
b | Tiles for general areas such as rooms, sittingroom and kitchen shall be 600x600 ceramic glazed tiles or sizes approved by client and tiles for wet area such as toilets balconies shall be of 450x450 ceramic non-skid tiles on floor and 450x600 ceramic tles up to ceiling or as approved by the client, also tiling addon such as borders and decorative tiles for bathroom shall be included and all materials for floor finishes shall be subjected to written spproval by client
8.1 | GROUND FLOOR |  |  |  |  | 0
Floor Tiles
| 600x600 homogenous floor tiles fixed with tile adhesive | m2 | 54.21 |  |  | 0
| 300x300 homogenous non skid floor tiles fixed with water proof tile adhesive | item | 3 |  |  | 0
Wall Tiles
| wall tiles fixed with tile adhesive | m2 | 18 |  |  | 0
END OF BILL NO 08: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
9 | BILL NO. 09 - HYDRAULICS AND DRAINAGE
9 | GENERAL
a | Rates shall include for: valves, sockets, running joints, connectors, elbows, junctions, reducers, expansion joints; backnuts and similar; incidental fittings, clips, saddles, brackets, straps, hangers, screws, nails and fixing complete, including cutting and forming holes; excavating, laying pipes and backfilling trenches.
b | Sanitary fixtures complete including brackets, flush pipes, valves, overflows, plugs and washers, as specified. All fixtures and fittings shall be newly purchased for this project and subjected to inspection by the client
c | Toilet fittings to be stailess steel or chrome plated and fixtures to be cotto or equivalent or the fittings shall be approved by writing by the client
d | The contractor shall take delivery and fixing
9.1 | GROUND FLOOR |  |  |  |  | 0
Supply and Drainage
1 | Running Internal fresh water pipes followed from Shut-off valves to all Tiolets, Kitchens & Laundrys which reduces from 25mmØ to 20mmØ and finally 16mmØ to the outlet fixtures or mixer as given in the detail drawings | item | 1 |  |  | 0
2 | Complete Rainwater Drainage pipework, required trays, chains and ducting as given in the drawing | item | 1 |  |  | 0
3 | Complete waste water Discharge pipework, required trays and ducting as given in the drawing | item | 1 |  |  | 0
4 | Plumbing fixtures and accessories
| Floor Drain | nos | 2 |  |  | 0
| Floor Gully | nos | 3 |  |  | 0
| Gully Trap | nos | 1 |  |  | 0
| Manhole | nos | 1 |  |  | 0
| Bottle Trap | nos | 3 |  |  | 0
| Clean Out Point | nos | 2 |  |  | 0
| Wall Tap | nos | 2 |  |  | 0
| Basin Faucet | nos | 1 |  |  | 0
| Bidet Shower | nos | 1 |  |  | 0
| Water Closet | nos | 1 |  |  | 0
| Gate Valve | nos | 3 |  |  | 0
| MWSC or FENAKA Meter | nos | 1 |  |  | 0
END OF BILL NO 09: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
10 | BILL NO. 10 - ELECTRICAL INSTALLATIONS
10 | GENERAL
a | Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
b | Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil
c | Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces
c | Lighting fixture and electrical wires and other electrical euquipement such as fans and such shall comply with STELCO standard and all fixtures and fitting shall be subjected to written approval by the client
d | Each Light/ light fixture and its switch is measured as one point; similarly each fan or each socket outlet is measured as one point;
e | The contractor shall take delivery and complete installation
10.1 | GROUND FLOOR |  |  |  |  | 0
1) | Electrical Wiring
| Main Electrical Connection | item | 1 |  |  | 0
| Electrical wiring with copper conductor cable in conduites in wall and slabs as specified to 2.5mm² wiring to sockets and 1.5mm² wiring to light fixtures, fans and its switches | item | 1 |  |  | 0
| Cabling for internet and medianet | item | 1 |  |  | 0
2) | Lighting and electrical accessories
| Ceiling Light (12W) | nos | 10 |  |  | 0
| Recessed Ceiling Light (12W) | nos | 1 |  |  | 0
| Weather Proof Wall Light IP55 (12W) | nos | 8 |  |  | 0
| HPS Low Bay Light (60W) | nos | 10 |  |  | 0
| Ceiling Mounted Exhaust Fan | nos | 1 |  |  | 0
| Wall Mounted Exhaust Fan | nos | 5 |  |  | 0
| Centrifugal external motor fan | nos | 2 |  |  | 0
| Fresh air intake grille or screen | nos | 2 |  |  | 0
| Light Switch (1 Gang ) | nos | 1 |  |  | 0
| Light Switch (2 Gang ) | nos | 2 |  |  | 0
| Light Switch (3 Gang ) | nos | 2 |  |  | 0
| Light Switch (4 Gang ) | nos | 2 |  |  | 0
| 13A Power Socket | nos | 9 |  |  | 0
| 13A Twin Socket | nos | 18 |  |  | 0
| 15A Socket In Polycarbonate Box | nos | 9 |  |  | 0
| 15A Switch | nos | 4 |  |  | 0
| 15A Switched Socket at High Level | nos | 4 |  |  | 0
| Distribution Board | nos | 1 |  |  | 0
| Computer Network Outlet | nos | 6 |  |  | 0
| Emergency Light | nos | 6 |  |  | 0
| Telephone Outlet | nos | 2 |  |  | 0
| Internet Switchboard | nos | 1 |  |  | 0
END OF BILL NO 10: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
11 | BILL NO. 11 - FIRE DETECTION AND PROTECTION
11 | GENERAL
a | Rates shall include for: wirerin with 2.5mm2 fire retardant low smoke (FRLS) cables in FRLS conduits and instalation
b | all dry riser pipes should be galvanized
c | all dry riser pipes should be painted in red as per regulation
d | all support/brackets shall be hot dippedd galvanized to 100mm
e | all fire extinguishers shall be in cabinets (cabinets should be provided)
11.1 | GROUND FLOOR |  |  |  |  | 0
1 | CO2 Extinguisher (load: 2kg) In Polycarbonate Enclosure | nos | 4 |  |  | 0
2 | H2O Extinguisher (load: 9L) In Polycarbonate Enclosure | nos | 3 |  |  | 0
3 | DCP Extinguisher (load 6kg) In Polycarbonate Enclosure | nos | 2 |  |  | 0
4 | Heat Detector | nos | 5 |  |  | 0
5 | Manual Call Point | nos | 3 |  |  | 0
6 | Smoke Detector | nos | 5 |  |  | 0
7 | Beacon | nos | 1 |  |  | 0
8 | Sounder Bell | nos | 1 |  |  | 0
9 | Fire Blanket | nos | 1 |  |  | 0
10 | Exit Sign | nos | 4 |  |  | 0
11 | Fire Alarm Control Panel | nos | 1 |  |  | 0
END OF BILL NO 11: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
12 | BILL NO. 12 - MECHANICAL SYSTEMS
12.1 | AIR-CONDITIONING SYSTEM
a | Rate shall include for signal cables for each unit, which has to be laid above the ceiling. copper tubes and refnet joints refnet header needed for completion. electrical connection required for all indoor units and isolator switches for out door units
12.1.1 | Ground Floor |  |  |  |  | 0
1 | Wall mount Air conditioner9,000 BTU with out-door condensing unit | item | 2 |  |  | 0
2 | Wall mount Air conditioner12,000 BTU with out-door condensing unit | item | 1 |  |  | 0
END OF BILL NO 12: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
13 | BILL NO. 13 - PARKING SHED WORKS
13 | GROUND WORKS |  |  |  |  | 0
13.0.0 | General
a | Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating, additional working space and disposing surplus soil.
13.0.1 | Excavation
a | Excavation quantities are measured to the faces of concrete members. Rates shall include for all additional excavation required to place the formwork , back fill , dewatering and others
1) | Foundation Pad | m³ | 5.0625 |  |  | 0
13.0.2 | Back filling
a | Rates shall include for: leveling, grading, trimming and compacting.
b | Ground need to be compacted to the density required by the consultant
1) | Foundation Pad | m² | 3.5438 |  |  | 0
13.0.3 | Damp Proof Membrane
a | Rates shall include for: dressing around and sealing to all penetrations, laps and turnups.
1) | Polythene damp proof membrane (500 gauge) laid on blinding layer. | m² | 5.0625 |  |  | 0
13.1 | CONCRETE WORKS |  |  |  |  | 0
13.1.0 | General
a | Rates shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
b | Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6 by volume.
c | Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
13.1.1 | LEAN CONCRETE
50mm thick lean concrete below Foundation
1) | Foundation Footings | m² | 5.0625 |  |  | 0
13.1.2 | REINFORCED CONCRETE
FOUNDATIONS
1) | Foundation Pad | m³ | 1.5187 |  |  | 0
GROUND FLOOR
COLUMNS
1) | Column Stump | m3 | 0.432 |  |  | 0
13.1.3 | FORM WORK
a | Exposed surface shall have fair finish while remaining may have rough finish.
b | Timber used for unexposed concrete surface shall sound dressed and seasoned good quality common timber while for exposed concrete surfaces dressedand matched boards uniformly thick and not more than 251mm wide.
c | Plywood used for forms shall be of commercial standard, moisture resistane conrete form plywoodnot lessthan 6mm thick and atleast 12mm thick.
d | Rates shall include for; all necessary boarding,supports, erecting, framing, temporary cambering cutting, perforations for reinforcing bars, bolts,straps,ties, hangers, pipes and removal of formwork.
FOUNDATIONS
1) | Foundation Pad | m2 | 0.9 |  |  | 0
GROUND FLOOR
COLUMNS
1) | Column Stump | m2 | 8.64 |  |  | 0
13.1.4 | REINFORCEMENT WORK
a | Main reinforcement steel shall be high tensile steel hot rolled deformed bars complying with BS 1119 or BS 1172 Characteristic strength not less than 160N/mm2.
b | Stirrups shall be hot rolled mildsteel round bars complying with BS 1119, Characteristic strength not less than 250N/mm2
c | Rates shall include for; distribution steel, cleaning, fabrication, placing, the provision for all necessary temporary fixings, and supports including chairs and tie wire , laps and wastage.
BELOW GROUND
FOUNDATIONS
1) | Foundation Pad
| 10mm dia deformed bars - 6m | kg | 41.85 |  |  | 0
GROUND FLOOR
COLUMNS
1) | Column Stump
| 10mm dia deformed bars - 6m | kg | 26.784 |  |  | 0
| 6mm dia deformed bars - 6m | kg | 12.7872 |  |  | 0
13.2 | PAINTING |  |  |  |  | 0
13.2.0 | General
a | Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window furniture.
b | All painting work shall be carried in accordance with the Specifications
c | Rate shall include for weather proof paint finish for exterior surfaces of the steels two coats of weather bond paint
GROUND FLOOR
13.2.1 | Painting exterior surfaces of Steel columns | item | 1 |  |  | 0
13.2.2 | Painting exterior surfaces of Steel Truss | item | 1 |  |  | 0
13.3 | METAL WORK |  |  |  |  | 0
13.3.0 | General
a | Rates shall include for ; all labour in framing, cutting, welding, cleats, baseplates, flanges,screws, nails, bends, and similar complete with grinding, surface smoothening and polish finishes.
13.3.1 | GALVANIZED STEEL HOLLOW SECTION RAILING WELDED TOGETHER IN BETWEEN THE POSITIONS OF THE EXISTING COLUMNS
Columns , Truss & Roof covering
1) | Supply, Fabrication and Fixing Steel Columns as per details drawing | nos | 9 |  |  | 0
2) | Supply, Fabrication and Fixing Steel truss as per details drawing | nos | 3 |  |  | 0
3) | Supply, Fabrication and Fixing Roof Covering as per details drawing | m2 | 49.28 |  |  | 0
END OF BILL NO 13: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
14 | BILL NO. 14 - COMPOUND AND BOUNDARY WALL
14 | GROUND WORKS |  |  |  |  | 0
14.0.0 | General
a | Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating, additional working space and disposing surplus soil.
14.0.1 | Excavation
a | Excavation quantities are measured to the faces of concrete members. Rates shall include for all additional excavation required to place the formwork , back fill , dewatering and others
b | Rates shall include for: dressing around and sealing to all penetrations, laps and turnups.
c | Rates shall include for: leveling, grading, trimming and compacting.
d | Polythene damp proof membrane (2000 gauge) laid on blinding layer.
1) | Foundation Beam and Foundation Pads | Lm | 118.61 |  |  | 0
14.1 | CONCRETE WORKS |  |  |  |  | 0
14.1.0 | General
a | Rates shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
b | Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6 by volume.
c | Rates shall be inclusive for any additional concrete required to place the formwork.
d | Main reinforcement steel shall be high tensile steel hot rolled deformed bars complying with BS 1119 or BS 1172 Characteristic strength not less than 160N/mm2.
e | Stirrups shall be hot rolled mildsteel round bars complying with BS 1119, Characteristic strength not less than 250N/mm2
f | Rates shall include for; distribution steel, cleaning, fabrication, placing, the provision for all necessary temporary fixings, and supports including chairs and tie wire , laps and wastage.
g | Exposed surface shall have fair finish while remaining may have rough finish.
h | Timber used for unexposed concrete surface shall sound dressed and seasoned good quality common timber while for exposed concrete surfaces dressedand matched boards uniformly thick and not more than 251mm wide.
i | Plywood used for forms shall be of commercial standard, moisture resistane conrete form plywoodnot lessthan 6mm thick and atleast 12mm thick.
j | Rates shall include for; all necessary boarding,supports, erecting, framing, temporary cambering cutting, perforations for reinforcing bars, bolts,straps,ties, hangers, pipes and removal of formwork.
14.1.1 | LEAN CONCRETE
50mm thick lean concrete below Foundation
1) | Foundation Footings & Tie beams | item | 1 |  |  | 0
14.1.2 | REINFORCED CONCRETE
FOUNDATIONS
1) | Foundation Beam FB | item | 1 |  |  | 0
2) | Foundation Pad | item | 1 |  |  | 0
14.1.4 | GROUND FLOOR
COLUMNS & CAPPING
1) | MC (Main) | item | 1 |  |  | 0
2) | GC (Gate Column) | item | 1 |  |  | 0
3) | RC Capping Beam | item | 1 |  |  | 0
14.2 | MASONRY AND PLASTERING |  |  |  |  | 0
14.2.0 | General
a | Rates shall include for cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs.
b | Cutting or leaving holes and openings as recesses for and building in pipes, conduits , sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joints.
c | All external wall and all inetrenal walls shall be 100mm thick Solid cement blocks and for masonry mix ratio 1:5 (cement and river sand)
MASONRY
14.2.1 | BELOW GROUND LEVEL
150mm thick Solid block wall
(1) | 300 x150 x 150mm solid block single wall - 150mm thick above all Foundation beams. | Lm | 118.61 |  |  | 0
14.2.2 | ABOVE GROUND LEVEL
Boundary walls
(1) | 300x150x100mm Hollow block single wall - 100mm thick | Lm | 118.61 |  |  | 0
PLASTERING
a | 20mm thick Cement plastering on Exterior surface of External masonry walls and concrete surfaces and 15mm thick plastering on interior walls and concrete surface as specified incl. wire mesh shall be fixed at the joints of concrete surfaces and walls before plastering. Quantity is measured including concrete surfaces - Parapetwalls, Liftwalls, columns & beams.
b | Rates shall include for External plastering shall 20mm thick (12+8mm) 2 coats in 1:4 cement and river sand mix ratio
c | Rates shall include for approved brand water proofing compound shall be mixed with cement mortar for external wall plastering as per manufacturers specifications.
14.2.3 | BELOW GROUND LEVEL
25mm thick Plastering
(1) | Both surface of below ground walls | Lm | 118.61 |  |  | 0
14.2.4 | ABOVE GROUND LEVEL
Both Side Plastering 25mm thick
(1) | Both surface of boundary wall | Lm | 118.61 |  |  | 0
14.3 | DOORS AND WINDOWS |  |  |  |  | 0
14.3.0 | General
a | Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
b | Rates shall include for door frames and window frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings and installation.
14.3.1 | GROUND FLOOR
External
1 ) | G1 | no | 1 |  |  | 0
2 ) | G2 | no | 1 |  |  | 0
14.4 | PAINTING |  |  |  |  | 0
14.4.0 | General
a | Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window furniture.
b | All painting work shall be carried in accordance with the Specifications
c | Rate shall include for weather proof paint finish for exterior surfaces of the wall complete including application of two coats of oil based wall sealer and two coats of weather bond paint
d | Rate shall include for putty and paint finish for interior surfaces of the wall and ceilings complete including application of two coats of wall sealer, two coats of putty finish and two coats of emulsion paint finish on top for Interior painting.
14.4.1 | GROUND FLOOR
1) | Painting both sides of the Wall, Columns & beams, Capping Beam | Lm | 118.61 |  |  | 0
14.5 | METAL WORK |  |  |  |  | 0
14.5.0 | General
a | Rates shall include for ; all labour in framing, cutting, welding, cleats, baseplates, flanges,screws, nails, bends, and similar complete with grinding, surface smoothening and polish finishes.
14.5.1 | GALVANIZED STEEL HOLLOW SECTION RAILING WELDED TOGETHER IN BETWEEN THE POSITIONS OF THE EXISTING COLUMNS
ABOVE BOUNDARY WALL
1 ) | Railing
| Supply, Fabrication and Fixing Steel Fence on the Compound wall as per details | Lm | 118.61 |  |  | 0
14.6 | ELECTRICAL INSTALLATIONS |  |  |  |  | 0
14.6.0 | General
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil
(c) Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces and also all elecetrical work shall be carried out according to MEA/STELCO standards and specifications.
(d) Each Light/ light fixture and its switch is measured as one one point; similarly each fan or each socket outlet is measured as one point;
(e) Rates shall include for supply and complete installation , fittings and fixtures.
GROUND FLOOR
14.6.1 | ELECTRIC BOARDS
1) | Supply and Installation | nos | 1 |  |  | 0
14.6.2 | ELECTRIC FIXTURES
1) | Solar Powered LED Gate Lights (12W) IP65 | nos | 4 |  |  | 0
2) | 100W LED Flood Light IP65 @ 6m Light Post and it's footing | nos | 5 |  |  | 0
3) | Light Switch - 1 Gang | nos | 5 |  |  | 0
14.6.3 | ELECTRICAL WIRING
1) | 2.5mm2 Wiring to Light Points | points | 5 |  |  | 0
14.7 | PAVING BLOCKS |  |  |  |  | 0
14.7.0 | General
a | Rates shall include for cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs.
b | Cutting or leaving holes and openings as recesses for and building in pipes, conduits , sleeves and similar as required for all trades; leaving surfaces rough or raking out joints and flashings, bedding frames or plates, building in joints.
c | Before laying the paving block must compact the earth and level the area.
14.7.1 | PAVING BLOCKS
PAVING BLOCKS LAYING
| 200 x 100 x 65mm Solid paving blocks | m2 | 143 |  |  | 0
END OF BILL NO 14: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
15 | BILL NO. 15 - ADDITIONS |  |  |  |  | 0
1 | Additions
END OF BILL NO 15: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0
16 | BILL NO. 16- OMISSIONS |  |  |  |  | 0
1 | Omissions
END OF BILL NO 16: CARRIED OVER TO GENERAL SUMMARY | [5 empty] | 0