## PREAMBLES
PREAMBLE NOTES
1.1 | Abbreviations
m - metre
No - numbers
m³- cubic metre
m² - square metre
LM - Linear metre
t - tonnes
incl - including
mm - millimetre
SS - Stainless Steel
GI - Galvanised Iron
dia - diameter
G.L - Ground level
1.2 | General Notes
1. The Bill of Quantities shall be read in conjunction with the Instruction to Bidders, General Conditions of Contract, Appendix to bid, Technical Specification and Tender Drawings.
2. The rates and prices tendered in the priced Bill of Quantities shall, except in so far as it is otherwise provided under the Contract, include all constructional plant, labour, supervision, materials, transportation, installation/erection, profit, together with all general risks, liabilities and obligations set out or implied in the Contract.
3. The rates and prices shall be quoted entirely in Maldivian Rufiyaa.
4. A rate or price shall be entered against each item in the Bill of Quantities, whether quantities are stated or not. The cost of items against which the Contractor has failed to enter a rate or price shall be deemed to be covered by other rates and prices entered in the Bill of Quantities and no separate payment shall be made for such un-priced items.
5. The whole cost of complying with the provisions of the Contract shall be included in the items provided in the priced Bill of Quantities, and where no items are provided but required for completion of contract works, the cost shall be deemed to be distributed among the rates and prices entered for the related item of work. Only properly executed variation orders shall be recognized for additional payment for items not entered in the Bill of Quantities.
6. General directions and descriptions of work and materials are not necessarily repeated or summarized in the Bill of Quantities. The Bidder shall refer to relevant sections of the Contract Document to fully understand the item requirements before entering rates or prices against each item in the Bill of Quantities.

## SUMMARY
CONSTRUCTION OF NEW FUEL STORAGE TANK AND PUMP ROOM, AND RELOCATION OF EXISTING FUEL TANKS
SUMMARY OF BILL OF QUANTITIES
BOQ.NO | Description | Amount (Mrf)
1 | NEW TANK FOUNDATION
2 | NEW FUEL TANK
3 | PUMP ROOM
4 | EXISTING TANK RELOCATION - 01
5 | EXISTING TANK RELOCATION - 02
SUB TOTAL
GST
GRAND TOTAL

## BOQ (FNDTN)
BILL OF QUANTITIES FOR NEW TANK FOUNDATION
SL.No | Description | Unit | Qty | Rate | Amount
GENERAL
Rate shall include for mobilisation, site management costs, materials, labour, water, electricity, site clearing including removing site vegetation & trees, grubbing up roots, filling voids, levelling, cleaning & proper disposal, demobilisation, vehicles, vessels, permits, equipment & tools including all necessary transport & storage required for the proper execution & completion of the works.
1. GROUND WORKS
1 | EXCAVATION
Note: Excavation quantities are measured to the faces of concrete members. The quantities given are the bulk before excavating and no allowance is made for subsequent variations to bulk or for extra space for working space or to accomodate earthwork support. Rate shall include for all additional excavation required to place the formwork/shuttering, working space and dewatering the trenches for the required days.
Rate shall also include for providing proper earthwork support to faces of excavations, disposal of surplus excavated materails offsite to a selected location in the island.
Rate shall also include for filling to excavation with available sand arisen from excavations, in 150mm thick layers well ram and consolidate. Rate shall also include for Compacting Bottoms of excavations. Rate shall also include for leveling & compaction to achieve appropriate degree of compaction. Compaction shall be done using appropriate method such as compactor to achieve 150Kpa strength.
1 | Excavating for foundation beams as shown in drawing. | m³ | 4.14
2 | Excavating trenches as shown in drawing. | m³ | 118.8
2 | DPC
Note: Rates shall include for: dressing around and sealing to avoid all penetrations
1 | Polythene DPC membrane below RCC foundation slab (500 gauge - black color) | m² | 28.75
2. CONCRETE WORKS
2.1 | GENERAL
(a) The volume of concrete measured includes that occupied by reinforcement, other metal sections & chamfers or internal splays each not exceeding 0.01m² in cross-section area.
(b) Rate shall include for: formwork, provision to place in position; casting of all required items and finishing after removal of formwork and additional concrete required to conform to structural and excavated tolerances.
(c) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:4 by volume
(d) Rate shall also include for application of two coats of bitumastic paint (Fosroc or equivalent) to all concrete surfaces below ground level or in contact with soil.
(e) Any required chemical bonding agent shall be approved by client.
2.2 | LEAN CONCRETE
Note: Quantity is measured to the edges of concrete members. Rate shall be inclusive of any additional concrete required to place the formwork.
1 | Beds, thickness 50mm, below foundation ring beam, bund slab & foundation slab | m³ | 10.22
2.3 | REINFORCED CONCRETE
In-situ reinforced concrete to:
(a) Rates shall include for reinforcing bars: cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports, hooks and tying wire, spacers and chairs and any wastage.
(b) All reinforcing bars except 6mm dia bars shall be high strength deformed bars
2.3.1 | Foundation
1 | Ring beam | m³ | 8.27
2 | Slab | m³ | 4.31
2.3.2 | Bund
1 | Slab | m³ | 24.98
2 | Wall | m³ | 15.21
2.3.3 | Trench
1 | Trench | m³ | 59.4
2 | Cover | m³ | 32.4
3. PAINTING WORKS
3 | PAINTING
3.1 | GENERAL
(a) All painting work shall be carried out in accordance with the Manufacturers specifications & instructions.
(b) External exposed wall surfaces shall be painted with one coat of primer and two finishing coats of external wall paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
(b) External exposed floor surfaces shall be painted with one coat of primer and two finishing coats of external floor paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
* Primer - Loxon (Concrete & Masonry primer/sealer interior/exterior latex A24W8300)
* Wall paint - A-100
* Floor paint - Porch & Floor Enamel (Interior/Exterior Acrylic Satin A32-200 series)
3.2 | Floor
1 | Bund slab & foundation slab (colour code - Earl Gray SW7660 or equivalent) | m² | 187.69
3.3 | Wall
1 | Bund wall & sides of foundation slab (colour code - Earl Gray SW7660 or equivalent) | m² | 209.31
4. MISCALLANEOUS WORKS
4.1 | STEEL STAIR CASE
1 | Supply, fabricate, erect and fixing into position of steel stair case as specified in the drawing & specifiction. Rate shall include for GI pipe framing, 6mm thick aluminum checkered plate steps & SS handrails, with concrete bottom support (600x250x150mm), including painting (Sherwin williams steel paint, Earl Gray SW7660 or equivalent). | No | 1
4.2 | KIOSK
1 | Supply, fabricate, erect and fixing into position fuel kiosk as shown in drawing. | No | 1
TOTAL OF BILL

## BOQ (NEW TANK)
BILL OF QUANTITIES FOR NEW FUEL STORAGE TANK
SL.No | Description | Unit | Qty | Rate | Amount
GENERAL
Rate shall include for mobilisation, site management costs, materials, labour, water, electricity, site clearing including removing site vegetation & trees, grubbing up roots, filling voids, levelling, cleaning & proper disposal, demobilisation, vehicles, vessels, permits, equipment & tools including all necessary transport & storage required for the proper execution & completion of the works.
1. STEEL TANK
1.1 | NEW FUEL STORAGE TANK
1 | Supply, fabricate, erect and fixing 200m3 steel welded fuel storage tank as specified in the drawing & specification. Rate shall include for internal pipe work, nozzles, manholes, vents, handrails and attachements, access caged ladder, roofing structure, roof support and roofing, tank walls and base, all pipe connections. | No | 1
2 | Hydro-testing the tank to assure leak proof. Leak testing methodology shall be submitted as per API standard for client approval. | No | 1
2. PAINTING WORKS
2 | PAINTING
2.1 | GENERAL
(a) All painting work shall be carried out in accordance with the Manufacturers specifications & instructions.
(b) External exposed wall surfaces shall be painted with one coat of primer and two finishing coats of external wall paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
(b) External exposed floor surfaces shall be painted with one coat of primer and two finishing coats of external floor paint (Sherwin Williams) as specified to manufacturers instructions.
* Primer - Rust proof Enamel paint
* Wall paint - Rust proof Enamel paint
* Floor paint - Rust proof Enamel paint
2.2 | Base
1 | Tank base (colour code - Positive Red SW 6871) | m² | 33.4
2.3 | Wall
1 | Tank wall interior and exterior (colour code - Positive Red SW 6871) | m² | 266.5
2.4 | Roof painting
1 | Tank roof painting interior and exterior (colour code - Positive Red SW 6871) | m² | 133.52
2.5 | Miscellaneous
1 | Railing, caged ladder, manhole and all other accessories and fixtures (colour code - Positive Red SW 6871) | LS | 1
TOTAL OF BILL

## BOQ (PUMP ROOM)
BILL OF QUANTITIES FOR PUMP ROOM
SL.No | Description | Unit | Qty | Rate | Amount
GENERAL
Rate shall include for mobilisation, site management costs, materials, labour, water, electricity, site clearing including removing site vegetation & trees, grubbing up roots, filling voids, levelling, cleaning & proper disposal, demobilisation, vehicles, vessels, permits, equipment & tools including all necessary transport & storage required for the proper execution & completion of the works.
1. GROUND WORKS
1 | EXCAVATION
Note: Excavation quantities are measured to the faces of concrete members. The quantities given are the bulk before excavating and no allowance is made for subsequent variations to bulk or for extra space for working space or to accomodate earthwork support. Rate shall include for all additional excavation required to place the formwork/shuttering, working space and dewatering the trenches for the required days.
Rate shall also include for providing proper earthwork support to faces of excavations, disposal of surplus excavated materails offsite to a selected location in the island.
Rate shall also include for filling to excavation with available sand arisen from excavations, in 150mm thick layers well ram and consolidate. Rate shall also include for Compacting Bottoms of excavations. Rate shall also include for leveling & compaction to achieve appropriate degree of compaction. Compaction shall be done using appropriate method such as compactor to achieve 150Kpa strength.
1 | Excavating for foundation beams as shown in drawing. | m³ | 1.24
2 | DPC
Note: Rates shall include for: dressing around and sealing to avoid all penetrations
1 | Polythene DPC membrane below RCC foundation beams and slab (500 gauge - black color) | m² | 16.38
2. CONCRETE WORKS
2.1 | GENERAL
(a) The volume of concrete measured includes that occupied by reinforcement, other metal sections & chamfers or internal splays each not exceeding 0.01m² in cross-section area.
(b) Rate shall include for: formwork, provision to place in position; casting of all required items and finishing after removal of formwork and additional concrete required to conform to structural and excavated tolerances.
(c) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:4 by volume
(d) Rate shall also include for application of two coats of bitumastic paint (Fosroc or equivalent) to all concrete surfaces below ground level or in contact with soil.
(e) Any required chemical bonding agent shall be approved by client.
2.2 | LEAN CONCRETE
Note: Quantity is measured to the edges of concrete members. Rate shall be inclusive of any additional concrete required to place the formwork.
1 | Beds, thickness 50mm, below foundation ring beam, bund slab & foundation slab | m³ | 0.21
2.3 | REINFORCED CONCRETE
In-situ reinforced concrete to:
(a) Rates shall include for reinforcing bars: cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports, hooks and tying wire, spacers and chairs and any wastage.
(b) All reinforcing bars except 6mm dia bars shall be high strength deformed bars
1 | Foundation beam | m³ | 1.23
2 | Slab | m³ | 1.64
3 | Column | m³ | 0.552
4 | Roof beam | m³ | 1.24
1 | Lintel/Capping beam/Stiffener column | LS | 1
3. MASONRY WORKS
3.1 | GENERAL
(a) Rate shall include for: All neccesary equipment, tools, materials, supplying, handling charges.
(b) All painting work shall be carried out in accordance with the Manufacturers specifications & instructions.
(c) External exposed wall surfaces shall be painted with one coat of primer and two finishing coats of external wall paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
(d) External exposed floor surfaces shall be painted with one coat of primer and two finishing coats of external floor paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
3.2 | Masonry walls
1 | 100mm solid masonry walls | m² | 60.24
3.2 | Plastering
1 | 25mm plastering (interior and exterior) | m² | 120.48
3.2 | Painting
1 | Interior wall painting (colour code - Cappucino white 45YY 74/073 or equivalent) | m² | 60.24
2 | Exterior wall painting (colour code - Cappucino white 45YY 74/073 or equivalent) | m² | 60.24
4. ROOFING WORKS
1 | Supply and install roofing structure as shown on drawing. Rates shall inlude all timber members, laps, connections and all items shown in drawing. | LS | 1
1 | Supply and install lysaght roofing sheets over areas shown on drawing. Rates shall inlude all laps, connections and provision of intermediate supports to firmly fix the elements to the main structure. Rate shall include ridge capping, flashing, insulation and other necessary to make roofing water proof. | m2 | 23.8
2 | Supply and install gutter system with downpipes as shown on drawing. Rates shall include for fascia board, rain water down pipes at each end with soakpits at ground level. | m | 7
5. DOORS AND WINDOWS
5.1 | GENERAL
(a) Rate shall include for: All neccesary equipment, tools, handling charges & fixing.
(b) Doors and windows shall be fabricated after taking site measurements.
(c) Alunimium members and panels shall be high quality standard.
5.2 | Doors and windows
1 | Doors | No | 2
1 | Ventilation louver windows | No | 2
6. ELECTRICAL WORKS
6.1 | GENERAL
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus soil
(c) Rates shall include for electrical conduits, fittings, equipment and similar items shall include for: all fixings to various building surfaces
(d) A point wiring for power points is measured as one point for each socket; other end of wire is not included in the quantity.
(e) Rates shall include for supply and complete installation
(f) Rate shall include conduit pipes, sunk boxes, switches, screws, nuts, bolts etc.. Complete.
6.2 | Electrical Wiring and fixtures
1 | Distribution board | No | 1
2 | CF Tube Light (CL3) | No | 2
3 | LED water proof wall mount light (WL1) | No | 1
4 | LED type Emergency Light (with weather proof socket) (EL1) | No | 2
5 | 1 Gang switch | No | 2
6 | 2 Gang 13A switched socket outlet | No | 2
7 | 2 Gang 15A switched socket outlet | No | 1
8 | Install earthing rods according to STELCO approved standards | No | 1
6.2 | Diesel pump
1 | Supply and installation of diesel oil pump. Pump shall be able to deliver diesel from pump room to power house, and to incinerator. Provision shall be made for pipe connection from both new tank and existing tank (moved to new location). Specifications of pump shall be submitted for client approval. | No | 1
TOTAL OF BILL

## BOQ (EXST TANK 01)
BILL OF QUANTITIES FOR RELOCATION OF EXISTING FUEL TANK 01 (8,000L)
SL.No | Description | Unit | Qty | Rate | Amount
GENERAL
Rate shall include for mobilisation, site management costs, materials, labour, water, electricity, site clearing including removing site vegetation & trees, grubbing up roots, filling voids, levelling, cleaning & proper disposal, demobilisation, vehicles, vessels, permits, equipment & tools including all necessary transport & storage required for the proper execution & completion of the works.
1. GROUND WORKS
1 | EXCAVATION
Note: Excavation quantities are measured to the faces of concrete members. The quantities given are the bulk before excavating and no allowance is made for subsequent variations to bulk or for extra space for working space or to accomodate earthwork support. Rate shall include for all additional excavation required to place the formwork/shuttering, working space and dewatering the trenches for the required days.
Rate shall also include for providing proper earthwork support to faces of excavations, disposal of surplus excavated materails offsite to a selected location in the island.
Rate shall also include for filling to excavation with available sand arisen from excavations, in 150mm thick layers well ram and consolidate. Rate shall also include for Compacting Bottoms of excavations. Rate shall also include for leveling & compaction to achieve appropriate degree of compaction. Compaction shall be done using appropriate method such as compactor to achieve 150Kpa strength.
1 | Excavating for foundation beams as shown in drawing. | m³ | 0.89
2. CONCRETE WORKS
2.1 | GENERAL
(a) The volume of concrete measured includes that occupied by reinforcement, other metal sections & chamfers or internal splays each not exceeding 0.01m² in cross-section area.
(b) Rate shall include for: formwork, provision to place in position; casting of all required items and finishing after removal of formwork and additional concrete required to conform to structural and excavated tolerances.
(c) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:4 by volume
(d) Rate shall also include for application of two coats of bitumastic paint (Fosroc or equivalent) to all concrete surfaces below ground level or in contact with soil.
(e) Any required chemical bonding agent shall be approved by client.
2.3 | REINFORCED CONCRETE
In-situ reinforced concrete to:
(a) Rates shall include for reinforcing bars: cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports, hooks and tying wire, spacers and chairs and any wastage.
(b) All reinforcing bars except 6mm dia bars shall be high strength deformed bars
1 | Perimeter beam | m³ | 1.7
2 | Slab | m³ | 2.06
2 | Wall | m³ | 1.99
3. PAINTING WORKS
3 | PAINTING
3.1 | GENERAL
(a) All painting work shall be carried out in accordance with the Manufacturers specifications & instructions.
(b) External exposed wall surfaces shall be painted with one coat of primer and two finishing coats of external wall paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
(b) External exposed floor surfaces shall be painted with one coat of primer and two finishing coats of external floor paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
* Primer - Loxon (Concrete & Masonry primer/sealer interior/exterior latex A24W8300)
* Wall paint - A-100
* Floor paint - Porch & Floor Enamel (Interior/Exterior Acrylic Satin A32-200 series)
3.2 | Floor
1 | Bund slab & foundation slab (colour code - Earl Gray SW7660 or equivalent) | m² | 13.69
3.3 | Wall
1 | Bund wall & sides of foundation slab (colour code - Earl Gray SW7660 or equivalent) | m² | 41.44
4. MISCALLANEOUS WORKS
4.1 | STEEL TANK
1 | Relocation of existing tank from existing location to new tank foundation as shown in the drawing & specifiction. Rate shall include all preparations, removing tank from existing location, transfer and installation of tank, including painting (Sherwin williams steel paint, color code Positive Red SW 6871 or equivalent) complete. | No | 1
2 | Hydro-testing the tank to assure leak proof. Leak testing methodology shall be submitted as per API standard for client approval. | No | 1
TOTAL OF BILL

## BOQ (EXST TANK 02)
BILL OF QUANTITIES FOR RELOCATION OF EXISTING FUEL TANK 02 (24,000L)
SL.No | Description | Unit | Qty | Rate | Amount
GENERAL
Rate shall include for mobilisation, site management costs, materials, labour, water, electricity, site clearing including removing site vegetation & trees, grubbing up roots, filling voids, levelling, cleaning & proper disposal, demobilisation, vehicles, vessels, permits, equipment & tools including all necessary transport & storage required for the proper execution & completion of the works.
1. GROUND WORKS
1 | EXCAVATION
Note: Excavation quantities are measured to the faces of concrete members. The quantities given are the bulk before excavating and no allowance is made for subsequent variations to bulk or for extra space for working space or to accomodate earthwork support. Rate shall include for all additional excavation required to place the formwork/shuttering, working space and dewatering the trenches for the required days.
Rate shall also include for providing proper earthwork support to faces of excavations, disposal of surplus excavated materails offsite to a selected location in the island.
Rate shall also include for filling to excavation with available sand arisen from excavations, in 150mm thick layers well ram and consolidate. Rate shall also include for Compacting Bottoms of excavations. Rate shall also include for leveling & compaction to achieve appropriate degree of compaction. Compaction shall be done using appropriate method such as compactor to achieve 150Kpa strength.
1 | Excavating for foundation beams as shown in drawing. | m³ | 1.43
2. CONCRETE WORKS
2.1 | GENERAL
(a) The volume of concrete measured includes that occupied by reinforcement, other metal sections & chamfers or internal splays each not exceeding 0.01m² in cross-section area.
(b) Rate shall include for: formwork, provision to place in position; casting of all required items and finishing after removal of formwork and additional concrete required to conform to structural and excavated tolerances.
(c) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:4 by volume
(d) Rate shall also include for application of two coats of bitumastic paint (Fosroc or equivalent) to all concrete surfaces below ground level or in contact with soil.
(e) Any required chemical bonding agent shall be approved by client.
2.3 | REINFORCED CONCRETE
In-situ reinforced concrete to:
(a) Rates shall include for reinforcing bars: cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports, hooks and tying wire, spacers and chairs and any wastage.
(b) All reinforcing bars except 6mm dia bars shall be high strength deformed bars
1 | Perimeter beam | m³ | 2.86
2 | Slab | m³ | 5.58
2 | Wall | m³ | 3.57
3. PAINTING WORKS
3 | PAINTING
3.1 | GENERAL
(a) All painting work shall be carried out in accordance with the Manufacturers specifications & instructions.
(b) External exposed wall surfaces shall be painted with one coat of primer and two finishing coats of external wall paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
(b) External exposed floor surfaces shall be painted with one coat of primer and two finishing coats of external floor paint (Sherwin Williams or equivalent) as specified to manufacturers instructions.
* Primer - Loxon (Concrete & Masonry primer/sealer interior/exterior latex A24W8300)
* Wall paint - A-100
* Floor paint - Porch & Floor Enamel (Interior/Exterior Acrylic Satin A32-200 series)
3.2 | Floor
1 | Bund slab & foundation slab (colour code - Earl Gray SW7660 or equivalent) | m² | 37.21
3.3 | Wall
1 | Bund wall & sides of foundation slab (colour code - Earl Gray SW7660 or equivalent) | m² | 82.96
4. MISCALLANEOUS WORKS
4.1 | STEEL TANK
1 | Relocation of existing tank from existing location to new tank foundation as shown in the drawing & specifiction. Rate shall include all preparations, removing tank from existing location, transfer and installation of tank, including painting (Sherwin williams steel paint, color code Positive Red SW 6871 or equivalent) complete. | No | 1
2 | Hydro-testing the tank to assure leak proof. Leak testing methodology shall be submitted as per API standard for client approval. | No | 1
TOTAL OF BILL