## Cover
BILL OF QUANTITIES
PROJECT: HITHADHOO ISLAMIC CENTER
PROPOSED TWO-STOREY BUILDING
CLIENT: MINISTRY OF ISLAMIC AFFAIRS
OCTOBER 2022

## SUMM-GRAND
PROJECT: HITHADHOO ISLAMIC CENTER
CONSTRUCTION OF 02 STOREY BUILDING
GRAND SUMMARY
SL.NO | BILL NAME | AMOUNT (MRF)
1 ) | SUMMARY OF MOSQUE
2 ) | SUMMARY OF MINARET
GRAND TOTAL

## SUMM-MOSQUE
PROJECT: HITHADHOO ISLAMIC CENTER
CONSTRUCTION OF 02 STOREY BUILDING
SUMMARY OF BILLS OF QUANTITIES (MOSQUE)
SL.NO | BILL NAME | AMOUNT (MRF)
1 ) | TOTAL OF BILL NO. 01 (PRELIMINARIES)
2 ) | TOTAL OF BILL NO. 02 (GROUND WORKS)
3 ) | TOTAL OF BILL NO. 03 (CONCRETE WORKS)
4 ) | TOTAL OF BILL NO. 04 (MASONRY AND PLASTERING)
5 ) | TOTAL OF BILL NO. 05 (METAL WORKS)
6 ) | TOTAL OF BILL NO. 06 (WOOD WORKS & ROOFING)
7 ) | TOTAL OF BILL NO. 07 (CEILINGS)
8 ) | TOTAL OF BILL NO. 08 (DOORS AND WINDOWS)
9 ) | TOTAL OF BILL NO. 9 (FINISHES)
10 ) | TOTAL OF BILL NO. 10 (PAINTING)
11 ) | TOTAL OF BILL NO. 11 (HYDRAULICS AND DRAINAGE)
12 ) | TOTAL OF BILL NO. 12 (ELECTRICAL INSTALLATIONS)
13 ) | TOTAL OF BILL NO. 13 (MECHANICAL INSTALLATION)
14 ) | TOTAL OF BILL NO .14 (SOLAR SYSTEM)
15 ) | TOTAL OF BILL NO. 15(LIFT)
16 ) | TOTAL OF BILL NO. 16 (ADDITIONS)
17 ) | TOTAL OF BILL NO. 17(OMISSIONS)
GRAND TOTAL

## BOQ-MOSQUE
BILLS OF QUANTITIES
CONSTRUCTION OF 02 STOREY BUILDING
SL.NO | DESCRIPTION | QTY | UNIT | LABOUR RATE | MATERIAL RATE | LABOUR AMOUNT | MATERIAL AMOUNT | TOTAL AMOUNT
Bill No: 01
PRELIMINARIES
GENERAL NOTES
Abbreviations
m - metre
Nos - numbers
m³ - cubic metre
m² - square metre
lm - Linear metre
kg - Kilograms
incl. - including
mm - millimetre
SS - Stainless Steel
GI - Galvanised steel
(a) The General Contractor is to provide any sum he considers necesssary in complying with the following requirements and terms. The monetary value of any item which is left unpriced shall be deemed to have been included in the rates of each item of work in the Bill of Quantities.
(b) The Contractor shall be deemed to have satisfied himself as to the correctness and sufficiency of his tender for the works and of the rates and prices stated in the priced Bill of Quantities, which rates and prices shall be inclusive of all ancillary and other works and expenditure whether separately or specifically mentioned or described in the Contract Documents or not, which are either indispensably necessary to carry out and bring completion the works described in the Contract Documents or which may continently become necessary to overcome difficulties’ before completion.
(c) Where any clause or item in these Bills of Quantities is not priced, it shall be deemed that the cost of such clause or item has been allowed elsewhere within these Bills of Quantities. No subsequent claim against such item or clause will be considered.
(d) The General Contractor is requested to check the number of pages of the Bill of Quantities and if any page is missing or duplicating or if any figure is indistinctive, he shall notify the Project Manager who will rectify the matter. No claims for loss consequent upon the General Contractor's failure to observe this Clause will be considered.
(e) Approved equivalent” shall mean material, product, component or assembly having a similar standard of quality and identical level of performance in all respect of the materials and/or product specified. The contractor shall ensure such instruction adhered when submitting the sample for approval. Any sub standard materials and performance will be subjected to a cost reduction by Engineer.
(f) Wherever the term "Provisional Sum" occur in the Main Works, the General Contractor shall provide cost on such items. The cost indicated on such items will be subject to remeasurement based on the actual quantity installed. Provisional Sums may be used in whole or in part as directed in writing by the Project Manager. The balance shall be deductible from the Contract Price.
(g) All items in the Bill of Quantities shall be priced in detail not grouped together as total prices for any trades or sections.
(h) The items of work and corresponding quantities indicated in the Bill of Quantities should remain unchanged.
(i) The General Contractor shall be deemed to have taken into account all possible inclement weather when preparing his Bid and shall not be entitled to extra payment by reason of the occurrence or effect of excessive wind, typhoon or other meteorogical phenomena.
(j) The General Contractor shall be responsible for checking all drawings issued to him and if he finds discrepancies in the drawings he shall, before proceeding with the works, inform the Engineer of such discrepancies and the Engineer's ruling shall be taken as final. No claims by the Contractor for any extra costs incurred as a result of discrepancies in the Contract Drawings will be entertained if he fails to inform the Engineer of such discrepancies before proceeding with the Works.
(k) The rates and prices inserted shall be deemed to have allowed for compliance with the above stipulations and other documents forming part of the Contract. All rates and prices entered against items measured and described in the Bills of Quantities shall be for the full inclusive value of the finished work described or shown on the Drawings or stipulated in the Specifications.
1.2 | Site Management Costs
1 ) | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone,fax,hoardings and similar. | 1 | item
1.3 | Sign Board
1 ) | Allow for sign board (1500 mm x 900 mm) Design should be approved by client. | 1 | no
1.4 | Clean - up
1 ) | Allow for clean - up of completed works and site upon completion. | 1 | item
1.5 | INSURANCE, BONDS, GUARANTEES AND WARRANTIES
1.5.1 | Insurance as stated in the general conditions (Clause 13) | 1 | item
1.6 | AS-BUILT
1.6.1 | The contractor shall provide all "As-built" drawings and operation and maintenance manuals, which shall include 1-set hard copy orginal & soft copy for Architectural/Civil (with complete products specs, origin,supplier name & details) and 1 set hard copy original | 1 | item
As built drawing as stated in Particular Conditions 55.1
1.7 | TEMPORARY FENCING & HOARDING
1.7.1 | Supply, erect & maintenance of a fence through out the construction period & hoarding all along the perimeter of the site. Hoarding shall be according to Regulation (2019/R-156) Hoarding guideline under section 12. | 1 | item
TOTAL OF BILL NO. 01 (PRELIMINARIES)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 02
GROUND WORKS
2.1 | GENERAL
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating and disposing surplus soil.
2.2 | SITE CLEARING
| Clear the area of site from rubbish and vegetable matters, stumps, roots. Demolition shall be included (if any) | 3716.12 | m²
2.3 | EXCAVATION
Excavation quantities are measured to the faces of concrete members. Rates shall include for all additional excavation required to place the formworks
1 ) | Excavation for Footings and Tie beams | 675.96 | m³
2.4 | BACK FILLING
(a) Rates shall include for: levelling, grading, trimming, compacting and similar.
(b) Ground need to be compacted to the required density by the consultant.
1 ) | Earth Filling as per drawings | 2020 | m²
2 ) | 50 mm thick sand blinding layer to receive damp proof membrane | 2020 | m²
2.5 | DAMP PROOF MEMBRANE
(a) Rates shall include for: dressing around and sealing to all penetrations, laps and turnups
1 ) | Polythene damp proof membrane (500 gauge) laid on blinding layer under footings, tie beams and ground floor slab | 2472 | m²
2.6 | DEWATERING
| This item shall include for all the piping, pumps, etc. Water needs to be pumped to an assigned area as per local regulation. | 1 | Item
TOTAL OF BILL NO. 02 (GROUND WORKS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 03
CONCRETE WORKS
3.1 | GENERAL
(a) Concrete is measured net without deduction for the volume of reinforcement.
(b) All concrete admixtures shall be administered in accordance with manufacturer's recommendations.
(c) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:3:6 by volume
(d) Rates for concrete shall include;
1) mixing, depositing, hoisting or pumping and placing in position
2) Compacting by suitable means
3) Packing and tampering around reinforcement including mechanical vibration
4) Curing and protection
5) Removing or cutting rebates, grooves, chases, mortises and the like, including making good after removal of formwork and casting in all required items
6) All formworks, reinforcements as described in FORMWORK (3.2) & REINFORCEMENT (3.3).
7) Additional concrete required to place the formwork and to conform to structural and excavated tolerances.
(e) All concrete test according to the engineers instructions. Test for estimation on strength of concrete in structure, compressive strength test shall be conducted for prepared test pieces (150 x 150mm Test Cubes) on the 07th day (3nos cubes) and 28th day (03nos cubes). Strength test shall be conducted for Foundation works, Columns, Slabs and Slab beams according to British Standards.
(f) Rates shall be inclusive for any additional concrete required to place the formwork.
3.2 | FORMWORK
(a) | Approved film coated 12mm plywood or 3mm thick steel plate shuttering and centering for structural concrete work in locations called for including strutting, propping, bracing, bolting, wedging, casing, striking, removal etc. complete for any size, section, thickness. Props shall consist of well designed steel pipes adequately braced (wooden ballies as props shall not be permitted).
(b) | Rates shall include formwork shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork.
(c) | Allow for forming grooves, drip course, chamfers, cut-outs, openings etc. where called for and for dressing with approved shuttering oil to prevent adhesion. The finished surface should be smooth and as per direction as well as to the Engineer's approval. Rate shall include all cost for shuttering and deshuttering as well.
3.3 | REINFORCEMENT
Main reinforcement steel shall be high tensile steel hot rolled deformed bars complying with BS 4449, Characteristic strength not less than 460N/mm2
Stirrups shall be hot rolled mildsteel round bars complying with BS 4449, Characteristic strength not less than 250N/mm2
Rates shall include for; distribution steel, cleaning, fabrication, placing, the provision for all necessary temporary fixings, and supports including chairs and tie wire , laps and wastage.
No allowance has been made in the weight of steel reinforcement for rolling margin, tying wires, spacers, chairs and weight of weld etc.
Rates for bar reinforcement shall include;
(1) allowance for rolling margin, weight of welds and wastage
(2) cutting to length and fabricating including bending to various bend and radii
(3) placing in position, holding and supporting
(4) providing and tying with galvanised steel wire at all intersections
(5) providing and seating of spacer blocks and chairs
(6) Providing all necessary laps, bends and anchorages including stirrup rebars, weld connections..etc
(7) cleaning by wire brushing
1 ) | Allow for concrete testing | 1 | item
3.1 | Lean Concrete
| 50mm thick lean concrete under the strip footing and tie beam with a mix of 1:2:6 | 451 | m²
3.2 | Reinforced Concrete
In-situ reinforced concrete to:
*Add water proofing compound / admixture to concrete mix for walls GL and Roof Slabs
3.2.1 | Foundation
1 ) | Footings, Foundation beams, Foundation strips | 197.66 | m³
2 ) | stair starter, lift walls | 10 | m³
3 ) | Columns upto GFFL | 12.08 | m³
3.2.2 | Ground Floor
1 ) | RCC Ground Slab 75 mm thick, (Rate shall include for reinforcement and shuttering required as per the drawings) | 128 | m³
2 ) | staircases | 15 | m³
3 ) | Columns | 43.48 | m³
4 ) | Attched beams and slab at 3450 mm level | 29.56 | m³
5 ) | Attched beams and slab at 4500 mm level | 289.3 | m³
3.2.3 | First Floor
1 ) | Columns | 34.36 | m³
2 ) | Attched beams and slab at level | 137 | m³
3 ) | Arches | 10 | m³
3.3 | Formwork
a) Rates shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes, removal of formwork and normal practices used.
3.3.1 | Foundation
1 ) | Footings, Foundation beams, Foundation strips | 773.08 | m²
2 ) | stair starter, lift walls | 150 | m²
3 ) | Columns upto GFFL | 135.8 | m²
3.3.2 | Ground Floor
1 ) | staircases | 80 | m²
2 ) | Columns | 488.85 | m²
3 ) | Attched beams and slab at 3450 mm level | 240.2 | m²
4 ) | Attched beams and slab at 4500 mm level | 1883.85 | m²
3.3.3 | First Floor
1 ) | Columns | 332.82 | m²
2 ) | Attched beams and slab at level | 958.05 | m²
3 ) | Arches | 198 | m²
3.4 | Reinforcement
a) Rates shall include for: cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and chair supports, laps, and wastages.
3.4.1 | Foundation
1 ) | Footings, Foundation beams, Foundation strips
| 20 mm dia bars | 2964 | kgs
| 16 mm dia bars | 8027 | kgs
| 12 mm dia bars | 1344 | kgs
| 10 mm dia bars | 3739 | kgs
| 6 mm dia bars | 2149 | kgs
2 ) | stair starter, lift walls
| 12 mm dia bars | 1620 | kgs
| 10 mm dia bars | 205 | kgs
3 ) | Columns upto GFFL
| 20 mm dia bars | 2727 | kgs
| 16 mm dia bars | 847 | kgs
| 12 mm dia bars | 263 | kgs
| 10 mm dia bars | 178 | kgs
| 6 mm dia bars | 768 | kgs
3.4.2 | Ground Floor
1 ) | staircases
| 12 mm dia bars | 2486 | kgs
| 10 mm dia bars | 75 | kgs
2 ) | Columns
| 20 mm dia bars | 5454 | kgs
| 16 mm dia bars | 1694 | kgs
| 12 mm dia bars | 526 | kgs
| 10 mm dia bars | 356 | kgs
| 6 mm dia bars | 1536 | kgs
3 ) | Attched beams and slab at 3450 mm level
| 20 mm dia bars | 712 | kgs
| 16 mm dia bars | 241 | kgs
| 12 mm dia bars | 383 | kgs
| 10 mm dia bars | 2880 | kgs
| 6 mm dia bars | 215 | kgs
4 ) | Attched beams and slab at 4500 mm level
| 25 mm dia bars | 11365 | kg
| 20 mm dia bars | 312 | kg
| 16 mm dia bars | 1682 | kg
| 12 mm dia bars | 12846 | kg
| 10 mm dia bars | 17945 | kg
| 6 mm dia bars | 1388 | kg
3.4.3 | First Floor
1 ) | Columns
| 20 mm dia bars | 4980 | kgs
| 16 mm dia bars | 354 | kgs
| 12 mm dia bars | 114 | kgs
| 10 mm dia bars | 356 | kgs
| 6 mm dia bars | 924 | kgs
2 ) | Attched beams and slab at level
| 25 mm dia bars | 5020 | kgs
| 20 mm dia bars | 4070 | kgs
| 16 mm dia bars | 1728 | kgs
| 12 mm dia bars | 1234 | kgs
| 10 mm dia bars | 11550 | kgs
| 6 mm dia bars | 996 | kgs
3.5 | OTHER CONCRETE WORKS
1 ) | Lintel Beam as per the specifications and drawings | 1 | Item
2 ) | Sill Beam as per the specifications and drawings | 1 | Item
3 ) | Steps as shown | 1 | Item
4 ) | Terrace Parapet walls including RC gutter as shown | 1 | Item
5 ) | Doors / Windows concrete fins | 1 | Item
6 ) | Ramps as shown | 1 | Item
3.6 | WATER PROOFING
Rate shall include for: dressing arround and sealing to all penetrations
1 ) | Apply bituminous type waterproofing to all surfaces of concrete below ground level in accordance with the specifications and manufacturer's instructions | 1 | item
2 ) | Apply waterproofing to all surfaces of concrete roof level in accordance with the specifications and manufacturer's instructions | 1 | item
3 ) | Apply waterproofing to all surfaces of toilets and balconies in accordance with the specifications and manufacturer's instructions | 1 | item
TOTAL OF BILL NO. 03 (CONCRETE WORKS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 04
MASONRY AND PLASTERING
4.1 | General
a) Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good.
4.2 | Cement block work
4.2.1 | Solid blocks, laid on and incl. 1:5 Cement Mortor, tie rods, compression gap filler, nylon / plastic mesh as specified.
All External walls
1 ) | Below Ground level (200 mm thick walls) | 180 | m²
2 ) | Ground Floor (200 mm thick walls) | 515 | m²
3 ) | Ground Floor (150 mm thick walls) | 317 | m²
4 ) | First Floor (200 mm thick walls) | 491 | m²
4.2.2 | 150mm wide solid blocks, laid on and incl. 1:5 Cement Mortor, tie rods, compression gap filler, nylon / plastic mesh as specified.
All Internal walls
1 ) | Ground Floor | 665 | m²
2 ) | First Floor | 275 | m²
4.3 | Plastering
4.3.1 | a) 25mm cement plastering on external walls and concrete surfaces with 1:4 Cement mortor mix as specified incl. wire mesh at joints of concrete surfaces and walls (first,second coats).
1 ) | Below Ground level | 205 | m²
2 ) | Ground Floor | 895 | m²
3 ) | First Floor | 539 | m²
4.3.2 | a) 15mm cement plastering on internal walls and concrete surfaces with 1:4 Cement mortor mix as specified incl. wire mesh at joints of concrete surfaces and walls (one coat).
1 ) | Ground Floor | 2447 | m²
2 ) | First Floor | 1029 | m²
4.4 | Cement Screed Finish
4.4.1 | 35mm thick Cement screeding on the
concrete floor with 1:4 cement mortar
mix incl. trowel finish; General Areas
1 ) | Ground Floor | 1523 | m²
2 ) | First Floor | 1625 | m²
3 ) | Terrace Floor | 525 | m²
4.5 | Boundary wall
1 ) | Boundary wall with 150 mm thick block works as per the drawings (Rate shall include Foundation beam, RC columns coping etc) | 410 | m²
2 ) | Plastering on both sides | 840 | m²
TOTAL OF BILL NO. 04 (MASONRY AND PLASTERING)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 05
METAL WORKS
5.1 | General
a) Rates shall include for: all fabrication work, welding, marking, drilling for bolts incl. those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
b) Rates shall include for fabrication and erection and temporary supports and fixing into position.
5.2 | Roof frame
Roof Truss (RT1) with 75 X 3.2 mm thick and 68 X 3.2 mm thick GI Pipes as shown in drawings (rate shal include for all fabrication and fixings etc)
1 ) | Truss TR1 | 20 | Nos
2 ) | 50 X 150 X 3.2 mm 'C' purlin as shown in drawings | 1040 | m
5.3 | Mosque Dome
1 ) | Metallic dome as specified in the drawings for Minaret | 1 | Item
5.4 | Railings
1 ) | Staircase railing as per drawings | 1 | Item
2 ) | Ramp railing as per drawings | 1 | Item
3 ) | Disabled toilet guide rail | 1 | Item
TOTAL OF BILL NO. 05 (METAL WORKS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 06
WOOD WORKS & ROOFINGS
6.1 | General
a) Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
b) Rate shall include for: timber priming and all painting as specified in the drawing
6.2 | Roof frame & coverings
1 ) | MSP or Equivalent Roofing | 832 | m²
2 ) | 50 mm thick heat insulation with Al. foil on both sides and wire mesh | 832 | m²
3 ) | End flashing | 121 | m
4 ) | Fascia board | 66 | m
5 ) | Down pipes | 1 | Item
6.3 | Wooden stage
1 ) | Wooden stage with 25 mm thick plywood, timber joist including timber staircase etc as shown in drawings | 1 | Item
TOTAL OF BILL NO. 06 (WOOD WORKS & ROOFING)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 07
CEILING
7.1 | General
a) Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
b) Rate shall include for: timber priming and all painting as specified in the drawing
7.2 | Ceiling
1 ) | Concelead ceiling at first floor | 820 | m²
TOTAL OF BILL NO. 07 (CEILINGS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 08
DOORS AND WINDOWS
8.1 | General
a) Rates shall include for: locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
b) All Aluminium windows shall be white powder coated aluminium.
c) All timber doors shall be solid timber panneled door with varnish finish.
d) All glazing shall be 6mm green Tinted.
(Profiles to be chosen by client).
8.2 | Door Units
1 ) | Door D1a | 1 | nos
2 ) | Door D1 | 8 | nos
3 ) | Door D2 | 2 | nos
4 ) | Door D3 | 12 | nos
5 ) | Door D4 | 5 | nos
6 ) | Door D5 | 5 | nos
7 ) | Door D6 | 3 | nos
8 ) | Door D7 | 2 | nos
9 ) | Door D8 | 2 | nos
10 ) | Door D9 | 7 | nos
11 ) | Door D10 | 10 | nos
8.4 | Window Units
1 ) | Window W1 | 13 | nos
2 ) | Window W2 | 8 | nos
3 ) | Window W3 | 19 | nos
4 ) | Window W4 | 29 | nos
5 ) | Window W5 | 2 | nos
6 ) | Window W6 | 6 | nos
7 ) | Window W7 | 2 | nos
8 ) | Window W8 | 12 | nos
TOTAL OF BILL NO. 08 (DOORS AND WINDOWS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 9
FINISHES
9.1 | General
a) Rates shall include for: fixing, bedding, grouting, pointing, finishing and any other similar works to ensure the required finish.
b) Rates shall include for all other beading works required at the corneres
9.2 | Ground Floor
1 ) | 300 X 300 mm porcelain tiles including 100 mm high skirting for general area | 1108 | m²
2 ) | 300 X 300 mm ceramic Non-skid tiles for toilets/ ablution areas | 125 | m²
3 ) | 300 X 300 mm ceramic glazed tiles for toilets/ ablution wall areas | 385 | m²
4 ) | 300 X 300 mm ceramic out door tiles with skirting | 38 | m²
5 ) | 300 X 300 mm Homogeneous Non-skid tiles for staircases including risers, landings, skirting etc | 510 | m²
9.3 | First Floor
1 ) | 300 x 600 Homogeneout tiles black & white as per the design at prayer areas | 580 | m²
2 ) | 300 x 600 Homogeneout tiles black / white as per the design at prayer area walls | 185 | m²
3 ) | 300 X 300 mm porcelain tiles including 100 mm high skirting for general area | 131 | m²
4 ) | 300 X 300 mm ceramic out door tiles with skirting | 410 | m²
5 ) | Carpet floor finish at prayer area | 420 | m²
9.4 | Terrace Floor
1 ) | 300 X 300 mm ceramic out door tiles with skirting | 535 | m²
9.5 | Paving Blocks
1 ) | 65X100X200 mm paving blocks in compound area | 1698 | m²
TOTAL OF BILL NO. 9 (FINISHES)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 10
PAINTING
10.1 | General
a) Rates shall include for: the provition, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and / or making floors, fittings and similar work, removing and replacing door and window furniture
b) All painting work shall be carried in accordance with the specifications.
Painting system shall be Nippon or Equivalent
10.2 | Walls
Weather proof emulsion paint system with textured finish on plastered and concrete surfaces of external and normal emulsion paint on internal walls.
10.2.1 | External painting 1 coat of wall sealer, 1 coat tex compound & 2 coats of paints
1 ) | Ground Floor | 895 | m²
2 ) | First Floor | 539 | m²
3 ) | Parapet walls | 1 | Item
10.2.2 | Emulsion paint putty finish system on plastered and concrete surfaces of internal walls.
Internal Painting 1 coat of wall sealer & 2 coats of paints
1 ) | Ground Floor | 2447 | m²
2 ) | First Floor | 1029 | m²
10.3 | Ceilings
Emulsion paint putty finish on concrete slab and beams, plywood / cement fibre board of all internal surfaces.
1 coat of primer & 2 coats of paints
1 ) | Emulsion putty paint finish | 3473 | m²
10.4 | Boundary wall
1 ) | Boundary wall painting | 840 | m²
TOTAL OF BILL NO. 10 (PAINTING)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 11
HYDRAULICS & DRAINAGE
11.1 | General
a) Rates shall include for: sockets, running joints, connections, elbows, junctions, reducers, expansion joints; backnuts and similar; incidental fittings, clips, saddles, brackets, straps, hanges, screws, nails and fixing complete, including cutting and
11.2 | Ground water supply pipework
| Allow for water connection to fixtures from ground water well. | 1 | item
11.3 | Fresh water supply pipework
1 ) | Allow for water connection to fixtures from future fresh water source | 1 | item
11.4 | Sanitary Fixtures & Accessories
Sanitary Fixtures complete including brackets flush pipes, overflows and washers etc.
1 ) All toilet fittings shall be "Cotto" or equivalent - chrome plated
2 ) All toilet fixtures shall be "Cotto" or equivalent brand.
3 ) All piping shall be of UPVC
4 ) All kitchen sinks shall be of SS type with chrome plated taps.
5 ) All water pumps shall be of "Davie Jet" brand or equivalent.
1 ) | Water Closet | 15 | nos
2 ) | Wash basin | 5 | nos
3 ) | Wash basin tap | 5 | nos
4 ) | Muslim Shower | 15 | nos
5 ) | Floor waste with gully trap | 22 | nos
| Floor waste with gully trap drain 38 mm dia | 24 | nos
6 ) | Mirror with accessories | 5 | nos
7 ) | Water Taps / Faucet | 46 | nos
8 ) | Valves | 65 | nos
11.5 | Pumping System
Supply and installation of water pump complete including connecting valves to pipework and electricity as per requirements.
1 ) | Well water pump | 1 | nos
11.6 | Drainage
Discharge pipework
1 ) | Complete Discharge pipe work | 1 | item
2 ) | Connecting Septic tank and soak pit | 1 | item
3 ) | Construction of Septic Tank and Soakpit as per the drawings shown | 1 | item
4 ) | Constructing Inspection Chamber of required size with all provisions to connect pipelines as per drawing. | 8 | nos
TOTAL OF BILL NO. 11 (HYDRAULICS AND DRAINAGE)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 12
ELECTRICAL INSTALLATIONS
12.1 | General
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rate shall include for electrical conduits, fittings, equipment and similar all fixings
c) Each light / light fixture and its switches shall measure as one one point: similarly each sockets or each fans shall measured as one point.
d) Rate shall include for supply and complete installation of all floors.
e) Provide junction box for each separate unit of telephone and cable tv system.
12.2 | Main Connection
| Allow for three phase main connection from STELCO board to Panel board from STELCO Transformer / Road DB | 1 | item
12.3 | Electrical boards
Complete installation incl. for all connection earthing, painting, testing and similar of;
1 ) | Main panel board / Meter Board | 1 | Item
2 ) | Distribution boards | 7 | nos
12.4 | Electrical wiring
Electrical wiring with copper conductor cable in conduits in walls and slab as specified to
1 ) | 2.5mm2 Wiring to light fixtures, fans and its switches | 565 | points
2 ) | Wiring to Socket Switches | 177 | points
3 ) | Cabling to Distribution boards | 7 | points
4 ) | Cabling to Telephone/networking sockets | 27 | points
12.5 | Fans
1 ) | Ceiling fans "USHA" or equivalent 1200 mm dia | 82 | nos
2 ) | Fan dimmer | 82 | nos
3 ) | Wall mount fan |  | nos
3 | Exhaust fans | 3 | nos
12.6 | Lighting and others
1 ) | 40 bulb main chandelier | 5 | nos
2 ) | Ceiling mount LED light | 109 | nos
3 ) | 1 X 2 ' LED tube light | 14 | nos
4 ) | 1 X 4' LED tube light | 95 | nos
5 ) | 600 X 600 mm 2 X 18watt LED tube lights | 60 | nos
6 ) | Wall mount Light | 24 | nos
7 ) | Wall mount weather proof Light | 38 | nos
8 ) | Wall mount weather proof Light (Terrace) | 22 | nos
9 ) | Floor mount up light weather proof | 12 | nos
10 ) | Emergency Light | 29 | nos
12.7 | Socket outlets
All sockets shall be "Clipsal"or equivalent
1 ) | 13 Amps Socket Switch single | 132 | nos
2 ) | 15 Amps Socket Switch | 42 | nos
3 ) | 15 Amps Socket Switch (W) | 3 | nos
4 ) | Telephone / Networking Socket | 27 | nos
5 ) | SPN isolators | 26 | nos
12.8 | Light Switches
All switches shall be "Clipsal"or equivalent
1 ) | One Way switches | 160 | nos
12.9 | PA System
1 ) | PA system as shown in drawings | 1 | Item
TOTAL OF BILL NO. 12 (ELECTRICAL INSTALLATIONS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 13
MECHANICAL INSTALATION
13.1 | Fire fighting system
13.1.1 | General
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rate shall include for electrical conduits, fittings, pumps, contolr boards and other quipment and similar all fixings
c) Rate shall include for all necessary electrical wiring and accessaries required for completion of fire fighting system installation in acconrdance with the drawings, specification and NSS regulations
13.1.2 | Dry riser system and Alarm System
1 ) | Control panel for fire alram | 1 | Nos
2 ) | Manual call point for fire alram system | 1 | Nos
3 ) | Loop sounder for fire alram system | 1 | Nos
4 ) | Smoke detector for fire alarm system | 22 | Nos
5 ) | Exit sign light | 8 | Nos
6 ) | CO2 Extinguisher | 4 | Nos
7 ) | H2O Extinguisher | 4 | Nos
8 ) | Fire blanket | 1 | Nos
13.2 | MVAC
Supply of spit air conditioner unit with indoor,outdoor units, pipes and other accessories as per the engineers instruction and specifications
1 | Refrigerant supply | 910 | m
2 | Refrigerant return | 910 | m
3 | Condense drain pipe | 220 | m
4 | Outdoor unit | 42 | nos
5 | Indoor wallmounted split unit 12000BTU | 42 | nos
TOTAL OF BILL NO. 13 (MECHANICAL INSTALLATION)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 14
SOLAR SYSTEM
1 | Solar panels | 60 | nos
2 | 200KVA solar inverter | 1 | nos
3 | MPPT solar controller | 1 | nos
4 | 12V battery solar storage bank | 4 | nos
5 | Cabling & conduits | 1 | Item
TOTAL OF BILL NO. 14 (SOLAR SYSTEM)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 15
LIFT
15.1 | General
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rate shall include for electrical conduits, fittings, equipment and similar all fixings
c) Rate shall include for all necessary electrical wiring and accessaries required for completion of lift installation.
15.2 | LIFTS
| Supply and install lift complete: "Mitsubushi, to lift 6 person capacity, serving all levels (2 floors) as per manufacturer's instructions. | 1 | no
TOTAL OF BILL NO. 15(LIFT)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 16
ADDITIONS
Bill No: 01
Bill No: 02
Bill No: 03
Bill No: 04
Bill No: 05
Bill No: 06
Bill No: 07
Bill No: 08
Bill No: 09
Bill No: 10
Bill No: 11
Bill No: 12
Bill No: 13
Bill No: 14
TOTAL OF BILL NO. 16 (ADDITIONS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 17
OMISSIONS
Bill No: 01
Bill No: 02
Bill No: 03
Bill No: 04
Bill No: 05
Bill No: 06
Bill No: 07
Bill No: 08
Bill No: 09
Bill No: 10
Bill No: 11
Bill No: 12
Bill No: 13
TOTAL OF BILL NO. 17(OMISSIONS) | [7 empty] | 0
(CARRIED OVER TO THE GENERAL SUMMARY)

## BOQ-MINARET
SL.NO | DESCRIPTION | QTY | UNIT | LABOUR RATE | MATERIAL RATE | LABOUR AMOUNT | MATERIAL AMOUNT | TOTAL AMOUNT
Bill No: 02
GROUND WORKS
2.1 | GENERAL
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating and disposing surplus soil.
2.2 | SITE CLEARING
| Clear the area of site from rubbish and vegetable matters, stumps, roots. Demolition shall be included (if any) | 1 | Item
2.3 | EXCAVATION
Excavation quantities are measured to the faces of concrete members. Rates shall include for all additional excavation required to place the formworks
1 ) | Excavation for Foundation beams | 75 | m³
2.4 | BACK FILLING
(a) Rates shall include for: levelling, grading, trimming, compacting and similar.
(b) Ground need to be compacted to the required density by the consultant.
1 ) | Earth Filling as per drawings | 25 | m²
2 ) | 50 mm thick sand blinding layer to receive damp proof membrane | 25 | m²
2.5 | DAMP PROOF MEMBRANE
(a) Rates shall include for: dressing around and sealing to all penetrations, laps and turnups
1 ) | Polythene damp proof membrane (500 gauge) laid on blinding layer under footing | 25 | m²
2.6 | DEWATERING
| This item shall include for all the piping, pumps, etc. Water needs to be pumped to an assigned area as per local regulation. | 1 | Item
TOTAL OF BILL NO. 02 (GROUND WORKS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 03
CONCRETE WORKS
General
a) Rate shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
b) Mix ratio for reinforced concrete shall be 1:2:3
1 ) | Allow for concrete testing | 1 | item
3.1 | Lean Concrete
| 50mm thick lean concrete under the foundation footing with a mix of 1:2:6 | 25 | m²
3.2 | Reinforced Concrete
In-situ reinforced concrete to:
*Add water proofing compound / admixture to concrete mix for walls GL and Roof Slabs
3.2.1 | Foundation
1 ) | Foundation pad 5000 X 5000 X 2500 mm | 62.5 | m³
2 ) | RC walls 150 mm thick upto pavement level | 0.07 | m³
3.2.2 | Above Ground Level
1 ) | RCC Ground Slab 100 mm thick, (Rate shall include for reinforcement and shuttering required as per the drawings) | 0.38 | m³
2 ) | RC walls 150 mm thick upto landing -01 | 9.4 | m³
3 ) | RC walls 150 mm thick landing 01-02 | 7.2 | m³
4 ) | RC walls 150 mm thick landing 02-03 | 3.2 | m³
5 ) | RC walls 150 mm thick landing above 03 | 1.3 | m³
3.3 | Formwork
a) Rates shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes, removal of formwork and normal practices used.
3.3.1 | Foundation
1 ) | Foundation pad 5000 X 5000 X 2500 mm | 50 | m²
2 ) | RC walls 150 mm thick upto pavement level | 13.82 | m²
3.3.2 | Above Ground Level
1 ) | RC walls 150 mm thick upto landing -01 | 124.5 | m²
2 ) | RC walls 150 mm thick landing 01-02 | 96.2 | m²
3 ) | RC walls 150 mm thick landing 02-03 | 41.48 | m²
4 ) | RC walls 150 mm thick landing above 03 | 16.96 | m²
3.4 | Reinforcement
a) Rates shall include for: cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wire and chair supports, laps, and wastages.
3.4.1 | Foundation
1 ) | Foundation pad 5000 X 5000 X 2500 mm
| 10 mm dia bars | 1025 | kg
2 ) | RC walls 150 mm thick upto pavement level
| 10 mm dia bars | 38 | kg
3.4.2 | Above Ground Level
1 ) | RC walls 150 mm thick upto landing -01
| 10 mm dia bars | 325.5 | kg
2 ) | RC walls 150 mm thick landing 01-02
| 10 mm dia bars | 255 | kg
3 ) | RC walls 150 mm thick landing 02-03
| 10 mm dia bars | 112 | kg
4 ) | RC walls 150 mm thick landing above 03
| 10 mm dia bars | 52 | kg
3.5 | OTHER CONCRETE WORKS
1 ) | Concrete borders as specified in drawings | 1 | Item
2 ) | Concrete ledge | 1 | Item
3.6 | WATER PROOFING
Rate shall include for: dressing arround and sealing to all penetrations
1 ) | Apply bituminous type waterproofing to all surfaces of concrete below ground level in accordance with the specifications and manufacturer's instructions | 1 | item
TOTAL OF BILL NO. 03 (CONCRETE WORKS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 04
MASONRY AND PLASTERING
4.1 | General
a) Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good.
4.2 | Plastering
4.2.1 | a) 25mm cement plastering on external walls and concrete surfaces with 1:4 Cement mortor mix as specified incl. wire mesh at joints of concrete surfaces and walls (first,second coats).
1 ) | Minaret external plastering | 110 | m²
4.2.2 | a) 15mm cement plastering on internal walls and concrete surfaces with 1:4 Cement mortor mix as specified incl. wire mesh at joints of concrete surfaces and walls (one coat).
1 ) | Minaret internal plastering | 110 | m²
4.3 | Cement Screed Finish
4.3.1 | 35mm thick Cement screeding on the
concrete floor with 1:4 cement mortar
mix incl. trowel finish; General Areas
1 ) | Minaret base | 4 | m²
TOTAL OF BILL NO. 04 (MASONRY AND PLASTERING)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 05
METAL WORKS
5.1 | General
a) Rates shall include for: all fabrication work, welding, marking, drilling for bolts incl. those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
b) Rates shall include for fabrication and erection and temporary supports and fixing into position.
5.2 | Stainless Steel Ladder
1 ) | SS ladder as per the drawings for Minaret | 1 | Item
5.3 | Minaret Dome
1 ) | Metallic dome as specified in the drawings for Minaret | 1 | Item
TOTAL OF BILL NO. 05 (METAL WORKS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 06
WOOD WORKS & ROOFINGS
6.1 | General
a) Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
b) Rate shall include for: timber priming and all painting as specified in the drawing
TOTAL OF BILL NO. 06 (WOOD WORKS & ROOFING)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 07
CEILING
7.1 | General
a) Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
b) Rate shall include for: timber priming and all painting as specified in the drawing
TOTAL OF BILL NO. 07 (CEILINGS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 08
DOORS AND WINDOWS
8.1 | General
a) Rates shall include for: locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
b) All Aluminium windows shall be white powder coated aluminium.
c) All timber doors shall be solid timber panneled door with varnish finish.
d) All glazing shall be 6mm Tinted.
(Profiles to be chosen by client).
8.3 | Door
1 ) | Minaret door | 1 | nos
TOTAL OF BILL NO. 08 (DOORS AND WINDOWS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 9
FINISHES
9.1 | General
a) Rates shall include for: fixing, bedding, grouting, pointing, finishing and any other similar works to ensure the required finish.
b) Rates shall include for all other beading works required at the corneres
TOTAL OF BILL NO. 9 (FINISHES)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 10
PAINTING
10.1 | General
a) Rates shall include for: the provition, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and / or making floors, fittings and similar work, removing and replacing door and window furniture
b) All painting work shall be carried in accordance with the specifications.
Painting system shall be Nippon or Equivalent
10.2 | Walls
Weather proof emulsion paint system with textured finish on plastered and concrete surfaces of external and normal emulsion paint on internal walls.
10.2.1 | External painting 1 coat of wall sealer, 1 coat tex compound & 2 coats of paints
1 ) | External walls of Minaret | 110 | m²
10.2.2 | Emulsion paint putty finish system on plastered and concrete surfaces of internal walls.
Internal Painting 1 coat of wall sealer & 2 coats of paints
1 ) | Internal walls of Minaret | 110 | m²
TOTAL OF BILL NO. 10 (PAINTING)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 11
HYDRAULICS & DRAINAGE
11.1 | General
a) Rates shall include for: sockets, running joints, connections, elbows, junctions, reducers, expansion joints; backnuts and similar; incidental fittings, clips, saddles, brackets, straps, hanges, screws, nails and fixing complete, including cutting and
11.2 | Drainage
Discharge pipework
1 ) | Complete Discharge pipe work with required drains and connections etc | 1 | item
TOTAL OF BILL NO. 11 (HYDRAULICS AND DRAINAGE)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 12
ELECTRICAL INSTALLATIONS
12.1 | General
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rate shall include for electrical conduits, fittings, equipment and similar all fixings
c) Each light / light fixture and its switches shall measure as one one point: similarly each sockets or each fans shall measured as one point.
d) Rate shall include for supply and complete installation of all floors.
e) Provide junction box for each separate unit of telephone and cable tv system.
12.2 | Main Connection
| Allow for three phase main connection from STELCO board to Panel board from STELCO Transformer / Road DB | 1 | Item
12.3 | Electrical boards
Complete installation incl. for all connection earthing, painting, testing and similar of;
1 ) | Distribution boards | 1 | Item
12.4 | Electrical wiring
Electrical wiring with copper conductor cable in conduits in walls and slab as specified to
1 ) | 2.5mm2 Wiring to light fixtures, fans and its switches | 12 | points
2 ) | Wiring to Socket Switches | 6 | points
3 ) | Cabling to Distribution boards | 1 | points
12.5 | Lighting and others
1 ) | Weather proof floor mount lights | 12 | nos
2 ) | Emergency Light | 2 | nos
12.6 | Socket outlets
All sockets shall be "Clipsal"or equivalent
1 ) | 13 Amps Socket Switch single | 4 | nos
2 ) | 15 Amps Socket Switch | 2 | nos
12.7 | Light Switches
All switches shall be "Clipsal"or equivalent
1 ) | One Way switches | 4 | nos
12.8 | PA System
1 ) | PA system as shown in drawings for Minaret from main Mosque | 1 | Item
TOTAL OF BILL NO. 12 (ELECTRICAL INSTALLATIONS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 13
ADDITIONS
Bill No: 01
Bill No: 02
Bill No: 03
Bill No: 04
Bill No: 05
Bill No: 06
Bill No: 07
Bill No: 08
Bill No: 09
Bill No: 10
Bill No: 11
Bill No: 12
TOTAL OF BILL NO. 13 (ADDITIONS)
(CARRIED OVER TO THE GENERAL SUMMARY)
Bill No: 14
OMISSIONS
Bill No: 01
Bill No: 02
Bill No: 03
Bill No: 04
Bill No: 05
Bill No: 06
Bill No: 07
Bill No: 08
Bill No: 09
Bill No: 10
Bill No: 11
Bill No: 12
TOTAL OF BILL NO. 14 (OMISSIONS)
(CARRIED OVER TO THE GENERAL SUMMARY)

## SUM- MINARET
PROJECT: HITHADHOO ISLAMIC CENTER
CONSTRUCTION OF 02 STOREY BUILDING
SUMMARY OF BILLS OF QUANTITIES (MINARET)
SL.NO | BILL NAME | AMOUNT (MRF)
2 ) | TOTAL OF BILL NO. 02 (GROUND WORKS)
3 ) | TOTAL OF BILL NO. 03 (CONCRETE WORKS)
4 ) | TOTAL OF BILL NO. 04 (MASONRY AND PLASTERING)
5 ) | TOTAL OF BILL NO. 05 (METAL WORKS)
6 ) | TOTAL OF BILL NO. 06 (WOOD WORKS & ROOFING)
7 ) | TOTAL OF BILL NO. 07 (CEILINGS)
8 ) | TOTAL OF BILL NO. 08 (DOORS AND WINDOWS)
9 ) | TOTAL OF BILL NO. 9 (FINISHES)
10 ) | TOTAL OF BILL NO. 10 (PAINTING)
11 ) | TOTAL OF BILL NO. 11 (HYDRAULICS AND DRAINAGE)
12 ) | TOTAL OF BILL NO. 12 (ELECTRICAL INSTALLATIONS)
13 ) | TOTAL OF BILL NO. 16 (ADDITIONS)
14 ) | TOTAL OF BILL NO. 17(OMISSIONS)
GRAND TOTAL