## COVER
Bill Of Quantities (BOQ)
BOQ for:
Interior & MEP Works For Koveli Building New Operation Theaters at 5th Floor , Hulhumale Hospital , Maldives.
Project Title:
New Operation Theaters Hulhumale Hospital

## BOQ Summary Comment (hidden)
Interior & MEP Works For Koveli Building New Operation Theaters at 5th Floor , Hulhumale Hospital , Maldives.
BOQ Summary
Bill Item No | Description | Total Amount ( MVR ) |  | For Progress / Update |  | #REF!
1 | Preliminaries | #REF! | Bill 1- Prilims'!A1 |  | #REF!
2 | Ground Works | #REF! | Bill 2 - Ground Works'!A1 | Detail enough
3 | Concrete Works | 0 | Bill 3 - Concrete Works'!A1 | Detail not enough. Done approx. basis.
4 | Masonry Works | 0 | need internal wall details.
5 | Metal Works | 0 | No details. But can do estimate/tentative basis.
6 | Ceiling Works | 0 | need finishing shedule
7 | Door , Window & Glass Works | 0 | need door & window shedule.
8 | Painting Works | 0 | need finishing shedule
9 | Tiling & Clading Works | 0 | need finishing shedule
10 | Electrical Installation | 0
11 | Hydraulics , Drainage and Sanitary Fixtures | 0
12 | Air Conditioning Works | 0
13 | Lift Installation | #REF! | Bill - 13 Lift'!Print_Area
14 | Fire Fighting Works | 0
15 | Steel Structures Works | #REF! | Bill - 15 Steel Structures'!Print_Area | Detail not enough. Done approx. basis.
16 | Additional Works | 0
17 | Omission Works | 0
| Total Amount ( MVR ) | #REF!
| GST - 6% | #REF!
| Grand Total ( MVR ) | #REF!

## BOQ Summary
Interior & MEP Works For Koveli Building New Operation Theaters at 5th Floor , Hulhumale Hospital , Maldives.
BOQ Summary
2021-12-19
Bill Item No | Description | Total Amount ( MVR )
1 | Preliminaries
2 | Ground Works ( N/A )
3 | Concrete Works
4 | Masonary & Plastering Works
5 | Metal Works
6 | Ceiling Works
7 | Door , Window & Glass Works
8 | Painting Works
9 | Floor & Wall Finishing Works and Partition Wall ( ProStud Walls )
10 | Electrical Installation
11 | Hydraulics , Drainage and Sanitary Fixtures
12 | Air Conditioning Works
13 | Lift Installation ( N/A )
14 | Fire Fighting & Alarm Works
15 | Theater Equipments & Machines
16 | Furnitures & Common Equipments
17 | Additional Works
18 | Omission Works
Total Amount ( MVR )
GST - 6%
Grand Total ( MVR )

## Bill 1- Prilims
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No : 1
Preliminaries
1.1 | General Notes
(a) Allow for all costs and expenses for complying with the General Conditions of Contract and General Requirements in Specifications.
(b) Any services not specifically provided for herein will be deemed to be included in the rates of other items in the BOQ or under additional works.
1.2 | Site Management , Staff & Office Maintain Cost
1 | Allow for site management cost including technical staff etc. | Item | 1
2 | Allow for temporary office maintain at site & maintaining facilities including office equipment , stationeries , computers & printers , if any other cost. | Item | 1
3 | Allow to the Contractor to include plant , machineries and equipment cost related to the works. | Item | 1
1.3 | Safety On Site and Site Security Works
1 | Providing and maintains adequate safety measures for whole workers , staff and authorized visitors and site security works for the works and people until completion of the works. | Item | 1
1.4 | Name Board and Sign Board
1 | Allow for making & maintain name board until completion the works. | Item | 1
2 | Allow for making & maintain sign board until completion the works. | Item | 1
1.5 | Clean-up
1 | Allow for keeping all the site tidy and clean, and for clearance of the site to the satisfaction of the Engineer/the Employer on completion of the contract. | Item | 1
1.6 | Precautionary , protect on ground or underground existing utilities , structures , services until complete the works.
1 | Allow for precaution measures & maintaining for existing building , structure, or service until completion the works as required. If there is any existing services to be protected can be included under this item. | Item | 1
1.7 | Contractual Requirement
( Note : The contractor can price below work items, if those items apply only. )
1 | Provide all insurances under the contract as in Conditions of Contract. | Item | 1
2 | Provide performance bond as per the conditions of contract. | Item | 1
3 | Provide advanced payment bond as per the conditions of contract. | Item | 1
4 | Provide monthly progress report ( couple of original copies ) with photos prints each month. | Item | 1
5 | Provide originals and copies of "As Built Drawings" as per the contact. | Item | 1
6 | Provide originals and copies of operation and maintenance data manuals as per the contract stated. | Item | 1
Total of Bill No: 01 - Carried to Bill Summary

## Bill 2 - Ground Works
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 02
Ground Works
2.1 | General
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, dewatering, keep sides plumb, backfilling, consolidating and disposing surplus & debris from site.
(b) All are according to the detailed drawing and specification.
(c) Rate shall include all the works completely unless other wise measured separately.
(d) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed for completion.
(e) This item not applicable.
Total Of Bill No: 02 - Carried to Bill summary

## Bill 3 - Concrete Works
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 03
Concrete Works
3 | General
(a)The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Rates shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
(c) Mix ratio for reinforced concrete shall be 1:3:6 and lean concrete shall be 1:2:4 by volume.
(d) Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork and excavated tolerances.
(e) Rate to include water proofing compound/admixtures to concrete for wet area unless other wise measured separately. separately.
( f ) All works are according to the drawing and Rate to include all the work items unless other wise measured separately.
(g) All works are according to the drawing and technical specification.
(h) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
1 | Allow for concrete testing works until completion the works. | Item | 1
3.1 | Concrete Works
Reinforced Concrete
In-situ reinforced concrete to:
1 | Allow to make new structural concrete parts as requested by the engineer. Rate to include concrete , steel reinforcement , formwork and other related works for successfully complete. | Item | 1
2 | Allow to include any demolishing of structural/concrete works as requested by the engineer. Rate to include disposal of debris. | Item | 1
3.2 | Other Concrete Works
Lintel Works
1 | Provide lintel where the door/windows do not touch the concrete surface. Rate to include reinforcement , formwork & concrete completely . | Item | 1
2 | Vanity for Toilets & Pantry
| Preparation of vanity for toilets & pantry area as shown in the drawing. Rate to include reinforcement , formwork & concrete completely . | Item | 1
Water Proofing for Wet Surface
3 | Application of approved water proofing chemical for toilets floor , in accordance with the drawings , specifications and manufacture instructions. | m² | 24 |  |  | Toilets and Bathrooms walls.
Total Of Bill No: 03 - Carried to Bill Summary

## Bill 4 - Masonry & Plastering
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 04
Masonry & Plastering Works
4.1 | General
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Rates shall include for cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary fractional size blocks , all necessary machine cutting , filling of gaps , cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding , temporary supports to openings and for all necessary making good.
(c) Suitable filling material shall be used in all joints of concrete and masonry as a bonding agent according to the drawing.
(d) Rate shall include water proofing chemicals/admixtures unless other wise measured separately.
(e) All in accordance with the drawing and specification & The rates shall cover all the works completely unless other wise measured separately.
(f) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
4.2 | Cement Block Work
Internal Wall
1 | 150 mm thick vertical Block wall in 1:5 cement sand mortar | m² | 312
4.3 | Cement Screed/Flooring ( 38 mm thk. )
For General Floor
1 | Cement sand mortar screed 1:3 with rough finish for tilling works. | m² | 548
4.4 | Demolishing Existing Block Works
1 | Allow to demolished existing internal block work done , as shown in the drawing . Approx. area 6.60 m². | Item | 1
Total Of Bill No: 04 - Carried to Bill Summary

## Bill 5 MetalWorks
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 05
Metal Works
5.1 | General
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Rates shall include for: all fabrication work, welding, marking, drilling, for bolts including those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
(c) Rates shall include for all painting and finished as specified.
(d)Rates shall include for fabrication and erection and temporary supports and fixing in to position.
(e) The contractor shall submit sample of SS and GI sections and all other accessories for approval for the Engineer.
(f) All are according to the drawings and specification. The rates shall cover all the works completely unless other wise measured separately.
(g) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
5.2 | Stainless Steel Flush Mount Corner Guard
| Supply & fixing full height stainless steel flush mount corner guard as shown in the drawings , technical specification etc.. | nr | 72
Drg No : T600-11-104R00
5.3 | Stainless Steel Wall Guard
| Supply & fixing 38 x 140 mm stainless steel wall guard at 900 mm from finish floor level as shown in the drawings , technical specification etc.. | m | 302
Drg No : T600-11-104R00
Total Of Bill No: 05 - Carried to Bill Summary

## Bill 6 - Ceiling
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 06
Ceiling Works
6 | General
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
(c) The rates shall cover all the works completely according to the drawing unless otherwise measured separately.
(d) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(e) Please see finishing schedule ''note'' for more details.
6.1 | Proprietary Steel Frame Ceiling With Calcium Silicate Board & BIOCLAD Antimicrobial PVC Sheet
For Operation Theatres Only
| Supply , fabricate & fixing proprietary steel ceiling frame hanger tie screw fixed to slab including steel frame spacing 600 mm , 125 mm thk. R-13 unfaced insulation on celling paneling , M board ceiling sheet , 2.5 mm tk. BIOCLAD antimicrobial pvc sheet fixed to ceiling panel joints heat welded according to the drawing , manufactures speficiation completely. | m² | 129
Rate to include R-50 x 2.5 mm thk. PVC cove base seamless sheet fix to proprietary bioclad panel by heat welding as shown in the drawing completely.
6.2 | Steel Frame & Insulation For General Area
| Supply & fabricate/fixing proprietary steel ceiling frame hanger tie screw fixed to the slab including steel frame spacing 600 mm and laying 125 mm thk. R-13 unfaced insulation on ceiling panel as shown in the drawing , schedule & speficiation completely. | m² | 400
General Area Ceiling Finishing Works
6.3 | Acoustic Ceiling Panel
| Supply & fixing Acoustic Ceiling panels , sound absorption rating of 0.70-1.00 NRC , fire performance class A rating, according to the finishing schedule , specification & drawings completely. | m² | 356
Brand/Model : Armstrong , CALLA Health Zone or equivalent
6.4 | Decorative Ceiling Panels
| Supply & fixing 1220 x 2500 x 2.5 mm decorative panels with joint strip and edge trim, according to the finishing schedule , specification & drawings completely. | m² | 10
6.5 | M Board Ceiling with PVC cladding system
| Supply & fixing M board with antimicrobial PVC cladding system , Brand/Model : Biocote, according to the finishing schedule , specification & drawings completely. | m² | 12
6.6 | M Board Ceiling
| M board with 2 coat of water based primer and 3 coats of Hygienic Anti Fungal , Anti Bacterial Polyurethane wall coating . Brand/Model : Nippon or Dulux or equivalent | m² | 22
6.7 | Cornice
Supply & fixing cornice as shown in the drawings , specification & schedule of finishes.
1 | 55 mm light weight paper faced cove | m | 507
Brand/Model : USG Boral , Sheetrock cover or equivalent
2 | Antimicrobial PVC cove | m | 120
Brand/Model : Biocote or equivalent
Total Of Bill No: 06 - Carried to Bill Summary

## Bill 7 - Door&Window
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No : 07
Door , Window & Glass Works
7.1 | General
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware with other accessories. Material should be with superior quality.
(c) Rates shall include for door frames and window frames, mullions, transoms, trims, glass, tinting, timber panels, boardings, framing, lining, fastenings and all fixings and installation.
(d) All louvers, windows and sliding doors shall be as specified in the drawing & schedules..
(e) Rates shall include for all painting/coating as specified.
(f) The contractor shall submit sample for aluminum frames, timber door & window hardware , tempered heat reflective glass , shutter sample , sealants for door and windows , accessories and other similar for approval of the Engineer.
(g) All are according to drawings and specifications. The rates shall cover all the work items completely unless other wise separately.
(h) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(i) The contractor shall refer schedules of door and window for more details to pricing.
7.2 | Door Units
Fifth Floor
1 | D1 - 1000 x 2100 mm size , 80 mic white powder coated aluminum frame with fixed 4 or 5 mm white cladding sheet for both side. | nr | 1
2 | D1A - 1850 x 2400 mm size , 80 mic white powder coated aluminum frame with 6 mm thick clear fixed glass, white cladding sheet for both side. Rate to include hand sensor. | nr | 1
3 | D1B - 4300 x 2100 mm size foot operated door . Rate to include foot button sensor for both side. | nr | 4
Foot operate sliding door must be install as per supplier specification. Dimensions must be taken at site. Control position must be confirm before purchasing. And materials quality & specification must be submitted with bid proposal. Rate to include both side foot button control & hand sensor.
4 | D1C - 2258 x 2400 mm size , 80 mic white powder coated aluminum frame with 6 mm thick clear fixed glass, white cladding sheet for both side. Rate to include hand sensor. | nr | 1
5 | D1D - 1650 x 2400 mm size , 80 mic white powder coated aluminum frame with 6 mm thick clear fixed glass, white cladding sheet for both side including frosted sticker. Rate to include hand sensor. | nr | 4
6 | D1E - 4300 x 2100 mm size foot operated door . Rate to include foot button sensor for both side. | nr | 2
Foot operate sliding door must be install as per supplier specification. Dimensions must be taken at site. Control position must be confirm before purchasing. And materials quality & specification must be submitted with bid proposal. Rate to include both side foot button control & hand sensor.
7 | D2 - 1000 x 2100 mm size , 80 mic white powder coated aluminum frame with 6 mm thick clear fixed glass white cladding sheet for both side. | nr | 6
8 | D2A - 1000 x 2100 mm size , 80 mic white powder coated aluminum frame with fixed 4 or 5 mm white cladding sheet for both side. | nr | 12
9 | D3 - 1050 x 2100 mm size , 80 mic white powder coated aluminum frame with fixed 4 or 5 mm white cladding sheet for both side. | nr | 3
10 | D4 - 1000 x 2100 mm size single panel sliding door , 80 mic white powder coated aluminum frame with fixed 4 or 5 mm white cladding sheet for both side. | nr | 1
11 | D5 - 850 x 2100 mm size , 80 mic white powder coated aluminum frame with fixed 4 or 5 mm white cladding sheet for both side. | nr | 8
7.3 | Other Works
1 | Supply & fixing glass window as shown in the drawings , specification & manufacture's details. ( Approx. area 24.00 m² ) | Item | 1
2 | Supply & fixing aluminum louver sliding door for cover DB & Electrical Panel. | Item | 1
3 | Supply & fixing glass "FL" door as shown in the drawings , specification & manufacture's details. | Item | 1
4 | Supply & fixing sliding window with bell as shown in the drawings , specification & manufacture's details. | Item | 1
7.4 | Existing Window Conceal
Conceal existing windows as shown in the detailed drawing .
Rate to include timber framing , 16 mm thk X GWB type Gypsum Board fix to timber frame , 50 mm thk R-13 unfaced insulation & etc..
Drg : T6-11-502R00 to T6-11-505R00
1 | Type 01 - 700 x 1700 mm | nr | 5
2 | Type 02 - 1350 x 1700 mm | nr | 24
3 | Type 03 - 3483 x 1700 mm | nr | 1
4 | Type 04 - 2417 x 1700 mm | nr | 1
Total Of Bill No: 07 - Carried to Bill Summary

## Bill 8 - Painting
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 08
Painting Works
8 | General
Painting Works
(a) Rates shall include for the provision , erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window furniture.
(b) All painting work shall be carried in accordance with the Specifications
(c) Colour to be approved by the Architect & the Engineer.
(d) The brand of paint shall be with approved manufacture.
(e) The rates shall cover all the works completely according to the drawing unless otherwise measured separately.
(f) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(g) Please see finishing schedule for more details.
Painting Works
8.1 | Slab Soffit Painting
1 | Emulsion paint by approved manufacture finishing with two coat of primer , one paint coat interior grade on slab soffit. Rate to include smoothing works etc. | m² | 548
Total Of Bill No: 08 - Carried to Bill Summary

## Bill 9 - Floor & Wall Finishing
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 09
Floor & Wall Finishing Works and Partition Wall
9.1 | General
(a) Rates shall include for supply , fixing , paving , grouting , pointing , assembling , fabricating , joining , stick by adhesive and any other similar works to ensure the required finish.
(b) Tile bed has measured separately under Masonry works.
(c) All materials shall be approved quality/brand or similar as given in the technical specifications and finishing schedule.
(d) The contractor shall submit samples of all finishing materials for approval of the Engineer / the Architect.
(e) All tiles shall be fixed using a proper adhesive/bonding material.
(f) BIOCLAD antimicrobial pvc sheet shall be fixed by heat welded system and shall be according to the manufacture's specification.
(g) The rates shall cover all the works completely according to the drawing unless otherwise measured separately.
(h) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(i) Please see finishing schedule for more details.
9.2 | Floor Finishes - General Area
1 | Supply & laying/fixing Homogeneous Poly(Vinyl chloride) floor covering completely according to the specification , drawings. | m² | 388
Brand/Model : Tarkett or equivalent
2 | Supply & laying/fixing Antimicrobial safety flooring completely according to the specification , drawings. | m² | 12
Brand/Model : Biocote or equivalent
9.3 | Floor Finishes - Theatres Area
BIOCLAD Antimicrobial PVC Sheet & R-50 x 2.5 mm thk. PVC Cover Base Seamless Sheet
Antimicrobial Safety Flooring
1 | Supply & fixing 2.5 mm thk proprietary bioclad antimicrobial pvc sheet fixed to floor as shown in the detailed drawing & manufactures technical specification completely. | m² | 129
Rate to include R-50 x 2.5 mm thk. PVC cove base seamless sheet fix to proprietary bioclad panel by heat welding as shown in the drawing completely.
9.4 | Skirting Finishes
1 | Supply & laying/fixing 150 mm thk Homogeneous Poly(Vinyl chloride) floor skirting completely according to the specification , drawings. | m | 409
Brand/Model : Tarkett or equivalent
2 | Supply & laying/fixing Antimicrobial PVC cover base skirting completely according to the specification , drawings. | m | 102
Brand/Model : Biocote or equivalent
9.5 | ProStud Steel Frame Wall System
1 | ProStud Wall System ( Internal Partition )
| Supply & fixing prostud steel frame wall system as shown in the detailed drawing & manufactures technical specification completely. | m² | 469
Rate shall 125 x 33 mm floor plate , SS taping screws , 38 x 12.7 mm U channel , 125 x 33 mm steel frame work at 600 mm spacing , 125 mm thk R-13 unfaced insulation and other necessary fittings , accessories etc..
2 | M Board To Stud Frame ( Whole Floor )
| Supply & fixing M board adhesive fixed to stud frame as shown in the detailed drawing & manufactures technical specification completely. | m² | 938
9.6 | Wall Finishing Works
1 | BIOCLAD Antimicrobial PVC Sheet & R-50 x 2.5 mm thk. PVC Cover Base Seamless Sheet
For Theatres
| Supply & fixing 2.5 mm thk proprietary bioclad antimicrobial pvc sheet fixed to M board substrate as shown in the detailed drawing & manufactures technical specification completely. | m² | 257
Rate to include R-50 x 2.5 mm thk. PVC cove base seamless sheet fix to proprietary bioclad panel by heat welding as shown in the drawing completely.
2 | Water Based Primer , Hygienic Paint & Anti Bacterial Wall Coating
| 2 coat of water based primer and 3 coats of Hygienic Anti Fungal , Anti Bacterial Polyurethane wall coating . Brand/Model : Nippon or Dulux | m² | 1192
M - board will be measured under BOQ Bill : 9.5.2
3 | Fixing Decorative Panels
| 1220 x 2500 x 2.5 mm decorative panels with joint strip and edge trim. | m² | 28
M - board will be measured under BOQ Bill : 9.5.2
4 | Antimicrobial PVC Wall Cladding
| M board with Antimicrobial PVC wall cladding system | m² | 48
Brand/Model : Biocote
M - board will be measured under BOQ Bill : 9.5.2
9.7 | Other Finishing Works
1 | Vanity Finishing ( Toilets , Pantry & Other Rooms )
| Supply & fixing polished brown granite with glossy finish for vanity according to the drawing , finishing details. | Item | 1
2 | Wall Art
| Supply & fixing of wall art for wall area according to the drawing , finishing details & specification completely. ( Item Code : 62-201 ) | nr | 16
Total Of Bill No: 09 - Carried to Bill Summary

## Bill 10 Electrical
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No : 10
Electrical Installation
10.1 | General
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) All materials, equipment, wiring and workmanship shall good quality as required by STELCO.
(c) Rates shall include for electrical conduits , Cable , PVC sun box , fittings, equipment and similar all fixings to various building surfaces.
(d) Rates shall include for screws , nails , bolts, nuts , standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
(e) Rates for work in trench shall include for excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus soil from site.
(f) Rates shall include all costs associated with provision of all holes , openings , chases in block walls , duct and other builders work completely.
(g) Electrical fittings shall in approved manufactures & it will be measured under separately.
(h) A point wiring for power point is measured as one point including all for each socket outlets and wiring for light & fan is measured as one point including all. All the fitting will be measured separately.
(i) Rates shall include for supply and complete installation
(j) CAT 6 cable type shall be used for wiring works including access control , data , telephone , CCTV , printers etc..
(j) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
10.2 | Main Connection
| Supply STELCO main connection as required completely. Rate to include main cable and laying cost from transformer to main panel board completely. | Item | N/A
10.3 | Main Panel Board/Main Switch Board
| Supply and installation of Main Panel Board completely including all the accessories as shown in detailed electrical drawings and technical specifications. Rate to include proper earthing system , connections , testing and commissioning as to the requirement of STELCO , wiring , switch and other fittings etc. Rate to include necessary builders work completely finishing. | Item | N/A
10.4 | Distribution Board
| Supply and installation Distribution Board for power distribution with cable from Main Panel Board to require location with other required fittings completely as shown in the drawings and technical data. Rate to include cable , conduit and all the builders work completely. | nr | 2
1 | Theaters | nr | 4
2 | General Area | nr | 4
3 | Terrace/Roof | nr | 1
4 | AC works | nr | 6
10.5 | Testing and Commissioning Works
| Allow for whole electrical works testing and commissioning. | Item | 1
10.5.1 | Cable Provision For Generator
| Allow to make cable provision for between existing panel board , existing generator and new operation theaters floor completely. | Item | 1
10.6 | Electrical Wiring
Electrical wiring with copper conductor cable in conduits through walls , casing on soffits of slab or through soffit , through ceiling as specified. Rates shall include related fittings and accessories completely.
1 | Wiring with 1.5 mm² cable to lighting points | nr | 498
2 | Wiring with 2.5 mm² cable to power points | nr | 166
3 | Wiring for network outlet & TV - ( CAT 6 cable ) | nr | 14
4 | Wiring for addition data point ( CAT 6 cable ) | nr | 10
5 | Wiring for additional data provision near CCTV camera point using CAT cable. | nr | 17
6 | Wiring for network switch required to cater all the IT outlet | Item | 1
10.7 | Light Fittings
Supply and fixing light fittings completely with approved manufactures.
All are accordance to the drawings and specification.
1 | 4 x 18 W fluorescent lamp in surface mount louvered luminaries , Ceiling Recessed ( Item Code : T6-88-401 ) | nr | 134
2 | 4 x 40 W fluorescent lamp in surface mount louvered luminaries , Ceiling Recessed ( Item Code : T6-88-404 ) | nr | 69
3 | 1 x 35 W dimmable halogen light in surface mount luminaries ( Item Code : T6-88-302 ) | nr | 33
4 | Bathroom light , Recessed square down light IP 44 2 x 8W LED lamp ( Item Code : T6-88-402 ) | nr | 35
5 | Lobby/Balcony light , Recessed circular down light IP 44 , 2 x PLC LED lamp ( Item Code : T6-88-403 ) | nr | 2
6 | 1 x 36W , IP 65 wall mounted fluorescent luminaries mirror light ( Item Code : T6-88-201 ) | nr | 3
7 | 2 x 28W T5 , surface mounted fluorescent lamp with diffuser and cover ( Item Code : T6-88-405 ) | nr | 28
8 | Emergency power pack | nr | 141
9 | UV Disinfection Light / 60W Sterilization Lamp UV Germicidal Lamp, Led UV Light Bulb Ozone Free Disinfection Light E26 (Bulb&Remote) | nr | 20
10.8 | Socket Outlets
Supply and fixing socket outlets completely with approved manufactures.
All socket outlets shall be accordance to the drawings and specification.
1 | 1 Gang 13A socket outlet ( Item Code : T6-82-101 ) | nr | 70
2 | 2 Gang 13A socket outlet ( Item Code : T6-82-201 ) | nr | 63
3 | 1 Gang 15A socket outlet for ceiling ( Item Code : T6-82-401 ) | nr | 16
4 | 1 Gang 15A socket outlet ( Item Code : T6-82-401 ) | nr | 4
5 | 1 Gang 15A socket outlet for ceiling concealed ( Item Code : T6-82-701 ) | nr | 40
6 | Computer network outlet , RJ 45 connector ( Item Code : T6-83-201 ) | nr | 18
7 | Floor concealed multimedia outlet consisting of 2 gang 13A socket , RJ11 & RJ45 female connector ( Item Code : T6-82-601 ) | nr | 4
8 | TV point ( Item Code : T6-83-701 ) | nr | 10
9 | Additional Data Point | nr | 10
10 | Additional Data provision for near CCTV camera point. | nr | 17
10.9 | Switches
Supply and fixing light switches completely with approved manufactures.
All are accordance to the drawings and specification.
1 | 2 Gang 1 Way Switch ( Item Code : T6-81-301 ) | nr | 12
2 | 1 Gang 1 Way Switch ( Item Code : T6-81-201 ) | nr | 18
3 | 3 Gang 1 Way Switch ( Item Code : T6-81-401 ) | nr | 3
4 | 4 Gang 1 Way Switch ( Item Code : T6-81-501 ) | nr | 10
5 | 2 Gang 2 Way Switch ( Item Code : T6-81-801 ) | nr | 6
6 | Fan Dimmer ( Item Code : T6-81-601 ) | nr | 16
7 | Additional Isolators For Equipment Room | Item | 1
8 | Network switch as required to cater for all the IT Outlet, to be confirmed by the IT contractor. | Item | 1
10.1 | Other Works
1 | CCTV Camera System
Supply & fixing IP CCTV camera fixed type as shown in the location drawing, specification & manufacture's instruction. Rate to include power supply , data cable(CAT 6 - Type) , conduit & shall be connect with building main CCTV system panel etc…
1.1 | General Area | nr | 15
1.2 | Lift Inside | nr | 2
2 | Signage & name board
| Supply & fixing signage , name boards for the operation theaters complex area as shown in the detailed drawings completely. Rate to include power supply for a each unit and etc… ( Approx. 30 Signage & Name Boards ) | nr | 30
3 | Access Control System
Supply & fixing/install below access control units as shown in the drawings , manufactures details. Rate to include cables( CAT 6 - Type ) & other necessary fittings , accessories completely.
1 | Card Reader | nr | 17
2 | Magnetic Contact | nr | 17
3 | Exit Push Button | nr | 17
4 | Access control panel for access door system | nr | 1
4 | Equipment for Nurse Call
Supply & fixing/install below access control units as shown in the drawings , manufactures details. Rate to include cables( CAT 6 - Type ) & other necessary fittings , accessories completely.
1 | Master station | nr | 2
2 | Systevo-master/slave central control unit | nr | 1
3 | Call/cancel push button | nr | 11
4 | Pear push button ( NC ) | nr | 6
5 | Duty(light) , room calls | nr | 2
6 | Room electronic module | nr | 12
7 | Power supply | nr | 1
8 | Nurse director PC | nr | 1
9 | Cable for whole network system including data bus , bed data bus , power supply & other necessary fittings , accessories. | Item | 1
5 | Generator
| Supply & install generator as shown in the drawings , manufactures details. Rate to include cables , builders works , other necessary fittings , accessories completely. | Item | N/A
6 | Transformer
| Supply & install transformer as shown in the drawings , manufactures details. Rate to include cables , builders works , other necessary fittings , accessories completely. | Item | N/A
7 | Public Address System
Supply & fixing/install below access control units as shown in the drawings , manufactures details. Rate to include cables & other necessary fittings , accessories completely.
1 | 6/9 W ceiling mounted loud speaker | nr | 44
2 | Volume controller | nr | 7
3 | Public Address System - Main Unit | nr | 1
4 | 2.5mm² fire resistant cable with 25 mm pvc conduit | m | 221
Total Of Bill No: 10 - Carried to Bill Summary

## 11 Hydraulics & Drainage
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 11
Hydraulics , Drainage and Sanitary Fixtures
11 | General
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Rates shall include for pipe laying works cutting & waste of pipe etc. & joining pipes , connecting pipes to sanitary fixture and appliances , valves , sockets, running joints, connectors, elbows, junctions, reducers, expansion joints , backnuts and similar , incidental fittings, clips, saddles, brackets, straps, hangers, screws, nails and fixing complete.
(c) Rates shall include cutting and forming holes , mortises , chases and casting to block walls.
(d) Drainage works shall include excavation , pipe laying & backfilling and disposal of surplus soil from site. Rate to include necessary bends , junctions , reducers , valve & etc.
(e) All pipe work shall be uPVC.
(f) Rates for the sanitary fittings and applications shall include all the material for proper fixing as shown in the drawings with approved manufactures , assembling , jointing together with fixing component parts and perfect working order on completion and protecting the works.
(g) All sanitary fixtures used shall be of superior quality and approved by the Architect / the Engineer on submission of samples.
(h) Rates shall include all the works completely unless otherwise measured separately.
(i) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(j) All pipes shall connect to the existing pipes in the building.
11.1 | Pipe work - Fresh water
Allow for supply and installation of pipe work to floor including all the necessary pipes , fittings and other accessories as shown in the detailed drawings. ( PPR-PN10 )
1 | 15 mm dia. Pipe | m | 78
2 | 20 mm dia. Pipe | m | 24
3 | 25 mm dia. Pipe | m | 18
11.1.1 | Pipe work - Hot Water
Allow for supply and installation of pipe work to floor including all the necessary pipes , fittings and other accessories as shown in the detailed drawings. ( PPR-PN10 )
1 | 15 mm dia. Pipe | m | 100
11.2 | Pipe Work - Sewage , Waste Water & Storm Water
Allow for supply and installation of pipe work to floor including all the necessary pipes , fittings and other accessories as shown in the detailed drawings. ( uPVC Pipe )
1 | 40 mm dia. | m | 60
2 | 50 mm dia. | m | 10
3 | 80 mm dia. | m | 20
4 | 100 mm dia. | m | 30
11.3 | Sanitary Fixtures & Accessories
Supply and fixing sanitary fixtures according to the given drawing and technical specifications complete including brackets, flush pipes, overflows, plugs , washers , necessary fittings & accessories.
All the works according to the drawings and technical specifications.
1 | WC Complete Set ( Item Code : 51-101 ) | nr | 3
2 | Wash Basin/Bathroom Sink with Faucet ( Item Code : T6- 51-602 ) | nr | 3
3 | Hand Held Bidet Spray ( Item Code : T6-51-502 ) | nr | 3
4 | Toilet Paper Holder ( Item Code : T6-52-401 ) | nr | 3
5 | Soap Dish ( Item Code : T6-52-501 ) | nr | 3
6 | Zink with Faucet ( Item Code : T6-51-603 ) | nr | 2
7 | Hook ( Item Code : T6-52-101 ) | nr | 1
8 | Bathroom Shower Set - Mixing ( Item Code : T6- 51-401 ) | nr | 3
9 | Automatic Soap Dispenser ( Item Code : T6-52-601 ) | nr | 4
10 | Automatic Hand Dryer ( Item Code : T6- 52-801 ) | nr | 3
11 | Tissue Paper Dispense ( Item Code : T6- 52-802 ) | nr | 4
12 | Towel Bar ( Item Code : T6- 52-201 ) | nr | 4
13 | Kitchen Sink ( Item Code :T6- 53-201 ) | nr | 1
14 | Sink ( Item Code :T6- 51-604 ) | nr | 1
15 | Wall Mirror ( Item Code : T6-62-301 ) | nr | 4
16 | Wall Mirror ( Item Code : T6-62-302 ) | nr | 1
17 | Spray ( Item Code : T6-62-601 ) | nr | 2
18 | Bath Mat ( Item Code : T6-63-101 ) | nr | 2
19 | Water Heater ( Electric , Tank less , Mounted On Wall ) | nr | 1
11.4 | Floor Trap/Floor Waste
Supply and fixing floor drain according to the drawing & specification. Rate to include pipe , fittings and accessories.
1 | Floor Waste ( 276 x 254 mm ) | nr | 4
2 | Floor Trap/Floor Waste ( 276 x 254 mm ) | nr | 9
11.5 | Water Meters
| Supply and fixing of MWSC water meter at ground floor, for 5th floor completely according to the drawing. | Item | 1
( The contractor can price this item if apply only )
11.6 | Inspection Chamber
Allow to supply & fixing inspection chamber as shown in the detailed drawing completely.
1 | 413 x 413 mm | nr | 3
2 | 550 x 550 mm | nr | 2
Total Of Bill No: 11 - Carried to Bill Summary

## Bill 12 - AC works
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No : 12
Air Conditioning Works
12.1 | General
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Rates shall include for complete supply, installation, ducting, wiring, pipe work (insulated liquid, gas and drain), electrical and fixings as per the drawings.
(c) Rate to include builders works as necessary complete the works.
(d) Rate to include indoor & out door A/C unit as shown in the drawing completely.
(e) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(f) Rate shall include all the works completely unless otherwise measured separately.
12.2 | Ceiling Mounted FCU
Supply and install ceiling mount FCU according to the detailed drawing , schedules , specification completely . Rate to include power supply works , related builder's works completely , gas pipes , liquid pipe and fixing fittings and accessories.
1 | 7500 BTU/HR cooling lord | nr | 3
2 | 12000 BTU/HR cooling lord | nr | 11
3 | 15000 BTU/HR cooling lord | nr | 1
4 | 18000 BTU/HR cooling lord | nr | 2
5 | 24000 BTU/HR cooling lord | nr | 3
6 | 30000 BTU/HR cooling lord | nr | 1
12.3 | Condenser Unit ( CU )
Supply and install condenser units (CU) according to the detailed drawing , schedules , specification completely . Rate to include power supply works , related builder's works completely , gas pipes , liquid pipe and fixing fittings and accessories.
1 | Condenser Unit - 1 & 2 Cooling Lord 81.48 KW | nr | 1
2 | Condenser Unit - 3 & 4 Cooling Lord 81.48 KW | nr | 1
3 | Condenser Unit - 5 & 6 Cooling Lord 81.48 KW | nr | 1
4 | Condenser Unit - 7 & 8 Cooling Lord 81.48 KW | nr | 1
5 | Condenser Unit - 9 Cooling Lord 36000 BTU/HR | nr | 1
6 | Condenser Unit - 10 Cooling Lord 24000 BTU/HR | nr | 1
7 | Condenser Unit - 11 Cooling Lord 78000 BTU/HR | nr | 1
8 | Condenser Unit - 12 Cooling Lord 92000 BTU/HR | nr | 1
9 | Condenser Unit - 13 Cooling Lord 84000 BTU/HR | nr | 1
12.4 | Fresh Air Handling Unit ( FAHU )
Supply and install/fixing fresh air handling unit (FAHU) according to the detailed drawing , schedules , specification completely . Rate to include power supply works , related builder's works completely , gas pipes , liquid pipe and fixing fittings and accessories.
1 | FAHU - 01 Cooling Capacity 81.48 KW | nr | 1
2 | FAHU - 02 Cooling Capacity 81.48 KW | nr | 1
3 | FAHU - 03 Cooling Capacity 81.48 KW | nr | 1
4 | FAHU - 04 Cooling Capacity 81.48 KW | nr | 1
12.5 | Exhaust Fans
Rates shall include for supply , installation, wiring , conduit, electrical supply , fittings and necessary accessories as per the drawings & specification.
1 | EF - 1 Capacity 80 CMH | nr | 1
2 | EF - 2 Capacity 750 CMH | nr | 1
3 | EF - 3 Capacity 200 CMH | nr | 1
4 | EF - 4 Capacity 250 CMH | nr | 1
5 | EF - 5 Capacity 480 CMH | nr | 1
6 | EF - 6 Capacity 200 CMH | nr | 1
7 | EF - 7 Capacity 270 CMH | nr | 1
8 | EF - 8 Capacity 1100 CMH | nr | 1
12.6 | Fire Damper ( FD )
| Rates shall include for supply , installation, wiring , conduit, electrical supply , fittings and necessary accessories as per the drawings , schedule & specification. | nr | 8
12.7 | Volume Control Damper( VCD )
| Rates shall include for supply , installation, wiring , conduit, electrical supply , fittings and necessary accessories as per the drawings , schedule & specification. | nr | 16
12.8 | Laminar Canopy Diffuser
| Rates shall include for supply , installation, wiring , conduit, electrical supply , fittings and necessary accessories as per the drawings , schedule & specification. | nr | 4
12.9 | Air Exhaust Square Ceiling Diffuser
Rates shall include for supply , installation, wiring , conduit, electrical supply , fittings and necessary accessories as per the drawings , schedule & specification.
1 | 150 x 150 mm | nr | 16
2 | 225 x 225 mm | nr | 4
3 | 300 x 300 mm | nr | 7
12.1 | Ducting Work
Supply , fabricate & fixing duct with insulation including all the fittings & related accessories according to the manufactures specification & drawings.
1 | 600 x 500 mm | m | 61
2 | 650 x 550 mm | m | 94
3 | 200 x 150 mm | m | 11
4 | 500 x 400 mm | m | 14
5 | 450 x 300 mm | m | 15
6 | 150 x 150 mm | m | 42
7 | 500 x 350 mm | m | 21
8 | 150 x 100 mm | m | 5
9 | 100 x 100 mm | m | 6
10 | 250 x 200 mm | m | 7
11 | 200 x 200 mm | m | 19
12.11 | Pre Insulated Flexible Duct
Supply and fixing Aluminum Flexible Duct with insulation including all the fittings & related accessories according to the drawing.
1 | 250 mm dia. | m | 32
2 | 350 mm dia. | m | 38
12.12 | Exhaust Air Grill - External
Supply and fixing air grill with cover as shown in the detailed drawing & specification completely.
1 | 350 x 350 mm | nr | 1
2 | 200 x 150 mm | nr | 13
3 | 250 x 200 mm | nr | 1
4 | 150 x 150 mm | nr | 2
5 | 300 x 300 mm | nr | 3
6 | 250 x 250 mm | nr | 2
12.13 | Exhaust Air Grill - Internal ( Toilets )
Supply and fixing air grill with cover as shown in the detailed drawing & specification completely.
| 150 x 150 mm | nr | 6
12.14 | Wall Mounted Exhaust Air Grill - Internal ( Return Air )
| Supply and fixing air grill with cover as shown in the detailed drawing & specification completely. | nr | 10
12.15 | Heat Recovery Ventilation Unit ( HRV )
Supply and fixing heat recovery unit as shown in the drawing , schedules & manufactures specification completely. Rate shall cover builder's work , power supply , piping works and necessary fittings , accessories.
1 | HRV-01 - Ventilation Rate 1000 | nr | 1
2 | HRV-02 - Ventilation Rate 2000 | nr | 1
12.16 | Sand Trap Louver With Insect Screen
| Supply and fixing sand trap louver with insect screen unit as shown in the drawing , schedules & manufactures specification completely. Rate shall cover builder's work , power supply , piping works and necessary fittings , accessories. | nr | 8
Total Of Bill No: 12 - Carried to Bill Summary

## Bill - 13 Lift
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 13
Lift Works
13.1 | GENERAL
(a) The Bidder is requested to refer Drawings, Specifications and other relevant documents.
(b) Rates shall include for all necessary electrical wiring and accessories required for completion of the lift installation.
(c) All items shall be supply and complete installation completely.
(d) All the works are according to the drawing and directed by the Engineer.
(e) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(e) This item not applicable.
Total Of Bill No: 13 - Carried to Bill Summary

## Bill 14 - Fire Fighting & alarm
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 14
Fire Fighting & Alarm Works
14.1 | GENERAL
(a) The Bidder is requested to refer the General Notes, Schedules, Drawings, Specifications and other relevant documents.
(b) Shop drawings of the system shall be prepared to the standard of the government's relevant authority and submitted to the Consultant for approval.
(c) All are according to the drawing and specification. Rates shall include all the works completely unless otherwise measured separately.
(d) Rate to include valves , flexible connections , clean agent , pipes , conduits , cables and other fittings & necessary accessories.
(e) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
14.2 | Fire Fighting System
Rate to include supply and fixing completely with proper manufactures quality.
1 | Portable H₂O - 9KG Extinguisher with cover | nr | 4
2 | Portable CO₂ - 4.5KG Extinguisher with cover | nr | 7
3 | Portable DCP - 6KG Extinguisher with cover | nr | 3
14.3 | Fire Alarm System
Rate to include supply and fixing completely with proper manufactures quality.
1 | Break Glass Manual Call Point | nr | 16
2 | Smoke detector - addressable type | nr | 98
3 | Heat detector - addressable type | nr | 6
4 | Fire alarm bell | nr | 16
5 | Flash light | nr | 16
6 | Main fire alarm control panel | nr | 1
14.4 | Fire Resistance Cable
| Supply & laying fire resistance cable with pvc conduit pipe as shown in the drawings & specification completely. | m | 322
14.5 | Pipes for Fire Alarm Related Works
| Supply & laying wet & dry pipes for floor vertical & horizontal, as shown in the drawings & specification completely. | Item | 1
Total Of Bill No: 14 - Carried to Bill Summary

## Bill 15 OT Equipment
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 15
Theater Equipment's & Machines
15 | General
(a) The Bidder is requested to refer Drawings, Specifications and other relevant documents.
(b) All items shall be supply and complete installation/fixing placing completely.
(c) All the works are according to the manufacture's technical specification & requested by the employer/engineer.
(d) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(e) The rates shall cover all the works completely according to the bid details unless otherwise measured separately.
15.1 | Medical Pipes & Gas System
1 | Allow to provide medical pipes & gas supply system . Detailed layout shall be provided by specialized medical gas installation contractor. | Item | 1
2 | Rate to include Oxygen Pipes , Nitrous Oxide Pipes , Medical Air 4 Bars Pipes , Surgical Air 7 Bars Pipes , Vacuum Pipes , Anesthetic Gas SCAVENGING .
15.2 | Manpower providing on Equipment installation.
| Below mentioned equipment’s supply and installation works will be done by medical equipment supplier. Contractor to be provide workmanship and material for the small adjustment works, if required. The rates shall cover any cutting, wiring, extra gas pipe connection, ceiling adjustments or any structural changes or support works needed to installation of machinery and equipment’s. | Item | 1
1 | Pendants (Anesthesia and surgical) Installation Works
2 | Bedheads Unit Installation Works
3 | Wall mount medical gas and air system (AGSS, SURGICAL AIR, MEDICAL AIR, VACUUM, N2O AND O2)
4 | OT light
5 | OT table
6 | UV Disinfection Light
Total Of Bill No: 15 - Carried over to summary

## Bill 16 Furniture-common
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 16
Furnitures & Common Equipments
16.1 | General
(a) The Bidder is requested to refer Drawings, Specifications and other relevant documents.
(b) All items shall be supply and complete installation/fixing placing completely.
(c) All the works are according to the manufacture's technical specification & requested by the employer/engineer.
(d) Where there may be any discrepancies between the drawings and BOQ , details given in the drawings shall proceed.
(e) The rates shall cover all the works completely according to the bid details unless otherwise measured separately.
16.2 | Furnitures & Common Equipments
Supply & placing furniture works as shown in the drawings , schedules , manufacture's specification completely.
1 | Workstation Table ( Item Code : T6-31-401 ) | nr | 4
2 | Nurses Workstation 3 Pax ( Item Code : T6-31-402 ) | nr | 1
3 | Nurses Workstation 5 Pax ( Item Code : T6-31-403 ) | nr | 1
4 | Storage Rack ( Item Code : T6-35-401 ) | nr | 1
5 | Washer/Disinifector ( Item Code : T6-53-601 ) | nr | 1
6 | Bed Pan Washer ( Item Code : T6-53-602 ) | nr | 1
7 | Storage Cabinet With Zink ( Item Code : T6-54-201 ) | nr | 1
8 | Storage Cabinet With Zink ( Item Code : T6-54-202 ) | nr | 1
9 | Storage Cabinet With Zink ( Item Code : T6-54-203 ) | nr | 1
10 | Kitchen Cabinet ( Item Code : T6-55-101 ) | nr | 1
11 | Storage Container ( Item Code : T6-68-101 ) | nr | 1
Total Of Bill No: 16 - Carried over to summary

## Bill 17 Additional
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 17
Additional Works
17.1 | General
The Contractor shall describe and price hereunder any items/quantities shown on the drawings, mentioned in the Specifications, or required for the satisfactory completion of the project, not mentioned in the BOQ.
Total Of Bill No: 17 - Carried over to summary

## Bill 18 -Ommission Work
Item | Description | Unit | Quantity | Rate (MVR) | Amount (MVR)
Bill No: 18
Omission Works
18.1 | General
Total Of Bill No: 18 - Carried over to summary