TECHNICAL SPECIFICATIONS

(Section VI – Employer’s Requirements)

Client: Ministry of Health

Consultant: Riyan Pvt Ltd

Funding Agency: Government of Maldives

TECHNICAL SPECIFICATIONS

1.      PRELIMINARIES .................................................................................................................................... 1

1.1        STANDARD AND CODES ............................................................................................................................ 1

1.2        DRAWINGS AND SPECIFICATIONS ................................................................................................................ 1

1.3        TRANSPORTATION TO THE SITE................................................................................................................... 1

1.4        SCHEDULE AND EXECUTION PLAN ............................................................................................................... 1

1.5        REPAIRING AND CORRECTION .................................................................................................................... 1

1.6        WORKMANSHIP AND MATERIALS................................................................................................................ 1

1.7        OBVIOUS WORK ..................................................................................................................................... 2

1.8         PROTECTION ......................................................................................................................................... 2

1.9        SCAFFOLDING......................................................................................................................................... 2

1.10      CONSTRUCTION MACHINERY, PLANTS AND EQUIPMENT’S ................................................................................2

1.11      SAMPLES............................................................................................................................................... 3

1.12      ORDERING MATERIALS............................................................................................................................. 3

1.13      WATER AND ELECTRICITY FOR THE WORKS ................................................................................................... 3

1.14      SITE OFFICES FOR CONTRACTOR ................................................................................................................. 3

1.15      CONTRACTOR’S SITE AREA ........................................................................................................................ 4

1.16      PROGRESS MEETINGS .............................................................................................................................. 4

1.17      PROGRESS PHOTOGRAPHS ........................................................................................................................ 4

1.18      SETTING OUT ......................................................................................................................................... 5

1.19      BILLBOARDS........................................................................................................................................... 5

1.20      LOADING IN EXCESS OF DESIGN LOAD .......................................................................................................... 5

1.21      BUILDING PERMIT ................................................................................................................................... 5

1.22      PERMANENT DRAINAGE, ELECTRICITY AND WATER CONNECTION ....................................................................... 6

1.23      HANDING OVER...................................................................................................................................... 6

2. SITE WORKS............................................................................................................................................... 7

2.1        DEMOLITION.......................................................................................................................................... 7

2.2        SITE CLEARANCE ................................................................................................................................... ...8

2.3        EXCAVATION ........................................................................................................................................ ..8

2.4        DE‐WATERING...................................................................................................................................... ..9

2.5        BACKFILL............................................................................................................................................. 10

3. CONCRETE WORKS.................................................................................................................................. 11

3.1        GENERAL............................................................................................................................................. 11

3.2         CEMENT............................................................................................................................................. 11

3.3        AGGREGATE......................................................................................................................................... 11

3.4        WATER ............................................................................................................................................... 13

3.5        HANDLING AND STORAGE OF MATERIAL..................................................................................................... 13

3.6        MIX PROPORTION AND STRENGTH ............................................................................................................ 13

3.7        PRODUCTION OF CONCRETE .................................................................................................................... 14

3.8        TRANSPORTING AND PLACING.................................................................................................................. 15

3.9        CONCRETE CURING................................................................................................................................ 16

3.10      TEST .................................................................................................................................................. 16

3.11      CONCRETE........................................................................................................................................... 17

3.12      DEFECTIVE CONCRETE AND FINISHES ......................................................................................................... 17

4. CONCRETE FORMWORK.......................................................................................................................... 18

4.1        STRUCTURE AND MATERIAL..................................................................................................................... 18

4.2        PERFORMANCE..................................................................................................................................... 18

5. STEEL REINFORCEMENT .......................................................................................................................... 21

5.1        MATERIAL ........................................................................................................................................... 21

5.2        CLEANING ........................................................................................................................................... 21

5.3        BENDING AND LAPS ............................................................................................................................... 21

5.4        REINFORCEMENT COVER......................................................................................................................... 21

5.5        PLACING ............................................................................................................................................. 21

6. WATER PROOFING.................................................................................................................................. 23

6.1        DESCRIPTION OF WORK .......................................................................................................................... 23

6.2        MATERIALS.......................................................................................................................................... 23

6.3        STORAGE OF MATERIALS ......................................................................................................................... 23

6.4        SURFACE PREPARATION .......................................................................................................................... 23

6.5        APPLICATION ....................................................................................................................................... 24

6.6        CURING .............................................................................................................................................. 24

7. EMBEDDED DAMPPROOF MEMBRANE.................................................................................................... 25

7.1        GENERAL............................................................................................................................................. 25

7.2        PRODUCTS........................................................................................................................................... 25

7.3        WORKMANSHIP.................................................................................................................................... 25

8. STRUCTURAL STEEL................................................................................................................................. 26

8.1        SCOPE ................................................................................................................................................ 26

8.2        MATERIALS.......................................................................................................................................... 26

8.3        FABRICATION ....................................................................................................................................... 26

8.4        BOLT.................................................................................................................................................. 27

8.5        WELDING............................................................................................................................................ 27

8.6        ERECTION AND FIELD PAINTING................................................................................................................ 28

8.7        ANCHOR BOLT...................................................................................................................................... 29

9. MASONRY .............................................................................................................................................. 30

9.1        MATERIALS.......................................................................................................................................... 30

9.2        GENERAL............................................................................................................................................. 30

9.3        BLOCKWORK ........................................................................................................................................ 31

10. PLASTERING.......................................................................................................................................... 33

10.1      GENERAL............................................................................................................................................. 33

10.2      MATERIALS AND STORAGE ...................................................................................................................... 33

10.3      MIXING RATIO...................................................................................................................................... 33

10.4      THICKNESS OF COATING ......................................................................................................................... 33

10.5      FINISH ................................................................................................................................................ 34

10.6      GENERAL PREPARATION ......................................................................................................................... 34

10.7      EXTERNAL PLASTERING........................................................................................................................... 34

10.8      INTERNAL PLASTERING ........................................................................................................................... 35

10.9      EXTERNAL RENDERING ........................................................................................................................... 35

10.10         METAL MESH LATHING / REINFORCEMENT FOR PLASTERED/COATINGS........................................................ 36

11. CARPENTRY AND JOINERY..................................................................................................................... 37

11.1      MATERIALS.......................................................................................................................................... 37

11.2      PRESERVATION OF TIMBER ...................................................................................................................... 37

11.3      HARDWARE ......................................................................................................................................... 37

11.4      DIMENSIONS AND FINISH ........................................................................................................................ 37

11.5      WORKMANSHIP.................................................................................................................................... 38

12. ALUMINIUM DOORS AND WINDOWS................................................................................................... 39

12.1      ALUMINIUM DOORS AND WINDOWS......................................................................................................... 39

12.2      ALUMINIUM LOUVERS ............................................................................................................................ 40

12.3      TOP HUNG WINDOWS, VENTILATORS AND SIDE HUNG DOORS .......................................................................... 41

12.4      INSTALLATION ...................................................................................................................................... 41

12.5      SEALING JOINTS .................................................................................................................................... 42

12.6      GLASS INSTALLATION ............................................................................................................................. 42

13. DRY WALL PANELS................................................................................................................................ 44

13.1 REFERENCES.............................................................................................................................................. 44

13.2 SYSTEM DESCRIPTION.................................................................................................................................. 44

13.3 SUBMITTALS.............................................................................................................................................. 45

13.4 QUALITY ASSURANCE .................................................................................................................................. 46

13.5 DELIVERY, STORAGE & HANDLING ................................................................................................................. 46

13.6 PROJECT CONDITIONS ................................................................................................................................. 47

13.7 WARRANTY............................................................................................................................................... 47

PRODUCTS .................................................................................................................................................... 47

13.8 COMPOSITE FIRE RESISTIVE METAL PANELS ....................................................................................................... 47

13.9 PRODUCT SUBSTITUTIONS ............................................................................................................................ 47

13.10 COMPOSITE METAL PANEL MATERIALS ......................................................................................................... 47

13.11 ACCESSORIES........................................................................................................................................... 48

13.12 RELATED MATERIALS................................................................................................................................. 48

13.13 FABRICATION........................................................................................................................................... 48

13.14 FINISHES ................................................................................................................................................ 48

13.15 SOURCE QUALITY ..................................................................................................................................... 49

EXECUTION ................................................................................................................................................... 49

13.16 MANUFACTURER’S INSTRUCTIONS................................................................................................................ 49

13.17 EXAMINATION ......................................................................................................................................... 49

13.18 PREPARATION.......................................................................................................................................... 49

13.19 INSTALLATION.......................................................................................................................................... 49

13.20 FIELD QUALITY REQUIREMENTS ................................................................................................................... 49

13.21 ADJUSTING ............................................................................................................................................. 49

13.22 CLEANING............................................................................................................................................... 50

13.23 PROTECTION ........................................................................................................................................... 50

14. ROOFING .............................................................................................................................................. 51

14.1      SCOPE ................................................................................................................................................ 51

14.2      ROOF CLADDING................................................................................................................................... 51

14.3      PRODUCTS........................................................................................................................................... 51

14.4      WORKMANSHIP.................................................................................................................................... 51

14.5      FIXING................................................................................................................................................ 52

14.6       FITTINGS AND FEATURES ........................................................................................................................ 52

15. FINISHES............................................................................................................................................... 54

15.1      GENERAL............................................................................................................................................. 54

15.2      MANUFACTURERS ................................................................................................................................. 54

15.3      CERAMIC AND VITREOUS TILE MATERIALS .................................................................................................. 54

15.4       FLOORING........................................................................................................................................... 54

15.5       WALL PAPERS ..................................................................................................................................... 56

15.6       WOOD VENEERS ................................................................................................................................... 56

15.7       CEILING.............................................................................................................................................. 56

15.8       CORNER GUARDS ................................................................................................................................. 57

15.9       SKIRTING ............................................................................................................................................ 57

15.10     CRASH RAILS ....................................................................................................................................... 57

15.11     SPLASH PROTECTION ............................................................................................................................. 57

15.12     RADIATION PROTECTION ........................................................................................................................ 58

15.13     BENCH TOPS……………….......................................................................................................................... 58

15.14     PARTITION WALLS .............................................................................................................................. 58

15.15     MORTAR MATERIALS ............................................................................................................................ 58

15.16     CEMENT COLOURS............................................................................................................................... 59

15.17     WATERPROOFING ……………................................................................................................................. 59

15.18     INSTALLATION REQUIREMENTS .............................................................................................................. 59

15.19     FLOOR TILE INSTALLATION ..................................................................................................................... 59

15.20     WALL TILE INSTALLATION   ………………..................................................................................................... 60

15.21     GROUTING ……................................................................................................................................... 60

15.22     DEFECTS IN TILES AND TILE LAYING ......................................................................................................... 60

15.23     GUARANTEES ..................................................................................................................................... 61

16. PAINTING ................................................................................................................................................ 62

16.1      MATERIAL ............................................................................................................................................... 62

16.2      DEFINITION OF TERMINOLOGY ..................................................................................................................... 62

16.3      PAINT FINISH SYMBOLS .............................................................................................................................. 63

16.4      PAINTING IN GENERAL ............................................................................................................................... 63

16.5      PROCEDURE OF PAINTING ........................................................................................................................... 64

17.PLUMBING...................................................................................................................................................71

17.1      GENERAL ..............................................................................................................................................71

17.2      DRAWINGS AND INFORMATION REQUIRED...................................................................................................72

17.3      RECORD DRAWING.................................................................................................................................72

17.4      OPERATING AND MAINTENANCE INSTRUCTIONS............................................................................................72

17.5      TESTS .................................................................................................................................................72

17.6      WORK IN COMMON PIPING......................................................................................................................73

17.7      WATER SUPPLY WORK ............................................................................................................................79

17.8      WATER PUMPS .....................................................................................................................................79

17.9      SPACING OF SUPPORTS ..........................................................................................................................80

17.10    DRAINAGE WORK .................................................................................................................................80

17.11    LAYING OF PIPES ..................................................................................................................................80

17.12    LAYING OF SEWER WATER MAINS............................................................................................................. 81

17.13    SEWERS .............................................................................................................................................81

17.14    U.P.V.C PIPES ......................................................................................................................................82

17.15    BENDS AND OTHER SPECIALS ..................................................................................................................82

17.16    FLANGED JOINTS .................................................................................................................................82

17.17    SUPPORT FOR U.P.V.C PIPES ...................................................................................................................82

17.18    SEWER PIPES ......................................................................................................................................83

17.19    AIR VALVES ........................................................................................................................................83

17.20    SCOUR WASHOUT VALVE.......................................................................................................................83

17.21    FOOT VALVES AND STRAINERS ................................................................................................................83

17.22     PRESSURE REDUCERS ..........................................................................................................................83

17.23     WATER METER ..................................................................................................................................83

17.24      EQUILIBRIUM BALL VALVES .................................................................................................................83

17.25      FITTINGS.........................................................................................................................................84

17.26      MANHOLES, MANHOLE COVERS AND FRAMES...........................................................................................84

17.27      INTERCEPTOR MANHOLE ....................................................................................................................85

17.28      FIXTURES AND ACCESSORIES ...............................................................................................................85

17.29      AS BUILT DRAWINGS .........................................................................................................................85

17.30      MISCELLANEOUS ..............................................................................................................................85

18.ELECTRICAL INSTALLATIONS...................................................................................................................90

18.1      GENERAL .............................................................................................................................................90

18.2      CONDUIT AND CONDUIT ACCESSORIES ........................................................................................................93

18.3      WIRES, CABLES AND CORDS ......................................................................................................................94

18.4      WIRING ACCESSORIES..............................................................................................................................95

18.5      LIGHT FIXTURES .....................................................................................................................................96

18.6      TESTING ...............................................................................................................................................98

18.7      INSTALLATION INSTRUCTION .....................................................................................................................98

18.8      DISTRIBUTION BOARD .............................................................................................................................99

18.9      TELEPHONE SYSTEM................................................................................................................................99

19.HVAC SYSTEM………………….....................................................................................................................100

19.1      GENERAL .............................................................................................................................................100

19.2      BASIS OF DESIGN ...................................................................................................................................100

19.3      REGULATION AND SHOP DRAWING ............................................................................................................100

19.4      HVAC SYSTEM........................................................................................................................................100

19.5      AIR CONDITIONING SYSTEM ......................................................................................................................100

19.6      REFRIGERENT AND CONDENSATE PIPEWORK .................................................................................................101

19.7      DUCT WORK AND INSULATION ..................................................................................................................102

19.8      AIR DIFFUSERS/ REGISTERS/ GRILLES/ LOUVRES .............................................................................................102

19.9      MECHANICAL FANS.................................................................................................................................102

19.10    SITE TESTING AND COMMISSIONING…………………………….............................................................................103

20.CCTV SPECIFICATION……….....................................................................................................................104

20.1      SYSTEM DESIGN .....................................................................................................................................104

20.2      SYSTEM PERFORMANCE CRITERIA ..............................................................................................................104

20.3      GENERAL REQUIREMENT OF CCTV EQUIPMENT ..............................................................................................105

20.4      REGULATIONS AND CODE OF PRACTICE........................................................................................................105

20.5      TESTING ..............................................................................................................................................105

20.6      ITEM SPECIFICATION …………………………….................................................................................................106

21.PUBLIC ADDRESSING SYSTEM & BACKGROUND MUSIC (PA & BGM) SYSTEM SPECIFICATION………........113

21.1      SYSTEM DESIGN .....................................................................................................................................113

21.2      SYSTEM PERFORMANCE CRITERIA ..............................................................................................................113

21.3      GENERAL REQUIREMENT OF PA & BGM EQUIPMENT........................................................................................114

21.4      REGULATIONS AND CODE OF PRACTICE........................................................................................................114

21.5      TESTING ..............................................................................................................................................114

21.6      ITEM SPECIFICATION …………………………….................................................................................................115

22.FIRE DETECTION AND PROTECTION SYSTEM…………………………………………………………………………..……........122

22.1      GENERAL...............................................................................................................................................122

22.2      STANDARDS AND CODES ……………............................................................................................................122

22.3      TECHNICAL SPECIFICATION FOR WET RISER / FIRE HOSE REEL SYSTEM...................................................................123

22.4      TECHNICAL SPECIFICATION FOR PORTABLE FIRE EXTINGUISHER...........................................................................131

22.5      TECHNICAL SPECIFICATION FOR FIRE DETECTION AND ALARM SYSTEM .................................................................133

23.ELECTRONIC ACCESS CONTROL SYSTEM (EACS)………………………………………………………………………..…….......149

23.1      APPLICATION OF THE SECTION....................................................................................................................149

23.2      GENERAL……………………… ……………............................................................................................................149

23.3      OPERATION AND MAINTENANCE MANUALS………………………………………...................................................................149

23.4      APPROVAL OF INFORATION SUBMITTED…………………………………............................................................................149

23.5      TESTING AND COMMISSIONING OF SYSTEMS ………………………………................................................................149

23.6      EQUIPMENT, MATERIALS, FITTINGS AND ACCESSORIES……………………................................................................149

23.7      PRODUCT BRANDS ……………………………….................................................................................................150

23.8      DRAWINGS ………………………………..........................................................................................................150

23.9      MAINTENANCE ACCESS AND OPENINGS ………………………………......................................................................150

23.10    CODES AND STANDARDS ……………………………….........................................................................................150

23.11    SYSTEM DESIGN ………………………………....................................................................................................150

23.12    SYSTEM PERFORMANCE CRITERIA ………………………………..............................................................................151

23.13    GENERAL REQUIREMENT OF EACS EQUIPMENT ……………………………….............................................................151

23.14    REGULATIONS AND CODE OF PRACTICE ……………………………….......................................................................152

23.15    TESTING………………………………...............................................................................................................152

23.16    ITEM SPECIFICATIONS ……………………………….............................................................................................153

24.NURSE CALL SYSTEM SPECIFICATION……………………………………………………………………………………..…….........162

24.1      SYSTEM DESIGN .....................................................................................................................................162

24.2      SYSTEM PERFORMANCE CRITERIA….............................................................................................................162

24.3      GENERAL REQUIREMENT OF NURSE CALL SYSTEM EQUIPMENT……….....................................................................163

24.4      REGULATIONS AND CODE OF PRACTICE………………………………….............................................................................163

23.5      TESTING………………………………...............................................................................................................163

23.6      ITEM SPECIFICATIONS ……………………………….............................................................................................164

25.ELECTRONIC ACCESS CONTROL SYSTEM (EACS)………………………………………………………………………..…….......167

25.1      SCOPE OF WORK.....................................................................................................................................167

25.2      PABX SYSTEM IN GENERAL…..………............................................................................................................167

25.3      SYSTEM HARDWARE………………………………….………………………………………...................................................................168

25.4      SYSTEM SOFTWARE………………………………….....................................................................................................169

25.5      SYSTEM CAPACITY ……………………………….................................................................................................170

25.6      NUMBERING PLAN…………………….............................................................................................................170

25.7      PABX FEATURES AND FACILITIES……………….….................................................................................................170

25.8      PC BASED ATTENDANT CONSOLE.……..........................................................................................................174

25.9      DIGITAL TELEPHONE……………………………. ………………………………......................................................................180

25.10    SINGLE LINE TELEPHONE SET.………………………….........................................................................................180

25.11    EARTHING ………………………………...........................................................................................................180

25.12    TECHNICAL SUPPORT STAFF ……………………………….....................................................................................180

25.13    WARRANTY ……………………………….........................................................................................................180

25.14    TRAINING ………………………………...........................................................................................................180

26.TELEPHONE SYSTEM SPECIFICATION……………………………………………………………………………………..…….........181

26.1      GENERAL ...........................................................................................................................................181

26.2      TELEPHONE WIRING AND INSTALLATION......................................................................................................181

26.3      TELEPHONE MANHOLE AND PIT……………………………………………………….....................................................................182

26.4      EARTHING…………………………………………..………………………………….............................................................................183

26.5      TESTING AND COMMISSIONING…................................................................................................................183

27.SOLAR PANEL SYSTEM……………………………………………………………………………………………………….…..……........184

1.    PRELIMINARIES

1.1         Standard and Codes

1.1.1      The Contractor shall, perform the Works in compliance with all regulations, standard specifications or statutes of the Government of Maldives unless otherwise conform to this specification.

1.1.2      The current British Standard Specifications and Codes of Practice, And Australian Health Facility Guidelines (AusHFG) shall apply to and form part of these specifications unless otherwise specified in respect of all materials and works to which they have application.

1.2         Drawings and Specifications

1.2.1      Drawings and Specifications are intended to complement each other, so that if anything is shown on the Drawings, but not mentioned in the specifications or vice  versa, it is to be furnished and built as though specifically set forth in all three. If any discrepancies, errors, ambiguities, or omissions occur in the Drawings or Specifications, the same shall be referred to the Consultant before proceeding with the Works, and the Consultant decision on such discrepancies, errors, ambiguities or omissions shall be final.

1.2.2      In addition to the Drawings and Specifications attached hereto, the Consultant will during the progress of the Works furnish additional Drawings, Specifications,  and  instructions  as may  be  necessary,  in  the  opinion  of the  Consultant  for  the  purpose  of the  proper  and adequate execution and maintenance of the Works, and the Contractor shall make his work conform.  Such drawings and instructions shall  be  deemed  to  be  part  of  the  Contract Documents.

1.3         Transportation to the Site

1.3.1      The Contractor shall provide all necessary transport, handling and storage of all materials, components  and the like to their points of installation  on site including  transport  to and from storage. The Contractor shall provide all necessary transport of labour to and from the site.

1.4         Schedule and Execution Plan

1.4.1      The Contractor  shall prepare  and submit  to the Consultant  for approval  the  construction schedule and an execution plan of temporary facilities, stockyards, etc., before the start of the Works.

1.5         Repairing and Correction

1.5.1      Any breakage(s) or defect(s) of existing buildings, road utilities, or part(s) of them caused by the  Works  including  transportation  for  the  works  shall  be  repaired  or  corrected  by  the Contractor with his responsibility.

1.6         Workmanship and Materials

1.6.1     All workmanship shall be of the best standard. All goods and materials to be incorporated in the Works must be new, unused, of the most recent or current models and incorporate all recent improvements in design and materials unless provided otherwise in the contract.

1.6.2     The Contractor shall submit for the approval of the Consultant a list of names and addresses of the manufacturers  and trade marks or names of all the various types of  materials  and

goods he propose to use in the Works. The list shall include reference to the specifications clause or article to which the materials and goods apply.

1.6.3     Materials  shall  be  obtained  from  approved  sources  and  used  in  accordance  with  the manufacturer’s  printed  instructions.  In  the  absence  of  a  specification  all  materials shall comply with a relevant standard. The consultant  shall order the removal of any materials, which he has not approved.

1.6.4     No orders for materials and goods shall be placed until approval has been obtained for the materials and goods from the consultant.

1.6.5     The Contractor shall note that it is his responsibility to include in his price for the cost of the materials and products as specified and no adjustment will be allowed should the consultant reject the alternatives.

1.7         Obvious Work

1.7.1      Where an item of work is obviously required for the type of work being undertaken then it shall be deemed to have been included even though the item is not specifically mentioned or shown in the Drawings or Specifications.

1.8          Protection

1.8.1      The Contractor  shall have  the Works  and  adjoining  properties  protected  from  inclement weather.  Any loss or damage  caused by weather,  carelessness  or lack of  skill of workers, accident or otherwise shall be of such property that is affected. The Contractor shall provide all necessary dustsheets, barriers and guardrails and clear away at completion.

1.8.2      The  work  shall  be  suspended  for  such  time  as may  be  directed  and/or  approve  by  the

Consultant if the specified quality of work is difficult to maintain during inclement weather.

1.9         Scaffolding

1.9.1      The  Contractor  shall  provide,  erect,  maintain,  dismantle  and  clear  away  at  completion proper and adequate including that required for subcontractor  and suppliers. Putlog holes shall be made good to match the adjacent surface as the scaffolding is dismantled.

1.9.2      The  Contractor  shall  be  responsible  for  all  safety  precautions  in  connection  with  the scaffolding including the provision of all bracing, scaffold boards, toe boards and the like and for entire sufficiency for the work.

1.10       Construction Machinery, Plants and Equipment’s

1.10.1   All necessary construction machines shall be provided and maintained by the Contractor and shall be approved by the Consultant.

1.10.2   If cranes or any other type of plant which places any load on the structure are proposed, all details of such plant shall be submitted  to the Consultant  for approval before the work is actually   commenced.   If   approved   by   the   Consultant   and   contractually   acceptable, permission may be given for the structure to be strengthened,  in order to carry out loads, and the Contractor shall be responsible for any resulting additional costs.

1.10.3   The Contractor shall be responsible for making good to the satisfaction of the Consultant any damage to the permanent structure that may be caused by his plant and equipment.

1.11       Samples

1.11.1   The Contractor  shall furnish  for the approval  with reasonable  promptness,  all  samples as directed  by the consultant.  The  Consultant  shall  check  and  approve  such  materials  with reasonable promptness only for conformance with the design concept of the Works and for compliance  with  the  information  given  in the Contract  Document.  The  Work  shall  be in accordance with the approved samples

1.11.2   All  samples  shall  be  delivered  to  the  Consultant’s  office  with  all  charges  in  connection therewith paid by the Contractor and deemed to be included in the Contract Price.

1.11.3   Duplicate final approved samples, in addition to any required for the Contractor’s use, shall be furnished to the Consultant, one for office use and one for the site.

1.11.4   Samples shall be furnished so as not to delay fabrication, allowing the consultant reasonable time for consideration of the sample submitted.

1.11.5   Each  sample   shall  be  properly   labelled   with  the  name  and  quality  of  the   material, manufacturer’s  name, name of project, the contractor’s name and date of submission, and the specification clause to which the sample refers.

1.12       Ordering Materials

1.12.1   The Bills of Quantities shall not be used as a basis for ordering materials and the Contractor is entirely responsible for assessing the quantities of materials to be ordered.

1.12.2   Upon  receipt  of  the  Consultant’s  order  to  commence  the  Works,  the  Contractor  shall immediately  place  orders  for all required  materials  and  will be held  responsible  for  any delays occurring due to late placing of such orders.

1.12.3   The Contractor  shall pay all expenses, taxes and dues etc. incurred on the procurement of materials from abroad

1.13       Water and Electricity for the Works

1.13.1   The Contractor shall make all necessary arrangements  and provide all water for the proper execution  of  the  Works,  together  with  all  transport,  temporary  plumbing,  storage  and distribution, pay all charges and alter, adept and maintain temporary work as necessary and remove and make good at completion.

1.13.2   The Contractor shall make all necessary arrangements  and provide all artificial lighting and power  (maintain  a generator  if necessary)  for  the  proper  execution  and  security  of the Works and its protection, with all meters, temporary wiring and fittings, pay all charges and alter adapt and maintain the temporary work as necessary and remove and make good at completion.

1.14       Site Offices for Contractor

1.14.1   The  Contractor  shall  provide  maintain  and  clear  away  on completion  of the  Contract all necessary site offices, canteens, messing and welfare facilities, temporary buildings, toilets and the like for all site staff employed by the Contractor and required by subcontractors and suppliers.

1.14.2   The offices shall be open at all normal working  hours to receive instructions,  notices  and other communications.

1.14.3   The Contractor shall obtain the approval of the Consultant of the proposed site layout, type and drainage arrangement of all the buildings prior to erection of same. All buildings shall be supplied and maintained in good condition and of neat appearance, all maintenance to same as instructed by the Consultant shall be carried out at the Contractor's expense.

1.14.4   Under no circumstances  shall overnight accommodation  be permitted  on Site except for the site watchman in carrying out his duties.

1.15       Contractor’s Site Area

1.15.1   Throughout   the  period  of  the  Contract  the  Contractor  shall  maintain  the  area  of  his operation  within  the  limits  of  the  Site  in  a  clean,  tidy  and  safe  condition  by  arranging materials and the like in an orderly manner. All rubbish, debris, waste materials and the like shall be systematically cleared from the Site as it accumulates.

1.15.2   The Contractor  shall take all steps necessary  as directed by the Consultant  to minimize or eliminate dust, noise or any other nuisance, which may occur. Plant emitting dust, smoke, excessive noise or other nuisance shall not be permitted.

1.16       Progress Meetings

1.16.1   During the course of the Works, progress meetings shall be held at fortnightly intervals for the purpose  of co‐ordinating  the Contractor's  works and to ensure that full  compliance  is maintained.

1.16.2   Minutes  of  such  meetings  should  be  recorded;  copies  will  be  distributed  to  all  persons concerned and full effect shall be given to all instructions contained therein.

1.16.3   Prior to such meetings the Contractor shall give to the Consultant's Representative details in writing of that portion of the Works he proposes to construct during the coming two weeks with  details  of the  plant  and  method  he  proposes  to  employ.  These  proposals  shall  be discussed at the meeting and no work based on such proposals  shall proceed without the approval of the Consultant's Representative.

1.16.4   The Contractor  shall submit all reports as instructed  by the Consultant  in connection with progress meetings and the day to day management of the Works.

1.17       Progress Photographs

1.17.1   The Contractor  shall supply once a month, at the time of submitting  his Interim Certificates, twelve photographs  from 36 exposures  showing  the progress  of the Works.  The Consultant shall direct the times and position from which the photographs are to be taken.

1.17.2   The photographs shall be submitted in three copies un mounted of a size not less than 15 x

10  centimetres  with  the  description  of  the  viewpoint  stamped  in  ink  on  the  back.  The negative shall have the date on it and remain the property of the Consultant and no prints from these negatives may be supplied to others unless previously authorized in writing by the Consultant.

1.18       Setting Out

1.18.1   The Contractor  shall be responsible  for accurately  setting  out the Works  to the  specified positions,  dimension,  levels  and  Building  Lines  and  also  checking  the  site  surveys  for dimensional   and  level  accuracy  and  reporting  any  discrepancies  before  building  work commences.

1.18.2   The  Contractor  shall  provide  the  Consultant  with  all  facilities,  equipment  and  labour to enable him to check the setting out and levels of the Works at all times. The checking of any setting out point, line or level by the Consultant shall not in any way relieve the Contractor of his responsibility

1.18.3   All setting out points, benchmarks,  site rails, pegs and other survey points shall be clearly marked and protected from damage or disturbance during the execution of the Works

1.19       Billboards

1.19.1   The Contractor  shall provide and maintain  two billboards  for the Site each consisting  of a plastic board panel of size not more than 2.4m x1.2m (2.88m2) supported 2.5m above the ground with steel angle framing or similar material and fixed in concrete foundations.

1.19.2   Each board shall have the following written in both Dhivehi and English (letter height not to exceed 100mm) by a skilled sign writer:

The name of Project

The name of Employer

The name and address of Consultant

The name and address of Contractor

1.19.3   A  scaled  layout  shall  be  prepared   and  submitted   for  the  Consultant's   approval  before fabrication.

1.19.4   No advertising material other than the above will be permitted.

1.19.5   The location and layout of Sub‐Contractors  or Manufacturer's  billboards,  if allowed, must be submitted for the Consultant's approval.

1.20       Loading in Excess of Design Load

1.20.1   No loading  in excess  of the design  loading  shall be placed  on any portion  of the  structure without the written permission of the Consultant

1.20.2   If such permission is granted, all beams or other members of the structure which are subjected to  loading  other  than  the  designed  loading  shall  be  strengthened  and  supported  to  the satisfaction  of  the  Consultant,  and  the  Contractor  shall  be  responsible  for  any  resulting additional costs

1.20.3   The Contractor shall be responsible for making good to the satisfaction of the Consultant any damage to the permanent structure that may be caused by such excess loading.

1.21       Building Permit

1.21.1   The Contractor shall allow for obtaining the building permit and for paying all fees in connection therewith.

1.22       Permanent Drainage, Electricity and Water connection

1.22.1    The Contractor  shall allow for arranging  and obtaining  the permanent  drainage,  water  and electricity connections to the proposed development and he shall be responsible for making all payments in connection therewith.

1.23       Handing Over

1.23.1    Prior to handing over the proposed development  the Contractor shall gain the approvals and respective Completion Certificates from all the local government authorities and the like that the  work  has  been  completed  in  accordance  with  their  requirements.   Any  payment  in connection therewith shall be paid by the Contractor.

2. SITE WORKS

2.1         Demolition

2.1.1      Demolition includes the complete demolition including grubbing up of foundations and the proper  termination  of all services  as required  by the  Drawings  including  the  removal  and disposal of all demolished  materials.  The demolition  work shall be  executed  in a systematic manner.

2.1.2 	Demolition  operations  and  the removal  of debris  shall  be carried  out  to ensure  minimum interference with roads, streets, footpaths and other adjacent occupied or used facilities.

2.1.3 	Damage  caused  to  adjacent  facilities  by  demolition  operations  shall  be  repaired  by  the Contractor  at his own expense.  The Contractor  shall arrange and pay for the  disconnecting, removing and capping of utility services, notify the affected utility agency in advance and obtain written approval before commencing work.

2.1.4 	Before  commencement  of work,  submit  a method  statement  to the  Consultant  as to  the proposed  method and sequence  of demolition  of the building and a safety plan  which shall cover the risk assessment  and safety measures  for such method  statement.  The Consultant reserves the right to prohibit any method of execution of the Works which he regards as unsafe.

2.1.5 	Drawing  information,  particularly  for unconventional  layouts  and  special  structures,  will  be made available to the Contractor if possible. The Contractor shall state in his method statement if it is based  on such drawings.  In the absence  of drawings,  the Consultant  may require  a detailed structural survey to be carried out and endorsed by a Registered Structural Engineer (or equivalent) to define the existing structure and the appropriate method and sequence of demolition.

2.1.6 	No work on site shall be allowed to commence until the proposed method statement has been accepted   and   all   precautionary    measures,   hoardings,    covered   walkways,   and   other requirements are in place.

2.2         Site Clearance

The  Site  shall  be cleared  of all vegetation,  rock,  boulders,  etc.  and  surface  soil  shall  be removed  as  directed  by  the  Consultant.  The  trees  which  are  to  be  retained  shall  be protected from damage

Spreading,  levelling and consolidating  on site where required,  shall be made with suitable surplus  excavated  material  obtained  from  the  Site.  Other  soils  used  for  filling  shall  be approved by the Consultant

The Contractor shall dispose all unsuitable and surplus excavated material

The Contractor shall tidy up and leave the Site in a clean and sanitary condition at all times during the execution of the Works.

2.3         Excavation

2.3.1      Excavation shall be performed to the required depth as shown in the Drawings.

2.3.2      A survey of the existing site shall be made and the results of same submitted to the Consultant before commencement of the work

2.3.3      Excavation area shall be protected from any water flowing in. Sides of excavations shall be shored or inclined to retain excavation unless otherwise specified

2.3.4      Excavation near adjoining structures shall be executed with care so as not to damage those structures.

2.3.5      The Contractor  shall  take  all necessary  precautions  during  the excavation  for the  Works particularly  those excavation  which are adjoining  existing buildings  and shall  protect such buildings  from  the  damage  or  collapse  by  means  of  temporary  or  permanent  shoring, strutting, sheet piling or underpinning  or excavation in short lengths and/or other methods as he deems fit and also he shall properly support all  foundations,  trenches,  walls, floors, etc. affecting the safety of the adjoining existing buildings.

2.3.6      The Contractor shall alter, adopt and maintain all such works described above for the whole period of the Contract and shall finally clear away and make good all damages done.

2.3.7      The construction  and efficiency of the shoring, underpinning,  strutting and the like for the purpose  for which  it is erected  shall  be the responsibility  of the Contractor,  should  any subsidence or any other damage occur due to the inefficiency of the shoring, underpinning, strutting and the like or any other support provided, the damage shall be made good by the Contractor at his own expense and responsibility.

2.3.8      The shoring, strutting, piling and the like, shall be executed in such a manner as to cause as little inconvenience as possible to adjoining owners or the public and the Contractor shall be responsible for negotiating with the adjoining owners the means to safeguard their property and for the use of any portion of their land for the purpose of executing the excavations and no claims submitted on this ground will be entertained.

2.3.9      The Contractor shall be held solely responsible for the safety of the adjoining existing buildings, the sufficiency of all temporary or permanent shoring, underpinning, piling, and the like.

2.3.10   The Contractor  shall  keep  the Consultant  informed  as to manner  in which  he  intends  to proceed  with the execution  of the excavations  and obtain  his approval.  Such approval  if given shall not absolve the Contractor of his responsibility.

2.3.11   Excavation shall extend a sufficient distance from walls, footings, etc. to allow space for placing and removing shoring and formwork,  for performing  all work in the excavations and for the inspection of same.

2.3.12   Excavated  material  shall be deposited  within specified  areas as directed  unless  otherwise specified.

2.3.13   The Contractor is deemed to have inspected the site and to leave ascertained for himself as to the nature of the soil, etc. and also the areas where to collect and stack the materials for which necessary site clearance shall have to be made at his own cost.

2.3.14   Stacking or excavated materials shall be done at places approved by the Consultant and he shall have  recorded  the original  ground  levels  of such  places  jointly  with  the  Contractor before commencement of stacking operation.

2.3.15   Extra  excavation  and  allied  lead/lift  required  specifically  for  providing  working  space  to workmen or shuttering to walls of basement etc. shall be measured for payment, no extra claim being allowed for such work incidental to development  and executions of allied jobs. Only authorized excavation approved by the Consultant shall be paid for

2.3.16   Sufficient  clear  working  space  shall  be  left  all  around  excavated  area.  The  disposal  of waste/unserviceable  materials may be in filling and/or in embankment  according to nature of place of disposal. The appropriate specifications for filling and/or embankment shall apply

2.3.17   All foundation  trenches  shall  be excavated  to the  full  widths  and  depths  shown  on  the drawings or to such greater or smaller depths as may be found necessary in the opinion of the Consultant and so instructed by his representative.

2.3.18   Should any excavation be taken down below the specified levels, the Contractor shall fill in such  excavation  at  his  own  cost  with  cement  concrete  specified  for  foundations,  well rammed in position until it is brought up to the level.

2.3.19   The  Contractor  shall  notify  to the Consultant  when  the excavation  is completed  and  no concrete  or masonry  shall be laid until the Consultant  has inspected  of the soil  for  each individual footing.

2.3.20   All foundation  pits  shall  be refilled  to the  original  surface  of the  ground  with  approved materials, which shall be well consolidated as instructed by the Consultant.

2.3.21   The Contractor  shall erect temporary  barricades  around  the excavations  and if  necessary make provisions of red lamps.

2.3.22   The Contractor shall remove/maintain/restore all service lines like telephone, water supply, electricity etc. without any extra charges.

2.4         De‐watering

2.4.1      Where  the  excavation  level  is below  the natural  water  table  and  it is necessary  to  pump continuously from the excavation or to install a specialist type of dewatering equipment around the perimeter  of the site or excavation,  the Contractor  will be  responsible  for ensuring  the safety and stability of all adjoining structures and services or utilities above or below ground level.

2.4.2 	It will also be the responsibility of the Contractor that the equipment installed shall ensure that the excavation and subsequent construction is carried out in dry conditions.

2.4.3 	Continuous or permanent de‐watering of the excavation or Site may not be undertaken without the written approval of the Consultant and the methods to be employed shall also comply with Codes of Practice and Local Authority requirements.

2.4.4 	The water pumped from the excavations or well points shall be pumped to disposal points or sumps approved  by the Consultant  and the Local Ward Office and if so  required  be passed through settling tanks before disposal.

2.4.5 	Unless prior approval has been obtained no water must be disposed of in the Municipality's sewer systems.

2.5         Backfill

2.5.1     All earth used for filling shall unless otherwise stated, be selected hard dry material from the excavation The maximum dry density of the fill material shall be not less than 1600 kg/m3.

2.5.2     The  backfill  of excavations  shall  be  placed  in horizontal  layers  not  exceeding  300mm  in thickness. Each layer shall be compacted by hand or other mechanical means to the required density before the next layer is added

2.5.3     Care shall be taken when filling or back‐filling to avoid any wedging action or eccentric action upon or against the structure of the work.

2.5.4      Before placing of fill, the surface of the sub‐grade  shall be compacted  at optimum  water content to the same percentage of maximum dry density required of subsequent lay.

2.5.5     The Consultant  will inspect all compacting  devices that the Contractor  proposes  and  shall have the right to reject any device which he feels is unsuitable for the job.

2.5.6     Heavy equipment for spreading and compacting fill and backfill shall not be operated closer to walls than a distance to the difference in height between the top of the footings and the layer being compacted.

2.5.7     When  back‐filling  behind  retaining  walls,  basement  walls and the like the said  structures shall be kept propped during the complete operation. The hydraulic compaction of fill shall not be permitted  and the back filling shall be carried out in  layers not exceeding  150mm thick.

2.5.8     Each layer shall be compacted to 90% of the modified compaction.  No back filling shall be carried out until the wall concrete has achieved its full works cube strength and care shall be exercised so as not to damage the external tanking membrane and its protection.

3. CONCRETE WORKS

3.1         General

3.1.1      Materials  used in the Works shall be new, of the qualities and kinds specified  herein  and equal to approved samples. Delivery shall be made sufficiently in advance to enable further samples to be taken and tested if required. No materials shall be used until approved and materials not approved shall be immediately removed from the Works.

3.1.2      Materials  shall  be  transported,  handled  and  stored  on  the  site  or  elsewhere  in  such  a manner to prevent damage, deterioration or contamination.

3.2          Cement

3.2.1      Cement shall be Ordinary Portland cement of an approved brand.

3.2.2      Cement shall conform to BS 12.

Cement shall be of recent manufacturer and used within 6 months of manufactured date. The Contractor shall with each fresh consignment of cement delivered to the site furnish the

Consultant  with  a copy  of  the  Manufacturer's  statement  of  compliance  with  the  above Standard Specifications together with the date of manufacture, certified by an independent agency in the country of origin and its date of delivery to Site.

Check  tests  will  be  required  by  the  Consultant.  These  tests  shall  be  carried  out  at  the

Contractor's expense.

Any cement  failing  to meet  the required  standards  will be rejected  and replaced  at  the

Contractor's expense.

Any cement not conforming  to BS 12 shall not be used unless otherwise  approved by the

Consultant.

3.3         Aggregate

3.3.1      Fine aggregate shall be river sand conforming to BS 882.

3.3.2      Coarse  aggregate  shall be crushed  stone  excluding  limestone  or derivatives  of  limestone conforming to BS 812.

3.3.3      Aggregate shall not contain injurious amount of rubbish, dirt, organic impurities and other foreign matters.

3.3.4      Strength of aggregate shall be more than that of hardened concrete paste.

3.3.5      Shape of coarse aggregate shall not be flat or slender.

3.3.6      Aggregate to be used in concrete shall possess the qualities indicated in the following tables.

Quality of Aggregates

| Aggregate type | Open dry specific gravity | Percentage of water absorption (%) | Percentage of solid volume for the evaluation of particle shape (%) | Clay lump (%) | Loss in washin g test (%) | Organic impurity (%) | Water soluble chloride (%) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Coarse aggregate | <= 2.5 | <= 3.0 | => 55 | <= 0.25 | <= 1.5 | 0 | <= 0.25 |
| Fine aggregate | >=2.5 | <= 3.5 | ‐ | <= 1.0 | <= 3.0 | 0 | <= 0.01 |

Colour of test solution not to be darker than standard solution

Grading requirements for aggregates

Percentage passing each sieve by weight (%)

| Agg. | Max. size (mm) | Nominal sieve size (mm) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 40 | 30 | 25 | 20 | 15 | 10 | 5 | 2.5 | 1.2 | 0.6 | 0.3 | 0.1 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |
| Coarse | 25 | 100 | 100 | 90 | 60 |  | 20 | 0 | 0 |  |  |  |  |
|  |  |  |  | ‐ | ‐ |  | ‐ | ‐ | ‐ |  |  |  |  |
|  |  |  |  | 100 | 90 |  | 50 | 10 | 5 |  |  |  |  |
|  | 20 |  |  | 100 | 90 |  | 20 | 0 | 0 |  |  |  |  |
|  |  |  |  |  | ‐ |  | ‐ | ‐ | ‐ |  |  |  |  |
|  |  |  |  |  | 100 |  | 55 | 10 | 50 |  |  |  |  |
| Fine |  |  |  |  |  |  | 100 | 90 | 80 | 50 | 25 | 10 | 2 |
|  |  |  |  |  |  |  |  | ‐ | ‐ | ‐ | ‐ | ‐ | ‐ |
|  |  |  |  |  |  |  |  | 100 | 100 | 90 | 65 | 35 | 10 |

3.3.7        Manufactured  sand and blast furnace  slag to be use in concrete  shall not be used  unless otherwise specified or approved by the Consultant.

3.3.8     In  case  of  using  fine  aggregate  of  0.01%  or  more  water  soluble  chloride  content,  the necessary  measures  for  corrosion  inhibiting  of  reinforcement  shall  be  instructed  by  the Consultant.

3.3.9     The maximum size of coarse aggregate shall be 25 mm.

3.3.10   Sources of aggregate  shall be to the approval of the Consultant  and samples of aggregate from the proposed source shall be submitted to the Consultant  at least 28 days before its intended use.

3.4         Water

3.4.1      Water shall not contain injurious amount of impurities that may adversely affect concrete and reinforcement.

3.4.2      Ground water shall not be used for concrete works.

3.4.3     Water shall be obtained from a public supply where possible, and shall be taken from any other sources only if approved by the Consultant.

3.4.4     Only water of approved quality shall be used for washing out formwork, curing concrete and similar surfaces.

3.5         Handling and Storage of Material

3.5.1      Cement

3.5.1.1                Cement shall be stored in a manner to prevent weathering.

3.5.1.2                Bagged cement  shall be piled no more than 10 bags so as to permit  easy inspection

3.5.2      Cement  caked  even to the slightest  extent  shall not be used.  Such  cement  and  rejected cement shall be immediately separated from other bags of cement so that they shall not be mistaken for others.

3.5.3      Aggregate

3.5.3.1                Aggregate shall be stored in a manner effectively separating coarse and fine aggregate  according  to type and shall be prevented  from inclusion  of dirt, rubbish and other undesirable foreign matters.

3.5.3.2                Coarse  aggregate  shall  be  unloaded  and  piled  in  a manner  not  to  cause segregation of small and large particles. Aggregate to be stored in piles shall be in mounds of moderate height and at a location where good drainage is provided.

3.6         Mix Proportion and Strength

3.6.1      Mix ratio for reinforced concrete shall be in the proportion  1:2:3 (cement: fine aggregate:

coarse aggregate) by dry volume.

3.6.2      Mix ratio for lean concrete shall be in the proportion 1:2:6 (cement: fine aggregate: coarse aggregate) by dry volume.

3.6.3      Water‐cement ratio for concrete shall be 0.4% to 0.45%

3.6.4      The specified design strength of reinforced concrete shall be 25 N/mm²

3.6.5      The required slump of concrete shall be 100 mm.

3.6.6      Design mix proportion shall be to obtain required workability, consistency and durability.

3.6.7      The lean concrete shall be 15 N/mm²

3.7         Production of Concrete

3.7.1      Field‐mixed Concrete Plant

3.7.1.1                The  Contractor  shall  select  the  necessary  facilities  for  storage,  batching, mixing  and  transporting  of  each  of  the  materials  and  submit  them  for approval of the Consultant prior to start work.

3.7.2      Measuring

3.7.2.1                All materials shall be measure by volume for each batch and water may be measured volumetrically.

3.7.2.2                Cement  shall  be  measured  by  number  of  bags  unless  automatic  cement weight measure is in use.

3.7.3      Mixing Control

3.7.3.1                Concrete   mixture   shall   be   constantly   controlled   to   obtain   required workability  and  mixed  strength.  Mixing  time  for  each  batch  shall  be  not more than 3 minutes.

3.7.4      Quality Control

3.7.4.1                The Contractor  shall conduct tests for quality control toward insuring  that concrete of the required quality is constantly produced.

3.7.4.2                The   Contractor   shall   have   all   quality   control   tests   report   ready   for submission as required by the Consultant.

3.7.5      Quality Inspection of Concrete at the Point of Placement

3.7.5.1                The Contractor  shall conduct tests on concrete at the point of  placement.

When test results meet the tolerances  given below, the concrete  shall  be qualified to have passed the tests.

The tolerance  between  actual  slump  and required  slump  of the  concrete shall be    2.0 mm

3.7.5.2                For  the  estimation  of  compressive  strength  of  concrete  in  compressive strength tests, when the average value of compressive strength of concrete obtained in a test is not less than the specified design strength, it shall be qualified   to   have   passed   the   test.   In   case  of   failure   to   the   above requirements,  the  Contractor  shall  take  necessary  measures  such  as  to perform appropriate test as instructed by the Consultant.

3.8         Transporting and Placing

3.8.1      General

3.8.1.1                The  Contractor  shall  establish  manner  and  schedule  for  transporting  and placing of concrete and obtain approval of the Consultant.

3.8.1.2                Concrete shall be transported in a manner to minimize segregation, spill, age and other changes in quality thereof.

3.8.1.3                Concrete shall be placed and consolidated in a manner to insure uniformity and optimum density.

3.8.1.4                In case of rain or other conditions  that may affect the quality of  concrete during   concreting,   the   Contractor   shall   take   necessary   measures   as instructed by the Consultant.

3.8.2      Time Limit

3.8.2.1                The time limit from start of mixing to completion of placing of a batch as a rule shall be 30 minutes.

3.8.3      Preparation prior to Placing.

3.8.3.1                The place where concrete is to be deposited shall be cleaned and sheathing shall be sprinkled with water. Subsequently, water accumulated in the form shall be removed.

3.8.4      Construction Joint

3.8.4.1                Joint  surfaces  shall  be  cleaned,  made  free  of  laitance  and  other  foreign matters, and wetted prior to concreting. Joint surface shall be roughened if directed by the Consultant.

3.8.4.2                The  locations   of  shapes  of  construction   joints  shall  be  consulted   and approved by the Consultant.

3.8.5      Concrete Placing

3.8.5.1                Concrete placing shall be proceeded to keep the surface of placed concrete as horizontal as possible.

3.8.5.2                Concrete shall be continuously  poured to compact around reinforcing bars and corners of formwork.

3.8.5.3                The maximum  time interval between placements  of continuous  concreting shall not exceed 0.5 hours. However, when special measures are taken this time  limit  may  be  changed  according  to  instruction  or  approval  of  the Consultant.

3.8.6      Consolidation

3.8.6.1                Vibrating of concrete and tapping of formwork shall be performed to wall, column and other places difficult for concrete to proceed. Proper number of workers for placing and compacting concrete shall be arranged.

3.8.6.2                Vibrator shall be operated  for concrete called for water tightness,  difficult portion for concrete to proceed and other cases directed by the Consultant. However,  vibrator  shall  not be touched  reinforcing  bars  and shall  not be operated more than 30 seconds at same spot.

3.8.6.3                Concrete shall be placed 300 ‐ 600 mm thickness at once in case vibrator is performing. In case flexible‐insert‐vibrator is called for, concrete shall not be placed thicker than the length of the insert or vibrator at one pouring.

3.8.7      Placing Speed

3.8.7.1                Concrete  shall  be  placed  at  the  speed  suited  for  the  workability  of  the concrete  and  condition  of  the  place  of  placement,  which  insures  proper consolidation of concrete.

3.9         Concrete Curing

3.9.1      Curing Method

3.9.1.1                After concrete has been placed, the concrete surface shall be kept moist by sprayed with water or by other appropriate methods, and shall be protected from direct sunlight and rapid drying. The top surface of slabs shall be kept flooded with water at all times after concreting  for the  duration  of curing period. This curing period shall be for not less than 14 days.

3.9.1.2                As a rule, no foot traffic or loads shall be permitted on concrete for at least

24 hours after placement.

3.10       Test

3.10.1   General

3.10.1.1              The contractor shall be required to conduct all tests according to BS method and procedure.

3.10.1.2              Test, as a rule, shall be conducted at the locations directed or at the testing institutions approved by the Consultant.

3.10.1.3              The Consultant shall conduct test, as a rule.

3.10.1.4              In  case  of  failure  in  test,  measure  shall  be  taken  as  instructed  by  the

Consultant.

3.10.1.5               The Contractor shall keep test records during the work and for 2 years after completion of the contracted work.

3.10.2   Material

3.10.2.1              Cement Test

(1) Setting test.

(2) Soundness test.

(3) Compressive strength test.

Note:      Item (1) shall be conducted once in every manufacturer.

Item (2) & (3) shall be conducted once in every 2,000 bags.

3.10.2.2              Aggregate test:

(1) Grading and fineness modules.

3.11       Concrete

3.11.1   Fresh concrete

Slump, air content, shall be conducted daily, and more often at request of the Consultant.

3.11.2   Compressive strength test of concrete

Test for estimation on strength of concrete in structure:

3.11.2.1              In  order  to  assume  estimated   strength  of  concrete   in  structure,   compressive strength test shall be conducted  for prepared test pieces on the 7th day and 28th day and those test pieces shall be made for sampling at placing of concreting.

3.11.2.2              Strength  test  shall  be conducted  for each  of the following  conditions:  each  days pour, each class of concrete, each change of supplies or source and each 100 cubic meter of concrete or fraction thereof. The number of test pieces to be used in a test shall  be  not  less  than  3  for  each  test  of  the  7th  day  and  the  28th  day  unless otherwise instructed by the Consultant.

3.11.2.3              Test pieces shall be made in accordance  with British Standards,  and sampling shall be taken as near as possible at the point of placement.

3.11.2.4              Test pieces shall be stored without being disturbed and shall be covered during the first 24 hours, and carefully  transported  specimens  to the testing  laboratory.  Test pieces  shall be cured in water after de‐moulding.  The  temperature  of test pieces shall be kept as close as possible  to the  temperature  of the concrete  in structure until the time of testing.

3.11.2.5              The test results shall be expressed  in the average value by calculating  the average compressive  strength  of  all  test  pieces.  The  average  value  must  be  equal  to  or greater than the specified strength.

3.12       Defective Concrete and Finishes

3.12.1   Honeycombed  surfaces shall be made good or on the instruction  of the Consultant  be cut out by the Contractor and make good at his own expense.

3.12.2   Concealed  concrete  faces  shall  left as from  the formwork  except  honeycombed  surfaces shall  be made  good.  Faces  of concrete  to be rendered  shall  be roughened  by approved means to form a key. Faces of concrete that are to have finished other than those specified shall be prepared in an approved manner as instructed by the Consultant

4. CONCRETE FORMWORK

4.1         Structure and Material

4.1.1      Structure

4.1.1.1                Formwork  shall  be performed  to obtain  accurate  concrete  in  accordance with the designated drawings.

4.1.1.2                Formwork shall be firmed and secured to bear the force of concreting and tightened to avoid cement paste seeping.

4.1.2      Materials

4.1.2.1                Sheathing for formwork shall be waterproof plywood of not less than 12 mm thick. Joint of sheathing shall be butt joint and firmly assembled. In case of sing wood board for sheathing,  boards shall be 15 mm thick and  applied planer.  Joint shall be tongued  and grooved  unless  otherwise  approved  by the Consultant.

4.1.2.2                Form liners shall be sound and suitable  materials  to accurately  and  safely cast the in‐situ concrete structure as shown on the Drawings.

4.1.2.3                Timber form boards for sheathing where used for fair‐faced concrete shall be of such new materials as not to cause any defects to the surface of the concrete. Special care shall be taken in fabrication, storage and protection of these boards.

4.1.3      Other Material

4.1.3.1                Fastening hardware to be used shall be those with allowable tensile strength guaranteed by manufacturer through strength tests.

4.1.3.2                Form  oil  shall  not  have  injurious  effects  on  quality  of  concrete  nor  to bonding of surface finishing materials and shall be subject to approval of the Consultant.

4.2         Performance

4.2.1      Design of formwork

4.2.1.1                Formwork   shall   be   designed   to   withstand   construction   leads   during concreting,  lateral  pressure  of fresh concrete,  shock  and  vibrators  due to concrete placing.

4.2.1.2                Formwork shall be free of injurious leakage of water, easy to remove, and shall not damage concrete at removal.

4.2.1.3                Supports  shall  be  provided  with  the  adequate  horizontal  and  diagonal bracing   and/or   stays   to   prevent   collapsing,   heaving   and   twisting   of formwork due to horizontal loads working during concrete placing.

4.2.2       Tolerance

The  dimensional  tolerances  in  location  and  cross  section  of  concrete  member  used  for designing and construction of formwork shall conform to the following table.

Standard Values of Dimensional tolerances

| Item | Tolerance (mm) |
| --- | --- |
| Tolerance in distance from datum line of each floor to respective members | + 10 |
| Tolerance in cross section of columns, beams and walls | ‐ 5 , + 10 |
| Tolerance in thickness of floor and roof slabs | 0, +10 |

4.2.3      Fabrication and Erection

4.2.3.1                Erection of formwork,  and transportation  and storage of materials thereof shall be started  only after previously  placed  concrete  has  reached  an age which  acceptance  of these  loads  will not have  any  adverse  effect  on the concrete.

4.2.3.2                Sheathing shall be fabricated and installed accurately to match the locations, shapes and dimensions of members called for in the Drawings.

4.2.3.3                Sheathing  shall  be  installed  tightly  so  as  not  to  permit  cement  paste  or mortar to escape from joints.

4.2.3.4                Pipes,  boxes  and other  embedded  hardware  shall be properly  secured  to sheathing or others so that they will not move during concrete placing.

4.2.3.5                Supports shall be erected plumb. Supports at any two vertically consecutive floors  shall  be  erected  as  near  as  possible  to  identical  locations  on  a common plane.

4.2.3.6                Shoring shall be erected paying special attention to safety.

4.2.3.7                If  sheathing  is reused,  the  surface  in  contact  with  the  concrete  shall  be thoroughly  cleaned  off  and  sufficiently  repaired  before  reuse.  In  case  of using for fair‐faced concrete, the same sheathings shall be used twice after approval of the Consultant.

4.2.4      Inspection

4.2.4.1                Formwork shall be inspected by the Consultant prior to placing of concrete.

4.2.5      Striking of forms

4.2.5.1                 The minimum period for keeping the forms in position and for watering after laying the concrete shall be as stated below, except otherwise specified in drawings.  Forms  shall  be  removed  in  such  a  manner  as  to  ensure  the complete  safety of the structure,  so that there is no  shock or vibration  as would damage the reinforced concrete.

4.2.5.2                The responsibility  for the safety of the concrete shall rest entirely with the Contractor and the Contractor shall be held liable for any damage done and shall have to make good the same at his own expenses.

4.2.5.3                The  Contractor  shall  inform  the  Consultant  when  he  intends  to  remove shuttering  and shall obtain his consent, but the consent of the  Consultant shall not relieve the Contractor of his responsibility.

4.2.5.4                The  minimum  time  for  formwork  to remain  in  place  shall  be  as per  the following table.

| Vertical sides of beams, slabs and columns | 24 hours |
| --- | --- |
| Soffits of slab | 10 days |
| Soffits of beams | 21 days |
| Cantilevers | 28 days |

4.2.6      Relocation of Support

4.2.6.1                Supports under concrete shall be not relocated

4.2.7      Removal of formwork

4.2.7.1                Formwork shall be removed gently, after its removal has been approved by the Consultant.

4.2.7.2                Inspection   by  the  Consultant   shall  be  obtained   immediately   after   the removal of sheathing and defects shall be immediately  remedied according to instruction of the Consultant.

4.2.7.3                After shoring  has been removed,  members  shall be carefully  observed  for cracking and deflection, when found, they shall be reported immediately to the Consultant.

5. STEEL REINFORCEMENT

5.1         Material

5.1.1      Reinforcing steel shall be of the dimensions given in the Drawings.

5.1.2      Reinforcing  bars shall comply  with the requirement  of B.S.4449.  and welded  wire  fabric, square bar fabric and expanded metal shall comply with appropriate part of B.S.4483.

5.1.3      Dia 6mm reinforcing  steel shall be round  mild steel bars, and 12mm,  16mm,  20mm  and

25mm shall be deformed high strength bars.

5.1.4      Any  other  non‐specified  reinforcing  steel  shall  be  used  only  with  the  approval  of  the

Consultant.

5.1.5      All  reinforcing  steel  and  binding  wire  shall  be  stored  under  cover  and  shall  be  at  least

250mm above the ground.

5.2         Cleaning

5.2.1      Reinforcing  bars shall be cleaned before use so that it is free from rust, oil, dirt or  other coatings that reduce bond.

5.3         Bending and Laps

5.3.1      The reinforcement shall be bent cold in an approved bar bending machine.

5.3.2      Preferably bars of full length shall be used. Lapping of bars where necessary shall conform to

BS1487 ‘Bending Dimensions of Bars of Concrete reinforcement.’

5.4         Reinforcement Cover

5.4.1      Concrete cover for reinforcement shall be as follows:

FOR ANY STEEL IN UNDER GROUND CONRETE                                    50          MM CLEAR COVER IN SLABS                                                                            25‐30    MM CLEAR COVER IN BEAMS SOFFIT                                                             30‐35    MM CEAR COVER IN SIDES OF BEAMS                                                           30          MM CLEAR COVER IN COLUMNS                                                                    40          MM

5.5         Placing

5.5.1      Reinforcement intended for contact when passing each other shall be securely tied together with binding wire.

5.5.2      Binders and stirrups shall tightly embrace the longitudinal reinforcement to which they shall be security bound or spot welded.

5.5.3      Binding wire shall be turned in from the formwork and shall not project beyond reinforcing bars.

All reinforcement shall be inspected by the Consultant and approved before concrete is placed in the forms.

6. WATER PROOFING

6.1         Description of work

6.1.1      Extent of water proofing work is shown on drawings.

6.1.2      Install slurry type waterproofing  to top surfaces of balcony slabs and external  surfaces  of underground concrete work.

6.1.3      Install crystalline  type water proofing to underground  water tanks and roof slabs in  strict accordance with the approved manufacture’s printed instructions.

6.2         Materials

6.2.1      Crystalline   Type:   Material   used   shall  be  a  cementatious   coating   containing   catalytic chemicals  which migrate in to the concrete using moisture present in the concrete as the migrating  medium,  and  which  cause  the  moisture  and  the  un‐hydrated  cement  in  the concrete to react causing the growth of non‐soluble crystals of dendritic fibers in the void and capillary  tracks of the concrete  that allow  passage  of water,  there  by rendering  the concrete itself water proof.

6.2.2      Acceptable products: Xypex concentrate, modified, ultra plug and quick set as manufactured

Xypex chemicals (Canada) Limited (or equivalent).

6.3         Storage of materials

6.3.1      General: All materials shall be stored in original undamaged  containers with manufactures seals and labels intact. Material shall be stored off the ground in a dry enclosed area.

6.4         Surface preparation

6.4.1      General:   All   surfaces   shall   be   examined   for   form   tie   holes   and   defects   such   as honeycombing,  rock pockets, cracks, etc. These areas shall be repaired in accordance with these specifications and the manufactures printed instructions.

6.4.2     Concrete finish: concrete surfaces shall have an open capillary system to provide tooth and suctions  shall be clean;  free from scale,  excess  form oil, laitance,  curing  compounds  and other foreign matter.

6.4.3     Smooth surfaces  or surfaces  covered  with excess form oil or other contaminants  shall  be washed lightly sandblasted, water blasted, or acid ‐etched with muriatic acid, as required to provide a clean absorbent surfaces.

6.4.4     Horizontal surfaces shall not be troweled or power ‐ troweled, and shall be left with a rough float  finish  or  a  broom  finish.  Vertical  surfaces  may  have  a  sacked  finish.  Comply  with manufactures specifications for requirements pertaining to minimum ‘age’ of concrete deck surface scheduled to receive water proofing.

6.4.5      Surface moisture:  Water proofing  shall be applied to ‘green’ concrete as soon as  possible after forms have been stripped  or to older pours which have been  thoroughly moistened with clean water prior to application. Free water shall be removed prior to application.

Mixing of crystalline water proofing compound: comply with manufactures specification for

2‐coat installation.

6.5         Application

6.5.1      General: Apply all materials under the direction of the manufacturer’s representative.

6.5.2      Constructions     joints    and    surface    defects:    Comply    with    waterproofing    material manufacturer’s  printed directions  in the preparation,  and treatment  of construction  joints and surface defects.

6.5.3      Surface application: After all repair, patching and sealing strip placement has been prepared in  accordance  with  manufacturer’s   recommendations   and  approved  by  manufacturer’s representative,  treat concrete surface with first coat slurry mix of crystalline waterproofing compound.

6.5.4      Brushing:  Use a short bristle or broom to work the slurry well into the concrete,  filing  all hairline cracks and surface pores.

6.5.5      Second coat: Apply second coat while first coat is still ‘green’ but after it has reached  an initial set, all as recommended by the water proofing material manufacturer.

6.6         Curing

6.6.1     General: Curing shall begin as soon as the waterproofing materials have set up sufficiently so as not to be damaged by a fine spray. Treated surface shall be sprayed three times a day for a three‐day period. Allow material to set 12 days before filling the structure with liquid

6.6.2     Protect treated surfaces  from damage  due to wind, sun, rain and temperatures  below 35 degrees F. For a period of 48 hours after application,  arrange protections to permit proper curing conditions for waterproofing material.

6.6.3     Clean up: Remove all surplus materials from the premises and leave all areas broom‐clean.

In the case of temporary  protections  remove  all such items carefully  to avoid  damage to treated surfaces. Assemble all such materials and remove from premises followed by broom cleaning as noted

7. EMBEDDED DAMPPROOF MEMBRANE

7.1         General

7.1.1      This section deals with laying of flexible sheet as damp proof membranes or has chemical or vapour barriers embedded in the fabric of the building. It does not deal with the weather‐ proof roof sheeting, or with vapour barriers.

7.2         Products

7.2.1      Polythene sheets for under slab DPM: gauge 500, manufacturer and reference to approval.

7.2.2      Adhesive tape: A type recommended by the sheet manufacturer.

7.3         Workmanship

7.3.1      Manufacturers  Recommendations:  to be strictly  followed  for  all products  and  materials.

Apply sheets to clean, dry surfaces with all joints sealed to give a completely  water proof continues membrane.

7.3.2      Polythene Sheet Under‐Slab Dpm: lay a level bed of fine sand, not less than 13mm thick or as specified to receive membrane.

7.3.3      Polythene Sheet Dpm: ensure that sheets are clean and dry. Lay single layer loose on base, lap edges 150mm and seal with mastic or adhesive tape.

7.3.4      Pipe Etc: where  pipe etc. pass through  sheeting  make  junction  completely  watertight  by forming collars fully bonded / sealed to both pipes and sheeting.

7.3.5      Project: finished sheeting adequately and prevent puncturing during following work sheet to be covered by permanent over laying construction as soon as possible.

8. STRUCTURAL STEEL

8.1         Scope

8.1.1      This section shall apply to the work involved with structural  steels. All incidental  items  of structural steel shall be stated in the particular specification.

| 8.2 | Materials |  |
| --- | --- | --- |
| 8.2.1 | Steel |  |
|  | 8.2.1.1 | Shape of steel shall be precise and straight and free of injurious scratches and rust. |
|  | 8.2.1.2 | All steel sections shall be galvanized sections of strength class 43 A. |
|  | 8.2.1.3 | Dimensions of steel section and tolerance of dimension shall conform to standard dimension of steel regulated in ASTM or BS standard. |
| 8.2.2 | Bolt |  |
|  | 8.2.2.1 | Shape of bolt, nut, and washer shall be in accordance with requirement of BS 4190 & BS 3692. |
|  | 8.2.2.2 | Quality of bolt shall be SC 43 A. |
| 8.2.3 | Welding Rod |  |
|  | 8.2.3.1 | Arc welding rod shall conform to materials to be welded, and position. |

8.3         Fabrication

8.3.1      Main fabrication shall be done in workshop unless otherwise specified or approved by the

Consultant.

8.3.2      Full scale drawing of each section shall be drawn prior to fabrication  and checked by  the

Consultant.

8.3.3      Section of each material shall be cut perpendicular  to axis unless otherwise specified in the drawing.

8.3.4      Saw and angle cutter shall be used for cutting, and cut section shall be free of any noticeable defect.

8.3.5      Deformation caused by cutting shall be corrected.

8.3.6      Normal temperature or hot drawn process shall do bending process. Steel shall be red heat in hot drawn process.

8.3.7      Those directed in the drawing shall be chiselled finish and completely attached. Materials shall be checked for bend, distortion, warp, etc. before fabrication.

| 8.4 | Bolt |  |
| --- | --- | --- |
| 8.4.1 | Bolt Hole 8.4.1.1 | Spacing of boltholes shall be as directed in the following table. |

| Diameter of Bolt | Standard Pitch | Minimum Pitch | End Distance | Edge Distance |
| --- | --- | --- | --- | --- |
| 12 | 50 | 30 | 30 | 25 |
| 16 | 50 | 40 | 40 | 30 |

8.4.1.2                Minimum pitch and end distance for lightweight  steel shape shall be more than 3 times and 2.5 times a Bolt diameter respectively.

8.4.1.3                Diameter  of  hole  shall  not  be  over  0.5  mm  larger  than  bolt  diameter.

However,  for  anchor  bolt  5mm  clearance  shall  be  allowed  between  bolt diameter and diameter of hole unless otherwise specified.

8.4.1.4                Bolthole shall either be drilled open or reamed after sub punching. Punching can only be permitted for a material thickness less than 13 mm.

8.4.1.5                Rolled edge around a hole shall be removed.

8.4.1.6                Position of a bolthole shall be precise so that the center of all holes aligns.

8.4.2      Protection against loosing of Nuts

8.4.2.1                Nuts shall be protected against loosing by concrete covering, double nuts or other proper means.

8.5         Welding

8.5.1      Welding

8.5.1.1                Welder shall have an authorized qualification  in Maldives and approved by the Consultant.

8.5.1.2                Other tests shall be conducted to confirm welder’s skill in accordance with type of work.

8.5.1.3                Tack welding shall be carried out by the welder approved by the Consultant.

8.5.2      Welding Machine

|  | 8.5.2.1 | Arc welding machine shall be alternate or direct current type, which provides sufficient and adequate current. |
| --- | --- | --- |
| 8.5.3 | Preparation |  |
|  | 8.5.3.1 | Welding shall be done as much downward as possible using a jig such as Rotary frame. |
|  | 8.5.3.2 | Welding rod shall be always kept in a dry area and if necessary, dried by drying equipment. |
|  | 8.5.3.3 | Welding surface shall be free of water, scale or others injurious to welding work. Slag appeared on the created surface in the middle of welding shall be cleaned before starting again. |
| 8.5.4 | Fabrication |  |
|  | 8.5.4.1 | Welding edge shall be smoothed by automatic gas cutting or other proper finishes. |
| 8.5.8 | Finishes |  |
|  | 8.5.8.1 | Surface of welds shall be as smooth as possible and size and length of welds shall not be less than designed dimensions. |
|  | 8.5.8.2 | Reinforcement of weld shall not exceed 0.1s + 1 mm (s: Designated size) in fillet welds. |
|  | 8.5.8.3 | Welded parts shall be free of undercut, overlap, crack, blow hole, lack of welds, and lack of weld settlement, rolled up slag or other defects. |
|  | 8.5.8.4 | Crater at the end of bead shall be carefully heaped up and slag, sputter, etc. shall be completely removed after welds. |

8.5.9      Safety

8.5.9.1                Safe scaffoldings shall be provided for the field welds work.

8.5.9.2                Welding  facilities  shall  be such  that  there  shall  be no electric  leakage  of electric shock. There also shall be sufficient protection for fire.

8.5.9.3                Electric shock protection  device shall be used and also care shall be taken not to get suffocated or intoxicated by gas when welding in small area.

8.5.10   Inspection

8.5.10.1              Welding   parts  shall  be  inspected   before,  during  and  after  welding   in accordance with work schedule.

8.6         Erection and Field Painting

8.6.1      Erection

8.6.1.1                Erection procedure shall be prepared by the contractor and be approved by the Consultant prior to the erection.

8.6.1.2                Material shall be stored on flat surface in order not to get distortion, twist or other  defects.  Correction  shall  be  made  to  those  distortions  or  twisted before erection.

8.6.1.3                Horizontal   reinforcement   and   bracing   shall   be   placed   and   bolts   are temporary tightened as trusses are put up.

8.6.1.4                Connection  of  materials  by  bolts,  etc.  shall  be  made  after  distortion  on plumb is thoroughly corrected.

8.6.1.5                Temporary  bracing  or other  reinforcement  shall  be placed  to resist  wind pressure or other loads erection.

8.6.1.6                When  heavy  objects  are placed  on a horizontal  element  in the course  of erection, they shall be reinforced with prior approval of the Consultant.

8.6.1.7  Care shall be taken on all facilities so that there is no accident.

8.6.2      Field Painting

All steel work shall delivered to site unprimed shall be cleaned of impurities, scrapped and wire  brushed  to  remove  rust  and  painted  with  one  coat  of  priming  paint applied by brush.

Steelwork delivered to Site primed shall be cleaned of impurities and damage to the priming paint and made good with priming paint.

Galvanized  steelwork  to  be  painted  shall  be  cleaned  of  impurities.  Where  rusting  has occurred the rust shall be removed by wire brushing and made good with an approved  rust  inhibitor.  The  surfaces  shall  be  coated  with  a  mordant solution,  washed  with clean water and painted  with two  coats of priming paint applied by brush.

Steelwork, which is to be concealed shall be prepared and primed as above and shall be painted with two priming coats and one finishing coat of paint applied by brush.

8.7         Anchor Bolt

8.7.1      The other methods for movable burying shall be as directed by the Consultant.

9. MASONRY

9.1         Materials

9.1.1      Material  used  for  masonry  and  plastering  work  shall  conform  to  Section  3 ‐  CONCRETE WORKS.

9.1.2      Masonry  work  shall  be  done  with  cement  bricks  or  blocks  of  approved  quality  unless specified otherwise.

9.1.3      The blocks  shall be free from excessive  amounts  of salt or other  impurities  and shall  be inspected and approved by the Consultant.

9.2         General

9.2.1      Execution Drawing

9.2.1.1                  Work shall be complied with this specification  unless otherwise stated on particular   Specification   or  Drawings.   Any  work  not  specified   shall  be discussed  and directed  by the Consultant.  Execution  drawing  of block or brick  alignment  (inclusive  of indication  for  hanging  bolt,  wood  plug  and conduit    pipe),    detail    reinforcement,    window    opening,    and    other requirement shall be prepared and submitted for the Consultant.

9.2.2      Stake‐Board

9.2.2.1                  Stake‐board  shall be provided at each 5m in length and shall be inspected by  the  Consultant  for  the  accuracy,  firmness  and  secureness.  However, suitable   ruler,   plumb   bob   and   leveller   shall   be   provided   for   minor performance of cement block and bricks.

9.2.3      Transportation and storing

9.2.3.1                  Care shall be taken for damage during transportation  of materials and any defect of natural finished concrete blocks or bricks shall be rejected.

9.2.3.2                  Different size of material shall be stored separately and projected from dirt and other impurities.

9.2.4      Curing

9.2.4.1                  Any shock or load shall not be applied until concrete mortar or other fills hardened.  Corner, projection and top of cement block or brick work shall be protected from rain, dryness, cold, damage and stain by covering.

9.2.4.2  Void between blocks or bricks shall not be intruded by rainwater.

9.3         Blockwork

9.3.1      Material

9.3.1.1                  Blocks shall be of standard quality low permeability blocks with no defects and sample shall be submitted for approval of the Consultant.

Blocks shall be Solid(For sizes refer to drawings)  . The   average compression strength should be not less than 2.8N/mm2   and shall comply  with physical requirements of ISO 6073: 1981

9.3.2      Horizontal reinforcement for concrete block wall;

9.3.2.1                 Horizontal  reinforcement  shall  be  provided  at  end  of  wall  adjoining  to concrete  column.  Reinforcing  bar  shall  be  anchored  into  end  block  and column.

9.3.2.2                 Horizontal reinforcing bar for block wall shall be 6 dia. @ 1000 mm.

9.3.3      Placing Blocks & Bricks

9.3.3.1                 Cement blocks shall be saturated with water and joint shall be cleaned.

9.3.3.2                 Bonding mortar shall be used immediately after mix, and mixed mortar left for more than one hour shall be rejected.

9.3.3.3                 Vertical and horizontal joint of blocks shall be filled completely and suitable with mortar on line shall not be moved or rearranged. Joint and surface of block of exposed finished block wall shall be cleaned immediately after joint is filled.

9.3.3.4                 In case concrete  block  wall is attached  to structural  concrete,  block  wall shall be placed before concreting structure.

9.3.3.5                 Mortar for joint shall be touched  with steel   trowel before hardened  and exposed  joint  shall  be finished  with  uniform  width  and  planned  without roughness or cavity.

9.3.3.6                 Height for placing block per day shall be maximum 1.2 m unless otherwise specified.

9.3.3.7                 Blocks shall be placed with cavity side under.

9.3.4      Joints

9.3.4.1                 The thickness of joints shall not exceed 10 mm and the joints shall be rated (13 mm dup.) when the mortar is still floor, so as to provide for proper bond for  the  plaster.  Any  mortar  which  falls  on  the  floor  from  this  joints  or removed due to raking of joints shall not be reused.

9.3.5      Lintel

9.3.5.1                 Lintel   shall   be   reinforced   concrete   as   approved   or   directed   by   the

Consultant.

9.3.5.2                 Main reinforcing  bar shall be anchored more than 40D ( 40 x diameter of the bar) at both end.

9.3.5.3                 In case lintel is prefabricated, shop drawing shall be submitted for approval of the Consultant.

9.3.6      Frame of Opening

9.3.6.1                 In case frame is temporarily  installed before placing of blocks, frame shall be firmly  placed  and joiner  shall be bonded  with mortar  as  placing  each block at side and top of frame.

9.3.6.2                 In case frame is installed after placing of blocks, joiner shall be bonded with additional mortar at space or every two blocks or more.

9.3.6.3                 Back  of  frame  shall  be  filled  and  compacted  with  mortar  by  providing shuttering board.

9.3.6.4                 Wood plug and anchor bolt shall be covered with mortar or concrete.

9.3.7      Piping

9.3.7.1                 Principally, piping shall not be placed in block wall unless piping block is in use.

9.3.7.2                 In case electric conduit pipe is placed in cavity of concrete blocks, care shall be taken  not  to obstruct  reinforcing  bar,  and  cavity  shall  be  completely filled.

9.3.7.3                 In case chipping and piping on face of blocks is unavoidable, performance shall confirm to instruction of the Consultant.

9.3.7.4                 Joiner and supporter for exposed piping shall be buried at joint which back is filled or otherwise approved by the Consultant.

10. PLASTERING

10.1       General

10.1.1   All masonry  walls shall have smooth finished cement plaster on both sides with a  surface setting coat of neat cement applied within an hour of the completion of rendering.

10.1.2   Cement rendering to floor shall be same as above.

10.2       Materials and Storage

10.2.1   Plaster materials which are affected by moisture such as plaster and cement shall be stored properly.

10.2.2   Materials used for plastering shall conform to those of Section 3 ‐ Concrete Works. Grading of sand, however, shall be as in table below

| Grading of sand | Mortar plastering | Plastering |
| --- | --- | --- |
| 5mm sifting thorough 100% 0.15mm sifting less than 10% | for first coat for finish coat | for first coat and dubbing out |
| 2.5mm sifting through 100% 0.15mm sifting less than 10% | for finish coat | for second coat |

10.2.3   White  cement  or filler  or similar  shall  confirm  to the  requirements  of Portland  cement, BS.12.

10.2.4   The use of mixtures shall be approved  by the Consultant’s  representative.  The  amount  of admixture shall be such that it affects mortar strength very little.

10.3       Mixing ratio

10.3.1   Mixing volume ratio of mortar shall be as in table below:

| Base | area of application | first coat cement:sand | Dabbing out cement:sand | Finish coat cement:sand |
| --- | --- | --- | --- | --- |
| Masonry blocks | Floor | ‐ | ‐ | 1:4 |
|  | Interior wall | 1:4 | 1:4 | 1:4 |
|  | Exterior wall | 1:4 | 1:4 | 1:4 |

10.4       Thickness of Coating

Standard thickness of coating (mm)

| Base | Area of application | First coat | Dubbing out | Second coat | Finish coat | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Masonry Block | Floor | ‐ | ‐ | ‐ | as per dwg | as per dwg |
|  | Interior wall | 8 | ‐ | 8 | 4 | 15 |
|  | Exterior wall | 8 | ‐ | 8 | 4 | 15 |

Thickness  of  coating  shall  be  standard  thickness  of  coating  unless  otherwise  indicated  on  the

Drawings.

10.5       Finish

10.5.1   Type of finish and work schedule

| Type | Work Schedule | Notes |
| --- | --- | --- |
| 1.Smooth Trowel finish | 1. Shall be applied flat by metal trowel 2. Shall be finished by pressing with the trowel. | Before applying second coat, corner and edge shall be screed well. |
| 2. Wooden float finsh | Shall be applied by wooden float |  |

10.6       General Preparation

10.6.1   Remove efflorescence, laitance, dirt and other loose material by thoroughly dry brushing.

10.6.2   Remove  all traces of paint, grease,  dirt and other materials  incompatible  with  coating by scrubbing with water containing  detergent  and washing off with plenty applying   coatings unless specified otherwise.

10.6.3   In‐situ  Concrete  Surfaces:  Scrub  with  water  containing  detergents  to  ensure  complete removal  of mould  oil, surface  retarders  and other materials  in compatible  with coating  . Rinse with clean water and allow to dry unless specified otherwise.

10.6.4   Organic Growths: Treat with fungicide to manufacturer’s recommendations and bush off.

10.6.5   Hacking for Key: roughen specified surfaces thoroughly  and evenly by removing the entire surface  to  a  depth  of  3mm  by  scabbling,  bush  hammering  or  abrasive  blasting,  clean surfaces by washing and brushing.

10.6.6   Smooth  Concrete  Surfaces:  where  no  keying  or  mix  or  bonding  agent  is  specified,  wet smooth concrete surfaces immediately before plastering.

10.7       External Plastering

10.7.1   Dissimilar Solid Backgrounds for Plastering: where plaster is to be continued without break across joints between dissimilar solid backgrounds which are rigidly bonded together, cover the joints  with a 200mm  wide mesh  strip (back  grounds  in the same  plane)  or with the corner  mesh  (internal  angle)  fixed  at not more  than  600mm  centers  along  both  edges  , unless specified or otherwise.

10.7.2   Dissimilar Solid Backgrounds for Plaster: where plaster is to be continued without break and without change of plane across the face of a 300mm and rigidly bonded to the background.

10.7.2.1               Cover the face of the column /beam/ lintel with building paper extending 25 mm on the adjacent background.

10.7.2.2               Over lay with expanded metal lathing extending 50mm beyond the edges of the paper and securely  fixed with masonry  nails at not less  than 100mm centres along both edges.

Alternatively, an approved paper and mesh lathing may be used.

10.7.3   Dissimilar  Solid  Backgrounds  for  Rendering:  where  rendering  is to be continued  without break across joints between  dissimilar  solid backgrounds  which are in the  same plan and rigidly bounded together, cover joints with a 150mm wide strip of building paper overlaid with 300mm wide metal lathing fixed at not more than  600mm  centers along both edges unless specified otherwise.

10.7.4   Service Chases: cover with steel mesh strip fixed at not more than 600mm  centers  along both edges.

10.7.5   Conduits bedded in under coat to be covered with 90mm wide jute scrim budded in finishing coat mix, pressed flat and trowelled in. Do not lap ends of scrim.

10.8       Internal Plastering

10.8.1   Accuracy of plaster 15mm thick or more: maximum  permissible  gap between an 1800mm straight edge and any point on the surface to be 3mm.

10.8.2   Dubbing  Out: if necessary  to correct  inaccuracies,  dub out in thickness  of not more  than

10mm in same mix as first coat. Allow each coat to set before the first is applied .  Cross scratch surface of each dubbing out coat immediately after set.

10.8.3   Metal Mesh Lathing: Work undercoat well in to interstices to obtain maximum key.

10.8.4   Under Coats: generally to be not less than 8mm with thickness greater than 16mm applied as two equal coats. Rule to an even surface and cross scratch ‐ end coat to provide a key for the next hand applied coat.

10.8.5   Cement Based Under Coats: all to dry out thoroughly but not rapidly, to ensure that drying shrinkage is substantially complete before applying next coat.

10.8.6   Dissimilar  Backgrounds:  where  scrim  or  lathing  or  beads  are  not  specified,  cut  through plaster with a fine blade in a neat, straight line at junctions of :

10.8.6.1               Plastered rigid sheet and plastered solid backgrounds.

10.8.6.2               Dissimilar solid backgrounds.

10.8.7   Smooth  Finish:  trowel  or float  to product  a tight  matt,  smooth  surface  with  no  hollows abrupt  change  of  level  or  trowel  marks.  Do  not  use  water  brush  and  avoid  excessive trowelling and over polishing.

10.9       External Rendering

10.9.1   Dubbing Out: if necessary to correct inaccuracies,  dub out in thicknesses of not more than

10mm in same mix as first coat. Allow each coat to dry before the next is applied.  Cross scratch surface of each dubbing out coat immediately after set.

10.9.2   Under Coats for hand applied finishes:

10.9.2.1               Apply first undercoat or dubbing out coat by throwing from a trowel.

10.9.2.2               Coats  to be no less  than  8mm  thick,  with  thickness  greater  than  16mm applied as two equal coats. On weak backgrounds first under coat to be not less than 10mm thick.

10.9.2.3               Brush down each under coat to remove dust and loose particles and  wet thoroughly before application of next coat.

10.9.2.4               Cross scratch under coat without penetrating  the coat, to provide key  for following coat(s).

Drying:  Keep  each  coat  damp  for  the  first  three  days  by  covering  with  polythene  sheet and/or spraying with water. Thereafter prevent from drying out too rapidly. Work in shade whenever possible.

Allow  each  coat  to  dry  out  thoroughly  to  ensure  that  drying  shrinkage  is  substantially complete before applying next coat.

Playing Floated Finish: Finish with wood or other suitably faced float to give an even texture. Do not draw excessive laitance to surfaces.

10.10    Metal Mesh Lathing / Reinforcement For Plastered/Coatings.

10.10.1 Lathing  to be provided  as reinforcement  for  plastering  in columns,  walls  or  specified  in drawings products.

10.10.2 Products:

10.10.2.1 	Plain Expanded  Metal Lathing: To B.S 1369 with a minimum  weight of 1.9 kg/mm2. Manufacturer to approval of the Consultant.

10.10.2.2             Wire Ties: Unless other specified, annealed iron, galvanized to B.S 443.

10.10.2.3             Clout Nails: galvanized steel or stainless steel nails to B.S 1202: Part 1, table

3.

10.10.2.4             Staples: Galvanized steel wire staples to B.S 1494: Part 2.

10.10.3 Workmanship

10.10.3.1 	Framing: fix securely and accurately to help ensure that coatings on lathing , when finished,  are true to line and level , within specified  tolerances  and free from cracks, rippling, hollows, ridges and sudden changes of levels.

10.10.3.2 	Runners/Bearers spanning between concrete beams/ribs: fix with 3mm wire ties  twisted around 38 mm X 10 gauge screws driven well into fixing blocks or plugs in sides of beams/ribs.

10.10.3.3 	Wire Ties: twisted ends tightly together, cut off surplus and bend ends of wire away from face of coating.

10.10.3.4             Plain Expanded Metal Lathing:

(a)  Stretch   lathing   and  fix  securely   in  accordance   with   manufacturers recommendations to give a taut, firm base for plaster/ rendering.

(b) Fix with the long way of the mesh at right angles to supports and with all strands sloping in the same direction.

(b) Lap side  edges  not less than  25mm.  Lap ends  50mm  at supports  and

75mm between  supports.  Laps must not occur within 100mm of angles  or bends.

11. CARPENTRY AND JOINERY

11.1       Materials

11.1.1   Timber shall be in accordance  with the requirements  of BS 1186 ‘Quantity  of Timber  and

Workmanship in Joinery’, Part 1, ‘Quality of Timber’.

11.1.2   Timber  and  timber  products  shall  be  subject  to  the  inspection   and  approval  of  the

Consultant.

11.1.3   Timber  shall  be  seasoned  to  stable  moisture  content  compatible  with  the  finished  use, straight and true and free from wind, warp and distortion  and in lengths suitable  for the members required.

11.1.4   All timber shall be in long lengths and laps, scars or splices shall be over a bearing surface.

Where obtainable, finishing timber exposed to view shall be in single lengths.

11.2       Preservation of Timber

11.2.1   All timber shall be treated for insect attack and is to be of the correct moisture content and free from surface moisture content and dirt.

11.2.2   All rafters, purlins, framing scribe pieces, wall plates, and trusses etc. shall be treated  for insect attack with approved timber preservative.  No extra payment shall be made for such coating and will be considered inclusive in the rate of the respective item in the BOQ.

11.2.3   Treatment shall be carried out after all cutting and shaping is completed.

11.3       Hardware

11.3.1   Hardware  shall be standard  quality and samples shall be submitted  to the Consultant  for approval.

11.3.2   All hinges shall be stainless steel or brass and shall be approved by the Consultant.

11.3.3   The  dimensions  and  quality  of  hardware  shall  meet  the  requirements  and  shall  not  be rested, deformed or defective.

11.4       Dimensions and Finish

11.4.1   All dimensions of timber given are finished dimensions.

11.4.2   All elements and others of structural nature, which are exposed, must be machine planed to a smooth finish.

11.4.3   All unexposed timber shall be machine planed to a rough finish.

11.4.4   All joinery work shall be dressed on all four sides and hand dressed where necessary  and sanded  to  all  exposed  surfaces.  All  arises  in  any  way  accessible  shall  be  sanded  and smoothed off.

11.5       Workmanship

11.5.1   All connections whether nailed, screwed glued, mortised or dove‐tailed shall be accurately made and properly executed to provide sound, satisfactory connections for the class of work required.

11.5.2   Timbers containing defects or distortions shall not be used.

11.5.3   All joinery shall be manufactured by skilled tradesman with accurate tolerances and set out and with tools, jigs, machines and equipment appropriate for the work.

11.5.4   Assembly of the joinery units and joinery frames, etc. shall be by means of glued connections appropriate to the work ‐ mortise and tennon, housing and doweling, etc. where practicable including  the use of glued blocks wherever  required.  Nailing,  screwing  shall only be used with prior approval of the Consultant;  corrugated fasteners shall not be used for effecting connections

12. ALUMINIUM DOORS AND WINDOWS

12.1       Aluminium Doors and Windows

12.1.1   All windows  and doors are to be constructed  by approved  specialist  suppliers  of  medium section to the particular requirements  noted on the drawings as to weight and profile. All sections shall generally conform to relevant British Standard Specifications.

12.1.2   All frames  should  be made to fit the actual  openings  with a 3 mm clearance  all  around.

Discrepancies in overall width or height exceeding 3mm will not be allowed and the frames will be rejected in such cases. Any small discrepancies  shall have the gaps suitably backed and filled with gun‐applied water repellent mastic sealant

12.1.3   All sealants used in the assembly of, and in the fixing of cladding and window framing, shall be non‐setting  to allow thermal movement  without detriment to those joint sealants used for peripheral caulking and shall be one part silicone sealant and shall conform to BS 4245. All spliced  joints  between  mullions  should  be sealed  with  an  approved  silicone  product, compatible with other sealants and packings used.

12.1.4   The  auxiliary  components  in  sashes  as  locks,  pivots,  sliding  gear  etc.  shall  comprise  of stainless steel or resisting materials.

12.1.5   The tolerances are to be as follows:

a) Inside width of frame                3mm Maximum b) Inside height of frame               3mm Maximum c) Depth of frame                           2mm Maximum d) Opposite side, Inside distance 2mm Maximum

12.1.6   The performance ‐ associated requirements are

1) Strength (resistance to wind pressure and other forces applied in use)

2) Air tightness or ability to cut out drafts.

3) Water ‐ tightness against rain or dew.

4) Sound arresting effect to (shut off noise from outside as well as inside).

12.1.7   All surfaces shall have an anodized protective surface layer of minimum 60 Micron thickness.

12.1.8   Glazing shall be done as specified by the Consultant. Glass shall be tinted, or as specified in the drawings. Thickness shall be according to the size of panels as given hereunder.

| Not exceeding 1 sq. ft. | 2mm |
| --- | --- |
| Exceeding 1 sq. ft. but not exceeding 2 sq. ft. | 3mm |
| Exceeding 2 sq. ft. but not exceeding 4 sq. ft. | 4mm |
| Exceeding 4 sq. ft. but not exceeding 6 sq. ft. | 5mm |
| Exceeding 6 sq. ft. but not exceeding 12sq. ft. | 6mm |
| Exceeding 12sq. ft. | > 8mm or as approved by consultant |

12.1.9   Prior  to  import  and  / or  purchase  of  the  Aluminium  Doors  and  Windows,  the  relevant specification of the manufacturer, along with samples has to be submitted to the Consultant for approval. This clause shall not be contravened on any account.

12.1.10 The  fitting   shall  be  done  with  utmost   care  not  to  spoil  the  finishes   given  by   the manufactures,  and any cleaning done shall be done with cleaners etc. as specified  by the Manufactures.

11.1.11 The  Contractor   shall  provide   all  items,  articles,   materials,   operations,   mentioned,   or scheduled  on  the  drawings,  including  all  the  labour  materials,  including  fixing  devices, equipment and incidentals necessary as required for their completion.

12.1.12 The Contractor shall submit shop drawings and/or samples of each type of doors, windows, railings and other items of metal work to the Consultant  for approval.  The  shop drawings shall  show  full  size  sections  of  doors  and  windows  etc.  thickness  of  metal,  details  of construction  hardware  as well as connection  of windows,  doors and  other metal work to adjacent work.

12.1.13 Aluminium  doors  and shutters  shall  be manufactured  by an approved  manufacturer  and shall  be  of  sections,  sizes  combination  and  details  shown  on  the  drawings.  The  frame member shall be one piece, corners shall be electrically  welded, ground  smooth and true and glazing bare shall be threaded or interlocked as approved by the Consultant.

12.1.14 Glazing for doors and windows shall be of specified thickness and of approved quality and shall conform  to specification  of glazing.  Fixing  for glazing  shall be done  with  aluminium Snap‐On  beading  as  per  detail  drawing  and  instructions.  Necessary  continuous  rubber gaskets of approved make shall be provided.

12.1.15 Colour for doors and windows shall be approved by the Consultant.

12.2       Aluminium louvers

12.2.1   Product data shall be submitted for approval; this shall include specified model and AMCA

ratings or equivalent.

12.2.2   Contractor  shall  submit  all shop  drawings  indicating  materials,  construction,  dimensions, accessories, and installation details.

12.2.3  Contractor shall submit samples of the product for approval.

12.2.5  Louvers  shall  comply  with  AAMA  specification   2605  “Voluntary   Specification   for  High Performance  Organic  Coatings  on  Architectural  extrusions  and  panels”,  ASTM  B244  ‐68, AAC22A41 or equivalent.

12.2.6  Louvers  shall  be  well  suited  for  the  design  environment   (temperature,   humidity,  and ventilation); i.e., it shall be within manufacturer’s  recommended  design environment  limits for optimum results.

12.2.7   All louvers shall be installed according to manufacturer’s instructions.

12.2.8   All units shall be installed plumb, well fitted and securely attached to supporting frames.

12.2.9   Delivery of materials to site in shall be in manufacturers’  original, unopened containers and packaging with labels clearly indicating manufacturer, material and location of installation.

12.2.10 Materials shall be stored in a dry area indoors and protected  from damage in accordance with manufacturer’s specifications.

12.2.11 Materials and finishes shall be protected during handling & installation to prevent damage.

12.3       Top hung windows, ventilators and side hung doors

12.3.1   All windows and doors should be weather stripped. The weather protection should be achieved by a positive compressive action against the section and should not depend on external contact. At every contact between two profiles two weather stripping sections should be provided to complete weather protection.

12.3.2   The bottom section for hinges must be capable of being adjusted vertically if necessary. The gap  between  section  and  the  floor  should  be  covered  with  a  pair  of  special  splay‐tube sections.

12.3.3   The shutter sections for both windows as well as doors shall be hollow section type and shall be overall size 57 x 45 mm and the door sections shall be overall size 81 x 45 mm (including flanges).

12.3.4   The shutters of the windows and doors should be assembled  with stainless steel pins and nylon  washers.  Handles  shall  be  anodised  aluminium  finished  to  match  the  aluminium sections and mounted with self‐lubricating nylon washers.

12.3.5   A mortise cylinder rim automatic deadlock of high quality with double pin tumbler shall be used.

12.3.6   Windows   shall  have   anodised   aluminium   handles,   colour   as  framing   and  a   latching mechanism securing the shutter to the frame both at the top and bottom.

12.3.7   Required fittings;

12.3.7.1                Single action door closer concealed in the head bar of the outer frame and mounted on an adjacent pivot at the threshold and deadlock fitted.

12.3.7.2                The left hand leaf of double doors with flush bolts at head and sill with deadlock fitted to the right hand leaf.

12.3.7.3                Escape doors to have panic bolts assembly with vertical elements concealed in the sill and door closer as in 12.3.7.1.

12.4       Installation

12.4.1   Aluminium  work  shall  be  installed  adjusted  and  glazed  by  experienced  workmen  all  in accordance with the manufacturer's  installation instructions and in full conformity with the approved shop drawings, samples and other submitted data. Under no circumstances  shall materials  be installed on surfaces that contain  condensation,  dirt, grease or other foreign encountered materials that would hinder or prevent proper installation and functioning for the use intended.

12.4.2   Aluminium  work  shall  be  carefully  and  accurately  assembled  with  proper  and  approved provision for contraction and expansion and set in correct locations as per approved detailed shop  drawings,  all level,  square,  plumb  and  aligned  with  other  work.  All joints  between framing and structural building shall be sealed in order to be watertight and weather‐proof and to satisfy all other requirements of the Consultant.

12.4.3   Frames shall be designed and manufactured  with a maximum 2.5mm tolerance around the opening in the structure. These joints are to be finished by applying an approved sealant into a polystyrene foam backing strip.

12.4.4   All aluminium works are to be fully protected for the duration of the contract from damage by other trades. The Consultant shall approve the method of protection.

12.4.5   If for any reason  final finishes  become  scratched,  abraded  or damaged  during  transport, delivery, storage or erection, it shall be the Contractor's  responsibility  to remove or repair those defective  areas or components  as directed  and to the  complete  satisfaction  of the Consultant.

12.4.6   Repair work shall be identical to the manufacturer's applied finish with regard to gloss, finish and  visual  appearance.  Field  touch  up  of painted  aluminium  is permitted  only  with  the written permission of the Consultant. Where touch up is not an authorised means of repair the damaged materials must be replaced by new.

12.4.7   Upon  completion  of  work  all  protective  coverings  from  all  exposed  surfaces  shall  be removed.  All surfaces  shall be cleaned  using soap or detergents  as recommended  by the aluminium manufacturers to remove sealants, discolouration and any other foreign material. Defection  of any type determined  by the Consultant  shall be  repaired  at the Contractor's expense.

12.4.8   Extreme care shall be taken when cleaning the exterior portion to protect all other adjacent works.

12.5       Sealing joints

12.5.1   The  Contractor  shall  ensure  that  joints  are  dry  and  remove  all loose  material,  dust  and grease.

12.5.2   Joints shall be prepared in accordance with sealant manufacturer's  recommendations using recommended solvents and primers where necessary.

12.5.3   Adjoining  surfaces  which  would  be impossible  to clean  if smeared  with  sealant  shall  be masked.

12.5.4   Backing strips shall be inserted in all joints to be pointed with sealant. When using backing strips, the Contractor shall not leave gaps and shall not reduce depth of joint for sealant to less than the minimum recommended by the manufacturer.

12.5.5   Cavities  shall  be  filled  and  jointed  with  sealant  in  accordance  with  the  manufacturer's recommendations.  Sealant shall be tooled to form a smooth flat bead.

12.5.6   Excess   sealant   shall   be   removed   from   adjoining   surfaces   using   cleaning   materials recommended by the sealant manufacturer, and shall be left clean.

12.6       Glass installation

12.6.1   Workmanship shall generally be in accordance with CP 152 and respective British Standards.

12.6.2   The glass is to be delivered  to the site with adequate  protection  to prevent  damage  and where  possible  it  is  to  be  fixed  in  position  immediately  after  delivery.  When  fixed  the Contractor  is  to  take  all  necessary  precautions  to  prevent  damage  during  succeeding building operations  and will be entirely responsible  for the replacement  of any broken or damaged glass at his own cost.

12.6.3   The Contractor is to be solely responsible for determining the exact sizes of glass required, including a tolerance of 2mm to each edge and he is recommended  to check the necessary dimensions on site.

12.6.4   No glazing is to be carried out until rebates have been painted with primer. Glazing beads as applicable are also to be primed before fixing.

12.6.5   All mastic is to be neatly struck off to agree exactly with site lines inside and out.

12.6.6   Rates  are  to  include  for  all  necessary  springs,  clips,  setting  blocks,  location  blocks  and distance pieces and for taking off and later re‐fixing loose beads

12.6.7   Glass apertures  in timber  doors  are to be bedded  in chamois  leather  glazing  strip,  black ribbon velvet or P.V.C. glazing strip to the approval of the Consultant.

13. DRY WALL PANELS

13.1 References

13.1.1   General: Standards listed by reference, including revisions by issuing authority, form a part of this specification section to the extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title or other designation established by issuing  authority.  Standards  subsequently  referenced  herein  are referred  to by issuing authority abbreviation and standard designation.

A. ASTM International:

1. ASTM D1781 Standard Test Method for Climbing Drum Peel for Adhesives.

2.  ASTM  D1929  Standard  Test  Method  for  Determining  Ignition  Temperature  of

Plastics.

3. ASTM E84 Standard Test Method for Surface Burning Characteristics  of Building

Materials.

4. ASTM E108 (Modified) Standard Test Methods for Fire Tests of Roof Coverings.

5. ASTM E119 Standard  Test Methods  for Fire Tests of Building  Construction  and

Materials.

6.  ASTM  E283  Standard  Test  Method  for  Determining  the  Rate  of  Air  Leakage Through   Exterior   Windows,   Curtain  Walls,  and  Doors   Under   Specified Pressure Differences Across the Specimen.

7.  ASTM  E330  Standard   Test  Method   for  Structural   Performance   of   Exterior Windows,   Curtain   Walls,   and   Doors   By   Uniform   Static   Air   Pressure Difference.

8. ASTM E331 Standard  Test Method for Water Penetration  of Exterior  Windows, Curtain Wall, and Doors By Uniform Static Air Pressure Difference.

B. American Architectural Manufacturers Association (AAMA):

1.  AAMA   2605   Voluntary   Specification,   Performance   Requirements   and   Test Procedures   for   Superior   Performing   Organic   Coatings   on   Aluminum Extrusions and Panels.

B. International Organization for Standardization (ISO):

1. ISO 9001‐2000 Quality Management Systems ‐ Requirements. D. National Fire Protection Association (NFPA)

1.  NFPA   285  Standard   Fire  Test  Method   for  Evaluation   of  Fire   Propagation Characteristics  of  Exterior  Non‐Load‐Bearing   Wall  Assemblies  Containing Combustible Components

13.2 System Description

13.2.1   Performance Requirements: Provide composite metal panels that have been manufactured, fabricated and installed to withstand loads from deflection and thermal movement  and to maintain performance criteria stated by manufacturer without defects, damage or failure.

A. Water and Air Leakage: Provide systems that have been tested and certified to conform to the following criteria:

1. Air Leakage, ASTM E283: Not more than 0.06 cfm per ft2 of wall area (0.003 (L/s m2) when tested at 1.57 psf (0.075 kPa).

2. Water  Penetration:  No water  infiltration  under  static  pressure  when  tested  in accordance with ASTM E331 at a differential of 10% of inward acting design load, 6.24 psf (0.299 kPa) minimum, after 15 minutes.

a. Water penetration is defined as the appearance of uncontrolled water in the wall.

b. Wall design shall feature provisions to drain to the exterior face of the wall any leakage of water at joints and any condensation that may occur within the construction.

B. Fire Performance: Provide composite fire rated panels that have been evaluated and are in compliance with regulatory code agency requirements specified herein.

13.3 Submittals

13.3.1    General: Submit listed submittals in accordance with Conditions of the Contract.

13.3.2 		Product   Data:   Submit   product   data,   including   manufacturer’s   SPEC‐DATA   sheet,   for specified products.

A. Shop Drawings: Submit shop drawings showing layout, profiles and product components, including anchorage, accessories, finish colors and textures.

1. Include  details  showing  thickness  and dimensions  of the various  system  parts, fastening   and  anchoring   methods,   locations   of  joints  and  gaskets,   and   location   and configuration of joints necessary to accommodate thermal movement.

B. Samples: Submit selection and verification samples for finishes, colors and textures.

1. Selected  Samples:  Manufacturer’s  color charts or chips illustrating  full range  of colors,  finishes  and  patterns  available  for  composite  metal  panels  with  factory  applied finishes.

2. Verification Samples:

2.1.  Structural:  12  inch  ×  12  inch  (305  ×  305  mm)  sample  composite  panels  in thickness   specified   from   an  available   stock   color,   including   clips,   anchors,   supports, fasteners,  closures  and  other  panel  accessories,   for  assembly  approval.  Include  panel assembly samples not less than 24 inches × 24 inches (610 × 610 mm) showing 4‐way joint.

2.2. Include  separate  sets of drawdown  samples on aluminum  substrate,  not  less than 3 inches × 5 inches (76 × 127 mm), of each color and finish selected for color approval. Larger samples of standard colors are available with production‐applied coatings.

C. Quality Assurance Submittals: Submit the following:

1.   Test   Reports:   Certified   test   reports   showing   compliance   with   specified performance  characteristics  and physical  properties,  or a third  party  listing  documenting compliance to a comparable code section.

2.  Certificates:  Product  certificates  signed  by  manufacturer   certifying  materials comply with specified performance characteristics and physical requirements.

3. Manufacturer's Instructions: Manufacturer’s installation instructions.

4. Manufacturer’s Field Reports: Manufacturer’s field reports.

D. Closeout Submittals: Submit the following:

1. Warranty: Warranty documents specified.

13.4 Quality Assurance

13.4.1 Qualifications:

1.  Installer   Qualifications:   Installer  experienced   in  performing   work  of  this  section  who   has specialized in the installation of work similar to that required for this project.

a. Certificate: When requested, submit certificate indicating qualification.

2.  Manufacturer  Qualifications:  Company  with  a  minimum  of  5  years  of  continuous  experience manufacturing panel material of the type specified:

a. Able to provide specified warranty on finish.

b. Able to provide  a list of 5 other projects of similar size, including  approximate  date  of installation and name of Architect for each.

c. Able to produce the composite material without outsourcing of the coating or laminating process.

d. Able to provide a certificate of registration to ISO 9001‐2000.

3. Fabricator Qualifications: Company with at least 3 years of experience on similar sized metal panel projects  and qualified  by panel  material  manufacturer.  Capable  of providing  field service representation during construction

13.4.2   Mock‐Ups: Install at project site a job mock‐up using acceptable products and manufacturer approved  installation  methods.  Obtain  Owner’s  and Architect’s  acceptance  of finish color (drawdown  samples  to  be  used  for  color  approval  of  nonstandard  coil  coated  colors), texture and pattern and workmanship  standard.  Comply with Division  01 Quality Control, Mock‐Up Requirements Section.

1. Mock‐Up Size: to be proposed by contractor

2.  Maintenance:   Maintain  mock‐up  during  construction   for  workmanship   comparison;

remove and legally dispose of mock‐up when no longer required.

3.  Incorporation:   Mock‐up  may  be  incorporated   into  final  construction   upon  Owner’s approval.

13.4.3   Pre‐installation  Meetings:  Conduct pre‐installation  meeting to verify project requirements, substrate conditions,  manufacturer’s  installation  instructions  and  manufacturer’s  warranty requirements.  Comply  with  Division  01  Project  Management  and  Coordination,  Project Meetings Section.

13.5 Delivery, Storage & Handling

13.5.1   General: Comply with Division 01 Product Requirements Sections.

13.5.2   Ordering: Comply with manufacturer’s  ordering instructions and lead time requirements to avoid construction delays.

13.5.3   Delivery:  Deliver  materials  in  manufacturer’s  original,  unopened,  undamaged  containers with identification labels intact.

1. Protection: Protect finish of panels by applying heavy‐duty removable plastic film during production.

2. Delivery:  Package  composite  wall panels for protection  against  transportation  damage. Provide markings to identify components consistently with drawings.

3. Handling:  Exercise  care in unloading,  storing  and installing  panels  to prevent  bending, warping, twisting and surface damage.

13.5.4   Storage  and  Protection:  Store  materials  protected  from  exposure  to  harmful  weather

conditions and at temperatures recommended by manufacturer.

1. Storage: Store panels in well‐ventilated space out of direct sunlight.

a. Protect panels from moisture and condensation with tarpaulins or other suitable weather tight covering installed to provide ventilation.

b. Slope panels to ensure positive drainage of any accumulated water.

c.  Do  not  store  panels  in  any  enclosed  space  where  ambient  temperature  can exceed 120 degrees F (49 degrees C).

2. Damage:  Avoid contact  with any other materials  that might cause staining,  denting  or other surface damage.

13.6 Project Conditions

13.6.1   Field Measurements:  Verify actual measurements/openings by field measurements  before fabrication;    show    recorded    measurements     on    shop    drawings.    Coordinate    field measurements,   fabrication   schedule   with  construction   progress   to   avoid  construction delays.

13.7 Warranty

13.7.1 Project Warranty: Refer to Conditions of the Contract for project warranty provisions.

13.7.2   Manufacturer’s   Warranty:   Submit,   for   Owner’s   acceptance,   manufacturer’s   standard warranty document executed by authorized company official. Manufacturer’s warranty is in addition  to,  and  not  a  limitation  of,  other  rights  Owner  may  have  under  the  Contract Documents.

1. Warranty Period:

a. Panel Integrity: 10 years commencing on Date of Substantial Completion. b. Finish:  10 years commencing on Date of Substantial Completion.

PRODUCTS

13.8 Composite Fire resistive metal panels

13.8.1 Manufacturer: Mitsubishi Plastics Composites America, Inc.

13.9 Product Substitutions

13.9.1 Substitutions: No substitutions permitted.

13.10 Composite Metal Panel Materials

13.10.1 ALPOLIC/fr Composite Fire Resistive Metal Panels:

1. Panel Thickness: 4 mm.

2.  Core:   Thermoplastic   core   material   with   inorganic   fillers   that   meets   performance characteristics specified when fabricated into composite assembly.

3. Face Sheets: Aluminum alloy 3105 H14 and as follows:

a.  Coil  coated  with  a  fluoropolymer  paint  finish  that  meets  or  exceeds  values expressed in AAMA 2605 where relevant to coil coatings.

b. Spray coated with specified finish (quantities less than 7500 ft2 (700 m2)).

4. Bond Integrity: Tested for resistance to delamination as follows:

a. Peel Strength (ASTM D1781): 22.5 in‐lb/in (100 N‐m/m) minimum.

b. No degradation in bond performance after 8 hours of submersion in boiling water and after 21 days of immersion in water at 70 degrees F (21 degrees C).

c. Thermally bonded to the core material in a continuous process under tension.

5. Fire Performance:

a. Flamespread, ASTM E84: <25.

b. Smoke Developed, ASTM E84: <450.

c. Surface Flammability, Modified ASTM E108: Pass. d. Ignition Temperature:

1) Flash, ASTM D1929: 716 degrees F (380 degrees C).

2) Ignition: 752 degrees F (400 degrees C).

e. Flammability,  Exterior, Non‐load‐bearing  wall assemblies  and panels, NFPA 285:

Pass.

6. Product Transparency:

a. Provide a Product Transparency Declaration (PTD) for the Composite metal panels

13.10.2 Production Tolerances:

1. Width: +/‐ 2.0 mm.

2. Length: +/‐ 4.0 mm.

3. Thickness (4 mm Panel): +/‐ 0.008 inch (0.2 mm).

4. Thickness (6 mm Panel): +/‐ 0.012 inch (0.3 mm).

5. Bow: Maximum 0.5% length or width.

6. Squareness: Maximum 0.2 inch (5.1 mm).

7. Edges of sheets shall be square and trimmed with no displacement of aluminum sheets or protrusion of core material.

13.11 Accessories

13.11.1 General:  Provide  fabricator’s  standard  accessories,  including  fasteners,  clips,  anchorage devices and attachments for specific applications indicated on contract documents.

13.12 Related Materials

13.12.1 General: Refer to other related sections in Related Sections paragraph specified herein for related   materials,   including   coldform   metal  framing,   flashing   and  trim,  joint   sealers, aluminum windows, glass and glazing and curtain walls.

13.13 Fabrication

13.13.1 General: Shop fabricate to sizes and joint configurations indicated on drawings.

1. Where final dimensions cannot be established by field measurements,  provide allowance for field adjustment as recommended by the fabricator.

2. Form panel lines, breaks and angles to be sharp and true, with surfaces that are free from warp or buckle.

3. Fabricate with sharply cut edges and no displacement of aluminum sheet or protrusion of core.

13.14 Finishes

13.14.1  Factory  Finish:  Lumiflon‐based  fluoropolymer  resin coating  that meets  or exceeds  values expressed in AAMA 2605 where relevant to coil coatings.

1. Color: Prismatic Champagne ME010

13.15 Source Quality

13.15.1 Source Quality: Obtain composite panel products from a single manufacturer.

EXECUTION

13.16 Manufacturer’s Instructions

13.16.1 Compliance:   Comply   with   manufacturer’s   product   data,   including   product   technical bulletins, product catalog installation instructions and product carton instructions.

13.17 Examination

13.17.1 Site Verification of Conditions: Verify that conditions of substrates previously installed under other sections are acceptable for product installation.

13.18 Preparation

13.18.1 Surface Preparation: -

13.19 Installation

13.19.1 General:

1. Install panels plumb, level and true in compliance with fabricator’s recommendations.

2. Anchor panels securely in place in accordance with fabricator’s approved shop drawings.

3.  Comply  with  fabricator’s  instructions  for  installation  of  concealed  fasteners  and  with provisions of Section 07 90 00 for installation of joint sealers.

4. Installation  Tolerances:  Maximum  deviation  from  horizontal  and  vertical  alignment  of installed panels: 0.25 inch in 20 feet (6.4 mm in 6.1 m), noncumulative.

13.19.2 Related  Products  Installation  Requirements:  Refer  to  other  sections  in  Related  Sections paragraph herein for installation of related products.

13.20 Field Quality Requirements

13.20.1 Field   Quality   Control:   Comply   with   panel   system   fabricator’s   recommendations   and guidelines for field forming of panels.

13.20.2 Fabricator’s   Field   Services:   Upon   Owner’s   request,   provide   fabricator’s   field   service consisting of product use recommendations  and periodic site visit for inspection of product installation in accordance with fabricator’s instructions.

1. Site Visits: As requested by owner

13.21 Adjusting

13.21.1 Adjusting:

1. Repair panels with minor damage such that repairs are not discernible at a distance of 10 feet (3 m).

2. Remove and replace panels damaged beyond repair.

3. Remove  protective  film immediately  after installation  of joint sealers  and  immediately prior to completion of composite metal panel work.

4. Remove from project site damaged panels, protective film and other debris attributable to work of this section.

13.22 Cleaning

13.22.1 Cleaning:  Remove  temporary  coverings  and protection  of adjacent  work areas.  Repair or replace   damaged   installed   products.   Clean   installed   products   in   accordance    with manufacturer’s  instructions prior to owner’s acceptance.  Remove construction  debris from project site and legally dispose of debris.

13.23 Protection

13.23.1 Protection: Protect installed product’s finish surfaces from damage during construction.

1.  Institute  protective  measures  as  required  to  ensure  that  installed  panels  will  not  be damaged.

14. ROOFING

14.1       Scope

14.1.1   This Section deals with steel profiled sheeting used as external weather‐proof  cladding  of roofs.

14.2       Roof Cladding

14.2.1   Sheet  type:  Spandek  hiten  roofing  sheets  manufactured  by  John  Lysaght,  No.18  Benoi

Sector, Jurong, Singapore 2262 or equivalent.

14.2.2   Structural support: timber sections as per drawings.

14.2.3   Fastening: No. 12‐14x45mm hexagonal head self‐drilling and tapping screw seal.

14.2.4   End  laps:  200mm  and  should  be  sealed  with  a recommend  sealant  for  pitches  below  7 degrees.

14.2.5   Side laps: as per manufacturer’s recommendations.

14.3       Products

14.3.1   The profiled sheeting shall be in galvanized sheet steel with a factory per finished protective

PVC film with colour to approval.

14.4       Workmanship

14.4.1   Accessories: Flashing, trims, filler pieces, spacers, tapes, sealant, etc. where not specified to be the types recommended by the sheet manufacturer.

14.4.2   Fastening: Select types and location of fastenings to meet the following requirements.

14.4.2.1              Wind suction loaded: Calculate  in accordance  with CP 3: Chapter5:  Part2 , making due allowance for any  internal pressure.

               Basic wind speed: 45 m/sec.

               Topography  factory S1 : 1.0

	Ground  roughness,  building  size  and  height  Factory  (S2)  : as  determined from CP3:Chapter5 : Part 2, Table 3.

               Statistical factor ( S3) : 1.0

14.4.3.2               Imposed   loads   other   than   wind   and   maintenance   load,   1.5   KN/m2 concentrated   on  a  300mm2       which   ever   produces   the   greater   stress. Maintenance point load: 0.9 KN concentrated on any 125mm2.

14.4.3.3               Dead load: allow for self‐weight of sheeting.

14.4.3.4               Roof pitch: as indicated on drawings.

14.4.3.5               Distance between not less than 900mm or as indicated on the drawings.

14.5       Fixing

14.5.1   Quality of Work: Handle and store to preserve surface using clean dry gloves. Do not slide sheets over rough surface or each other. Packs of all sheets must be kept dry in transit and stored  clear  of  the  ground  under  cover  to  prevent  water  and  /or  condensation  being trapped  between  adjacent  surfaces.  If  packs  become  wet,  sheets  should  be  separated, wiped  with a clean cloth without  delay  and placed  so  that air calculation  completes  the drying process.

14.5.2   Structure:  Check that structure is in a suitable state to receive sheets before commencing fixing. Contractor must confirm acceptance to consultant

14.5.3   Structure: Do not fix profiled sheeting until final coats of paints have been applied to outer surfaces of supporting structure.

14.5.4   Isolating  Tape: Apply to those surfaces  of supports  which would  otherwise  be in  contact with sheeting or accessories after fixing.

14.5.5   Cutting and drilling:

14.5.5.1               Cuts sheets accurately with clean, true lines and no distortion with a power saw with abrasive cutting disc.

14.5.5.2               Cut openings in sheet for out lets, vent pipes , flues etc. to the  minimum size necessary . Reinforce edges of openings with structural members.

14.5.5.3               Drill all holes. Position at regular intervals in straight lines. Holes for primary fastenings  to be 1.5mm larger than the diameter  of fastening  unless self‐ drilling type is used.

14.5.5.4               Remove burrs, drilling swarf, lubricant,  dust and any other foreign matter before finally fixing sheets into position.

14.5.6   Direction of Laying: Lay sheets with exposed joints of side lap away from prevailing wind.

14.5.7   End Laps: to be fully supported.

14.5.8   Sealant:

14.5.8.1               Install to manufactures recommendation.

14.5.8.2               Position in straight, unbroken lines parallel to edges of sheets. Placed into corrugations. Do not allow to sag into position.

14.5.8.3               Ensure continuity and effectiveness of seal, especially at corners of sheets.

14.5.8.4               Do not over compress.

14.6        Fittings and Features

14.6.1   Profile Fillers: use where specified and wherever necessary to close off corrugation cavities from the outside and inside of the building. Position on the line of, or above, fastening and ensuring a tight fit and leaving no gaps. Where sealed laps are specified bed profile fillers in sealant  on  top  and  bottom  surface,  but  do  not  obstruct  channels  for  ventilation   or condensation drainage.

14.6.2   Flashing Trims: All fittings for flashing / trim shall be as per manufacturers’ recommendation and lapped at joints as follows:

13.6.2.1               Vertical and sloping flashing / trims: end lap to be the same as for adjacent sheeting.

13.6.2.2               Horizontal flashing / trims: end laps to be 150mm and sealed.

14.6.3   Gutter: Ensure that gutters are fully supported at each joint and at intermediate position not more than 900mm  apart.  Fix with spigot  ends up the slope  and make all the  joints  fully watertight.  Position  sheeting  to  leave  a  clear  width  across  the  gutter  of  not  less  than

230mm.

14.6.4    Insulation:

	75mm thick Rock Wool insulation blanket with aluminium foil backing on both sides laid between purlins at 1000 centres, including wire mesh. Manufacturer and reference ‐ to approval.

15. FINISHES

15.1       General

15.1.1   Glazed Ceramic Tile shall comply with British Standard specification  No. 1281 and  shall be approved  sizes  as  shown  on  Drawings  and  the  product  of  a  reputable  manufacturers approved by the Consultant.

15.1.2   Unglazed Ceramic Tile shall comply with the requirements  of British Standard No.1286 and shall  be  of  approved  sizes  as  shown  on  the  drawings  and  the  product  of  a  reputable manufacturer.

15.1.3   Contractor to get Client approval on all materials prior to purchasing.

15.2       Manufacturers

15.2.1   All tiles, ceramic  or homogenous,  for the project shall be manufactured  as mentioned  on finishing  schedule  / details  drawings.  Required  brands  of tile shall be use only  described locations and tile brands shall not change if only approved by consultant.

15.2.2   Following brands of tiles shall use for described locations as per finishing schedule / details drawings. All the tiles shall be submitted to Consultant for approval prior to use.

         Niro

         Cotto

         Lanka tile

         White horse

15.3       Ceramic and Vitreous Tile Materials

15.3.1   Ceramic and Vitreous clay Wall Tiles:

15.3.1.1               All  tiles  for  wall  installation   shall  be  have  cushion   edge,   impervious, polished or semi‐polished  porcelain and highly glazed surface. Colours shall be as selected by the Consultant and shall include trimmers, corner pieces, bullnose and all other special shapes indicated or required. All this shall be free from flaws, cracks and crazing.

15.3.2   Floor Ceramic and Vitreous Tiles

15.3.2.1               All  porcelain  floor  tiles  should  exhibit  required  texture  as  indicated  or required (polished,  semi‐polished,  no skid or heavy duty) and it  should be laid with 3mm groove. Floor tiles shall be specially prepared  for floor use but shall have all the qualities of ceramic tiles listed above for wall use.

15.4 Flooring

15.4.1 Vinyl flooring:

15.4.1.1               Marbleised,   directional   vinyl  sheet  and  tile  flooring  with  extra   strong polyurethane  reinforcement  with  a subtle  blend  of light  through  to dark tones.  All  vinyl  flooring,  homogenous   or  permanently  static  dissipative pressed, shall be utilised at specified locations as indicated in the drawing. It shall  have  the  required  thickness as  indicated  in  the  drawing  and  shall include coving, cover formers, end cap strip on coving top.

15.4.1.2              Following  brands of vinyl flooring shall use for described  locations  as  per finishing  schedule  / details  drawings.  All  types  of vinyl  flooring  shall  be submitted to Consultant for approval prior to use.

         Tarkett (United States of America)

         Objectflor Art and Design GmbH covering (Germany)

15.4.2 Carpeting:

15.4.2.1               Both loop and cut pile plain fiber carpets must meet the requirements of EN

1307 and should be 100% permanent  colour polypropylene  having a 5mm underlay  with  imported  grippers.  It  shall  include  aluminium  single  side edging and must be soil and stain resistant.

15.4.2.2              Following brands of carpets shall use for described locations as per finishing schedule  /  details  drawings.  All  types  of  carpets  shall  be  submitted  to Consultant for approval prior to use.

         danfloor (United Kingdom)

         Forbo flooring systems (Switzerland)

15.4.3 Cement Flooring:

15.4.3.1               Thin section cement render (2‐4 mm thick per coat) shall be used as cement rendering  over bricks and/or  blocks  to achieve  a modern  rendered  finish and shall possess high water resistance. Following brands of cement render shall use for described locations as per finishing schedule / details drawings. All types of cement  render shall be  submitted  to Consultant  for approval prior to use.

         SUPA COAT (Australia)

         Hanson Portland‐limestone Cement (Germany)

15.4.3.2               Provision  of external cement paving of 450mmX450mmX50mm as well  as

75mm interlocking paving as indicated in the drawing for external walkways and  car  port  area  respectively.  Following  brands  of  paving  shall  use  for described locations as per finishing schedule / details drawings and shall be submitted to Consultant for approval prior to use.

         PRIORA MARSHALLS (United Kingdom)

15.5 Wall papers

Provision of acrylic/vinyl coated wall papers on plastered walls with 100mm high timber  skirting.  The plastered  walls must be kept dry  before placing wall papers to ensure proper adherence of wall paper to the wall and also aides  for  future  removal.  Following  brands  of  wall  papers  shall  use  for described locations as per finishing schedule / details drawings and shall be submitted to Consultant for approval prior to use.

         Brewster Home Fashions (United States of America)

         Mirage Wall coverings (United States of America)

15.6 Wood veneer

Wood veneer  shall comply  with ISO 9001 (Quality  Management)  and  ISO

14001  (Environment   Management)   and  finish  up  to  ceiling  level  with

100mm  timber  skirting.  Its natural  wood  surface  shall be protected  by a proprietary  wear‐resistant  film or coat. Following brands of wood veneers shall use for described locations as per finishing schedule / details drawings and shall be submitted to Consultant for approval prior to use.

         Proligna (Prodin‐Prodema – Spain)

         Gunlocke (United States of America)

15.7 Ceiling

15.7.1 Suspended Ceilings:

15.7.1.1               Suspended   aluminium   ceilings  shall  be  powder  coated  with  a  material, preferably   epoxy,   polyester   or   epoxy   polyester   with   the   approval   of consultant.

15.7.1.2               Aluminium concealed clip‐in grid ceiling system comprising a “spring T” or ‘A spring” that supports the ceiling tiles. It shall be fixed to and below a primary grid, usually a galvanized  channel section as indicated and approved by the Consultant.

15.7.1.3               Provision  of  plain  mineral  fibre  acoustical  suspended  ceilings  with  fibres mixed  with  wet  process  with  a  high  quality  vinyl  emulsion  paint  surface coating.

15.7.1.4               Following  brands  of  ceiling  types  shall  use  for  described  locations  as  per finishing schedule / details drawings. All finishing materials shall be submitted to Consultant for approval prior to use.

         Technical Metal Industrial Co.L.C.C (United Arab Emirates)

         Hebei Optimum Construction Materials Co., Ltd (China)

15.7.2 Composite Board:

15.7.2.1               Zinc  Aluminium  Composite  board  with  multi‐layer  Ti‐Zinc  treated  surface protected by fluorocarboned  resin paint FEVE. Following brands of crash rails shall  be  used  for  described  locations  as  per  finishing  schedule  /  details drawings and shall be submitted to Consultant for approval prior to use.

         Alucobond (Germany)

15.8 Corner Guards

15.8.1                  Surface  mounted  guards  consisting  of a continuous  retainer  with  snap‐on Acrovyn 4000 cover. Color matched end caps to be provided for both partial and full height applications and shall be approved by Consultant.

15.8.3                 Following brands of corner guards shall be used for described locations as per finishing schedule / details drawings and shall be submitted to Consultant for approval prior to use.

C/S Acrovyn

15.8.3              Corner Guards rails must comply with relevant requirements in AS1428 (Australian Standards) series.

15.9 Skirting

15.9.1                  Integral coved, on-site formed, skirting involved dressing the floor dressing the floor material up the wall over a preformed coving fillet usually 20 to 38mm radius.

15.9.2                  Coved skirting should be a minimum of 150mm high. The skirting can either be tapered at the top to provide a minimal horizontal dust catching edge or finished with a capping seal profile.

15.9.3                  The combination of sheet resilient flooring with wielded seams and integral coved skirting, as described above, is generally recommended for all patient care, clinical, wet and other areas where hygiene, infection control, ease of cleaning and decontamination are desirable or required.

15.9.4                  For semi-industrial and food process / waste handling areas, seamless coatings or ceramic tiling, may be used as appropriate to function.

15.9.5                  Where used for wet, clean or similar applications, vinyl wall finishes may be welded to the vinyl floor finish provided that both finishes are homogenous with a matching or 2mm minimum thickness. The use of vinyl wall sheet products of 1mm thickness carried down over skirting and glued with an overlap is not recommended for healthcare use.

15.10 Crash Rails

15.10.1                  Crash rails must comply with relevant requirements in AS1428 (Australian Standards) series.

15.10.2                  Crash rails shall be 150mm wide and comprise of fireproof PVC plastic acrylic cover with aluminum alloy inner‐support.

15.11 Splash Protection

15.11.1                Apply Splash protection to walls in areas such as; laboratories, formula rooms, beverage bays, kitchen, bathrooms, showers, and dirty utility rooms in addition to hand basins, scrub troughs, cleaners and laundry sinks.

15.12 Radiation Protection

15.12.1                  Radiation protection will depend on individual room requirements. Material used and the extent of radiation shielding should be determined by a radiation services consultancy in accordance with governing regulations and guidelines.

15.13 Bench Tops

15.13.1                  Benchtops should have a smooth, impervious and durable finish and to be resistant to stains. Joins should be avoided where possible for ease of cleaning. The design and materials used should adequately meet all functional, sustainable and life cycle requirements. A range of products are suitable,

e.g. Laminates, synthetics and stainless steel.

15.13.2                  The junction between wall and bench top work surface may be sealed, provided with an upstand and / or wall protection, or designed with an upstand and / or cleanable gap, as required by function,

e.g. Cleaning, Infection control

15.14 Partition Walls

15.14.1 	Provision   of Aluminum   Composite   board   partition   wall   framed   with aluminum extrusion, covered by powder coating.  The infill panel shall be laminated glass consisting of two layers of normal glass sandwiched with the underlay polyvinyl butyral (PVB) firm. This shall be provided at described locations as per finishing schedule / details drawings with excellent sound & thermal insulation as well as 100% water proof and resistant to stains.

15.14.2 	Tempered   glass partition walls at described   locations   as per   finishing schedule / details drawings shall be 12mm thick and insulated properly.

15.14.3 	All laminated phenolic board partition systems shall be impregnated with melamine resin and decorated on both sides. It must be resistant to damage from impacts or stains, including indelible inks and highly durable.

15.14.4             Following brands of partition walls shall be used for described locations as per   finishing   schedule   / details   drawings   and   shall   be   submitted   to consultant for approval prior to use.

         Reliance Metal Industries Sdn Bhd (Malaysia)

         MDP Enterprises (India)

         Hufcor (United States of America)

         Ironwood Manufacturing (United States of America)

15.15    Mortar Materials

15.15.1 Standard brand of light gray or white Portland cement as specified in drawings/Finishing schedule/ BOQ, conforming to current British Standard specifications shall be used.

15.15.2 Sand:  shall be clean, sharp, river sand, conforming to British Standard Specifications and graded fine to coarse within the following limits: 100% passing 8 sieve, 90% to 100% passing

16 sieve, 60% to 90% passing 30 sieve, 25% to 55% passing 50 sieve and 0% to 15% passing

100 sieve.

15.16    Cement Colour

15.16.1 Dry cement colour, chemically inert, non‐fading, alkali fast, mineral pigment, as approved shall be used wherever refinished.

15.17    Waterproofing

15.17.1 Floors of toilet areas, corridors and planter boxes shall be treated with an appropriate water proofing coating, approved by the Consultant

15.18    Installation Requirements

15.18.1 As far as possible, tile lay out work should be in such a way that no tiles less than half size occurs.

15.18.2 Align joints in wall tile vertically and horizontally except where other patterns are shown or specified, Align joints in floor tiles at right angles to each other straight with walls to conform to the patterns selected.

15.18.3 Verify  locations  of  accessories   before  installing  tiles.  Work  shall  be  coordinated  with plumbing and other trades before starting of tile work.

15.18.4 Installation   of  ceramic   and  vitreous   tile  shall  be  in  accordance   with   manufacturer’s instructions.

15.19    Floor Tile Installation

15.19.1 All ceramic and vitreous clay tile floors shall be in Portland cement setting beds. Concrete surfaces shall be cleaned and surface of concrete shall be wetted prior to placing of setting bed mortar. Tiles shall be immersed in water for minimum of 4 hours before laying.

15.19.2 Setting Bed Mortar Mix: shall consist of one (1) part Portland cement and two (2) parts dry sand, by volume, to which not more than 1/10 part of hydrated lime may be added.

15.19.3 When mixed with water, the mortar mix shall be of such consistency and workability as to produce  maximum  density.  Determine  consistency  by stroking  the mortar  surface  with  a trowel. Where  of correct consistency,  the trowelled  surface readily  assumes  a smoothed, slickened appearance.

15.19.4 Spread  setting  bed  mortar  and  screed  to  provide  smooth,  dense  beds  with  true  planes

pitched to drains. The thickness of bed shall be such that the floor tile will finish flush with adjacent finished flooring, but bedding shall have average thickness of 38mm.

15.19.5 After  bed  has  set  sufficiently  to  be  worked  over,  trowel  or  brush  a thin  layer,  3mm  in thickness, of neat Portland cement or special tile adhesive (approved by Consultant)  paste over the surface of the back of tile.

15.19.6 Do not prepare larger setting bed than can be covered with tile before the mortar sets.

15.19.7 Press tile firmly into the bed tapping with wood blocks to obtain firm bedding of total tile area and a smooth top surface.

15.19.8 All tiles shall be properly  aligned with straight joints in even widths. Joints width  shall  be determined  by spacers  on ceramic  tiles. Tamping  shall be completed  within  one (1) hour after placing tile. Adjust work out of line within this period.

15.19.9 Tiles shall be fitted closely around  pipes running  through  walls and floors. Pitch  floors  to drains.

15.20    Wall Tile Installation

15.20.1 Base Plaster 13mm thick applied to masonry wall shall be one‐part Portland cement, three‐ parts of river sand by volume. Where additional thickness build‐up is required to conform to indicated lines, apply as separate coat at no cost to employer.

15.20.2 Setting bed of tiles shall be done with cement slurry or special tile Adhesive (approved by Consultant).  The thickness of slurry bed shall be 3mm thick minimum  for setting tiles and walls.

15.20.3 Installation  of  tiles  shall  be  in  accordance  with  standards  and  applicable  requirements previously specified for floor tile.

15.20.4 Tiles shall be installed in perfect vertical plumb and as per the pattern and joints if shown on drawings

15.21    Grouting

15.21.1 Grouting shall not commence for at least 24 hours after placing of tiles.

15.21.2 Grout for floor and wall ceramic and vitreous tiles shall be waterproof, neat white Portland cement  with  dry  cement  colour  added  as  directed  by  the  Consultant.  If  white  grout  is selected, cement shall be white.

15.21.3 Grout mixed to a creamy consistency in accordance with manufacturer’s  directions shall be used for joint filling. Maximum width of joints shall be 3mm.

15.21.4 Force maximum grout into the joints with trowel. Before grout sets, strike or tool joints to base of cushion  and fill all skips  and gaps.  Do not permit  setting  bed  materials  to show through grouted joints.

15.21.5 Cure grout joints by maintaining  damp condition  for three (3) days by sponging  down,  or other methods approved by the Consultant. Allow floors to set 48 hours before permitting ordinary foot traffic.

15.22    Defects in Tiles and Tile Laying

15.22.1 The surface of all tiled floors shall be perfectly in level and shall be executed by experienced workers in the field of tile laying.

15.22.2 A  sample  panel  of  laid  tiles  of  each  type  shall  be  approved  by  the  Consultant  before commencement of tile laying.

15.22.3 Mismatches of colour, chipped or damaged tiles installed by the Contractor shall be rejected and shall have to be replaced by the Contractor at his own cost and risk.

15.22.4 Mismatches of colour in tiles installed by the Contractor shall be rejected and shall have to be replaced by the Contractor at his own cost and risk.

15.23    Guarantees

15.23.1 Manufacturer  shall provide his standard guarantees  for work under this section. However, such guarantees shall be in addition to not in lieu of all other liabilities which manufacturers and Contractor may have by other provisions of the Contract Documents

16. PAINTING

16.1       Material

16.1.1   All paints shall be approved by the Consultant for colour, quality and type. All painting work shall  be  carried  out  in  accordance  with  the  paint  manufacturer’s  specifications  unless otherwise directed by the Consultant.

16.1.2   All paints and finishes used for the project shall be manufactured  by or under license from the following manufacturer;

Nippon Paints (Japan)

Imperial Chemical Industries (UK) Sigma Paints (Saudi Arabia)

Paints from manufacturers not listed above shall only be used with prior written approval of the Consultant

16.1.3   Paint shall be ready mixed and all paints, varnishes, enamels, lacquer stains, paste fillers and similar  materials  shall  be  delivered  to  the  site  in  the  original  containers  with  the  seals unbroken and labels intact. Each container shall give the manufacturer’s name, type of paint, colour of paint and instructions for reducing. Thinning shall be done only in accordance with the manufacturer’s directions.

16.1.4   Use of product by the same manufacturer shall be a general rule in each stage of work in this

Specification.

16.1.5   Colour,  luster,  colour  scheme,  finish  shall  be  decided  by  the  Consultant  after  checking sample paint test.

16.1.6   The painting shall be performed by experienced and competent painter.

16.1.7   Where walls are specified to be painted, all columns arises, groove, rough surfaces, reveals, soffits and returns, etc. shall be included and no extra shall be payable.

16.2       Definition of Terminology

16.2.1   Surface Sealing

Surface to be painted shall be sealed to have uniform suction and prevent lye from oozing out.

16.2.2   Spot Puttying

All cracks and depressions shall be filled flush with putty.

16.2.3   Puttying

All surfaces to be painted shall be puttied uniformly flat surface.

16.2.4   Spot painting

Spot puttied area shall be touched up by paint

16.2.5   Touch‐up

Any damaged area after the prime coat has been applied shall be touched up

16.2.6   Drying hour

The drying time of double‐coated  paint shall be measured at the temperature  of 20°C and humidity of 70%.

16.2.7   Amount of paint

The amount shall be standard amount of paint itself not including thinner. It shall increase or decrease depending on shape and surface condition in the process of painting.

16.3       Paint Finish Symbols

OP                              Synthetic resin mix paint finish

VP                              Solvent‐polyvinyl chloride resin paint finish EP                               Polyvinyl acetate resin emulsion paint finish AEP                            Synthetic resin emulsion paint finish

CL                               Clear lacquer finish

EXP                            Epoxy resin paint finish

Stipple (OP)              Stippled finish (oil mix paint finish)

Stipple (EP) Stippled finish (polyvinyl acetate resin emulsion paint finish

16.4       Painting in General

16.4.1   Preparation of Paint

17.4.1.1               Mixing: Paint content with pigment  shall be thoroughly  stirred to  make  a uniform consistency.

17.4.1.2               Thinning:  Portable water shall be used for thinning  of emulsion  paint  and water‐soluble  paint. Proper thinner, product of the same manufacturer  as paint,  as a rule, shall be used  for other  types  of  painting.  Percentage  of thinning and viscosity shall be conducted with direction of manufacturer or catalogue  as  they  vary  with  the  method  of  paint,  temperature,  type  of material to be painted.

17.4.1.3               Allowable period of Use: Paint mixed with more than 2 types shall be used with direction  of a manufacturer  or catalogue  as allowable  period  of use, mixing ratio and mixing method vary. The paint which has passed allowable period of use shall not be used.

16.4.2   Conditions of Painting

16.4.2.1               Work shall not be executed in the following situations

16.4.2.1.1            When humidity is above 85%

16.4.2.1.2            When raining or it is forecast

16.4.2.1.3            When dusts are present

16.4.2.1.4            When  temperature   of  surface  is  high  under  hot  weather  and bubbles are likely to develop on the painted surface.

16.4.2.2               Conditions of Surface to be painted: Work shall not be executed or proper means shall be taken in the following situations.

16.4.2.2.1            When surface is damp and wet

16.4.2.2.2            When condensation is likely to develop on the surface.

16.4.2.2.3            All nail holes on veneer, board. etc., shall be covered with proper rust‐proof   paint  before   the  subsequent   painting   is   applied   in accordance with this specification.

16.4.3   Performance

Paint shall be evenly and uniformed  applied  on the surface.  Areas of difficult  application such as pointed part, internal angle, welded part, etc. shall be thoroughly painted and double coated as necessary to deep uniform coating thickness.

Painting shall be properly done by carefully selecting the painting method by the shape of surface and types of paint.

16.4.4   Protection

17.4.4.1               Dangerous  material  such as paint,  thinner,  etc., excluding  emulsion  paint and  water‐soluble   paint  shall  be  kept  in  accordance   with   regulations concerned.

16.5       Procedure of Painting

16.5.1    Exterior ‐ Surface of Mortar, Plaster and Concrete

AEP‐ Weather shield Exterior paint

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface preparation |  | Dry, clean and free from impurities |  |
| 2. Surface sealing | 1 | Exterior Wall Sealer | As per manufacture’s specifications |
| 3. Texture base | 2 | texture base putty mechanically sprayed uniformly | As per manufacture’s specifications |
| 4. Surface finishing |  | Flatten with masonry trowel uniformly surfaced |  |
| 5. First coating | 1 | Weather shield paint | As per manufacture’s specifications |
| 6. Finish coating | 2 | Weather shield paint | As per manufacture’s specifications |

Notes:

Degree of dryness on the surface to be painted shall be kept under 6% in water content and below PH 9.5

Puttying  and  sanding  process  shall  allowed  to  omit  depending  on  the  conditions  of  the surface.

Drying time of putty shall be long enough for sanding to proceed.

Amount of sealer for surface sealing shall be adjusted with direction of the Consultant  as it varies with the surface conditions.

16.5.2    Exterior ‐ Iron Products in General

OP ‐ Synthetic resin mix paint

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface preparation |  | Completely remove rust, moisture, oil and other impurities by sander, cleaner and surface. |  |
| 2. First coating 24 hours | 1 | Rust proof oil paint | As per manufacture’s specifications |
| 3. Touch-up |  | Touch-up rustproof oil paint | As per manufacture’s specifications |
| 4. First coating | 1 | Rustproof oil paint |  |
| 5. Second coating | 1 | Synthetic resin mix paint | As per manufacture’s specifications |
| 6. Finish coating | 2 | Synthetic resin mix paint | As per manufacture’s specifications |

Note: Paint for touch-up, painting shall be the same as used for first coat in process No. 2

16.5.3    Exterior ‐ Wood

OP ‐ Synthetic resin mix paint finish

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface preparation |  | Clean and sand to plane surface |  |
| 2. Knot treatment | 1‐2 | Lacquer varnish | As per manufacture’s specifications |
| 3. First coating | 1 | First coat paint of oil mix paint | As per manufacture’s specifications |
| 4. Second Coating | 1 | Oil mix paint | As per manufacture’s specifications |
| 5. Finish coating | 1 | Oil mix paint | As per manufacture’s specifications |

Note:

Puttying and sanding shall be done after process No.2 when there are cracks, etc. on  the surface putty shall be oil‐putty, but drying time shall vary depending on condi

16.5.4    Interior ‐ Mortar, board, etc.

Stipple (EP) ‐ Polyvinyl acetate resin emulsion paint finish

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface preparation |  | Dry, clean and free from impurities |  |
| 2. Surface sealing | 1 | Sealer for emulsion paint | As per manufacture’s specifications |
| 3. Puttying |  | Putty for emulsion paint |  |
| 4. Grinding |  | Grind with proper grinding tool |  |
| 5. Spot painting |  | Second coating paint of polyvinyl acetate resin emulsion paint |  |
| 6. Second Coating | 2 | Polyvinyl acetate resin emulsion paint | As per manufacture’s specifications |
| 7. Finish Coating | 1 | Polyvinyl acetate resin emulsion paint for stipple‐finish | As per manufacture’s specifications |

Notes:

Degree of dryness on the surface to be painted shall be kept under 6% in water content and below PH 9.5

Puttying  and  sanding  process  shall  allowed  to omit  depending  on the  conditions  of  the surface.Drying time of putty shall be long enough for sanding to proceed.

Amount of sealer for surface sealing shall be adjusted with direction of the Consultant as it varies with the surface conditions.

16.5.5   Interior ‐ Mortar, plaster, concrete, etc. VP  Solvent ‐ Polyvinyl chloride resin paint finish

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface preparation |  | Dry, clean and free from Impurities |  |
| 2. Surface sealing | 1 | Sealer for emulsion paint | As per manufacture’s specifications |
| 3. Puttying |  | Putty for polyvinyl chloride resin paint |  |
| 4. Grinding |  | Grind with proper grinding tool |  |
| 5. Spot painting |  | Solvent‐polyvinyl chloride resin enamel emulsion paint |  |
| 6. Second Coating | 1 | Solvent‐polyvinyl chloride resin enamel emulsion paint | As per manufacture’s specifications |
| 7. Finish Coating | 2 | Solvent‐polyvinyl chloride resin enamel emulsion paint | As per manufacture’s specifications |

Notes:

(a)  Degree of dryness on the surface to be painted shall be kept under 6% in water content and below PH 9.5

(b)  Puttying and sanding process shall allowed to omit depending on the conditions of the surface.

(c)  Drying time of putty shall be long enough for sanding to proceed.

(d)  Amount of sealer for surface sealing shall be adjusted with direction of the Consultant as it varies with the surface conditions.

16.5.6   Interior ‐ Mortar, plaster, concrete, etc.

EP  Polyvinyl acetate resin emulsion paint finish

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface preparation |  | Dry, clean and free from impurities |  |
| 2. Surface sealing | 1 | Sealer for emulsion paint | As per manufacture’s specifications |
| 3. Puttying |  | Putty for emulsion paint |  |
| 4. Grinding |  | Grind with proper grinding tool |  |
| 5. Spot painting |  | Polyvinyl acetate resin emulsion paint |  |
| 6. Second Coating | 1 | Polyvinyl acetate resin emulsion paint | As per manufacture’s specifications |
| 7. Finish Coating | 1 | Polyvinyl acetate resin emulsion paint | As per manufacture’s specifications |

Notes:

(a)  Degree of dryness on the surface to be painted shall be kept under 6% in water content and below PH 9.5

(b)  Puttying and sanding process shall allowed to omit depending on the conditions of the surface.

(c)  Drying time of putty shall be long enough for sanding to proceed.

(d)  Amount of sealer for surface sealing shall be adjusted with direction of the Consultant as it varies with the surface conditions.

16.5.7   Interior ‐ Iron products, steel. OP ‐ Synthetic resin mix paint

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface preparation |  | Completely remove rust, moisture, oil and other impurities by sander, and surface cleaner |  |
| 2. First Coating | 1 | Synthetic resin rust‐proof. Red lead‐type, lead compound‐ type | As per manufacture’s specifications |
| 3. Touch‐up |  | Touch‐up rust proof paint |  |
| 4. First Coating | 1 | Synthetic resin rust‐proof paint. Red lead‐type, Lead compound‐ type | As per manufacture’s specifications |
| 5. Second Coating | 1 | Synthetic resin mix paint | As per manufacture’s specifications |
| 6. Finish Coating | 1 | Synthetic resin mix paint | As per manufacture’s specifications |

Notes:

(a)  Paint for touch‐up painting shall be the same as used for first coat in process No.2

(b)  When oil rust‐proof paint is used instead of synthetic resin rust proof, its specification shall conform to No. 5 and No.6.16.5.8   Floor ‐ Concrete and Mortar

EXP ‐ Epoxy resin paint finish

| Coating Process | No. of Coats | Type of Paint | Drying hour |
| --- | --- | --- | --- |
| 1. Surface treatment |  | Dry, clean and free from impurities |  |
| 2. First coating | 1 | First coating paint for epoxy | As per manufacture’s specifications |
| 3. Finish Coating | 2 | Epoxy resin paint | As per manufacture’s specifications |

Notes:

(a)  Degree of dryness on the surface to be painted shall be kept under 6% in water content and below PH 9.5.

(b)  Amount of paint and number of paint shall be as directed by the Consultant as they vary with the conditions of surface and required thickness of coating.

(c)  Painted surface shall be kept out of use for more than 7 days after application of final coat.

17. PLUMBING

17.1      General

The materials used and workmanship shall be of highest quality and grade unless otherwise specified

shall conform to the latest specifications of British Standards and Codes of Practice for  “ Water Supply

“Sanitary, Pipe Work “Building Drainage “ Surface Water and Sub- Soil Drainage” and applicable to

details and work indicated on the Drawing and Bill of Quantities. In case of any discrepancy / ambiguity

the decision of the Consultants shall be final, and the contractor will act and perform accordingly.

The work shall be executed strictly in accordance with the rules and regulations set by the relevant local

authority of the Maldives.

The Contractor shall be responsible for obtaining the necessary approvals and test certificates from the

concerned departments of Maldives.

Plumbing work shall be carried out by licensed plumbers and shall produce the copy of the license

along with the tenders, or approved by the Consultant.

Any damage done by the Contractor to any existing work during the course of execution of his work,

shall be made good by him at his own cost. Failing which it shall be get done by the Consultants

at Contractor’s risk and cost.

The Contractor shall be responsible to connect the drainage and water supply to the mains and to

obtain the necessary approvals and certificates from the relevant authorities of the Maldives.

All connections to mains and meter installation shall be arranged by the Contractor and payment of

fees thereof, if any, shall also be made by him.

The Contractor shall be responsible for the watch and ward of all fittings until the Works is fully

completed and handed over to the Project manager.

The levels, measurements and other information concerning the existing site as shown on  the

drawings or as described as are supposed to be correct. The Contractor shall, however, verify them by himself and no extra claim whatsoever shall be entertained on account of the errors or omissions in such matters or on account of the descriptions turning cut to be different from what was excepted.

The Consultant shall instruct the Contractor to purchase and use such materials of particular make

or from particular source as may in his opinion be necessary for proper and  reasonable compliance with the specification and execution of the Works.

After all plumbing fixtures and equipment have been set ready for use, and before the Contractor leaves

the job, he shall thoroughly clean all fixtures installed by him, removing all plaster, stickers, rust stains

and other foreign matter of discolouration on fixtures, leaving every part in acceptable condition and

ready for use to the satisfaction of the Consultants.

Substitution: Substitutions will only be considered when a product becomes unavailable from the manufacturer

due to no fault of the Contractor. The Contractor shall document each request with complete data substantiating

that the proposed substitution complies with the Contract Documents. Substitution request must be submitted

30 days prior to commencement of any plumbing works. Only one request for substitution will be considered for

each product. When substitution is not accepted, the Contractor shall provide the specified product.

QUALITY ASSURANCE - All pipe, fittings, valves, appurtenances and accessories furnished shall be new and from a current manufacturer. A certificate from the manufacturer stating the materials furnished are new and of a recent manufacture shall be furnished to the Engineer. The Contractor shall also provide the Employer with an affidavit (four copies) from the manufacturer stating that the pipe, fittings, valves, appurtenances and accessories comply with the provisions of these specifications. Certificates that the items comply with the relevant ISO 9000 series for manufacturing processes are also required from the manufacturer

17.2      Drawings and Information Required

The Contractor shall submit shop drawing for the entire installation including installation details for all

items required or asked for approval of the Consultant.

Approved by the Consultant of shop drawing for any material, apparatus, devices and layout, shall not

relieve the Contractor from the responsibility of furnishing same of proper dimension, size, quantity

and all performance characteristic to efficiently perform the requirements and intent of the Contract

Documents. Such approval shall not relieve the Contractor from responsibility for errors of any sort in

the shop drawing.

If the shop drawings deviate from the contract Documents the Contractor shall advise the Consultants

of the deviations in writing accompanying the shop drawings including the reasons for the

deviations. At the start of the Project the Contractor shall periodically and

thereafter submit to the Consultants list of all shop drawings which will be submitted in the course of the project. The list shall show the disposition of each item including date of submission approval etc. The list shall be kept up to date through the entire course of construction.

17.3      Record Drawing

During Construction the Contractor shall keep an accurate record of all deviations between the

work as shown on the Contract Drawings and that which is actually installed.

The Contractor shall secure from the Consultants after approval of his Shop Drawing a complete set

of drawing and note changes thereon in ink.

The Contractor shall make a complete record of all changes and revisions in the original design which

exist in the completed work.

The cost of furnishing above prints and preparing these for record “ shall be deemed to be include

in the tendered cost and its effects spread over other items of work, and as such item shall not be a

subject to payment”. When all revisions showing the work as finally installed the corrected  Original

Transparencies shall  be  submitted  to  the  Consultants  before  final payment for the completed

work will be made.

17.4      Operating and Maintenance Instructions

17.4.1   Three sets of operating and maintenance instruction covering completely the operation and maintenance of all plumbing equipment, controls, heaters, pumps and the like shall be furnished to the Project manager, by the Contractor.

17.5      Test

Leak test of plumbing and drain to be completed. Above ground pressure

The entire system of drains, waste and vent piping inside and outside the building shall be tested by

the Contractor under a water test, which shall include the entire system from the lowest point to the

highest pipes above the roof.

Ensure that all installation work related to the pipe network that are to be tested are completed. The Underground pipe works are to be leak tested prior to ground screed laying.

Once the leak tests are completed in portions of pipe networks, underground pressure pipe works are to be pressure tested as whole network unit as per site requirements.

Vent pipes to be tested for the purpose of remove trapped in air.

Supply water pipe works shall be pressure tested according to their respective utility company. (state the no. of bar and the time duration stated by the utility company.

The water test shall be made in accordance with all local requirement. Every portion of the system shall

be tested to a hydrostatic pressure equivalent to latest 15 feet head of water. After filling, the Contractor

shall shut off water supply and shall allow it to stand 2 hours under test during which time there shall be

no loss or leakage.

The Contractor shall furnish and pay for device, material supplies, labour and power require for all

tests. All tests shall be made in the presence and to the satisfaction of Consultant.

Defects disclosed by the test shall be repaired or if required by the Consultant defective work shall be

replaced with new work without any extra charge to the Project manager. Test shall be operated

as directed until the work is proved satisfactory.

Fixture shall be tested for soundness, stability of support and satisfactory operation.

The Contractor shall notify the Consultant at least one week in advance of making the required test, so

that arrangements may be made for their presence to witness the test.

Equipment shall be tested in service and the Contractor shall demonstrate that the equipment

performs the work intended for it and that it complies with the requirement of these specification for such equipment, to the satisfaction of Consultants.

The rates shall include for all costs associated with tests.

17.6      Work in Common Piping

17.6.1   Material

17.6.1.1              Piping and fitting material shall be uP.V.C, Hard Impact P.V.C. or  High

Temperature P.V.C. and approved by the Consultant.

17.6.1.2              Piping  material  shall  comply  with  requirements of  water  supply  and sewerage and other relevant authorities.

17.6.1.3              Materials for the piping and service requirements shall basically conform to the service pressures encountered.

FOR uPVC Pipes and Fittings:

- Pipes shall conform to ISO-4422 and shall be installed in accordance with the manufacturer’s guidelines. All jointing shall be by socket and spigots with sealing rings which shall conform to BS 7874. Solvent welded joints are not permitted. Pipes shall be capable of withstanding ultraviolet degradation and shall incorporate a rodent inhibitor. Pipes shall be furnished in standard laying lengths of 6 m and shall be grey in colour.

- Fittings made of uPVC shall conform to BS 4346 and shall be manufactured by heat injection moulding or extrusion machine only. Fittings shall have the same strength as the connecting pipe.

- All joints shall be designed to have the same characteristics and strength as the connecting pipe. Unless otherwise specified;

  - joints for underground pipes and fittings 90 mm and larger shall be push in type using rubber gaskets;

  - joints for underground pipes and bends of 63 mm shall be welded using solvent cement;

  - joints for other underground fittings of 63 mm shall be push in type using rubber gaskets;

  - joints for all exposed pipes, and pipes smaller than 63 mm, shall be welded using solvent cement.

- For push in joints, the pipes shall have an integral socket end and spigot end. The socket  shall be designed by the manufacturer. One neoprene ring shall be furnished for each joint. The neoprene ring shall conform to JIS K6353, BS 2494, ASTM F477, or equivalent.

- For welded joints, the pipes shall have an integral socket end designed by the manufacturer. Solvent cement shall conform to ISO 8588:1987 or BS 4346 and shall be mixed in strict accord with the manufacturer's instructions. Any impurities in the cement shall be cause for rejection. Data on the pot life of the cement shall be approved by the Engineer.

- Flanged joints shall be made using flange adapters.

- Testing of pipes and fittings shall be carried out in accordance with JIS K6741, JIS K6742 or equivalent. Each pipe and fitting shall be tested under an internal hydrostatic pressure of not less than 118 Pa for the duration of 60 seconds. The Contractor shall furnish test certificates of tests carried out for quality control during the manufacture of the pipes in accordance with ISO-4422

- and Appendices A to E of BS 3505:1986 and shall, if required by the Engineer, undertake such additional tests as the Engineer considers necessary.

- PIPELINE IDENTIFICATION - All exposed and/or non-buried pipe, including tubing, galvanized pipe, polyvinyl chloride pipe, GRP and stainless steel pipe, shall be identified by color to show its use function. Colour bands of an approved tape type may be used on PVC, and all other pipe not readily susceptible to painted finish. Markers shall be adhesive type with extra strength and suitable for continuous duty at 120°C. All markers shall have a protective silicone film. Both the direction of fluid flow, and the name of the fluid in the pipe shall be stenciled on all pipe at least once every six metres and at every change of direction. Color bands shall be spaced at four metre intervals and every change in direction. The size of the letters and color bands shall be as specified in the table below:

| Outside diameter of pipe or covering (mm) | Width of color band (mm) | Height of legend or letters (mm) |
| --- | --- | --- |
| 10 to 30 40 to 50 60 to 150 200 to 250 Over 250 | 25 25 150 150 150 | 5 15 50 60 90 |

- Testing - The Contractor shall submit, for the Engineer's approval, details of his proposed methods and program for testing (including details of test equipment) and shall arrange for all tests to be witnessed by the Engineer, or other person appointed by the Engineer. The Contractor shall provide all things necessary for carrying out testing and cleaning including water, pumps, compressors, gauges, piped connections, stop ends, and all other temporary works. Pipelines shall be properly completed and supported before being put under test except as hereinafter detailed. No testing will be permitted until ten days after thrust blocks and other holding down works have been completed. Trenches shall not be left open at joints prior to testing pipelines except in exceptional circumstances and as permitted by the Engineer who may lay down certain restricting conditions. In addition to any tests of individual joints or other interim tests, which may be specified elsewhere, the Contractor shall submit all parts of the pipelines to a final test. Notwithstanding the foregoing, the Contractor may at any stage of construction, carry out such other tests as he considers desirable to check materials and workmanship on the pipeline but this shall not relieve the Contractor of his obligations to achieve successful tests under the Contract. All water required for testing and cleaning the pipelines shall be treated or raw water, depending on the final product to be carried by the pipeline, and shall be provided by the Contractor at his cost. Potable water shall be used for potable water lines.

- Pressure pipelines carrying liquids shall be pressure tested as specified herein.

Gauges used for testing pressure pipelines shall be either of conventional circular type, calibrated in metres head of water or shall have a digital indicator capable of reading increments of 0.1 metre head. Before any gauge is used, the Contractor shall arrange for it to be checked independently and a dated certificate of its accuracy shall be provided to the Engineer. One additional gauge as above shall be handed over to the Engineer’s representative

- for purposes of verification during testing. Calibration of pressure gauges shall be carried out by the Contractor, at regular intervals, as required by the Engineer.

- The Contractor should note that since valves cannot be guaranteed to be perfectly drop-tight, testing against closed valves shall not be permitted unless with the written approval of the Engineer. The "open" ends of the pipeline (or sections thereof) shall normally be stopped off by blank flanges, or cap ends, additionally secured where necessary by temporary struts and wedges. No claims whatsoever will be entertained on account of leaking valves, or any other difficulties in closing of lengths of pipework for testing, which shall be entirely at the Contractor’s expense.

- The Contractor shall remain responsible for the care of the works during testing of the pipework. For purpose of interim testing, the pipeline shall be divided into sections. Each section shall be separately tested to the Engineer’s satisfaction for deflection and pressure when each section is completed. The Contractor shall submit to the Engineer detailed procedures for performing hydrostatic pressure tests of installed piping, fittings, valves, meters and appurtenances for approval. Procedures for performing hydrostatic pressure tests for each section of pipeline shall indicate:

- location and capacity of the test pump,

- test pressure at the pump and at the high and low points in the pipeline,

- procedures for venting the air from the pipeline,

- disposing the water after satisfactory testing.

- Each pipeline or section thereof shall be filled with water and all air removed as far as possible. If permanent air vents are not located at all high points, the Contractor shall install suitable cocks at such points so that the air can be expelled as the line is filled with water. The line shall be filled slowly to prevent possible water hammer. The test pump and gauge shall be connected to the pipeline at a location other than the highest point in the line to facilitate the release of air from the highest point. Pressure in the pipeline shall then be raised steadily up to 1.5 times the working pressure, and maintained at the working pressure for a period of not less than 24 hours, to allow for absorption and achieve conditions as stable as possible for testing. The standing period will commence from the time at which the working pressure was reached successfully, after which all exposed joints shall be carefully inspected for evidence of leakage.

17.6.2   Providing Drawings and Manuals

17.6.2.1              The Contractor shall submit one set of originals and further two copies of layout drawings to the Consultant after completion of the Works. These drawings must give the following information:

(a) Run of all piping and diameter on all floors and the vertical stacks. (b)  Location and sizes of all control valves, access panels and other equipment.

(c) Location of all manholes and their sizes.

17.6.2.2              No completion certificate will be issued until the drawings are submitted.

17.6.2.3              The Contractor shall submit to the Consultant for approval, samples, shop drawings, manufacturer’s drawings, equipment characteristics and capacity data etc. of all equipment, accessories devices etc. that he proposes to use in the installation.

17.6.3   Samples

17.6.3.1              The Contractor shall provide samples of all sanitary fittings, pipes and specials man-hole cover and frames, gratings and water supply pipes and fittings etc. and shall be deposited with the Consultant (which will be returned to the Contractor at the completion of the Works) and shall obtain approval from the Consultant before using in the Works. Any material rejected by  the Consultant shall be removed from the site within 24 hours of rejection.

17.6.4   Drawings

|  |  | 17.6.4.1 |  | The works shall be done in conformity with the plans and within the requirements of the general architectural, electrical and structural plans. This work shall be properly coordinated with the work of the other trades. Hangers and sleeves shall be furnished in time for their installation as other work proceeds. |
| --- | --- | --- | --- | --- |
|  |  | 17.6.4.2 |  | The plumbing drawings are diagrammatic, but shall be followed as closely as |
|  |  |  |  | actual construction. All deviations from drawings required to conform to the |
|  |  |  |  | building construction shall be made by the Contractor at his own expense. |
|  |  | 17.6.4.3 |  | The architectural drawings shall take precedence over the plumbing drawings |
|  |  |  |  | as to all dimensions. |
|  |  | 17.6.4.4 |  | Large size details shall take precedence over small size drawings. The special |
|  |  |  |  | dimensions in the specifications or schedule of quantities or instructions of |
|  |  |  |  | the Consultant shall supersede the drawings. The Contractor shall verify all |
|  |  |  |  | dimensions at site. |
|  |  | 17.6.4.5 |  | The recommend position of the fittings, fixtures, control valves, tanks etc.as |
|  |  |  |  | shown on the drawings will be adhered to as far as practicable. |
|  |  | 17.6.4.6 |  | Should there be any discrepancy due to incomplete description ambiguity or |
|  |  |  |  | omission in the drawings and other documents, whether original or |
|  |  |  |  | supplementary, forming the contract, either found on completion or during |
|  |  |  |  | the currency of the installations work, the Contractor shall immediately, on |
|  |  |  |  | discovering the same, draw the attention of the Consultants and the |
|  |  |  |  | Consultants decision in final and binding on the Contractor. |
| 17.6.5 |  | Existing pipes |  |  |
|  |  | 17.6.5.1 |  | The site shall be examined for field drains and those, when found, shall be |
|  |  |  |  | either entirely removed or diverted, trenches filled with dry earth in 200mm to 300mm layers and consolidated as directed by the Consultant. |
| 17.6.6 |  | Spare Parts |  |  |
|  |  | 17.6.6.1 |  | Necessary spare parts of the plumbing equipment for the one (1) year |
|  |  |  |  | operation shall be supplied by the Contractor. |
| 17.6.7 |  | Excavation |  |  |
|  |  | 17.6.7.1 |  | All excavations shall be timbered to the satisfaction of the Consultant and the |
|  |  |  |  | type of timber shall be suitable to the kind of earth encountered. Fixing of |
|  |  |  |  | timber and removal after completion of work shall be done as directed by the |
|  |  |  |  | Consultant. |
|  |  | 17.6.7.2 |  | Should any water accumulated in the trenches, headings or other excavation, |
|  |  |  |  | the Contractor shall do such work as may be necessary to drain away the |
|  |  |  |  | accumulated water and shall install pumps as may be required to keep the |
|  |  |  |  | excavation and trenches dry. The Contractor shall ensure that the flow water |
|  |  |  |  | in trenches or excavation does not injure or remove cement or aggregate of |
|  |  |  |  | any concrete that has not set. No subsoil water shall be discharged into open |
|  |  |  |  | drains or sewer at the site. |
|  |  | 17.6.7.3 |  | In refilling trenches after excavation this should be done in layers of 150mm |
|  |  |  |  | after consolidating each layer. Special care shall be to see that the earth is |
|  |  |  |  | packed uniformly and no injury to the pipe. |
|  | 17.6.7.4 |  | Rates for excavation should include for backfilling in consolidated layers where necessary and as directed by the Consultant. |  |
| 17.6.8 | Piping |  |  |  |
|  | 17.6.8.1 |  | The Contractor shall, as soon as possible after the award of the contract, prepare and submit to the Consultant for approval, working drawings showing exact locations and pipe runs for all pipework, the layout and setting up of equipment and the connection of piping to the equipment. Such drawings shall include details and methods of supports, anchors and sleeves etc. |  |
|  | 17.6.8.2 |  | Pipe runs shown in the drawings are approximate and intended to indicate the general run and locations only. The exact locations of all pipework shall be determined on Site. |  |
|  | 17.6.8.3 |  | All pipes, fittings etc. shall be kept closed against moisture and foreign matters when stored at site and during installation. |  |
|  | 17.6.8.4 |  | All pipes shall be fixed clear of one another and be so arranged as toprovide easy access for maintenance and repair. |  |
|  | 17.6.8.5 |  | All plumbing work shall be carried out by suitably qualified plumbers in accordance with the British Code of Practice and Regulations and requirements of related Authorities. |  |
|  | 17.6.8.6 |  | Materials for the piping and service requirements shall basically conform to the service pressures encountered. |  |
|  | 17.6.8.7 |  | Each part of the installation of the plumbing work shall be completed in all details as shown in the drawings or as specified and provided with all |  |
|  |  |  | necessary control valves, etc. that will be necessary for their satisfactory operation. |  |
|  | 17.6.8.8 |  | All piping shall be run plumb, and straight and parallel to walls, except drain line which shall pitch 6mm per 300mm in the direction of flow. |  |
|  | 17.6.8.9 |  | Pockets, unnecessary traps, turns and off-sets shall be avoided. When traps or pockets are unavoidable they shall be valved drains. |  |
|  | 17.6.8.10 |  | Piping installed on the concrete slab shall be firmly fixed or anchored to the floor with packing to prevent damage to pipes. Pipes shall not be bent with bender where cross with other pipe or change to upward. |  |
|  | 17.6.8.11 |  | Where pipes are to be laid directly in the ground, bed shall be sufficiently compacted, necessary protection for piping shall be taken. |  |
|  | 17.6.8.12 |  | Backfill shall be done after the approval of the Consultant in such a manner not to damage the pipe line and shall be restored to the original stage. |  |
|  | 17.6.8.13 |  | Where pipes penetrate through waterproof part or fire partition or fire wall, pipe sleeves shall be provided and clearance between pipe sleeve and pipe shall be filled with caulking material approved by the Consultant. |  |
|  | 17.6.8.14 |  | Pipes, fittings, valves and accessories shall be thoroughly cleaned, both internally and externally before installation and shall be cleaned before putting into service. |  |
|  | 17.6.8.15 |  | Plumbing work shall be completed in accordance with the details shown on the Drawings or as specified and provided with all necessary control valves, etc. that will be necessary for their satisfactory operation. |  |

17.6.8.16           All pipes shall be cut square and true to the pipe axis by means of suitable tools without reducing pipe diameter and cut ends shall be finished smooth. Before making connections, chips, dirt and other foreign matter shall  be removed from inside interior of each pipe. Fixing of hangars and embedding of pipe sleeves shall be carried out without delay along with the progress of the work where required.

17.6.8.17           Pipe connections for the water supply system shall be by uP.V.C high pressure. Jointing shall be generally by means of solvent cement according to manufacturer’s instructions

17.6.8.18            Vertical pipe shall be braced at more than 2 point in every story.

17.6.8.19           After pipes are laid out and before they are hidden, water pressure should be checked. It should only be hidden after determining there are no problems with the pressure

17.6.8.20          Water pipes and waste water pipes should be connected to the sewer systems

17.7      Water Supply Work

17.7.1   Materials

Pipes, joints and fittings for water supply work shall be high pressure uP.V.C.S

Materials   and   workmanship  shall   comply   with   the   local   water   supply   authority requirements.

- The use and installation of unplasticized PVC pipework shall comply with the relevant provisions of BS 3505.  Solvent welded joints and fittings for PVC-U pipes shall comply with the relevant provisions of BS 4346:  Part 1.  Mechanical joints and fittings for PVC-U pipes shall comply with the relevant provisions of BS 4346:  Part 2.

17.8      Water Pumps

The specification herein stated are basic guides only. Other items not so indicated but which

are obviously necessary for the proper operation of the system as intended shall be supplied and

installed, in accordance with accepted Consulting standard.

Manuals of operation and maintenance and list of spare parts shall be supplied together with

the equipment.

The contractor shall submit at least four copies of pump performance curves showing among

others, the pump rating and efficiency, properly marked out.

A metal name plate indication in indelible letters for the correct specification of the pump and motor

shall be properly attached to the assembly at a location such that the information written thereon

can be conveniently read by all concerned.

Well water pump and Fresh water pump: Flow rate = 60L/min, Head = 70m, Type : End suction Hydro

pneumatic pump, 220/440V, 3-Phase, 50 Hz. Alternate and parallel operation. Fire pump:

50L/min, 70m head, Vertical multistage pump with alternative operations.

Water pumps placed should be Grundfos or a pump of that standard. After it is placed it should be shaded and kept accessible in case there is a problem. All the procedures for electricity and water connections should be given to the pump.

17.9      Spacing of supports

17.9.1                 Support spacing for uP.V.C pipes shall be as follows

| Nominal Dia. | upto 40 | more than 50 |
| --- | --- | --- |
| Space (m) | 1.2 | 1.5 |

17.10    Drainage Work

17.10.1 General

17.10.1.1            High Pressure uP.V.C pipe and fittings shall be used for all drainage work including vent pipes.

17.10.1.2            Joints shall be made by the cold-jointing method, and the pipe interior shall have not offset at the joint interfering with the flow. Joint adhesive shall be good quality and shall not be affected by heat and shock.

17.10.1.3            Where horizontal drain  branch joints the  main, such branch shall  be connected to the main in a substantially horizontal position and at an acute angle of not more than 45 degree to the main in all cases.

17.10.1.4            Every toilet should have a gully attached for drainage purposes

17.10.2 Vent stack pipes

17.10.2.1            Vent  pipe  shall  be  vertically  branched out  upward from  a  horizontal drain branch pipe or other appropriate point. Horizontal branching of the vent pipe shall be done on approval of the Consultant.

17.10.2.2            Where vent pipes on each floor are to be connected to the vent stack, all connections  shall  be  made  at  least  150mm  above  the  respective overflow edges of fixture on that floor.

17.10.2.3            The provision of the preceding item shall also apply to the connection of vent stack vent pipe.

17.10.2.4            Vent stack shall be connected to the waste stack or soil stack at the lowest part to stack pipe.

17.10.2.5            Where vent pipe is to be connected to the horizontal drain pipe, such angle shall be more than 45 degree to upward.

17.10.2.6            Vent stack shall be extended 600 mm from the top of the roof or lead to the wall and top of pipe shall be covered with vent cap.

17.11    Laying of Pipes

17.11.1 The pipes shall be laid to proper lines and levels as shown in the plans and directed by the Consultant, as the main is laid, the front pipes in the trench shall always be closed with a plug either of iron or wood and security fastened. The plug shall not be removed except when pipe laying is resumed or for purposes of testing. (11.11)

17.11.1 The trench should be compacted before pipes of septic tank and leach field are placed

17.11.2 Water pipes and sewer pipes should be laid down in accordance to the drawing

17.12     Laying of sewer water Mains

17.12.1 All mains shall be laid on a good solid, bottom to prevent subsidence and consequent fracture.

17.12.2 Mains running under buildings, if unavoidable, shall be completely surrounded by 150mm

of concrete.

17.12.3 In case of mains passing through a well, the weight of the latter shall be carried by a lintel or a suitable relieving arches.

All rising mains shall be properly plugged to all wall brackets at regular intervals as given in the drawings.

All mains shall be concealed inside wall as far as possible except for vertical sewer mains, cleaning doors shall be provided in the walls whenever necessary and as directed by the Consultant.

17.13    Sewers

After the cement has had time to set, the pipes shall be tested in length between manholes

in following manner.

In the lowest manhole/intercepting trap as the case may be, a plug shall be inserted in the pipe. The

disc in the pipe at the upper manhole shall be fitted with a filling pipe with a right angle bend and

an air cook.

The pipe line shall then be filled with water by means of the pipe connection on the upper disc. The

air cock on the upper disc shall be kept open while the pipe line is being filled to permit the escape

of air.

When the pipes are filled with water and air excluded, the air cock shall be shut and the water

shall be poured into conical filler, attached to the filling pipe until the water remains in thefilter.

The filling pipe shall then be raised and fastened so that the height of surface of the water in the

filler above the invert of the pipe is 1828 mm which will be usual test pressure for S.W pipes.

If the water level does not fall more than 16mm (12mm) in a length of 91.4 metre the test may

be considered satisfactory.

The Contractor shall make good all defective work at his own expense

17.14    U.P.V.C Pipes

17.14.1 Manufacturer’s instruction should be followed in pipes to be used for water mains.

Where specified, pipes shall have integral rubber ring joints and where solvent cement joints  are specified,  a  sufficient  number  of  expansion/contraction  joints  shall  be incorporated  in  the length of mains to allow for variation of temperature to the recommendation of the pipe manufacturers.

17.14.2 These pipes shall be effectively protected from the direct rays of sun immediately after they  are  laid  and  until  permission is  given for the trenches to  be refilled by  the Consultant. Subject to such permission being obtained, trenches shall be refilled without delay. Final  connection at a fixed point shall be deemed unto the majority of the length of the pipe line has been covered by backfill in order to reduce the effect of expansion and contraction caused by temperature variations .

17.15    Bends and other Specials

17.15.1 In fixing bends care shall be taken to see that the axis of the bend is truly vertical or horizontal as the case may be and the spigot of the bend is well in the socket of the pipe with which a joint has to be formed. The Contractor shall be called on to replace any faulty work at his own expense.

17.16    Flanged Joints

17.16.1 All flanged joints shall be made by painting the faces of the flanged with red lead freely and bolting the flanges evenly on all sides. A thin fiber of lead wool may be used in making the joints water tight when facing of the flanges is not true. Rubber insertions may be used  with approval. Sewage resistant rubber insertion is to be used for sewer lines.

17.16.2 All joints should be connected properly with Aslon glue or equivalent.

17.16.3 Elbow or T joints should not be used for for drainage. Instead a junction should be kept

in the areas where T/Elbow joints were going to be used.

17.17    Support for U.P.V.C Pipes

17.17.1 When U.P.V.C pipe lines incorporate metal valves or other heavy fittings, it is essential to support the valves directly rather than allowing their weight to be carried by the uP.V.C pipe and support shall be placed on either side of the fittings mentioned above. Moulded plastic fitting also should be supported.

17.17.2 Maximum allowable horizontal support distance for uP.V.C are given below.

| Nominal bore | 12mm (1/2”) | 18mm (3/8”) | 25mm (1”) | 32mm (1 1/4”) | 38mm (1 ½”) | 50mm (2”) | 75mm (3”) | 100mm (4”) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Support distance | 533mm (1’9”) | 616mm (2’0”) | 686mm (2’3”) | 764mm (2’6”) | 840mm (2’9”) | 915mm (3’0”) | 1220mm (4’0”) | 1290mm (4’6”) |

18.12.1For vertical installation supports, distances shall be doubled.

17.18    Sewer pipes

17.18.1 All ‘P’, ‘S’, ‘I’ junctions bends etc. required shall be furnished and set without extra charge and shall confirm to the pipe specifications as to quality

17.19    Air Valves

These valves to be fitted as per drawings and Bill of Quantities shall be tested and accompanied by a certifying their efficiency.

The floating ball in the valve shall be suitable metal or vulcanite or rubber specially manufactured for tropical conditions.

17.20    Scour Washout Valve

These shall be provided at portions shown in place and shall contain in one unit a flanged scour valve with short connection pieces, cast iron bend and T pieces for connection to main pipe.

The rate shall also provide for short length of straight pipe to a convenient as per details complete with covers and surface boxes

17.21    Foot valves and Strainers

17.21.1 Foot valve and strainers should be of reputable manufacture approved by the Consultant and shall be fitted with flushing lever attachment where specified.

17.22    Pressure Reducers

17.22.1 Pressure reducing valves shall be of the equilibrium type of approved manufacture and capable of reducing the pressure to the valve required as per plan and Bill of Quantities.

17.23    Water Meter

17.23.1 The water meters shall be from FENAKA/MWSC and shall be approved by the consultant before installation.

17.24    Equilibrium Ball Valves

17.24.1 These should be of reputable manufacture approved by the Consultant and be of the angle pattern with gun metal valve seats guide bush, copper float with wrought iron lever and links with bronze pins.

17.25    Fittings

All sanitary pipes, gullies, water closets/bidets, squatting basins, sinks bath tubs etc. to be of

approved design and to be obtained from approved Manufacture and to be of the best

stoneware, glazed inside and outside, with burnt hard and sound, free from flaws, blisters, cracks

and other imperfections and best quality commonly called ‘Firsts’.

Rates should include for all bends, junctions, traps, cleaning, painting, fixing clear of wall etc.

complete as specified as per Bill of Quantities.

All pipes, fittings, flushing cisterns, valves, stop cocks, taps, tanks, surface boxes etc. to be of the

best of their kinds and in addition to complying with previous clauses to be from approved

Manufacturers and all taps, cocks, valves etc. to be screwed down pipe. Taps to be of brass/nickel

coated and valves to be of gun metal. All tanks to be made fly-proof and to the complete satisfaction

of the Consultant.

Rates should include for all cutting and waste, bends, taps junctures, cleaning eyes, tees.

17.26    Manholes, Manhole covers and Frames

Concrete cover slabs or top rings of manholes shall provide a suitable seating for a rectangular cover.

The frame shall have a clear opening of 0.61m x 0.61m or alternatively a circular or double triangular cover depending on the type of cast iron manhole cover to be used. The rate for manholes shall allow for such provision.

Where the supply of cast iron manhole cover and frames is payable separately the cost of setting, surrounding, painting and materials for same shall be allowed for in the rate for manholes.

Suitable lifting rings, hooks or brackets shall be provided in the precast manhole sections. Box holes shall be separately grouted with 1:2 cement mortar.

The contractor shall supply two manhole keys for each pattern of cover without additional charge over the rate for covers (or manholes).

Heavy duty (grade a) cast iron manhole cover and frames shall be of the double triangular type to bs and having a clear opening of 550mm dia.

Medium duty (grade b) cast iron manhole covers and frames shall be of the circular type having a clear opening of 550mm dia or the rectangular type having a clear opening of 0.61m x 0.61m and confirm to bs. They shall be of the single seal type, the weight of cover frame being approximately 127.00 kgs.

Light duty (grade c) cast iron manhole cover and frames shall be of the doubles seal flat type having a clear opening of 0.61m x 0.61m conforming to bs. Weight of cover and frame approximately 50.75kgs.

All manhole covers and frames shall be supplied, coated with a black bituminous composition and be given two coats of bituminous paint after bedding.

No extra rate is payable for drop and/or junction manholes but piping in and surrounds of drop lines are payable at that relevant rates for s.w piping and manholes.

In drop manholes where the difference in level between the incoming drains and the sewer does  not  exceed 0.610m in 75mm and there is sufficient room in the manhole, the connecting pipe may be brought directly through the manhole wall, and the fall accommodated by constructing  a ramp in the benching of the manhole. The ramp shall be of concrete and finished equal to that of the benches. No extra rate is payable.

17.27    Interceptor Manhole

17.27.1 All gravity sewer lines should be, connected through an intercepting inspection chamber before connecting to the main sewer line, and the dimensions of the manhole and trap to be in conformity with FENAKA.

17.28    Fixtures and Accessories

17.28.1 All sanitarywares shall be manufactured by one of the following manufacturers.

1.   American Standard

2.   Ideal Standard

3.    American Briggs

4.   Armitage Shanks

5.   Cotto

6.   Star sanitaryware

Sanitary ware from manufacturers not listed above shall only be used with prior written approval of the Consultant

17.29    As built Drawings

The Plumbing Contractor, shall mark down with red pencil on two sets of plumbing plans all the revisions, omissions and/or additions to the various plumbing installation drawings as the construction progress. One set of the plans as marked shall be submitted to the Consultant after completion of the work.

Before the final payment is made to the Contractor, he shall submit to the Project manager through the

consultant, all As-Built Drawings incorporating the changes made and noted in the marked plans

retained by him. The As-Built Drawing incorporating all the changes made and noted in the marked plans

retained by him. The As-Built Drawings shall be prepared on reproducible form

The Plumbing contractor shall prepare and submit the As-Built Drawings without extra cost to the Project manager.

17.30    Miscellaneous

Throughout the construction period, open ends of all installed pipelines shall be kept closed

by temporary plugs. Drainage lines shall not be used to conduct dirty construction wash- washer,

especially, those with cement, to avoid possible clogging.

A temporary fire protection system at each building shall be provided by the Contractor during the construction period. This shall be of sufficient capacity to put out any fire that may break out at any of the building floors due to construction period. This in addition to temporary fire extinguishers required.

A temporary potable water supply shall be available to construction workers at each building floor as construction work progresses.

A temporary human Excrete Disposal System shall be provided by the Contractor to serve the workers during the construction period.

1. There should have a Specs requirement for Testing and Commissioning/Start-up

HOT WATER SUPPLY SYSTEM:

The hot water system shall be capable of providing hot water at the locations, in the quantities and at the temperatures required and as specified.

- The following central hot water systems shall comply with the relevant provisions of BS 6700:

- direct vented system

- indirect vented system

- direct un-vented system

- indirect un-vented system.

- Pumped circulation shall be provided in all cases where the natural circulating pressure available is insufficient to circulate the water through the system. Immersed rotor (glandless) type circulating pumps shall be used on primary circuits only.  Pumps for boosting or secondary circulation shall be adequately resistant to corrosion. Inlet and outlet connections to a circulating pump shall be fitted with fullway valves.  Circulating pumps shall be quiet in operation. The circulating pump shall be installed in accordance with the manufacturer’s recommendations and space shall be allowed for maintenance and removal.  Circulating pumps shall comply with the relevant provisions of BS 1394.

- Pipes in hot water supply systems that exceed the maximum lengths given below, shall be thermally insulated in accordance with BS 5422.

| Outside diameter of pipes (mm) | Maximum length (m) |
| --- | --- |
| 12 | 20 |
| Over 12 up to and including 22 | 12 |
| Over 22 up to and including 28 | 8 |
| Over 28 | 3 |

- All hot water storage vessels shall be thermally insulated so that heat loss under normal operating conditions shall at no time exceeds 90 W/m2 surface area.

INSTALLATION OF WATER STORAGE TANK:

- Where possible and practicable, tanks shall be positioned in locations where they can be easily accessed for inspection, cleaning and maintenance.

- Tanks positioned outside buildings shall be provided with covers and a suitable shade.

- Each tank shall be fitted with a 25 mm diameter outlet for connection to a drain pipe. The outlet shall be flush with the bottom of the tank. The floor of tank shall be laid at a slight fall towards the outlet. A drain pipe and a stop-tap shall be fitted to the outlet.  The drain pipe shall be run to a point as detailed in the Project Specification or shown on the Project Drawings.

- Every pipe supplying water to a cistern shall be fitted with a float operated valve or some other equally effective device to control the inflow of water and maintain it at the required level.

- Distribution pipes from tanks shall be connected so that the lowest point of the outlet is not less than 50 mm above the bottom of the tank.

- Connections to distribution pipes feeding hot water apparatus shall be set at a level of at least 25mm above connectors to pipes feeding cold water outlets.

- Hot Water Storage Tank:

Hot water storage tanks shall be constructed in accordance the relevant provisions of BS 843 and the following:

    - galvanised steel tanks shall comply with the relevant provisions of BS 417: Part 2 of BS 1565

    - copper tanks shall comply with the relevant provisions of BS 699, BS 1566: Part 1,BS 1566: Parts 2 or BS 3198.

    - cast iron tanks shall comply with the relevant provisions of BS 1563

    - pressed steel sectional tanks shall comply with the relevant provisions of BS 1564.

A cistern type storage water heater incorporating a cold water feed cistern shall be so located that the water heater base is higher than the level of the highest outlet to be served and gives adequate flow at the outlets.

Unless otherwise stated, the temperature of the stored water shall never exceed 65C.

Every vessel shall be fitted with a thermostat acting on the heat input and in addition, every hot water storage vessel of capacity greater than 150 litres shall be fitted with an automatic control capable of stopping and starting the heat input to the stored water at pre-set times. A pressure relief valve shall be incorporated into the system, be mounted on the top of the tank and be vented to a suitable position.

# DISINFECTION

- All hot water systems and cold water systems installed shall be disinfected before being taken into use. For installation with more than one cistern, all cisterns shall be cleaned and chlorinated simultaneously as described below.

- All visible dirt and debris shall be removed from the cistern. Then the cistern and distributing  pipe work shall be filled with clean water and then drained until empty of all water.  The cistern shall be filled again and the supply closed.

- A measured quantity of sodium hypochlorite solution of known strength shall be added to the water in the cistern to give a free residual chlorine concentration of 50 mg/l in the water.

- The cistern shall be left to stand for 1 hour. Then each draw-off fitting shall be successively opened working progressively away from the cistern.  Each tap or draw-off fitting shall be closed when the water discharged begins to smell of chlorine. The cistern shall not be allowed to become empty during the operation; if necessary it shall be refilled and chlorinated as detailed above.  Should refilling be necessary, the cistern and pipes shall be left for a further hour before continuing the disinfection procedure.

- The tap furthest from the cistern shall be opened and the level of free residual chlorine in the water discharged from the tap shall be measured.  If the concentration of free residual chlorine is less than 30 mg/l the disinfecting process shall be repeated.

- Finally, the cistern and pipes shall remain charged with chlorinated water for at least 16 hours and then thoroughly flushed out with clean water until the chlorine concentration at the taps is no greater than that present in the clean water from the supply main.

- All potable water pipes, fittings, valves, meters and appurtenances shall be disinfected by the Contractor, as specified herein, unless otherwise directed by the Engineer. All water and chlorine required for disinfection of pipelines shall be provided by the Contractor at his own expense. Bacteriological testing will be performed by an approved laboratory. The attention of the Contractor is directed to the requirements of these specifications whereby he is responsible for preventing the entry of foreign material of any kind into the pipework. The Contractor shall take extreme care to keep the interior of the pipework free of direct and other foreign material. If in the opinion of the Engineer, dirt or other foreign material, which will not be removed by flushing, enters the pipework then the Contractor shall clean and swab the interior of the pipework with a five percent sodium hypochlorite disinfecting solution to the satisfaction of the Engineer.

- After testing, and immediately before commissioning, all pipelines shall be washed out and disinfected as follows:

  - All mains shall be flushed out with clean water until there is no evidence of foreign          matter or color in the waste flushing water

  - A stock disinfecting solution shall be prepared by mixing, for about 5 minutes, in a clean container, sodium hypochlorite solution (15 percent available chlorine) and distilled water in the proportion of 0.8 litres to 1000 litres water by volume. Stock solutions shall be made up fresh daily;

  - The main, to be disinfected, shall be filled with potable water at the same time as the stock solution is added through a convenient air valve in such quantities (to be determined by the Contractor and approved by the Engineer) as will result in a final solution containing 50 mg/l free chlorine. Care shall be taken to ensure that the stock solution is added at a constant rate, commencing when water is fed into the main and ending as soon as the main is full;

  - Every main charged with disinfecting solution shall stand for 24 hours, after which a sample shall be taken at a washout valve by the Contractor in the presence of the Engineer, from whom the sampling bottle shall be obtained. If the sample does not show at least 2 mg/l free chlorine, disinfection shall be repeated. If the sample is satisfactory the main shall be emptied, flushed out and filled with treated water and allowed to stand for 1 hour;

  - Two further samples shall then be taken as before, one for a further determination of free chlorine and the other, in a sterilized bottle, for bacteriological analysis. If the free chlorine determination shows more than 4 mg/l free chlorine the main shall be flushed out again. If the bacteriological analysis is unsatisfactory disinfection and sampling shall be repeated until satisfactory results are obtained before the main is commissioned;

  - The Contractor shall provide all equipment, materials and testing apparatus, etc., as may be necessary for the effective disinfection of all pipelines;

  - Water used for disinfection may be re-used in an adjacent section if the level of free chlorine is again brought to the level specified

18. ELECTRICAL INSTALLATIONS

18.1      General

18.1.1   The work shall be carried out strictly in accordance with the standard specifications and shall

also conform to the requirements of Electricity Rules in force in Male’, Republic of Maldives

18.1.2   All materials to  be  used in the Works shall be of standard make and shall bear the certification marks of local authorities. All materials shall be approved by the Consultant before use in the Works.

18.1.3   Earthing shall invariably be done in the presence of the Consultant or his representative.

18.1.4   All the conduits shall be continuously earthed. Check nuts shall be provided at the point where the conduct enter the I.C. box and junction box.

18.1.5   The Contractor shall arrange for the inspection of all Medium Pressure Installation by the Electrical inspector of the local electric supply authority from where the  electricity connections has to be obtained, and see that they are passed by him.

18.1.6   The Contractor shall be responsible for all necessary permits, approvals, fees, deposits etc., required to complete the Electrical works in accordance with the Contract.

18.1.7   Scope of work

18.1.7.1              The work consist of furnishing all tools, plants, labour, materials  and equipment and performing the internal electrical Works comprising of:

(a) Light and power wiring

(b) Fans and fixtures (c) Wires and Cables (d) Telephone System

(e) Sub- Station Equipments: (f) Distribution Fusegear

(g) Earthing System

(h) Lightening Protection System

(i)  Fire Alarm System

(j) Air Conditioning System

(k) Computer Network Cabling outlet work

18.1.8   Prequalification

18.1.8.1              The Electrification Work shall be carried out only by a licensed contractor authorized to under take such work under the Utility Regulatory Authority

18.1.9   Qualification

18.1.9.1              A licensed Electrical Contractors should have the following qualifications:

(a)  Must have in his employment a competent Electrical Engineer registered with Utility Regulatory Authority

(b) Must have in its employment an Electrical Consultant having certificate of competency who will exclusively supervise this work.

(c)  Must have necessary tools, plant and instruments.

(d) Must have adequate experience of similar works.

(e)  If a contractor does not posses the above qualifications he shall be allowed

to sublet the Work to a competent Sub-Contractor provided an application for his prequalification is made to the engineer for his approval. Decision of the Engineer in this case shall be binding on the Contractor.

18.1.10 Rules and Regulations

18.1.10.1            The installation in general shall be carried out in conformity with  the Electricity Rules, 1937 (UK), and the latest edition of the Regulations for the Electrical Equipment of Buildings issued by the Institution of Electrical Engineers, London (I.E.). However, in  case of  conflict between   these Specifications and the I.E. Regulations, these Specifications shall be followed.

18.1.11 Standards

18.1.11.1            The latest relevant British Specifications, and I.E. recommendations shall be applicable and be followed for the equipment specified herein.

18.1.12 Climatic Conditions

18.1.12.1            All equipment supplied shall withstand, without developing any detect, the following climatic conditions:-

Maximum Ambient Temperature              =            113° F or 45° C

| Minimum Ambient Temperature |  | = | 28° F or - 2.2° C |
| --- | --- | --- | --- |
| Maximum Humidity | = | 98% |  |

18.1.13 Specifications

The Contractor shall furnish all material and equipment at site, confirming fully to  the specifications given herein and to the accepted standards, the Institution of Electrical Engineers and the Maldives Energy Resource Unit.

It is not the intent of these Specifications to include all details of design and construction of various material and equipment to be supplied under this contract.

The Contractor shall supply and install all material and equipment specified herein and also all installation and small material such as  nuts, bolts, washers, shims angles, leveling material, insulation, tape, solder , etc. and all such required for complete installation as intended by the Specifications.

The contractor shall provide for all the required technical and non - technical personnel, skilled and non - skilled labour, construction equipment, transportation etc., as required for the completion of Work in strict accordance the Technical Specifications laid herein-after.

All material and equipment supplied by the Contractor shall be new and in all  respects conforming to the high standard of engineering design and workmanship.

All material and equipment which have to be supplied and installed by the Contractor shall be  passed/approved by the Consultant; even if the same is exactly in accordance with the Bill of Quantities and Drawings.

18.1.14 Submittal

18.1.14.1            The Contractor, after the award of work, shall submit for approval of the Consultant all drawings and cuts of equipment, appliances, fixtures

and accessories. Cuts, catalogues and drawings shall be clearly marked to indicate, the items furnished.

18.1.15 Approval of Drawings and Data

18.1.15.1            The Contractor shall provide detailed electrical drawings, wire diagrams, etc. for all electrical switchgear, fusegear and all other systems etc. for the Consultant to review and approval. Three sets of equipment drawings shall be provided for obtaining approval.

18.1.16 Drawings & Data

18.1.16.1            Three sets of drawings and data for each equipment shall be furnished by the Contractor for the Consultant approval before commencement of work. The drawings to be supplied by the Contractor shall be as follows:-

Electrical Drawings showing:- (a) Single-Line diagram

(b) Detailed wiring diagram

(c) All interconnections

(d) Relays, their locations, and internal wiring diagrams

(e) Other electrical devices including meters instruments and their wiring

diagram

18.1.17 Shop Drawings

18.1.17.1            The design drawings do not  show conduit routes and depict only the position of various fixtures and outlets. All the planning for the conduit routes shall be carries out, well in advance of the actual execution of work,  by  the Contractor to the satisfaction of the Consultant. For this purpose  the Contractor shall prepare shop drawings and obtain prior approval of the Consultant. There prints of each shop drawings shall be submitted for obtaining approval. work.

No piece of work shall be allowed to be executed at site without the availability of these approved shop drawings. These shop drawings shall clearly depict the load balancing chart of each Distribution Board.

Time required for the preparation and approval of shop drawings shall be considered to have been included in the total time allowed for the completion of the work.

18.1.18 Spare Parts list

18.1.18.1            A  list  of  spare  parts  required  for  the  one  year’s  operation  of  each equipment where deemed necessary together with unit price of each part, shall be supplied by the contractor.

18.1.19 Guarantee

The Contractor shall furnish written guarantee in triplicate of the manufacturer for successful performance of each equipment. Such guarantee shall be for replacement which may be found defective in material or workmanship.

The guarantee shall cover a minimum period of 12 months effective from the date  of completion certificate.

18.1.20 As-Built Drawings

The Contractor shall, during the progress of work keep a careful record of all changes  and revisions where the actual installation differs from that shown on shop drawings. These changes and revisions shall be accurately carried out on the shop drawings and submitted to the Consultant for approval. After approval these drawings shall become the property of the Project manager. These updated and approved shop drawings depicting clearly all changes and revisions made on site shall be called As-Built Drawings.

18.1.21 Test Reports

18.1.21.1         The Contractor shall be responsible for the submitting the  test reports/certificates and get the installation inspected passed by the Utility Regulatory Authority

18.2      Conduit And Conduit Accessories

18.2.1   Conduit Pipe

18.2.1.1              The conduit for the wiring of lights, socket outlets and other systems shall be made of PVC confirming to BSS 3505/1968 Class-D.

The conduit shall have following wall thickness and standard weights:

| Pipe Size | Wt/100Rft. | Wall thickness |
| --- | --- | --- |
| 20mm dia | 3.4 Kg | 0.04 to 0.05 |
| 25mm dia | 4.5 Kg | 0.045 to 0.055 |

18.2.1.2              Steel  conduit  shall  conform  to  BSS  31/latest.  The  conduit  shall  be enameled with good quality non- cracking and non-flaking black paint.

18.2.1.3              The  wires  running  throughout the  ceiling  and  walls  should  be  inside hard conduit.

18.2.2   Conduit Accessories

The use of factory made round PVC junction boxes shall be used and should have nipples to receive PVC pipe with force fit, shall be used for ceiling outlets. The wall type junction box shall also be PVC.

Each junction box shall be provided with one piece cover which shall be fitted on the box with screws.

18.2.2.3               Conduit accessories such as switch boxes, socket outlet boxes, pull boxes and inspection boxes shall be made of PVC having dust tight covers. All boxes shall have required number of conduit entry holes. All the rectangular or  square shaped boxes shall have nipples to receive PVC conduit force fit.

Manufactured smooth bends shall be used where conduit changes direction. Bending of Conduit by heating or otherwise shall be allowed only  at  special  situations with the permission of the Consultant. Use of sharp 90 degree bends and tees is prohibited.

Bends shall have enlarged ends to receive the conduit without any reduction in the internal diameter of the PVC pipe.

18.2.2.5              All accessories e.g. boxes, coupling, bends, solid plugs, bushes, reducers, checknuts etc. shall be equal in quality to the specified conduit.

18.2.2.6              The drawings do not show conduit routes and all the planning for arranging conduit routes shall be carried out by the Contractor to the satisfaction of the Consultant.

18.2.2.7              The entire conduit system shall be essentially completed before the wiring pulling is taken in hand. Each conduit run shall be tested for continuity and obstructions. All obstructions shall be cleared in an approved manner. Water and moisture that has entered any section of the conduit installation must be dried with suitable swabs to the satisfaction of the Consultant.

18.2.2.8              Adequate expansion joints shall be provided in all conduit runs passing across the expansion joints in the concrete slab of the buildings.

18.2.2.9              All the free ends of conduit shall be solidly plugged till such time as final and proper terminations are made.

18.3      Wires, Cables And Cords

18.3.1   Wires & Cords

The wires & cords for the conduit wiring shall be single core, made of stranded copper conductors, PVC insulated, tested to B.S. 6004, 1975. The voltage grade shall be 300/500 volts or 450/750 V unless otherwise specified on Drawings and Bills of Quantities.

All the wire and cables shall be of the approved standard of Utility Regulatory Authority

(a) For light or fan point wiring with 1.5 mm square or as specified in the BOQ. (b) For light circuit wiring with 1.5 mm square or as specified in the BOQ.

(c) For power plug 15A wiring with 4mm square or as specified in the

BOQ. Wires used must be 2.5sqmm(7/0.67mm) unicable or a wire of the same standard.

18.3.2   Installation Instructions

18.3.2.1              All wiring shall be continuous between terminations and use of connectors or joints is not be allowed. Spur and tee connections are strictly prohibited.

18.3.2.2              Manufacturers  recommended  lubricant  shall  be  allowed  to  facilitate pulling of wires. Use of any kind of oil and soap is prohibited.

18.4      Wiring Accessories

18.4.1   Switches

8.4.1.1 Indoor switches controlling lights and fans shall be single pole, 5A, one or two way, suitable for 250V,50 Hz. The body of the switches shall be  made  of moulded plastic, one, two, three or four gang with integral built in moulded plastic face plate.

8.4.1.2 Weatherproof switches shall conform to B.S. standard.

18.4.2   Switch Socket Outlet Units

18.4.2.1              Switch & socket units shall be single, pole, 3 pin rated 5A. 15A or 20A, 250V,

50 Hz. These shall be moulded plastic type with white integral built-in face plate. Each socket shall have its control switch by the side of it on a common face plate. Thus the complete unit specified in BOQ shall be as switch and a socket outlet unit.

18.4.2.2                        All the  circuits, sockets, switches, ELCB and MCCB must use Legrand or products in equivalent standards to this.

18.4.2.3                     Waterproof sockets must be used for areas which come in contact with water or water motors.

18.4.2.4                    All the lights and sockets inside and outside the building must follow the Maldives Electricity Bureau regulations while placing the circuit. (13Ampere with 2 socket- 1 circuit, 15Ampere with 1 socket and one circuit, and for six fans or 6 lights, there must be one circuit placed)

18.4.2.5                      Lights should have a circuit of 6 Amperes, and normal sockets should have a Socket of 10 Amperes. Air conditioner and high voltage appliances must have a circuit of 15 Amperes.

18.4.3   Fans

18.4.3.1               All fans shall be capacitor type Deluxe models or equivalent and suitable for operation on 200/220 volts, 50 Hz, A.C Supply. All ceilings fans shall have five speed dimmers. The air displacement shall be 10,000 c.f.m for 48” (1219 mm) Sweep and 12,000 c.f.m. for 56” (1423 mm) Sweep at maximum speed. The fan motor shall be capacitor type and bearings shall be groove type to  give noiseless and quiet operation. The noise level relative to a frequency of range 1000 Hz should be within the limits of +3 dB.

18.4.3.1              Ceiling fans used must be at least 1400mm in diameter and from Usha brand or equivalent to this

18.4.3.2              Exhaust fans used must be plastic

18.4.4   Dimmer

18.4.4.1              The dimmer shall be recessed type as required and shall be approved by

the Consultant.

18.4.5   Fan Hook

The fan hook shall be made of 12 dia mild 5/5 steel rod bent to shape of approved design. It should be in the form of a loop about 3-1/4” (87.5 mm) long and about 2” (50 mm) wide. The rod shall be bend to have at least 8” (200 mm) extension on both sides for tieing to the reinforcement steel of the slab. All ceiling fan shall be of one make only.

The fan hook shall be installed in the RCC slab of the ceiling at the time of pouring concrete.

18.5      Light Fixtures

18.5.1   General

The description of light fixtures is given in the Bills of Quantities, and stated on the

Drawings, and all relevant material are described in this Section.

The determination of quality is based on certified photometric data covering the coefficient of utilization, light distribution curves, construction material, shape, finish, operation, etc.

18.5.1.3              The Contractor shall submit samples of each and every lighting fixture specified for approval of the Consultant.

18.5.1.4              The type of fixtures with manufacturer catalogue reference are given in

Bill of Quantities.

18.5.1.5              The  lighting  fixtures  shall  be  manufactured  by  M/s.  Philips,  M/s.RZB Lighting, M/s Thorn or equivalent as approved by Consultant.

18.5.2   Incandescent Light Fixture

The glass globes/ shades/ diffusers of the incandescent light fixtures shall be first class quality glass free from any  air bubbles or  voids. The glass shall generally be of opal white colour unless otherwise specified. The shape of the glass may be spherical, hemispherical, flattened bottom or tablet shaped as required.

Surface mounted fixture shall have stove enamelled sheet steel body. It may also be satin brass or aluminium anodised finish as required. The fixing holes shall match the outlet box. Wall bracket light fixtures shall have back plates with matching holes of  the outlet box and decorative finish as required.

All the lighting fixtures shall be suitable for local climatic conditions.

18.5.2   Fluorescent Light Fixture

All the light fixtures shall have lamps and electronic ballasts of the wattage specified.

The fluorescent lamp shall be either 2 ft - 18 watts or 4 - 35 watts and the colour shall generally be day light, cool day light in the order of preference or as mentioned specifically.

The fluorescent lamps shall be Philips to BSS 1853 but having a minimum useful life of 5000 hours. The new generation of 26mm dia 18 watts and 36 watts  energy efficient lamps shall be preferred.

The ballast shall be totally enclosed electronic type suitable for operation on 220 V, 50

Hz, single phase supply, a wiring diagram, wattage, voltage and current ratings shall be printed on the body of the ballasts. The power loss shall not   more than 10 watts for 36 watts ballast. The ballast shall be noiseless in operation without any whistling sound.

The manufacture shall be called upon to guarantee a trouble free life of 3 years, effective from the date of completion certificate.

18.5.2.5              The starters shall have radio-interference suppressers.

18.5.2.6              The   internal   wiring   of   the   light   fixtures   shall   be   carried   out   at manufacturers factory with heat resistance wires of size not less than 1.5 mm square.

18.5.2.7              The louvers of light fixtures shall be made of anodized aluminium and/or moulded plastic. The diffusers shall be made of acrylic perspex.

18.5.2.8              All the lighting fixtures shall be suitable for local climatic conditions.

18.5.3   Installation Instructions

18.5.3.1            The light fitting shall be installed according to  manufacturers recommendations or as approved by the Consultant.

18.5.3.2              Flexible connecting wires from outlet box to the fixture shall be provided by the contractor; connector made of porcelain or thermoplastic material shall be provided and installed in the outlet boxes for connecting flexible wires to the point wires.

18.5.3.3              Outlet boxes or any openings in the ceilings and walls shall be covered with appropriately fabricated accessories to provide an architectural entity to conceal them.

18.5.3.4             All the lights outside the building and in the garden should be in accordance with the drawings with photocell switches placed.

18.5.3.5             Each light should be assigned to a different switch. Each switch should light up one light only.

18.5.4   Main L.T. Switchboard

The L.T. switchboard shall be indoor type, free standing, free supporting, floor mounted, totally enclosed, sheet cald, dust and suitable for operation on 3 phase 4 wire system, 415 v , 50 Hz, AC supply .

The board shall be suitable for installation back to the wall and capable of front attendance.

The switch board shall be designed to suit service conditions and ensure security and safety during operation , inspection , operation , cleaning and maintenance.

The  switch board shall be designed and tested to  IEC  recommendations. Each panel shall withstand strain of 2000 volts insulation level for one minute power frequency test.

18.5.4.4               The  L.T.  switch  board     shall  consist  of  the following: Maldives Energy Resource Unit incoming

panel.

KWh meters ( To be approved and checked by MEB ) Out going distribution feeders.

18.5.5   Distribution Feeder Panel

18.5.5.1Single line diagram of the L.T. switch board shall be approved by the consultant and Maldives Electricity Bureau before placing order for the switch board.

18.5.6   Earthing

18.5.6.1              The switchboard shall be effectively earth by means of a copper strip of 25mm x 3mm (1” x 1/8”) cross -section bolted to connections near the bottom of the switchboard.

18.5.7   Accessories

18.5.7.1              Designations labels, lifting lugs , foundation bolts, interconnecting nuts blots, and washers, thimbles, lugs, levelling shims cable glands and/or cable  end box for all the sizes of incoming and outgoing cable shall be supplied with the switchboard.

18.6      Testing

The following tests shall be conducted on each completed switchboard.

18.6.1.1              Type Tests

(a) Temperature rise test

(b) Mechanical    endurance

test            Making/Breaking

Capacity test

18.6.1.2              Routing    Test High	Voltage test

18.6.2 The Switchboard shall be tested to British/Electricity Council Standard 41-5. Preference shall however, be given to Switchboards fabricated from all components manufactured by only one manufacturer.

18.7 Installation Instruction

All labour, equipments, tools and plants required to complete the installation shall be provided by the contractor. The Switchboard shall be fixed firmly on the floor in perfect line, plumb and level position.

The  electrician  operating  must  be  someone  who  has  permission  from  the  Maldives  Energy

Authority Under no circumstances should someone without permission carry put the work.

After electrical connections are placed and wire testing is done, the STELCO certificate copy must be submitted to the consultant and client.

Before materials are bought for electrical wiring, it should be presented to the client and  their approval must be obtained

All incoming and outgoing cable connections shall be made from the bottom including  Earth connections.

18.8        Distribution Board

18.8.1   The distribution boards shall be either free standing, cubical type or wall mounting type suitable for recessed mounting. Each distribution board (d.b.) shall be tropical in design, fully dust and vermin proof and liquid repellent.

18.8.2   Distribution box(DB) used must be wall embedded. Under no circumstances should any other box be used

18.8.3   After the electrical wiring has been completed, the connection shall be taken from the main switch board to the distribution board. The thickness of the cable shall be approved by the consultant. Hence, the scope of work includes the installation of DB cables, burying of cables and other respective tasks should be carried out.

18.9      Telephone System

18.9.1 General

The design drawings do not show conduit routes and depict only the position of various telephone outlets. All the planning for the conduit routes shall be carries out, well in advance of the actual execution of work, by the Contractor to the satisfaction of the Consultant. For this purpose, the Contractor shall prepare shop drawings and obtain prior approval of the Consultant. Three prints of each shop drawings shall be submitted for obtaining approval before commencement of work.

No piece of work shall be allowed to be executed at site without the availability of these approved shops drawings. Time required for the preparation and approval of shop drawings shall be considered to have been included in the total time allowed for the completion of the work.

The contractor shall furnish and install the type of Telephone outlets approved by local telecommunications operator. All the floor mounted telephone boxes shall be concealed in a PVC box with openable cover for easy access.

Both ends of each set of conductors shall be properly identified with durable tags with the same identifications of both ends, at the outlet and the telephone terminal cabinets to facilitate the installations of the telephone instrument in the future and for trouble shouting purposes. Cable used shall be twisted and shielded 3 cables in the office area and the rest as shown in the drawing.

19.HVAC SYSTEM

19.1. General

The scope of the project includes the Design check, the Supply, Installation and commissioning of Air Conditioning System (VRV/VRF/ Inverter Units) and mechanical ventilation system for the specified project & as shown on drawings

19.2. Basis of Design

Heat load calculation shall be carried out to work out TR/KW capacities of units and nominal capacity of units shall be based on outdoor conditions being 35.0 Deg C db / 32 Deg C wb

The capacity of the unit shall be rated in accordance with ARI Standard 210 and shall not be less than the minimum required when operating under the specified conditions. The capacity shall have to be suitably derated to take into account any differences in level between the evaporator blower unit and the remote condensing unit and also the length of refrigerant piping involved.

19.3. Regulations and Shop Drawings

All work shall be carried out in keeping with the rules and regulations of the relevant local authorities and will comply with the latest codes of practice in this field. The minimum capacities, drawings and bills of quantities will serve only as a guide line. The contractor will be totally responsible for the ability of the system to achieve the conditions set out in these specifications, and as such will have to provide shop drawings, for the approval of the Engineer. The Contractor shall submit shop drawing for the entire installation including installation details for all items required or asked for approval of the Consultant. Approved by the Consultant of shop drawing for any material, apparatus, devices and layout, shall not relieve the Contractor from the responsibility of furnishing same of proper dimension, size, quantity and all performance characteristic to efficiently perform the requirements and intent of the Contract Documents. Such approval shall not relieve the Contractor from responsibility for errors of any sort in the shop drawing.

If the shop drawings deviate from the contract Documents the Contractor shall advise the Consultants of the deviations in writing accompanying the shop drawings including the reasons for the deviations. At the start of the Project the Contractor shall periodically and

thereafter submit to the Consultants list of all shop drawings which will be submitted in the course of the project. The list shall show the disposition of each item including date of submission approval etc. The list shall be kept up to date through the entire course of construction.

19.4. HVAC System

The Air conditioning system shall be a VRV/VRF /inverter system. It shall be composed of Wall mounted/Ceiling concealed/4 - way cassette type indoor units with a distributed refrigerant cycle, electrical components and enclosing cabinets. Ventilation system shall include axial fan, centrifugal fan, cabinet type fan etc, All accessories and appurtenances, spare parts, associated civil and external works required to complete, commission and maintain the systems to the fullest satisfaction of the company with all field and factory testing and inspections as required. Both indoor and outdoor units shall be properly assembled, internally piped, wired and completely suitable in the Maldives climate condition.

19.5. Air Conditioning System (VRV/VRF/INVERTER)

19.5.1. Air cooled- Condensing/compressor unit (Outdoor unit)

The VRV/VRF/Inverter outdoor unit shall be energy efficient and integrally built multiple type light weight with weatherproof construction suitable for balcony/roof top installation. Air cooled VRF / VRV system working in R410A / R -407C or equivalent refrigerant. The system shall be suitable to operate on 3 phase, 380-415 V, 50Hz AC power supply & shall comprises with multiple no’s of inverter, digital scroll/screw compressors, air cooled condenser fan with motor, microprocessor control panel, starter controls for all scroll/screw compressors and condenser fan motors along with internal control and power wiring, cooling coil with internally interconnected refrigerant pipes, charging port and all other required accessories, & hardware’s. The entire unit shall be with weather resistant powder coating paint for withstanding all ambient conditions for continuous outdoor operation.

19.5.2. Concealed type DX Air handling unit

Air Handling Units complete with, double skin sandwich panel with injected Puf foam minimum density 40-50 kg/cu.m, 40mm thick Panel, 0.6/0.8 GI inner skin & Pre-coated GI outer skin with thermal break aluminium extruded profile, Air Handling Units complete with DX coil, backward/forward curve belt driven/plug type fan, 18G SS drains pan, G4 prefilters & F8 fine filter. All units shall be suitable for 415+/-10% volts and required lengths of wiring as per site requirement to be included.

19.5.3. Wall Mounted

The wall mounted unit suitable for wall hang and comprising of DX Cooling coils, blower, electric motor, insulated sandwiched drain Tray, junction box for electrical connections, HDPE washable filter. wall mounted wireless remote control.

19.5.4. Cassette Unit

The cassette unit suitable for ceiling suspended and comprising of fan, motors, filters, built-in pump, drain pan, cooling coil, supply and return air grilles, fresh air provision, controls and all associated accessories.

19.5.5. Controls

Entire system shall have Microprocessor Controls. Microprocessor should have Auto Check Function to indicate Piping and cabling errors. Microprocessor should control speed or switching or by pass of Compressors, Condensers, Fans, and liquid management Functions along with the system for proper oil return and stable and safe operation of system.

19.6. Refrigerant and Condensate Pipework

The whole of the condensate and refrigeration pipe lines including gas suction line, all fittings, valve and strainer bodies, flanges, etc., on the refrigeration equipment’s shall be insulated with 25mm thick insulation. Thermal conductivity shall not exceed 0.0039 W/M degrees C for a mean temperature of 24 degrees C. All surfaces over which the insulation is to be applied shall be dry and grease free. Exposed pipe work will be provided with two layers of 25mm thick insulation. Suitable weather proof paint as per manufacturer’s recommendation shall be applied.

19.6.1. Pipe installation

• All pipework’s shall be so installed and supported so that it is free from excessive stressing due to its own weight and its contents, equipment vibration or movement, and thermal movement.

• Care shall be taken to achieve a neat installed appearance. All pipes and fittings shall be cleaned before erection and free from scales, burrs, sand and other foreign matters.

• Sufficient unions or flange joints shall be allowed for satisfactory removal and reassembly of equipment, valves fittings for inspection or repair.

• All pipes shall be laid to correct fall for venting and drainage. All high sections of pipework where air may collect shall be provided with an automatic air vent and drain provided at low point of horizontal run.

• All open ends of pipework during erection shall be blanked of by a metal or plastic cap.

• All refrigerant and condensate drain pipes shall be coordinated and run-in trucking or pipe tray.

• Maximum pipe length shall be as per equipment manufacturer recommendations

• Aluminium cladding over the insulation for the exposed Pipe work on roof.

19.7. Duct work and Insulation

The Contractor shall provide and install the galvanized sheet steel ductwork, dampers, make all ductwork, unless specifically noted otherwise, of galvanized sheet steel conforming to BS 2989 or ASTM A653A, 653M, G90 (Z275). The galvanizing shall be carefully done and the sheets shall be of such quality that they may be bent flat on themselves with no fracture to the coating or the base metal. Construction and jointing of ductwork & fittings shall be in accordance with the latest edition of SMACNA Low Pressure Standards. The Contractor shall in all cases ensure that sufficient bracing is provided to prevent sagging, drumming or vibration of ductwork. Volume dampers shall be installed at branch connections to main ducts regardless whether they are shown on the drawings or not.

The Contractor shall provide internally insulated ductwork (except Operation theater) of scrim covered mineral wool of 96 kg/cu.m. density or fibreglass 48 kg/cu.m. density insulation of specified thickness to Engineer's approval. The lining and facing material shall be suitable for velocities up to 12 m/s without erosion of the lining and to the Engineer's approval. Internal insulation shall be sheathed with fire resistant insulation with perforated galvanized iron sheets metal of free area not less than 30% with minimum average noise reduction co efficient of 0.70 between 400 and 2000 Hz to the approval of the Engineer.

19.8. Air Diffusers/Registers/Grilles/Louvers

All diffusers, grilles, louver and registers shall be supplied completely extruded aluminum factory powder coated. Finish colour shall be to the approval of the Interior Designer. All supply grilles and diffusers will have opposed blade balancing dampers. All will have foam rubber sealing band around the edge to seal to the structure

All diffusers shall be appropriately selected to meet the noise criteria of the space they are serving. Generally, two requirements are to be fulfilled:

• if the diffusers are spaced far apart, each diffuser shall be selected with acoustic performance to meet the noise criteria of the space.

• if the diffusers are spaced close to each other, group acoustic performance shall be considered for the selection in order to meet the criteria of the space.

All diffusers and registers shall be selected to meet (a) with acoustic performance at least 3dB lower than the criteria of the space they are serving, and 5dB to meet (b)

19.9. Mechanical Fans

19.9.1. Duct In Line Fans

In line duct fans, shall have non-overloading characteristics to suit the performance duty specified. In line duct fans, shall be of direct driven type. The fan blades shall be aerodynamically designed, backward/forward curved, constructed of aluminum plate and combing the impeller with the rotor of the external rotor motor. Motors and impeller shall be factory matched and statically and dynamically balanced. Motors shall be suitable for operating in atmosphere of up to 95% and up to 40 deg. C. The fan housing or casing shall be constructed in heavy gauge (1.4 mm minimum) mild steel with paint finish or epoxy powder coating and stored dried, and flanged at both ends for bolting direct to connection ductwork.

19.9.2. Toilet Exhaust Fan

The fan shall be suitable for wall mounted/ceiling mounting and comprising of Automatic reverse flow shutter, condenser motor with thermal cut-off. The fan shall be energy efficient with low noise.

19.10. Site Testing and Commissioning

Tenderer shall submit with the tender, a complete proposal with time schedule for testing and commissioning of the air conditioning & ventilation system. The program shall include a trial 77 operation of all main equipment with any necessary adjustments to ensure that the system is working correctly. The Contractor shall provide all instruments and equipment together with commissioning engineers and adequate assistance for carrying out the commissioning and testing activity which shall be done in accordance with the recommendations of relevant Standards. If any portion of the works fails to pass the tests, the Contractor shall, at his own expense carry out such alterations or replacements as are required to the satisfaction of the Engineer. The Contractor shall provide commissioning spares at his own expense.

20.CCTV SPECIFICATION

20.1. System Design

The system shall be designed taking into account following specification, tender drawing and the client requirement by specialist contractor with experience in the trade to provide a high quality uninterrupted CCTV images at each and every viewing points.

The CCTV system shall be capable to handle 512 IP camera streams in 25 frames per second in D1 resolution.  IT should be able to handle 1.2 Gbps data throughput. The CCTV system consist of indoor network fixed dome cameras, Outdoor network bullet cameras, pan tilt zoom cameras positioned in the hospital premises. All the cameras streams video to four Network Video Recorders installed in server room. The CCTV control room in ground floor is equipped with dedicated video decoders, monitors and a CCTV network keyboard. The viewing channel changing on monitor, split setup changes & PTZ controlling could be conducted via this keyboard. Any camera shall be viewed in any monitor via keyboard.

The video client software shall be installed in EACS PC in ground floor CCTV room (check EACS client PC configurations, it should match CCTV client software requirements (otherwise provide a CCTV client PC). The image play back & backup shall be conducted via this client PC. The video management server shall manage all user authentication, and video streams with e-map facility.

3m extra cable provision shall be kept inside ceiling for small scale changes. The system should view at highest resolution when single camera is viewed on a monitor. The lower resolution video stream shall be automatically set when multiple cameras are viewed on a monitor. Simultaneous ten client users could be view images simultaneously over the network.

Installer shall provide 30 days of recorded images under D1 resolution, 8 IPS in continuous recording of all cameras. The system shall have provision for expanding NVR storage up to 144TB for each NVR using external storage devices. The NVR should also have provision for RAID levels 0,1,5,6. The system also should have provision for N+1 redundancy of NVRs.

Exact location of cameras shall be proposed by architect. The positions shown are suggested locations in public areas as shown in the drawings.

20.2. System Performance Criteria

The system performance criteria shall follow international agreed standards and local regulations.  They shall be, but not be limited, to the following:

      - Live video clarity in real time

      - Achieving record duration

      - PTZ tour programming and tour function

      - Image record water mark testing

      - Play back image via calendrer

20.3. General Requirement of CCTV Equipment

All equipment to be supplied under this specification shall be new and the current model of a standard product of a Manufacturer of record.  A Manufacturer of record shall be defined as a company whose main occupation is the manufacture for sale of the items of equipment supplied.

      - Maintains a factory production line for the item submitted

      - Maintains a stock of replacement parts for the item submitted.

      - Maintains engineering drawings, specifications, and operating manuals and for the items submitted.

      - Has published and distributed descriptive literature and equipment specifications on the items of equipment submitted at least 30 days prior to the tender issue.

Specifications of equipment as set forth in this specification are minimum requirements, unless otherwise stated, and shall not be construed as limiting the overall quality, quantity or performance characteristics of items furnished in the CCTV system.  When the Contractor furnishes an item of equipment for which there is a specification contained herein, the item of equipment shall meet or exceed the specification for that item of equipment.

The total CCTV system shall be installed so that the combination of equipment actually employed does not produce any undesirable visual or aural effects such as signal distortions, noise pulses, glitches, hum bars, transients, ghosting, etc.

20.4. Regulations and Code of Practice

It shall be the Contractor’s responsibilities to ensure that the whole CCTV system shall comply with all statutory, regulations and requirements of all authorities having jurisdiction over the work.

20.5. Testing

The Contractor shall make all the necessary setting of the equipment after installation. The gain, IPS, resolution, recording channel frequencies of camera shall be adjusted to suit the usage. All settings shall be clearly marked upon final adjustments.

The contractor shall carry out performance tests in the presence of the Engineer with prior approved test methodology which shall incorporate a spectrum analyser before handling over the system.

20.6. Item Specification

| PROPOSED HITHADOO REGIONAL HOSPITAL |  |  |  |  |
| --- | --- | --- | --- | --- |
| CCTV |  |  |  |  |
| Technical Specifications |  |  |  |  |
| Item Number: 2 . Network Video Recorder |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| System throughput capacity |  | 340 Mbps |  |  |
| Throughput allocation @ D1 resolution in real time | Live Video | 128 channels or better |  |  |
|  | video playback | 20 channels or better |  |  |
|  | video forwarding | 20 channels or better |  |  |
| Network |  | 2 x 1Gbps Ethernet(Dual) |  |  |
| RAID controller |  | SAS 9260 (6Gb/s per port) |  |  |
| Maximum storage support |  | 48TB |  |  |
| Storage |  | 30TB |  |  |
| Expansionable Maximum total storage |  | 144TB |  |  |
| Hardware Redundancy |  | Power supply and fan module redundancy |  |  |
| Video Compression |  | H.264, MPEG4 |  |  |
| Video Resolution |  | 1080P / 720P / Megapixel / D1 / 4CIF / VGA / CIF |  |  |
| Frame Rate |  | 25 fps (PAL) |  |  |
| Recording Mode |  | Time and events, alarm, manual trigger, continuous video |  |  |
| Hard Disk Hot Plug |  | Support |  |  |
| Expansion Interface |  | SAS |  |  |
| RAID Level |  | RAID 0, 1, 5, 6 |  |  |
| Rack Mountable |  | Support |  |  |
| Certification |  | CE, FCC |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 3. Video Management Server |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Live Video Display with Different Layouts |  | Support |  |  |
| Digital Zoom In/Out |  | Support |  |  |
| Instant Playback from live view window |  | Support |  |  |
| Alarm / Event / Status / Log Management |  | Support |  |  |
| Digital Virtual Matrix(Any camera to any monitor) |  | Support |  |  |
| E-map support |  | Support |  |  |
| Record searching by time, camera number, event, devices |  | Support |  |  |
| Archive evidence at local storage / central storage / remote site |  | Support |  |  |
| playback modes |  | 8 / 16 / 32 / 64x |  |  |
| Configurable tours and patrols on workstation monitors or video walls |  | Support |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 4. Network Video Decoder |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Network |  | 1 Gigabit Ethernet |  |  |
| Video Compression |  | H.264, MPEG4 |  |  |
| Display Resolution |  | 1080P / 720P / Megapixel / D1 / 4CIF / VGA / CIF |  |  |
| Video Split |  | Full Screen, 2x2, 3x3, 4x4, 6, 8, 9, 13, 16 split screen |  |  |
| Video Output |  | 4 x HDMI ports to digital display screen |  |  |
| Certification |  | CE, FCC |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 5. Video Mattrix Controller(CCTV Keyboard) |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Joystick |  | 3-axis proportional control |  |  |
| Connection |  | LAN & USB |  |  |
| Password Protection |  | Support |  |  |
| Camera Functions |  | Pan/Tilt/Zoom |  |  |
|  |  | Program and run presets |  |  |
|  |  | Program and run tours |  |  |
| Decoder functions |  | change monitor split matrix |  |  |
|  |  | Assign any camera to any split screen slot |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 6. LED Monitor |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Video Input interface |  | HDMI |  |  |
| Design |  | Color |  |  |
| Panel type |  | Wall Mount |  |  |
| Resolution |  | 1366 x 768 |  |  |
| Size |  | 24" or better |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 7. Outdoor Network PTZ Camera |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| IP rating |  | IP66 |  |  |
| 360° continuous rotation |  | Support |  |  |
| True Day/Night (TDN) |  | Support |  |  |
| Wide Dynamic Range (WDR) |  | Support |  |  |
| High Light Compensation (HLC) |  | Support |  |  |
| Zoom |  | 37x |  |  |
| Resolution |  | D1 |  |  |
| Presets |  | 50 or better |  |  |
| Tours |  | 4 or better |  |  |
| IR beam |  | 100m |  |  |
| Digital Zoom |  | OFF / ON (X2 ~ X16) |  |  |
| Min. Illumination |  | IR LED ON - 0 Lux IR LED OFF - Color: 0.02 Lux, F1.6 B/W: 0.001 Lux, F1.6 |  |  |
| Focus length |  | f=3.5 - 129.5mm |  |  |
| Iris Control |  | Auto / Manual |  |  |
| Day/Night |  | Auto |  |  |
| Manual Speed |  | 0.1° - 150°/s |  |  |
| Auto Pan |  | Continuous |  |  |
| Dual Streams |  | Support |  |  |
| Network Protocols |  | IPv4, TCP, UDP, HTTP, HTTPS, SMTP, FTP |  |  |
| Frame Rate |  | 1fps - 25fps |  |  |
| Power Supply |  | DC12V |  |  |
| Certificate |  | FCC |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 8. Network IR Bulet camera |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| IP rating |  | IP66 |  |  |
| Power over Ethernet |  | IEEE 802.3af |  |  |
| True Day/Night (TDN) |  | Support |  |  |
| Wide Dynamic Range (WDR) |  | Support |  |  |
| High Light Compensation (HLC) |  | Support |  |  |
| Resolution |  | 1080P (1920 x 1080), |  |  |
| IR beam |  | 30 - 40m |  |  |
| Min. Illumination |  | IR LED ON: 0 LuxIR LED OFF: Color: 0.02 Lux @ F1.4 B/W: 0.005 Lux @ F1.4 |  |  |
| Focus length |  | 2.8 - 12mm |  |  |
| Iris Control |  | DC IRIS |  |  |
| Day/Night |  | Auto |  |  |
| Dual Streams |  | Support |  |  |
| Network Protocols |  | IPv4, TCP, UDP, HTTP, HTTPS, SMTP, FTP |  |  |
| Frame Rate |  | 1fps - 25fps |  |  |
| Certificate |  | FCC |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 9. Network Fixed Dome Camera |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Power over Ethernet |  | IEEE 802.3af |  |  |
| True Day/Night (TDN) |  | Support |  |  |
| Wide Dynamic Range (WDR) |  | Support |  |  |
| Resolution |  | 1280x1024 |  |  |
| IR beam |  | 15m |  |  |
| Min. Illumination |  | Color: 0.2 lux @ F1.2; B/W: 0 lux (IR on) |  |  |
| Focus length |  | 3.3 - 12mm |  |  |
| Iris Control |  | DC IRIS |  |  |
| Dual Streams |  | Support |  |  |
| Network Protocols |  | IPv4, TCP, UDP, HTTP, HTTPS, SMTP, FTP |  |  |
| Frame Rate |  | 1fps - 25fps |  |  |
| Certificate |  | FCC |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 12. Power Over Ethernet lightning arrester |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Power over Ethernet |  | IEEE 802.3af |  |  |
| Connection Method |  | RJ45 In/Out |  |  |
| Data Rate |  | Gigabit Ethernet |  |  |
| Max Continuous Current |  | 1.5 Amps |  |  |
| Protection Modes |  | Line-Ground (All) |  |  |
| Service Voltage |  | 48V |  |  |
| Clamp Voltage |  | 72V |  |  |
| Peak Surge Current |  | 30A/pair |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 13. Rack |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Features |  |  |  |  |
| Type |  | 19" floor standing |  |  |
| Size |  | Suitable to install all CCTV room items inside the rack |  |  |
| Ventilation |  | Suitable for heat dissipation from rack mounted items |  |  |
| Finish |  | heavy gauge steel with baked on paint finish |  |  |
| Security |  | Lockable, Two keys |  |  |
| Free Rack Space |  | 9U |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |

21. PUBLIC ADDRESSING SYSTEM & BACKGROUND MUSIC (PA & BGM) SYSTEM SPECIFICATION

21.1. System Design

The system shall be designed taking into account following specification, tender drawing and the client requirement by specialist contractor with experience in the trade to provide a high-quality audio broadcasting at each and every speaker of the hospital.

The PA & BGM is based on 100V audio system. The all-in-one digital audio unit (Digital Multi-audio Player) will be used as a CD/DVD player, FM tuner and USB loaded MP3 file player. There are four paging consoles in three locations to manage public addressing.

The system is based on IP distributed architecture. The Digital Integrated System Manager manages IP audio streams and it delivers the desired audio channels to Power amplifiers connected to it. The power amplifier will drive speakers connected. One backup power amplifier for each Digital Integrated System Manager is available and it should be automatically taken over function of faulty power amplifier.

The system should capable to switch any audio source to any speaker zones depicted in the schematic diagram. Further the system should allow creating zone groups which consists with multiple physical zones. For an example, there are several waiting areas zones in different floors. The system must be capable to define a global waiting area logical zone and it should be able to call from paging selector. The volume controllers should be overwritten during paging. The zones and logical zone groups could be selected from paging console.

The fire alarm panel should provide three dry contacts. One is to broadcast “Fire Alert Message” the second contact is to broadcast “Fire Evacuation Message”, third is to broadcast “All clear Message”. Predefined zones will receive corresponding messages on activation of dry contact. The volume controllers should be overwritten during message broadcasting.

The power amplifier wattages shall be selected according to the total speaker load it drives. 20% power margin should be kept in every power amplifier. The volume controller’s wattage must be equal or greater than that of the total speaker load it handles. It is PA & BGM installer’s responsibility to cable up to the fire alarm panel for integration.

21.2. System Performance Criteria

The system performance criteria shall follow international agreed standards and local regulations.  They shall be, but not be limited, to the following:

- The required sound pressure level shall be 70 dBA.

- STI shall be greater than 0.45

21.3. General Requirements of PA & BGM Equipment

All equipment to be supplied under this specification shall be new and the current model of a standard product of a Manufacturer of record.  A Manufacturer of record shall be defined as a company whose main occupation is the manufacture for sale of the items of equipment supplied.

- Maintains a factory production line for the item submitted.

- Maintains a stock of replacement parts for the item submitted.

- Maintains engineering drawings, specifications, and operating manuals and for the items submitted.

- Has published and distributed descriptive literature and equipment specifications on the items of equipment submitted at least 30 days prior to the tender issue.

Specifications of equipment as set forth in this specification are minimum requirements, unless otherwise stated, and shall not be construed as limiting the overall quality, quantity or performance characteristics of items furnished in the PA& BGM system.  When the Contractor furnishes an item of equipment for which there is a specification contained herein, the item of equipment shall meet or exceed the specification for that item of equipment.

The total PA & BGM system shall be installed so that the combination of equipment actually employed does not produce any undesirable visual or aural effects such as signal distortions, noise pulses, glitches, hum bars, transients, ghosting, etc.

21.4. Regulations and Code of Practice

It shall be the Contractor’s responsibilities to ensure that the whole PA & BGM system shall comply with all statutory, regulations and requirements of all authorities having jurisdiction over the work.

21.5. Testing

The Contractor shall make all the necessary setting of the equipment after installation. The power tapping of each speaker shall be adjusted to suit the usage. All settings shall be clearly marked upon final adjustments.

The contractor shall carry out performance tests in the presence of the Engineer with prior approved test methodology which shall incorporate a spectrum analyzer before handling over the system.

21.6. Item Specification

| PROPOSED HITHADOO REGIONAL HOSPITAL |  |  |  |  |
| --- | --- | --- | --- | --- |
| MATV |  |  |  |  |
| Technical Specifications |  |  |  |  |
| Item Number: 2 . Digital Integrated System Manager |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Input | Amplifier interfaces | 4 or better |  |  |
| Ethernet interfaces | Ethernet speed | 10 M / 100 M |  |  |
|  | Number of Ethernet interfaces | 4 or better |  |  |
| Output | 100V line dry contacts(Output channels) | 4 or better |  |  |
|  | circuit fault detection function | Available |  |  |
|  | Max. output load | 500W or better |  |  |
|  | Monitoring loudspeaker | Available |  |  |
| Storage space to upload audio files |  | 1 GB or better |  |  |
| Ability to store voice file & play via paging console |  | Available |  |  |
| Ability to store voice file & play via BGM software |  | Available |  |  |
| Ability to play message when trigger input is activaed in designated zones |  | Available |  |  |
| Run designated audio file in predefined recurrent shedule in predefined zones |  | Available |  |  |
| Power supply |  | ~100 - 240 V,50/60 Hz |  |  |
| Operating Temperature |  | -10 °C ~ +55 °C |  |  |
| Humidity |  | < 95 %, non-condensing |  |  |
| Certifications Voice Alarm | EN 54 (Part 16) | Available |  |  |
| Certifications Safety | CE | Available |  |  |
| 19"Rack mountable |  | Available |  |  |
| Control parameter memory |  | Retains after power off conditions |  |  |
| Accessories | Program | Software base full configuration with |  |  |
|  |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 4. Power Amplifier |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Audio signal input | Ethernet | Available |  |  |
| ventilation |  | forced air cooling fan |  |  |
| Fault detection | overheat | Available |  |  |
|  | overcurrent | Available |  |  |
|  | overvoltage | Available |  |  |
|  | under voltage | Available |  |  |
| Audio outputs |  | 100V |  |  |
| 19"Rack mountable |  | Available |  |  |
| Power supply |  | ~ 220 - 240 V, 50/60 Hz |  |  |
| Operating Temperature |  | 0 °C ~ +40 °C (0 ~ 104 °F) |  |  |
| Humidity |  | < 95 %, non-condensing |  |  |
| Safety Certifications | CE | Available |  |  |
| Available nominal power output (capacities)) | 500W | Available |  |  |
|  | 250W | Available |  |  |
|  | 125W | Available |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 5. Digital Multi-audio Player |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Inputs/sources | DVD player | Available |  |  |
|  | USB | Available |  |  |
|  | SD | Available |  |  |
|  | Mp3 file | Available |  |  |
|  | FM/AM tuner | Available |  |  |
|  | DVD videos | Available |  |  |
| Output | Stereo RCA | Available |  |  |
| Band frequency range (FM) |  | FM : 87.5MHz ~ 108MHz |  |  |
| Band frequency range (AM) |  | AM : 531KHz ~ 1710KHz |  |  |
| Antenna input impendence |  | FM:75Ω |  |  |
| Power supply |  | ~ 230V 50/60Hz |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 6. Network Resource Interface |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Auxiliary input | No. of Chanels | 4 or better |  |  |
|  | S/N | > 85 dB |  |  |
| Trigger inputs | No. of Chanels | 8 or better |  |  |
| Audio Storage |  | 4 GB SD card 500 MB Flash. |  |  |
| Power supply |  | ~ 220 - 240 V, 50/60 Hz. |  |  |
| Operating Temperature |  | -10 °C ~ +55°C |  |  |
| Humidity |  | < 95 %, non-condensing |  |  |
| Ability to store voice file & play via paging console |  | Available |  |  |
| Ability to store voice file & play via BGM software |  | Available |  |  |
| Ability to play message when trigger input is activated in designated zones |  | Available |  |  |
| Run designated audio file in predefined recurrent schedule in predefined zones |  | Available |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 8. Ceiling Speaker |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| IP Code |  | IP54 |  |  |
| Rated power |  | 6 W |  |  |
| Power taps @ 100 V |  | 6 W / 3 W / 1.5 W |  |  |
| SPL at 6 W /1 W (120 Hz-18 KHz,1 m) |  | 97 dB / 89dB |  |  |
| Mterial |  | ABS. |  |  |
| Frequency range(-10 dB) |  | 80 Hz - 20 KHz |  |  |
| Dispersion angle (1 Khz / -6 dB) |  | 184 / 90 |  |  |
| Certification |  | CE |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 9. Wall Speaker |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Rated power |  | 15 W |  |  |
| Power taps @ 100 V |  | 15 W / 5 W / 3W |  |  |
| SPL at 10 W / 1W ( 2k Hz, 1m) |  | 87 dB |  |  |
| Material |  | ABS. |  |  |
| Frequency response ( - 10 dB ) |  | 20 Hz - 20k Hz |  |  |
| Dispersion angle |  | H : 90° - V: 90° |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 10. Horn Speaker |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Rated power |  | 30W |  |  |
| Power taps @ 100 V |  | 10 W / 20 W / 30W |  |  |
| SPL at 1W ( 2k Hz, 1m) |  | 98 dB |  |  |
| Material | Horn cover | ABS. |  |  |
|  | Bracket | Stainless steel |  |  |
| Frequency response |  | 120 Hz - 15k Hz. |  |  |
| IP Code |  | IP65 |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number : 10. Network Paging Console |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| LCD |  | 4.3-inch color |  |  |
|  |  | touch screen |  |  |
| Microphone |  | gooseneck |  |  |
| Communication |  | TCP/IP. |  |  |
| Built-in monitor loudspeaker |  | Available |  |  |
| MIC Frequency response |  | 80Hz~16KHz. |  |  |
| Power supply |  | DC 12V / 24V |  |  |
| Operating Temperature |  | -10 °C ~ +55°C |  |  |
| Humidity |  | < 95 %, non-condensing |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |

| Item Number : 11. Volume Control |  |  |  |  |
| --- | --- | --- | --- | --- |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Rated power available |  | 6W / 30W/ 60W/ 120W |  |  |
| 24V DC forced overide relay |  | Available |  |  |
| wire systems |  | 4 wire |  |  |
| Size |  | standard 86 × 86 electrical back box |  |  |
| Accessories |  | Any required acessory not specifically refered to install/use the equipment |  |  |
| Item Number: 10. System Management Software |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Network Display |  | Display as a visual map |  |  |
| Device status monitoring |  | Available |  |  |
| Event logs |  | Available. |  |  |
| Fault logs |  | Available |  |  |
| Backing up the system data |  | Available. |  |  |
| Shedule playback configuration |  | Available |  |  |
| Logicl Zone groups |  | Available |  |  |
| Accessories |  | Any required acessory not specifically referred to install/use the equipment |  |  |

| Item Number: 14. Rack |  |  |  |  |
| --- | --- | --- | --- | --- |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Features |  |  |  |  |
| Type |  | 19" units mountable |  |  |
| Size |  | Suitable to install service duct equipment |  |  |
| Ventilation |  | Suitable for heat dissipation from rack mounted items |  |  |
| Finish |  | heavy gauge steel with baked on paint finish |  |  |
| Security |  | Lockable, Two keys, Fire rated |  |  |
| Free Rack Space |  | 9U |  |  |
| Accessories |  | Any required acessory not specifically referred to install/use the equipment |  |  |

22. FIRE DETECTION AND PROTECTION SYSTEM

22.1. General

This section outlines the minimum acceptance standards for equipment and materials which are to be provided.  Any deviation therefrom or alternative offer of materials must be approved by the Architect prior to placement of orders.

Minor equipment and materials not specified herein shall be provided in accordance with the best trade practice.

22.2. Standards & Codes

Fire Detections & Protection System should comply with following standards.

• Fire extinguishing systems     - BS EN 3.

• Foam fire protection system     - BS EN 13565.

• Fire extinguishing installations and equipment’s   - BS 5306

• Fire Detection and Fire Alarm System    - BS EN 54-20

• Fire Hose reel system      - BS EN 671-2011

• Fire Wet riser system      - BS 9990:2006

The Supply, installation and commissioning of the Fire hose reel system and wet riser system shall be in 100% compliance to British Standard excluding requirement of fire Engine in addition to their compliances to relevant Local Authority Fire Department Regulation.

Pipes should be sized using hydraulic calculation method in accordance with the recommendations of BS-EN-12845.

The development has all its common areas protected by an automatic fire alarm system. Manual break glass and alarm bell will be provided to all floors.  All fire alarms will be monitored by the main fire panel in the Fire command center. Mimic-panels will be provided on every lift lobby with the ability to interconnect with the main and other sub-panels to form a loop control in ensuring its reliability

• Do not use firefighting water pipes to supply water for other purposes.

• Support horizontal pipes at intervals not exceeding 3 m.

• Support vertical pipes at every floor.

• Install hangers without regard to location of pipe sleeves through walls. Center pipes in sleeves and do not use sleeves for pipe support. Attach to concrete ceilings with expansion bolts.

• Fire pump relief valve, when required, should be piped back into the suction, except where on-site storage tank is available.

22.3. Technical Specification for Wet Riser/ Fire Hose Reel System

22.3.1 Scope of Work

The System shall comprise of the following works to provide fully operational system:-

- 100 mm dia. Wet riser piping, valves including pressure regulating valves, canvas hose, hose cradle, coupling and nozzle, Pressure reducing Valves, Fire Hose reels.

- 4-way breeching inlet connected to the fire riser.

The installation shall be complete in every respect, including all fittings, materials and accessories necessary for the complete functioning of the system.

22.3.2 Piping Materials

Unless otherwise specified, all pipes used shall be hot dipped galvanized wrought steel pipes to BS EN 10255, Heavy Duty. All piping shall be new and free from defects. The pipe fittings shall be malleable iron and wrought iron galvanized conforming to the following British Standards:

- B.S 143 Malleable C.I Pipe Fittings

- B.S 1256 Malleable C.I and Cast Copper Alloy Pipe Fittings

- B.S 1740 Wrought Pipe Fittings.

Pipe joints shall, except otherwise indicated, be screwed and socketed joints. Welded joints shall not be used. All screw threads shall be made up to full depth of the socket and shall be cleaned and square with the axis of the pipe bore. Only Teflon or equal approved P.T.F.E thread sealing tape shall be used in jointing. Hemp or similar organic substances shall not be permitted.

An all piping, bends shall be long radius bends with turning not less than five time the pipe diameters. If this cannot be achieved, alternative bends of approved type shall be used.

Reduction in the diameter of through-flow pipes shall be by means of reduction sockets. Eccentric reducing sockets shall be used on horizontal pipes and concentric reducing sockets on vertical pipes only.

22.3.3 Hose Reel Assembly

The hose reel assembly shall be of either fixed or recessed swing-out type as indicated, being suitable for swift withdrawal of the hose in any direction.

Each hose reel assembly shall consist of a rubber hose, a metal reel, a stop valve, a hose guide and nozzle. The whole hose reel assembly is permanently connected to the water supply.

The reel shall be of metal construction of not less than 8 in. (200mm) inner case diameter and not more than 30 in. (750mm) rim diameter. It shall extend not more than 18 in. (450mm) from the wall or mounting surface.  The side plates shall extend at least 1/2 in. (12mm) radially beyond the wound-up hose. The Overall width of the reel should be no more than 850mm. The overall height of the reel should be less than 850mm including Hose and Integral Flexi guide for hose withdrawal guide. The overall depth of the Hose reel should be no more than 150mm. Color of the Reel should be red, fitted with operating instruction plate.

The hose shall be of non-kink smooth bore construction, conforming to the specifications of BS 3169 and rated for a bursting pressure of not less than 600 psi (4.14 MPa). The nozzle assembly shall be constructed of gunmetal, brass or other sufficiently robust and corrosion- resistant material. The nozzle shall be permanently marked to indicate the open and shut position. Product should be UL listed or FM approved.

The whole of the hose reel assembly shall rotate on the horizontal axis and the water supply connection to the hose shall be arranged such that the hose is not obstructed or kinked when the hose is wound up. The piping from the stop valve to the hose reel shall be of non-ferrous material or galvanized.

Wherever necessary, a pressure reducing valve or orifice plate shall be provided for the hose reel for controlling the static pressure to within 18-30 psi (0.12 - 0.2 MPa). The nozzle shall be adjustable for spray and jet discharge.

Every hose reel assembly shall bear the name of the manufacturer and the instructions for operation. Where hose reels are located in recesses or in non-prominent positions, a notice bearing the words “FIRE HOSE REEL” in red letters on a white background shall be provided. Hose reels shall be provided with recessed housing.

22.3.4. Breeching Inlets

The breeching inlet shall be of 4-way breeching in connections. Each inlet shall consist of a 2 1/2 in. (65mm) instantaneous male coupling and back pressure valve and protected by a cap secured with a suitable length of chain. A drain of 1 in. (25mm) diameter complete with drain valve shall be fitted at the lowest points of the riser. Product should be FM approved or UL Listed.

All fittings shall be located on the external wall of the building at ground level to the approval of the Local Fire Brigade and enclosed in a glass-fronted box.

Breeching inlet shall be of types approved by Fire Authority.

The door of the box containing the inlets shall be glazed with wired glass as indicated by the words " DRY RISER BREECHING INLET” painted on the inner face of the glass in 2" (50mm) block letter. It shall be fastened only by means of a spring lock which can also be operated from inside without the aid of a key after the glass have been broken.

The size of the inlet box shall be 22" x 22" x 12" (560mm x 560mm x 305mm) deep with a fall of 1" (25mm) towards the front at the base.

22.3.5. Pressure Regulating Landing Valves

Each landing valve shall be Constant Outlet Pressure Hydrant type and 65mm bore gunmetal with flanged of B.S.P screwed inlet, and 65mm instantaneous female coupling outlet fitted with removable plug secured by a chain. Product should be FM approved or UL Listed.

The valve shall be supplied with a 65 mm bore renewable valve washer for screw down valve and 20mm minimum diameter spindle and 165mm diameter handwheel.

It shall withstand a test pressure of 300 psig (20.7bar) and be marked with Manufacturer's Name. Landing valves shall be installed between 0.90m and 1.07m above level at the Riser Duct as shown in the accompanying drawing. They shall be installed such that ample clearance is allowed for easy insertion of canvas hose coupling.

Landing valves shall be normally kept in closed position by leather or canvas strap secured by padlock. All padlocks shall be operable by a master key.

22.3.6. Hose

The canvas hose shall be 2 1/2" (65mm) diameter and 30 m/45 m in length capable of withstanding a test pressure of 150psig. The canvas hose shall be of an approved type to the requirements of the local Fire Brigade & product should have UL Listed & FM approved.

22.3.7 Nozzle

The nozzle shall be of approved jet/spray type.

22.3.8 Couplings

Couplings shall be of gunmetal or other corrosion resisting material, which is sufficiently robust to withstand rough treatment.

22.3.9 Air Release Valve

Approved type automatic air release valve shall be provided at the highest point of every main riser to allow air in rising main to discharge to the atmosphere when water is being pumped in. Each air release valve shall be complete with an isolating valve and piped to the nearest drain or waste.

22.3.10 Pressure Relief Valve

A pressure relief valve shall be provided on a branch off the pump discharge before the non-return valve with the outlet piped to discharge over the suction tank.

22.3.11 Test Pipe

A test pipe branch with valve shall be taken from the discharge pipe, after the non-return valve assembly, and extend to discharge over the suction tank.

22.3.12 Earthing

The rising mains shall be electrically earthed to the external of the building. Earthing resistance shall not exceed 1 ohms.

22.3.13 Calibration

Each landing valve shall be separately adjusted to deliver water in accordance with Local Fire Department requirements.

22.3.14 Testing

The complete installation shall be tested hydraulically to one and a half time the working pressure measured at the base. The pressure shall be maintained over 24 hours and shall not drop more than 5% after correction for temperature.

22.3.15 Wet Riser Pumps

GENERAL REQUIREMENTS Pumps shall consist of:

- Casing impeller

- Suction and discharge connections

- Driven shaft

- Couplings

- Motor

- Shaft seal

(Pumps shall be complete with shaft water seals).

The motor terminal box shall be suitable for flexible conduit connection. Installations shall comprise:

I. Eccentric reducers for suction pipes and concentric reducers for discharge pipes

II. Expansion pieces directly connected to the pipe connection

III. Vibration isolation equipment

IV. Gland drain and tail pipes arranged to discharge into an open tundish adjacent to the pump base

V. Support brackets or plinths incorporating anti-vibration material.

Pumps and supplementary assemblies shall be entirely suitable for the systems pressures and temperatures specified in Drawings or Bill of Quantities.

Gate valves shall be provided on suction and discharge. Strainers shall be fitted on the inlet unless otherwise specified.

Final pump duties shall be verified taking into account certified resistances of system components. Unless otherwise specified, pumps shall be to:

I. BS 1394: Parts 1 and 2

II. BS 4082: Parts 1 and 2

III. BS 5257

Pump duties shall be achieved with the impeller shaft speed not exceeding 48rev/s (2900rpm) unless otherwise specified. Where duty and standby pumps are required, provision for automatic changeover shall be made with non-return valves fitted in each pump discharge line.

Pump connections shall be screwed to BS 21 up to DN 50 and flanged to BS 4504, PN 16 for DN 65 and above.

Pump suction and discharge flanges shall be drilled and tapped for pressure gauge connections. Closing plugs shall be supplied.

Pump casings shall have drain plugs fitted at the lowest point. Direction of rotation shall be indicated. All drive connections between drivers (motor or engine) and pumps shall be fully protected against accidental contact. Provision shall be made for shaft speed measurement.

Each pump shall be furnished with splash guards where applicable. Pumps shall be correctly aligned before start-up.

Tied bellows type flexible pipe couplings shall be installed at all pipework connections to pumps. No pump load shall be imposed on the connecting pipework.

Impellers and couplings shall be keyed to the drive shaft, the impeller being retained by a hexagonal nut. Shafts shall be fitted with water deflectors.

22.3.16 MATERIALS OF CONSTRUCTION

| Pump Component | Cast Iron | Stainless Steel | High Grade Gun- Metal | Phosphor Bronze |
| --- | --- | --- | --- | --- |
| Casing | x |  |  |  |
| Seal Housing | x |  |  |  |
| Baseplate | x |  |  |  |
| Sub frame | x |  |  |  |
| Shaft |  | x |  |  |
| Impeller |  |  | x |  |
| Renewable Casing |  |  |  |  |
| Wearing Rings |  |  |  | x |
| Glands shall be fitted with a self-adjusting mechanical seal unless otherwise specified. Impeller shaft extensions shall have a liquid shield. |  |  |  |  |

Generally, materials used for construction shall be:

I. Pump casings: close grained cast iron

II. Impellers: cast iron or gunmetal (bronze)

III. Shafts: stainless steel.

The permissible service pressure of cast iron pump casings shall be generally in accordance with the manufacturer's recommendations. No pump part or component part shall be subjected to a gauge pressure in excess of 16 bar, except where specifically listed in the Equipment Data Sheets.

22.3.17 PUMP OPERATION

22.3.17.1 END-SUCTION CENTRIFUGAL PUMPS

The pumps shall be selected to suit the type of service encountered. End covers, body rings, bearing, housing and casing shall generally be of cast iron construction. Impellers shall be of bronze or gunmetal and shafts of stainless steel. Case sealing rings, intermediate bushes and water lubricated journal bearings shall be of phosphor bronze material. Shaft seal shall be of high-quality gland packed type and bearings shall be ball thrust type on the outboard and self-aligning ball bearing type on the inboard end.

Pump casing shall be axially split or back pull type to permit removal of impeller without disturbing the piping connections. Each pump shall be fitted with an air valve, grease lubricator, water shaft seal connection, copper gland drains fitting and tapping’s in the pump head casing for discharge pressure gauge. Proper drainage shall be provided for all points around the pump set mounting. Copper gland drain shall be piped to the nearest drain or waste.

The pumps shall be constant speed with the pump driver coupled directly to the pump and the whole mounted on a common base plate bolted onto a concrete plinth. The plinth shall be provided to suit the manufacturer's requirements and shall raise the pumps to at least 6in. (150mm) above the known flood level of the pump set location. Mounting of the pump sets on the plinth shall be complete with adequate padding or vibration absorbers.

The hose reel pumps installation shall comply with the requirements of the authority having jurisdiction and the specifications in this contract.

The nominal ratings of the hose reel pumps shall be as specified in the Hose Reel Pump Schedule.

22.3.17.2 ELECTRIC MOTOR FOR FIRE PUMPS

The electric motors shall be AC squirrel cage induction motor of the totally enclosed fan cooled (TEFC) type. The motor shall be in compliance to BS 5000 and of sufficient capacity to effectively fulfill the pump horsepower requirements. The continuous maximum motor rating shall be to BS 2613 and shall have a minimum overload factor of 15% in excess of the power requirements at maximum pump discharge and minimum total head condition.

The motor windings shall be insulated to BS 2757, class `F' and suitably impregnated to withstand damp tropical conditions. Anti-condensation heaters shall be fitted for motors 10 HP and above. Stator frames, end shields, terminal box and cover shall be cast iron or other approved material.  Fan and fan cowl shall be of corrosion protected material.

The motor shall be suitable for 415V, 3 phase, 50 Hz power supply. All electrical works pertaining to the motor installation shall be provided. The motor shall be suitably earthed and provided with an overload trip protection. The thermistor protection is not required.

The motor shall comply with all the regulations of the local authorities and be provided with an approved type motor starter to limit the inrush starting current. Starters for the pumps motors shall be direct on line for motor with 1 to 3 Hp, star-delta for motor with 3 to 10 Hp and auto-transformer for 10 Hp and above. The starting current shall not exceed 150% of full load current. Capacitors shall be incorporated where necessary to maintain the power factor of the installation to 0.85 or higher. Unless otherwise specified, motor starters shall be to BS 4941:

I. Suitable for three-phase, four-wire 415/240V 50Hz ac supply.

II. Fitted with 220-250V ac operating coils.

The pump motor shall generally be flanged motor and suitable for horizontal operation. Coupling between the pump and the motor shall be by flexible self-aligning type complete with bolt-type metal guard. The pump and motor combination shall be mounted on a common base-plate of heavy-duty fabricated steel or cast iron and the complete unit installed on a suitable foundation plinth. The plinth shall be provided to suit the Manufacturer's requirements. Mounting of the pump sets on the plinth shall be complete with proper drainage and adequate vibration padding or an isolating efficiency of not less than 95% against the lower fundamental disturbing frequency. The minimum acceptable static deflection in the spring and shall be 1 inch (25mm) for machines having a fundamental frequency of 1000 rpm or above, increasing to 1/2 inch (40mm) at 500 rpm. Spring mounts shall be fitted with approved levelling devices.

The electric and power supply to the motor shall be always available. Any switches on the power feed to the motor shall be clearly labelled `POWER SUPPLY FOR FIRE PUMP. DO NOT SWITCH OFF'. An indicator lamp or lamps shall be provided to show that the power is available to the motor. In the event of power failure to the motor starting switch, an automatic warning shall be given visually and audibly at the Main Fire Alarm Control Panel.

The pumping system shall operate as follows:

a) A fall in the piping installation pressure shall activate the pressure switch.

b) The pressure switch transmits a signal to the pump control panel with automatically operates the electric booster pump.

c) The pump control panel shall indicate the actuation of the pump and transmit a signal to the FIB.

d) The FIB shall indicate the operation of the booster pump both audibly and visually.

e) Upon failure of the duty pump and/or further pressure drop in the piping installation a second pressure switch shall actuate the standby pump.

f) A signal shall be displayed at the FIB and pump control panel indicating the failure of the duty pump and/or the operation of the standby pump.

22.3.17.3 Jockey Pumps

Jockey pumps shall maintain system pressure on the installation side wet riser system. The following general requirements shall apply to jockey pumps:

a) A fall in the system pressure on the installation side of the control value will activate the pressure switch controlling the Jockey Pump.

b) The pressure switch transmits a signal to the jockey pump control panel and activates the jockey pump to maintain system pressure on the installation side of wet riser system.

c) Jockey pump shall have rated capacities not less than normal leakage rate and sized to make up the allowable leakage within 10 minutes at a rate of flow not exceeding 4 l/min.

d) Jockey pump shall have a shut-off pressure not exceeding the working pressure rating of the fire protection equipment.

e) The power supply to the jockey pump shall be such that any failure of this pump does not affect the power supply to the main fire pump.

Starter provisions and controls for each jockey pump shall be such that any failure of this pump’s panels.

Jockey pumps shall be low capacity in line centrifugal pumps. Pump impeller and shaft shall be stainless with a cast iron casing. Motors shall be totally enclosed, fan-cooled, squirrel-cage type.

22.3.17.4 PUMP NAME PLATES

Each pump shall be provided with a plate giving the output pressure at zero suction lift at the nominal flow rating. Where the performance characteristic of the pump is to be achieved using an orifice plate not integral with the pump delivery, the plate shall carry a reference to the fact that the performance given is that of the pump and orifice plate combination, together with the `K' factor of the orifice plate.

In all case, the pump plate shall give the rated speed for the pressure and flows specified and the              maximum power absorbed at the rated speed.

22.3.17.5 CONTROLS FOR FIRE PUMPS

The controller shall be arranged to include the following minimum requirements and specifically tested for fire pump service, all in accordance with Fire Authority Requirements: -

- Manual/Automatic control of the duty and stand by fire pumps with constant output governed by the discharge pressure control situated in the distribution mains.

- Operation of the fire pump sets in a duty/standby mode with manual facility for lead pump selection. The standby pump shall be set to come into operation on failure of the duty pump.

- The 'OFF-MANUAL-AUTOMATIC' selection sequence shall be controlled by a three-way switch. Any position other than AUTOMATIC shall sound an alarm.

- In addition to the automatic and manual starting systems, the control panel shall be provided with a device that will enable the pumps to be started from the control circuit in case of any failure.

- Operation of the controls shall be possible from the front of the panel without the need to open the panel doors.

- Pressure switches shall be provided for the starting of the pumps when the pressure in the fire service distribution main falls to a value not less than 80% of the rated operating pressure unless otherwise specified. The pressure switches shall have independent high/low calibrated adjustments and be able to withstand a hydrostatic pressure of 300% of the rated working pressure for five (5) minutes.

- Once started, the pumps shall run continuously until manually stopped or when the system pressure has reached the cut-out pressure setting. Starting of the pump(s) shall at the same time initiate a visual and audible alarm.

- The controllers shall be provided with pilot lights, common alarm bell and individual contacts for the connection of remote signal devices which operate in the event of the following: -

- AC power failure

- Failure of duty pump to start

- Failure of standby pump to start

- Provision in the form of contacts shall be included for the connections for remote alarm and signals which correspond to the pilot lamps in the controller.

- All alarm and signals shall be able to operate under manual as well as automatic conditions.

- Audible alarms shall be of minimum 85-dBA rating at a distance of 5 m.

- An electric motor lockout shall be provided for dis-connection of any wires that interconnect the electric motor control and shall not interfere with the proper operation of either controller.

- The fire pumps shall be monitored by the Main Fire Alarm Panel.

22.3.17.6 PUMP CONTROL PANEL

The fire pump control panel shall be a self-contained, extensible, wall- mounted flush-fronted metal cubicle board completely assembled, wired, and tested by the Fire Pump Supplier/Installer before delivery from the Factory. The controller shall be so arranged as free standing independent from the pumps and the contractor shall indicate if the controller is to be supplied with the enclosure designed to be inspected and service from the rear. The controller shall be fixed not further than 3 m from the pump, and be within sight of the driver.

The pump control panel shall be designed to receive an electrical supply of 415/240 V, 3 phase, and 50 Hz AC current. All motor starters shall be incorporated within the control panel. The control panel shall incorporate spare contacts that will close upon operation of the electrical and/or any warning signal. The contacts shall energize a remote electrical bell/or lamp within the main Fire Alarm Panel.

All switches, which are required to keep the controller in the `Automatic' positions shall be within locked cabinets having break glass panels.

All other items as required or standard to, the manufacturer's equipment shall be supplied.

22.3.17.7 PUMP PERFORMANCE TESTS

The fire pumps shall be tested for its performance prior to delivery to site at the pump manufacturer's factory. The pump casing hydrostatic test shall also be carried out in accordance to the Hydraulic Institute Standards. All testing certificates shall be submitted to the Engineer for approval prior to delivery.

The fire pumps shall also be tested for its head/flow characteristic under normal operating conditions after the installation.

- Pump Efficiency

Pump efficiency shall not be less than the following:

Shaft kW            Minimum Efficiency

Up to 1 kW                     0.35

1 to 2 kW                         0.5

2 to 5 kW                         0.6

5kW and above               0.7

22.4. Technical Specifications for Portable Fire Extinguishers

22.4.1. General

The Sub-contractor shall supply and install portable type fire extinguishers in the location as shown in the drawings.

All extinguishers provided shall meet with the requirements of the Local Fire Authority and with the relevant BS and NFPA Standards.

22.4.2. Location AND INSTALLATION

Extinguishers shall be conspicuously located where they will be readily accessible and immediately available in the event of fire. They shall, in general, be located along normal paths of travel and not to be obstructed or obscured from view.

In locations where visual obstruction cannot be completely avoided, means shall be provided to indicate the location.

Hangers, hooks and mounting brackets used for the installation of the extinguishers shall be to the approval of the Engineer. Where extinguishers are installed under conditions subject to dislodgement, such brackets shall be specifically designed to cope with the problem. Extinguishers installed under conditions where they are subject to physical damage shall be protected from impact. The exterior finish of the extinguishers shall be suitable for external or internal location as required. All extinguishers shall be installed such that the extinguisher operating instructions face outward. Extinguishers having a gross weight not exceeding 40 lbs. (18 kg) shall be installed so that the top of the extinguisher is not more than5 ft. (1.5m) above the floor. Except for wheeled types, all heavier extinguishers shall be so installed that the top is not more than 3 1/2 ft (1m) above the floor. In no case shall the clearance between the bottom of the extinguisher and the floor be less than 4 in (0.1m).

The words 'FIRE EXTINGUISHERS' shall be painted using luminous paint on the wall above where the fire extinguisher is installed.

22.4.3 Approval from Fire Authority

The contractor shall be responsible for obtaining approval from the Local Fire Authority for all extinguishers installed. The approval fee required for this purpose shall be deemed to have been included in the tender price.

22.4.4 Types of Extinguishers

All extinguishers shall be provided according to the type and capacities as indicated in the drawings. Classifications of five classes are according to BS4547.

22.4.5 Water Types

These shall be general purpose extinguishers of either gas pressure type, water/CO2 cartridge type, soda acid type or air-charge stored pressure type as specified, being suitable for Class 'A' fires. Each extinguisher shall be supplied complete with plunger, hose and nozzle and mounting brackets. Extinguishers shall comply with BS 1382, BS 138 and BS 3709 as applicable.

Water type extinguishers shall be painted in red.

22.4.6 Compressed Gas Types

These shall generally be CO2 type intended primarily for Class 'B', Class 'C' and Class 'E' fires, being provided complete with alloy cylinder, valve assembly, hose and discharge horn. Extinguishers shall be painted RED, and comply generally with BS 3326 or equivalent.

22.4.7. Foam Types

These extinguishers are intended for use on Class 'A' and Class 'B' fires, and can be either of AFFF type or CO2 cartridge type. They shall comply generally with BS 740 or equivalent.

These shall be installed complete with hose, nozzle and mounting brackets and painted RED in color.

22.4.8 Dry Chemical Types

These shall be ordinary dry chemical extinguishers (sodium bicarbonate base, potassium bicarbonate base, potassium chloride base or potassium bicarbonate urea base) suitable for use on Class 'B' and Class 'C' fires or multipurpose dry chemical extinguishers (ammonium phosphate base) suitable for Class 'A', Class 'B' and Class 'C' fires.

They may be either cartridge/cylinder operated type or stored-pressure type, and generally to BS 3465 or equivalent.

Where specified, they shall be provided with special long-range nozzles. Dry chemical type extinguishers shall be painted RED.

22.4.9 Dry Powder Types

These extinguishers and agents shall be intended for use on Class 'D' fires and specific metals, following special techniques and manufacturer's recommendations. They may be hand portable, cartridge- operated or wheeled models as applicable. The extinguishing agent shall generally be composed of sodium chloride base agent.

The body color for such extinguishers shall be RED.

22.5. Technical Specifications for Fire Detection & Alarm System

22.5.1. General

The system shall be of the analogue addressable type with voice command feature, microprocessor based, audibly and visually supervised, with detection and alert devices distributed where dictated by Code. The life safety system shall be composed of three subsystems for fire detection and alarm annunciation, emergency voice/alarm, and two-way communication. The system shall be zoned and non-coded.

The following measures shall be taken:

• Interface with other systems such as security and door access systems, firefighting, smoke control, stair pressurization, Building Automation and Control Network (BACnet), standby/emergency power supply, Audio Visual system, elevators, LP Gas etc shall be required,

• Standby emergency power supply system shall be provided to ensure continuity of power supply to loads that are essential to life safety such as the fire alarm system, the FCC and Main Communication Room, the fire pump and mechanical equipment used for smoke control procedures and at least one elevator in every bank with power transferable to any other elevator in the bank.

• A two-way telephone communication service is to be installed for fire fighters use. This system shall operate between the building central command and every elevator car, every elevator lobby and each floor level of exit stairs. Notification of occupants shall be achieved through a voice communication system.

The basic system components shall be the following:

• Main fire alarm annunciation and control panel MFAC, microprocessor based, addressable type, modular expandable, fully electronic, electrically supervised, divided into main compartments for control, annunciation and amplifiers. The system shall have batteries capable of monitoring the system for 24 hours and then sounding the alarm for 30 minutes.

• Color graphics CRT terminal

• Satellite Fire Alarm Panels SFACs for data acquisition, transmission and control. Wiring, between the speakers/horns, visual alert devices, emergency telephone, detectors, and control modules on one hand and the main control panel on the other hand, shall be via the satellite fire alarm panels that have multiplexing features and amplifiers rated for the required audio load. Each building shall have an SFAC assigned to serve its various floors.

• Automatic and manual detectors consisting of smoke, heat, manual, duct smoke and sprinkler water flow. Detectors shall be located to code.

• Alarm notification devices consisting of audible alarms (bells, speakers and horns) and visual alarms (strobe lights). The voice alarm system shall be capable of broadcasting pre-recorded messages and have an interface with the fire fighters’ station at the main panel. The main fire alarm panel or MFAC/SFAC shall house the amplifiers sized in accordance with the number of speakers and wattage. Speakers shall have different tap settings and shall be adjusted on site for optimum performance and maximum coverage. Alert devices shall be designed to ensure a sound level of 15 dB above ambient noise in each area.

• Interface and control modules for releasing of fire rated doors separating fire zones.

• Fire fighters communication system consisting of telephone handsets located next to the exits on each floor and in every elevator car and elevator lobby for high-rise structures.

• Interface with the Building Management System for smoke management and control, sprinkler and fire pumps and HVAC control and with other systems such as security, standby/emergency power supply, elevators, etc.

• Remote repeater panels at strategic locations such as the main entrances.

• Data Network: each MFAC/SFAC panel is a node of a network with direct communications into the network but operates on a stand-alone basis. Although performing different functions, each MFAC/SFAC serves as a "peer-to-peer" (equal) partner in controlling network communications. Network information is sequentially transmitted from one node to another.

The fire alarm system shall provide visual and audible warning on main annunciator panel for supervisory signals such as:

• Failure or disconnection of power supply to main control panel

• Failure of fuse or protective device

• Removal of detector head on any initiating circuit

• Break or short circuit in wiring of any initiating or alarm circuit

• Valve tamper at fire pumps

• Fire pumps running

• Fire pumps power loss

• Fire pumps phase reversal

• Emergency generator on

• Emergency generator start failure

• Emergency generator low fuel

• Emergency generator low oil pressure

Even though an addressable fire alarm system shall be installed, buildings shall still be divided into zones to identify the location of a fire to help reduce confusion. The following criteria shall be followed in the zoning:

• A single zone shall not exceed 2000m2.

• A zone shall not cover more than one story.

• Stairwells, elevator shafts and flue-like openings shall be treated as separate zones.

• The two hours fire separations dictated by the architectural requirements shall be used as separate zones.

The work outlined in this section covers the supply of all materials, which shall be new and unused, equipment and labor necessary for the complete installation, testing and commissioning and handing over in approved working order of the complete system. It shall also be in accordance with rules and regulations of the Local Fire Authority and of the following: -

a. Local Fire Authority

b. Fire and Accident Underwriters Association

c. BS 5839 Part1: 1988

22.5.2. Equipment Specification

The Main Fire Alarm Panel (MFAP) shall be of the multiple processors based truly Analogue Addressable Type, of modular architecture, being of the latest design and manufacture. The FCP shall be suitable for ambient conditions varying between 00C to + 550C, with relative humidity up to 95% non-condensing.

The MFAP shall be manufactured to BS 5750 ISO 9000 quality standards, by an approved and well-known manufacturer who provides design, service back up, and spare parts locally.

The processor system shall as a minimum once per day at the set time automatically adjust all sensing devices to compensate for sensitivity increase due to environmental conditions. This check should also incorporate a full "Check sum" evaluation to detect unauthorized programming changes, or data corruption.

The control panel shall be capable of being extended in modules of 4 loops, up to a maximum of 16 loops. Each 4-loop module shall incorporate its own microprocessor and shall be electrically isolated from the main processor board. The loop board shall incorporate dc/dc converters to prevent loop cross talk. Each converter board shall be provided with step up voltage converter to ensure the correct line voltages are maintained to the detection loops in the event of mains power failure in combination with low battery state.

To increase fault finding capability each loop processor board shall have the LED indicators.

It shall be possible to site a four-loop processor board remotely from the main control panel up to maximum distance of 1000 meters and interconnect with the main panel via a four wire screened data line.

Each loop shall be capable of accepting as a minimum 126 Analogue detectors or control devices. The loop PCB will incorporate "on board" short circuit isolators for both the incoming and outgoing loop wiring.

The system architecture and software will allow for random addressing of each device to suit field conditions, pre-set order or soft addressing will not be acceptable.

Each processor shall continuously monitor the Analogue signal from detectors, and evaluate this signal against a pre-determined set of fire algorithms, to accurately determine the existence of fire and to reduce unwanted alarms.

There shall be no limit to the number of detectors per loop which can be in alarm simultaneously, the vacuum fluorescent display (VFD) shall be capable of reporting all incoming alarms by use of a scroll function the scroll function shall be accessible at all times without the need for "key access".

The FAP shall incorporate as standard a vacuum fluorescent display module, which provides, for power conservation reasons, two levels of brightness output. Level 1 output will "low" for standby conditions, with level two providing "high" output, to signal change of state or alarm processing.

The display shall provide up to two rows of 40 characters.

The FAP shall be able to incorporate an integral printer unit, which shall record all changes of state, alarms, faults and operator actions, overall, the minimum requirements will be: -

a) list isolated devices

b) list loop devices

c) list event log

d) list panel outputs

e) list loop outputs

f) list loop output devices

g) list check sums for (programming and Eprom error checking)

h) list single device analogue value

The FAP shall be able to be expanded, to the following features.

(a) Repeat panel drive (for use to 40 repeat panels)

(b) remote printer (ASCII expanded text)

(c) mimic driver

(d) 32/64/96 way programmable outputs

(e) BMS system RS 232 output

22.5.3 Interfacing Facility

22.5.3.1 Interface with Building Automation System (BAS)

The system shall be provided with an RS232 ASCII protocol and to be integrated with the Building Automation System.

22.5.3.2 Interface with the CCTV systems

Provision shall be made for the Fire Graphics and Text workstation to link up with the CCTV system to provide a real time video display at the Fire GT monitor. The Fire Monitor shall display a live video of the camera capturing the fire location in the event of an alarm. A fire signal corresponding to the location of the fire shall be send to the CCTV system by the FACP to activate the CCTV camera such that a real time video picture can be display at the Fire GT monitor.

22.5.3.3 Interfacing works to future fire alarm panels

The Fire Alarm System shall be designed to interface with future fire alarm panels with a maximum of 64 fire controllers on the Network.

The networks shall be totally flexible and enable the fire controllers to be seamlessly linked together, providing a system capability of up to 160,000 detection addresses and over 14,000 digital I/O points.

The Central Fire Command Station shall be configured to monitor the status of all the fire controllers and transmit signals to the fire controllers for specific actions to be performed.

The system shall be able to incorporate the extension of the Fire Alarm Annunciator and Control Panel to provide remote start/stop of equipment such as fans, dampers etc.

22.5.4. Fire Alarm Software

The main processor shall incorporate a "Watchdog" system, which, in the event of processor failure will reboot the system in an attempt to correct the fault and return the system to full operation. Failure to reboot should result in a processor failure being announced both visually and audibly.

All software, program and data shall be held in non-volatile read only memories.

System configuration data shall be stored in memory, which can be electrically erasable or alterable. This system shall be backed up by on board PCB rechargeable batteries with a life span not less than 5 years. PCB battery should be continuously on charge to ensure correct operation. Altered or reconfigured whilst in a live on line situation.

All configured data shall be able to be downloaded to the on-board printer for verification and checking purposes.

Alarm processing should incorporate verification scanning before raising any fire or fault signals. The maximum permitted will be:

3 Scans Fire

6 Scans Fault

A priority interrupt signal will be used for all manual break glass units, which will override the scanning process for fire indication.

The processor systems shall include a software routine to enable pre alarm signals to be raised in the event of Analogue signal value from a detector reaching and maintaining a level of 80% of alarm threshold, after multiple scans.

All system configuration data shall be fully field programmable without exception, and shall be able to be

22.5.4.1 Non-Alarm Signals

The hardware and software shall be so configured as to allow for incoming "CHANGE OF STATE SIGNALS' Emanating from floor sprinkler control valve isolation including such signals as pump running. The control panel will process this as change of state only and not raise any executive actions or alarms. The internal printer will log such signals to hard print and also to the historical log function of the panel. All non-alarm signals shall be shown visually on the VFD and at the printer as "ALERT" signals only.

22.5.4.2 Walk Test Facility

A walk test facility shall be included which will allow for single man test and verification of loop or zone devices. This testing shall not at any time prevent a fire signal from being generated by devices on other loops or zones, which, will automatically cancel the test function and raise the normal executive actions of the fire system. It shall be possible to inhibit or have on line during the test all field programmable outputs associated with the detectors in the zone or loop being tested.

22.5.4.3 Historical Event Log

The historical log shall have sufficient memory size to log and record up to 200 fire events or combination or events including all operator actions taken. The details held within the log shall be capable of being down loaded to the fire alarm control panel integral printer.

22.5.5. Panel Hardware

The control panel cabinet shall be manufactured from sheet steel of not less than 1.5mm and be undercoated with corrosion resistant materials with final baked enamel paint finish.

Common master LED indication will be provided to give the following information: -

a) General Fire

b) Supply Healthy

c) Pre alarm

d) System Fault

e) Device Fault

f) External Fault

g) Processor Fault

h) Device Isolated

22.5.6. Zone Indication

Zone indicators up to a maximum of 96 zones will be provided. Expandable in 64 way membrane sections, all zone indicators shall be LED type. Each membrane will provide zone designation label stripe, which can be inserted from the rear side of each line of indicators.

22.5.6.1 Vacuum Fluorescent Display Panel

The fire alarm control panel display will employ vacuum fluorescent, twin brightness level type display. The two levels of display brightness output will be Level One "Low" (Standby condition) Level "Two" high (Including alarms or panel in access, and operator action).

The overall display will provide two-line output of up to 40 characters per line. The display will provide the following information.

a. Device Type (non-abbreviated)

b. Analogue Value

c. Device Location

d. Device address, zone number loop number

e. Normal condition

f. Access condition

g. Fire alarm

h. Device fault

i. Pre-alarm

j. Fault on loop

k. External fault

l. Control fault

m. Alarm fault

n. Supply fault

o. Alarms sounded

p. Alarms silenced

q. Panel reset

r. Maintenance mode

s. Devices isolated

t. Test mode.

22.5.6.2 Sub-Fire Indicator Board (Mimic Panels)

Sub-fire indicator boards (SIB) shall be supplied and mounted remotely from the FIB.

SIBs shall be microprocessor based and include watchdog timers or other appropriate mechanism to ensure ongoing operation. As a minimum configuration, the SIB shall include the following elements.

- Controller microprocessor

- EPROM based software

- Communications controller

- Display (perspex floor plan with colour reverse silk-screen printing)

- Display drives

- Power Supply

SIBs shall communicate with the FIB by means of a high-level communications interface. This shall conform to current ISO or CCITT standards and include error detection mechanism. The SIB and FIB shall communicate via an active transmit-respond polling sequence with appropriate timeout and monitoring mechanism.

The SIB shall annunciate the following events.

- All flow switch status on a per floor basis.

- All pressure switch status inclusive main stop valves shut, low

- tank water, pump running etc.

- Monitored stop valves status.

- Smoke detector groups alarms on a per floor basis and AHU basis.

- Pump status.

- Installation valve activation.

- Power supply and battery charger fault.

- System fault status including fault isolated.

- Provision for 100% annunciator expansion.

SIB annunciators shall be high quality LED type devices. A LED facility shall be supplied. All displays shall be updated with current system information once every 10 second interval.

The FIB and SIB in conjunction shall supply system software capability including the following.

- Ability to annunciate any system monitored point individually

- Be able to add and annunciate new individual or groups monitored points.

- Be able to configure point into groups as required and annunciate status of the group on one display.

- Test diagnostic to ensure communications integrity.

SIBs shall come complete with cabinet power supply and associate equipment that meet the requirements as specified for the FIB.

22.5.6.3 Master alarm board

The master alarm board shall provide as a minimum, the following common alarm and output facilities:

a) Four sets changeover contacts (Two sets isolatable via on board switch).

b) 4 alarm sounder monitored output lines rated at 1 amp. each.

c) Switch output for the following: -

i. Manual

ii. Fault

iii. Auxiliary

iv. Buzzer

v. Alarm

vi. Ext. alarm

d) A set of contact common/normal open will be provided which are delayed on power up and power down. This contact will be used for extinguishing system output to prevent spurious signals causing accidental operation of system.

e) Visual indicators shall be provided to announce.

i. Alarm fault

ii. Earth fault

iii. Aux. 1 isolated

22.5.7 Operator Controls

The minimum operator control will be as follows: -

a) Sound Alarms

b) Silence Alarm

c) System Reset

d) Scroll Alarms

Access to the operator control must only be achieved by authorized personnel and will only be accessible via a key "ACCESS" switch. Alarm scroll to be available at all times without the need for "Key Access".

A 12 way keypad touch sensitive membrane will provided, providing three levels of users control, level two and three only is accessible on successful entry of a pass number code. The levels will provide the following.

Level 1 (Accessible by key switch operation)

a) isolate/de a isolate device

b) Set date and time

c) List loop devices

d) Select test mode

e) LED test

f) Enable / Disable printer.

Level 2 (Assessable by 4 digit code when in level 1) Facilities

a) Print event log

b) Read a single device

c) List isolated devices

(d) Program outputs

e) Display checksums

Level 3 (Only available from level two) Facilities

a) Print panel outputs

b) Print loop devices

c) Print loop outputs

22.5.8. Programming

Level two and three shall be extended, when a hand held or portable computer is connected to allow for down-loading/up loading and programming of loop outputs, loop devices and panel outputs. The facilities required from he extended facility will be.

LEVEL 2                                        		LEVEL 3

Message handler              	 Program panel output

Program loop devices

Program loop outputs

Load/Save program data

Clear output

22.5.9 LOOP and Field Devices

22.5.9.1 Loop General

The "loop' shall be a two wire circuit starting and returning at the two associated loop return input terminals of the control.

The loop shall be capable of driving as a minimum up to 126 field Analogue Addressable devices offer a maximum total loop distance of 2 km.

22.5.9.2 Loop Communications

The communication to and from each device shall be based on pulse position modulation digitally encoded on the power voltage.

22.5.9.3 Device Addressing

There shall be no preset order for addressing the devices. The devices shall be addressed in an order appropriate to site conditions. This order will be determined during commissioning and the control panel will have facility to override the address order to re-check any device showing a tendency to the alarm condition.

22.5.9.4 Loop Short Circuit Isolators

Isolators shall be fitted at a maximum spacing of one per 20 devices, or to suit local maximum zone size regulations. The isolators shall protect against short circuits on the loop by isolating that section of the loop where the short circuit occurred, thus maintaining the integrity of the remainder of the system.

Short circuit isolators will be powered by the loop wiring, and will be limited to 10 per loop.

22.5.9.5 Loop Interface Equipment

The loop shall be of receiving information in addition to that from heat and smoke detectors e.g. operation of sprinkler system. The source of this information shall be identified by its own inquire address. Any interface equipment used to achieve this requirement shall be from the standard product range of the same manufacturer as the smoke and heat detectors provided for the loop.

22.5.9.6 Loop Power

The loop wiring shall power the detectors, address, and carry data to any from the field devices by digitally encoded signals superimposed on the power voltage.

22.5.9.7 Automatic Devices Identification

The control panel shall be able to identify what type of device is located at each address in order to protect against accidental fitting of an inappropriate sensor.

22.5.10 Detector Common Requirements

22.5.10.1 Detector Power

The detectors shall be suitable for connecting to a two-wire 24 V central system and operate satisfactory within the supply voltage range of 17V-28V DC.

22.5.10.2 Detector Alarm Indication

An indicator LED shall be provided on the detector, which illuminates when the detector has reached a pre-set alarm level. The indicator shall be operated independently of the detector, by a signal command from the central control panel.

22.5.10.3 Detector Remote Output

Provision shall be made for on output from the detector suitable for operating a remote indicator or other device with a current limitation of 4 milli-amps. This output will be initiated by a signal command from the control panel.

22.5.10.4 Detector Mounting Bases

Separate mounting bases shall be required which shall be common in design for all types of detectors to be used. Bases shall enable ready removal of the detectors for maintenance. The bases shall be fitted with stainless steel terminal springs and stainless steel terminal screw saddles; detector removal will not initiate an open circuit alarm. No detector base shall incorporate electronics of any type.

22.5.10.5 Detector Construction

The construction of the detector and bases shall be in white self-extinguishing polycarbonate plastic. Full circuitry must be protected against moisture and fungus. Smoke entry points will be protected against dust and insect ingress by corrosion resistant gauze. The detectors must be unobtrusive when installed, having a dimension not exceeding 50mm x 100mm diameter maximum, including the mounting base. The detector shall be supplied complete, fully tested and factory pre calibrated.

22.5.10.6 Detector Addressing Method

The unique address of the detector shall be set by the installer by means of a pre coded rigid plug in card, which when fully inserted into the detector base will program the detector address. The coded card when fully inserted will protrude from the detector base, this section of the card will show a pre numbered label for ease of detector identification. In the event DIL or rotary switches are utilized for the setting of address, then part 8.6.2 and 8.6.3 shall apply.

When the address code is set by means of a DIL switch it shall be obscured from sight by means of suitable label. The label shall indicate the relative positions of the DIL switch.

For all detectors with DIL addressing there shall be facility on the mounting base for writing in indelible ink the address of the base. The address code shall be obscured from sight when the detector is fitted to the base.

22.5.10.7 Detector Contamination

The build-up of dirty or similar contamination on the radioactive or optical source will cause the output signal from the detector to gradually change. The control panel shall be capable of monitoring this slow change in signal and at a predetermined level indicate that the detector is in need of servicing or as a minimum false a pre alarm.

22.5.10.8 Approvals

All detectors shall have the relevant manufacturing certificates and accepted for use by relevant authorities.

22.5.11 Detection devices

All analogue addressable field devices shall have an integral microprocessor on board. All these devices shall be BS EN54 LPCB approved. These devices shall include, but not be limited to multisensory detectors, smoke and heat detectors, interface modules and gas releasing and suppression modules.

22.5.11.1 Addressable Intelligent Detectors

Each intelligent smoke detector shall be capable of transmitting pre-alarm and alarm signals in addition to the normal, trouble and need cleaning information. It shall be possible to program control panel activity to each level. Each detector may be individually programmed to operate at any one of five (5) sensitivity settings

Each detector shall automatically change to standalone conventional device operation in the event of a loop controller communications failure. In the standalone detector mode, the detector shall continue to operate using sensitivity and environmental compensation information stored in its microprocessor at the time of communications failure. The MFAP shall monitor the loop and activate a loop alarm if any detector reaches its alarm sensitivity threshold.

Every intelligent detector shall be tested periodically for its sensitivity to ensure that the detector continues to operate accurately within its calibrated sensitivity windows. The detector shall be capable of performing independent check on its sensitivity window and should its sensitivity drifted outside this window a fault message shall be reported automatically to the MFAP. System offering this type of feature shall be supported with document from an independent testing authority such as Underwriters Laboratory (UL) or Loss Prevention Council (LPCB).

All detectors must be immune to external Electro-Magnetic Interference conforming to IEC1000-4-8:1995 and ENV 50149:1995/ En 500082-2:1995 and ENV 50140:1993/ EN 50082-2: 1995.

22.5.11.2 Electronic Horn/Strobe

All electronic horn/strobes shall be provided according to the drawings.

The horn/strobe shall have a red plastic housing, ultra slim, protruding from the wall less than one inch from the wall. It shall have an attractive appearance with no visible mounting screws. Is shall fit all standard one-gang electrical boxes with plenty of room behind the signal for extra wire.

A sound output level of 91 dBA average shall be provided.

The strobe shall provide 15 cd or 15/75 cd or 30 cd or 110 cd synchronized flash outputs. The strobe shall have lens markings oriented for wall or ceiling mounting. It shall be possible to replace the lens markings with lens marking kits. Ceiling mounted strobes shall have lens markings with correctly oriented lettering. Removal of an installed Horn/Strobe to change the lens markings shall not be acceptable.

Horn/strobe shall mount to a masonry electrical box (2-1/2” deep)

A delay timer with adjustment from 0 to 5 minutes to set off the building alarm bells after a predetermined delay shall be provided.  A manual switch shall also be provided to give an immediate alarm.

General:

Average ambient sound levels greater than 105 dBA require visible notification appliances.  Total sound pressure levels produced by ambient sound pressure levels and all operating audible notification appliances must not exceed 120 dBA within the occupied area.

Public areas

In Public areas signals must have a sound level of at least 15 dB above the average ambient sound level or 5 dB above the maximum sound level having duration of at least 60 seconds, whichever is greater. Measurements must be taken with an A-weighted scale (dBA) at 5 feet above the floor in occupied areas.

Apartment Areas

mode signals must have a sound level of at least 10 dB above the average ambient sound level or 5 dB above the maximum sound level for at least 60 seconds, whichever is greater. Measurements must be taken with an A-weighted scale (dBA) at 5 feet above the floor in occupied areas.

In sleeping areas, audible appliances must have a sound level of at least 15 dB above the average ambient sound level, or 5 dB above the maximum sound level for at least 60 seconds, or a sound level of at least 75 dB, whichever is greater. Measurements must be taken with an A-weighted scale (dBA) at pillow level in occupied area.

22.5.11.3 Optical Beam Smoke Detector

The smoke detectors shall be suitable for detecting invisible product combustion as well as visible smoke and be of the dual chamber dual source type to provide good stability in changing environmental conditions.

Detector coverage will be up to 100m (length) x 15m (wide).

The system shall comprise of a transmitter head, a receiver head and a control box.

22.5.11.4 Ionization Analogue Smoke Detectors

The Ionization smoke detectors shall be suitable for detecting invisible product combustion as well as visible smoke and be of the dual chamber dual source type to provide good stability in changing environmental conditions.

The radioactive source shall be Americium 241 mounted in such a way that it is mechanically secures. The device shall have been certified by the National Radiological Protection Board or a similar body. The detector shall be capable of operating within the following environmental limits.

Temperature operating rang - 20C to 60C

Humidity operating range 0% to 95% RH non-condensing.

Wind resistance up to 10 meters per second without false alarming

The detector shall be capable of protecting an area up to 100m2 at a height of up to 12m. The installation and sitting of the detectors must conform to BS 5839 1980 or similar Standards, ruling in the local region.

22.5.11.5 Photoelectric (Optical) Analogue Addressable Smoke Detectors

The photoelectric (Optical) smoke detectors shall be suitable for detecting visible smoke such as is produced by slow smoldering fires including decomposing PVC. Detector coverage will be 100m2 at a height of up to 12m.

The detector shall be capable operating within the following environmental limits. Temperature operating rang - 20V to 60C

Humidity operating range 0% to 95% RH non-condensing. Wind – non affected.

22.5.11.6 Analogue addressable Heat Detectors

The heat detector shall be electronic in operation and suitable for connecting to a two-wire 24V central system, which can operate within the voltage range of 17V - 28V DC. Detector coverage will be 50m2 at a height of up to 9m.

The device shall monitor ambient temperature by means of an NTC thermistor. The detector shall be capable of operating within the following environmental limits. Temperature operating range - 20C to +60C (no icing)

Humidity operating range 0% to 95% RH. (Non-condensing) Wind – effected.

22.5.12 Manual Call Stations

22.5.12.1 Break Glass Type

The Manual Call Stations shall be of the break glass type with key lock for test and reset, unless specified otherwise. The break glass unit shall be cast iron, cadmium plated or other approved type and painted red to BS 381C. The unit shall be of attractive and neat appearance and shall be suitable size and type for surface or flush mounted on the walls. Appropriate label showing “FIRE, BREAK-GLASS” shall be shown on the unit. Breaking the glass cover shall automatically operate the alarm in less than 10 seconds.

22.5.12.2 Analogue Addressable Manual Pull Handle Stations

The Manual Pull handle Stations shall be made of heavy-duty die cast metal or Lexan body and painted red colour. The unit shall be of attractive and neat appearance and shall be suitable size and type for surface or flush mounted on the walls. The unit shall be of a double action type whereby the front cover must be lifted up first before the Pull Handle can be pulled down to initiated an alarm. The unit shall be complete with station reset key.

22.5.12.3 Duct Air Sample Detection

The return air ducting for all zones of HVAC shall be protected by duct mounting detector probe units. The units shall be so designed to minimize the duct preparation work required to install the probe unit. The structure of the duct will be breached only for the insertion of the sample tube by means of two

25mm holes. The duct housing shall incorporate a polyester clear see thorough top, which will allow the detector, and detector led to be clearly seen from ground level.

The housing will be suitable for air sampling in air velocities of not less than 1m per second up to maximum of 20m per second. The velocity across the sample chamber sill is reduced to approximately

1% of the air velocity of the HVAC airflow. Probe units will be installed in straight lengths of the duct,

which are not less than 6 times the width of the duct section to ensure least turbulence at the probe unit.

22.5.13. Interface Module Common Requirements

Each interface unit for switch monitoring or output will have use DIL switched to set the address and will be of the same protocol and manufacture. As the detection devices, all interface modules will be supplied complete with LED indicators, which shall illuminate on the operation of the interface device.

22.5.13.1 Switch Monitor Units

Switch monitor units shall be provided to allow conventional to analogue connection for such devices as sprinkler flow switches, floor valve isolation (if applicable) or any such clean contact device as could be deemed necessary for inclusion within the fire system. The switch monitor unit shall be capable of receiving contact configurations of normally open or closed loop. All switch-monitoring units will be powered by the loop wiring without the need for external power source.

22.5.13.2 Input Output Units

Input output units will be provided for the connection to such items as pump start control, lift homing control, or local HVAC shut down.  As standard each input output module will corporate a set of change offer contacts to interface with the required service. The input output device shall be capable of being programmed at the control panel to allow for operation by any device on any loop. A separate 24-volt dc input will be required for the input output modules this supply must be derived from a monitored source and is battery backed up.

22.5.13.3 Sounder Circuit Controllers

Analogue addressable sounder circuit controllers shall be required; each unit shall have a unique address and be completely programmable from the fire alarm control panel. Each unit shall have a minimum output of 750 milli-amps. The addressing and switching power supply for the controller will be derived from the loop supply. However, the unit shall require a 24V d.c. supply to power the connected alarm load this supply must be derived from a monitored source and be battery backed up.

22.5.13.4 Multi Input Output Controller

Multi input output controllers shall be used for the collection of existing conventional detection or clean contact input devices. All input signals to the multi-input module will be fully monitored for open and short circuit. The multi-input unit will have minimum 8 inputs and 8 fully programmable outputs, with 2 monitored output circuits for external alarms.

The unit will be provided with 8 alarm and 8 fault LED indicators with internal buzzer and alarm silence control. The unit will generate 8 unique addresses for the conventional input lines and be fully compatible with the detector and main fire alarm control panel protocol.

Multi input output controllers will be used for the collection of the building Fire Water and Fire pumping signals suitably programmed to transmit ALERT/CHANGE OF STATE signals to the main fire alarm control panel. The following inputs will be required.

a) Pump start

b) "A" Pump Running

c) "A" Pump Fail

d) "B" Pump Running

e) "B" Pump Fail

f) Water High

g) Water Low

h) Low Pressure

The following programmed outputs will be required.

a) Pump Start (Programmed from pup start input signal and from fire panel, break glass or sprinkler flow switch alarms)

b) Pump changeover (Programmed to switch from pump "A" to pump "B" in the event of pump "A" input failure signal being received).

22.5.14. Standby Power Supply Equipment

The overall fire alarm system will be complete with a 24V D.C charger unit completes with sealed lead acid maintenance free batteries. The charging equipment will be of the approved type and be calculated in size to provide full standby back up load for a period of not less than 24hrs. with a full alarm, load for a minimum period of 2 hrs.  The battery and charger unit will be supplied in a sheet steel lockable cabinet of the same construction and finish as the main fire alarm control panel.

22.5.14.1 Battery Calculations

The full alarm load will be calculated for a period of two hours to ensure the battery terminal voltage is sufficient not to cause permanent damage to the battery cells. The charger output should be sufficient to run the full alarm load of the system in the event of battery failure. The output shall also be of sufficient capacity to run the full standby load of the system and fully recharge the battery within a 24-hour period.

22.5.15. Field Installation

Two cable system types are approved namely

a) Mineral insulated copper covered (M.I.C.C)

b) Fire resistant cable of the approved type.

Loop cables should be run separate of all other services including alarm power circuits for alarm outputs.

The minimum permitted core size will be 1.5mm2. For loop lengths of up to 1000 meters, 2.5mm2 will be used for 1000 meters to 2000 meters lengths.

22.5.15.1 Cable Terminations

All cable terminations at detectors and break glass devices will use spade type crimp connectors; all devices, which have standard enclosed terminal blocks, will use crimp pins for final termination.

22.5.15.2 Cable Markers

All cable cores will be identified using ferrules to provide numbering and symbols as required.

22.5.15.3 Spare Capacity

Each loop will populate to 80% capacity, providing 20% spare for future expansion and or change of use.

22.5.15.4 Hard Copy Program

The successful contractor shall supply for approval hard copies of all text programming information, including all input to output configurations.

23. ELECTRONIC ACCESS CONTROL SYSTEM (EACS)

23.1 Application of the section

Items described under this section shall apply to all the sub sections of this specification

23.2 General

    - This specification covers the submittals of shop drawings, sample approvals, setting to work, supply, installation, inspection, testing & commissioning, as built drawings and operation and maintenance manuals and periodic maintenance.

    - The Tenderer’s shall read this section in conjunction with Tender drawings and Bill of Quantities. They shall clarify any discrepancies between tender drawings and Bill of Quantities.

    - The Tenderer shall submit their offer complying with all the conditions of contract, specification, tender drawings and Bill of Quantities.

    - EACS System supplier with more than 5-year experience shall supply and install the system.

    - Specification, drawings and BOQ are meant to provide sufficient information to the tenderers and it is the contractor’s responsibility to supply and install complete systems to working order.

    - All the sub systems under this section shall be supplied, installed, tested & commissioned by the respective contractors.

23.3 Operation and Maintenance Manuals

The Contractor shall submit 3 copies of Operation & maintenance Manuals, which shall contain Product literature, Specific operating instructions and Maintenance instructions.

23.4 Approval Of information Submitted

The Consulting engineer has the right to decide the adequacy of information submitted by the contractor and request further information as necessary if required

23.5 Testing and commissioning of Systems

The contractor shall perform all the equipment and devices testing as directed by the Consulting Engineer.  The Contractor shall bear the cost for such tests and any items found defective shall be replaced at no extra cost.  Such replaced items shall be re- tested for verification.

23.6 Equipment, Materials, Fittings and Accessories

The equipment, material used, fittings and devices shall comply with the Architectural and design criteria, design concepts and performance requirements.

When selecting products the contractor shall consider the space limitations, weight limitations, compatibility with other existing devices and systems.

Contractor shall obtain approval from consulting engineer for all the equipment, material, fittings and accessories before commencing installation.

All the products supplied under this contract shall be guaranteed for a period of one (1) year from the final handover date.

23.7 Product Brands

All the Materials, Equipment and Devices and Accessories supplied under this contract shall bear the Manufacturer names and make.  The consulting Engineer has the right to accept or reject any Equipment, Material and device brands based on the past performance records.

23.8 Drawings

The contractor shall familiarize himself with the site conditions before preparing shop drawings.  He shall verify the dimensions shown in the drawings and advise the consulting engineer any discrepancies.

The contractor shall submit 3 copies of shop drawing for approval.  Contractor shall obtain approval for shop drawings before commencing installation work.

23.9 Maintenance Access and Openings

The contractor shall provide all necessary access openings where required for maintenance.

23.10 Codes and Standards

All equipment, materials and workmanship shall conform to the relevant British Standards, Maldives Standards and codes of Practice.  All electrical installations shall comply with 17th Edition of IEE wiring regulations. Keep 30cm distance from electrical and other interference sources or use metal enclosed earthed conduits/trunks if the distance could not be maintained.

Use earthed metal enclosure to install control panels in service ducts. The shield of all cables shall be earthed at control panel and the other end should be kept open.  Joints in cables shall not be permitted.

23.11 SYSTEM DESIGN

The system shall be designed taking into account following specification, tender drawing and the client requirement by specialist contractor with experience in the trade to provide a reliable access control solution.

The EACS system must have standalone two door controllers installed in service ducts. It should control two doors, i.e., two proximity readers, monitoring two door sensors, two push buttons & monitor two emergency door release units. Every control panel should be connected to EACS server via Ethernet. The card access rights should be able to program in EACS software and it could be uploaded to panels. The access rights should be based on combination of weekday, holidays, time zones & card reader. The control panels must be in normal operation even after shutting down the server. The events shall be automatically buffered in control panel until the server comes on line. Subsequently, the buffered events shall be automatically downloaded to server. No data losses shall experience in any condition.

Valid card, Invalid card, Inactive card, Invalid time zones, Door Ajar, Door forced open, Push Button pressing, Emergency door release press events should be reported in software real-time and it should be recorded.

The emergency door release unit shall directly disconnect EML power on activation. All alarms should popup and should be audio alerted.

All predefined doors should be open in fire alarm condition. It could be activated through EACS server automatically. A normally open dry contact will be provided at fire alarm panel for fire integration.

The system should able to produce history reports of all events.

The EACS database backup should weekly uploaded to given location automatically (Scheduled backup).

Backups, time & date updates of control panels should be able to scheduled. The panel date & time should be synchronized with server time automatically once a week.

The user rights for system monitoring & card programming (adding, editing & deleting) should be able to separately assign.

Control panel & field equipment shall be modular in construction. Exact location of readers, push buttons, BGU & locks shall be proposed by architect. The positions shown are suggested locations in public areas as shown in the drawings.

23.12 SYSTEM PERFORMANCE CRITERIA

The system performance criteria shall follow international agreed standards and local regulations.  They shall be, but not be limited, to the following:

- Door opening on valid card

- Opening of door for push button

- Directly disconnects lock power when emergence door release is pressed

- Proximity reader LED color change in valid card

- Real-time status reporting and events recording in database

- Data base backup & restoring

- (Automatic) scheduled backup

- (Automatic) scheduled Panel date & time update

- Manual door opening through EACS software

- Open door on fire alarm condition

23.13 GENERAL REQUIREMENT OF EACS EQUIPMENT

- General

All equipment to be supplied under this specification shall be new and the current model of a standard product of a Manufacturer of record.  A Manufacturer of record shall be defined as a company whose main occupation is the manufacture for sale of the items of equipment supplied.

- Maintains a factory production line for the item submitted.

- Maintains a stock of replacement parts for the item submitted.

- Maintains engineering drawings, specifications, and operating manuals and for the items submitted.

- Has published and distributed descriptive literature and equipment specifications on the items of equipment submitted at least 30 days prior to the tender issue.

Specifications of equipment as set forth in this specification are minimum requirements, unless otherwise stated, and shall not be construed as limiting the overall quality, quantity or performance characteristics of items furnished in the EACS system.  When the Contractor furnishes an item of equipment for which there is a specification contained herein, the item of equipment shall meet or exceed the specification for that item of equipment.

The total EACS system shall be installed so that the combination of equipment actually employed should work as a full functioning system which does not produce any undesirable visual or aural effects such as signal distortions, noise pulses, glitches, hum bars, transients, ghosting, etc.

23.14 REGULATIONS AND CODE OF PRACTICE

It shall be the Contractor’s responsibilities to ensure that the whole EACS system shall comply with all statutory, regulations and requirements of all authorities having jurisdiction over the work.

23.15 TESTING

The Contractor shall make all the necessary setting of the equipment after installation. The programming of door open time, Shunt times of door sensor shall be adjusted to suit the usage. All settings shall be clearly marked upon final adjustments.

The contractor shall carry out performance tests in the presence of the Engineer with prior approved test methodology.

23.16 Item Specifications

| PROPOSED HITHADOO REGIONAL HOSPITAL |  |  |  |  |
| --- | --- | --- | --- | --- |
| EACS |  |  |  |  |
| Technical Specifications |  |  |  |  |
| Item Number: 2 . SMART Card Readers |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Smart Card compatibility |  | ISO 15693, ISO 14443B4 on 13.56MHz |  |  |
| Indicators | Audio | Inbuilt buzzer |  |  |
|  | Host LED control | single tri-color (green-yellow-red) |  |  |
| Tamper output |  | Optical sensor |  |  |
| Output |  | Wiegand output |  |  |
| IP Rating |  | IP55 |  |  |
| Mounting Size |  | Switch plate size, single-gang electrical box |  |  |
| Typical Read Ranges |  | 3" |  |  |
| Operating Voltage |  | 5 - 16 VDC from control panel |  |  |
| Operating Temperature |  | 31º to 150º F (-35º to 65º C) |  |  |
| Operating Humidity |  | 5 to 95% relative humidity (non-condensing) |  |  |
| Approvals |  | USA : FCC ,Europe: CE Mark Approval |  |  |
| Other |  | Should work with reader/control panel/EACS software |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number: 3. Finger Print Readers |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Interface |  | Ethernet TCP/ IP |  |  |
| Fingerprint verification |  | 1:1 and 1:N |  |  |
| Fingerprints templates |  | 500 or better |  |  |
| No. of Transactions |  | 30000.00 |  |  |
| Fingerprint sensor |  | Optical fingerprint sensor without film |  |  |
| USB Interface |  | Available |  |  |
| False Rejection Rate |  | ≤0.01% or better |  |  |
| Web Server support |  | Available |  |  |
| First In- Last Out Report |  | Available |  |  |
| Multiple shift base configuration extend to two days |  | Available |  |  |
| Time & Attendance Management software |  | Included |  |  |
| Finger enrolment software |  | Included |  |  |
| Fingerprint Enrolment |  | Possible |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |

| Item Number: 5. Push Button |  |  |  |  |
| --- | --- | --- | --- | --- |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Type |  | Proximity |  |  |
| Operating Voltage |  | 5.0 - 12 VDC (works from control panel power) |  |  |
| Output |  | Normal open & Normally closed dry contact |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number: 6. Emergency Door Release |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Colors |  | Green |  |  |
| Output |  | Dry contact, Normally Close/ Normally open two contact, 2A/24VDC |  |  |
| Type |  | Plastic Resettable, No replacing items required to reset when unit is activated |  |  |
| Size |  | Switch plate size, single-gang electrical box |  |  |
| Item Number: 7. Electromagnetic lock with door position sensor |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Holding Force |  | 1200 lbs |  |  |
| Mount |  | Surface Mount |  |  |
| Construction |  | Magnet & Armature plate |  |  |
| Voltage Spike Suppressor |  | Available |  |  |
| Operating Voltage |  | Dual Voltage 12V / 24 V |  |  |
| Door Sensor |  | Available |  |  |
| Indication |  | LED dual color |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |

| Item Number: 8. Control Panel |  |  |  |  |
| --- | --- | --- | --- | --- |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Make |  |  |  |  |
| Model |  |  |  |  |
| Country of origin |  |  |  |  |
| Features |  |  |  |  |
| Operation | server off-line | Available |  |  |
| Connectivity | With server | Ethernet |  |  |
|  | With Proximity readers | Wiegand |  |  |
| Card Database |  | 10,000 cards or better |  |  |
| Transaction buffer |  | 25,000 transactions or better |  |  |
| Access level |  | 100 or better |  |  |
| Holidays |  | 200 or better |  |  |
| Time zone |  | 100 or better |  |  |
| Card reader formats |  | Wiegand format support |  |  |
| Credential facility codes |  | 6 or better |  |  |
| Dedicated tamper alarm |  | Available |  |  |
| Dedicated power fail alarm |  | Available |  |  |
| Real time clock |  | Available |  |  |
| Onboard I/O |  | 2 Readers, 8 Supervised inputs, 4 Relay outputs |  |  |
| Operational modes |  | Card only & Card and PIN |  |  |
| Anti-Passback support |  | Local, Global, Forgiveness |  |  |
| Approvals |  | USA and Canada: FCC ,Europe: CE Mark Approval |  |  |
| Humidity |  | 0 to 85% RHNC |  |  |
| Temperature |  | 0 to 50° C |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |

| Item Number: 9. Control Panel Enclosure |  |  |  |  |
| --- | --- | --- | --- | --- |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Features |  |  |  |  |
| Type |  | Metal, Powder coated, lockable |  | - |
| Size |  | Suitable to install control panel, power supply |  |  |
| Ventilation |  | Suitable for heat dissipation from control Panel/power supply |  |  |
| Tamper |  | Enclosure door tamper condition reports EACS software via control panel |  |  |
| Knockouts |  | Provision of knockouts |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |

| Item Number: 10. EACS Software |  |  |  |  |
| --- | --- | --- | --- | --- |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Features |  |  |  |  |
| Edition |  | Standard or Professional (Not Express version) |  |  |
| event monitoring |  | Real Time |  |  |
| Alarm monitoring |  | Control and response, including acknowledge, clear and annotate, Audible notification |  |  |
| Door modes |  | PIN Only, Card+PIN, Card or PIN, Card Only |  |  |
| Reporting |  | History Reports, Export facility, database info reports |  |  |
| Anti-pass back |  | Hard or Soft |  |  |
| Floor plan |  | GUI to locate devices |  |  |
| License |  | 5 user clients |  |  |
| Holiday types |  | 2 or better |  |  |
| Card numbers |  | up to 20 digits or better |  |  |
| Database Backup/Restore |  | Available |  |  |
| Scheduling Control panel Sync |  | Available |  |  |
| Manage the system from more than one workstation |  | Available |  |  |
| Server Application supported operating System |  | Windows Server 2012 R |  |  |
| Client Application supported operating system |  | Windows 7 Professional (64 bit) |  |  |
| Database |  | SQL Server 2012 Express or better |  |  |
| operator user right defining |  | Customizable |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |

| Item Number: 11. Smart Card |  |  |  |  |
| --- | --- | --- | --- | --- |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Features |  |  |  |  |
| Dimensions |  | 2.125" W x 3.370" H x 0.030" T (5.4cm W x 8.6cm H x 0.076cm T) |  | - |
| Finish |  | Gloss White |  |  |
| Construction |  | PVC Laminate |  |  |
| ISO Standards |  | ISO 15693, ISO 14443B4 on 13.56MHz |  |  |
| Operating Temperature |  | -40° - 158° F (-40° - 70° C) |  |  |
| Operating Humidity |  | Operating Humidity |  | - |
| Application AREA |  | 16 or better |  |  |
| Other |  | Should work with reader/control panel/EACS software |  |  |
| Accessories |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number: 15. EACS server |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Features |  |  |  |  |
| OS |  | Windows Server 2012 R |  |  |
| Processor |  | Intel® Xeon® or better |  |  |
| Miscellaneous |  | Branded unit |  | - |
|  |  | Must complied to EACS software requirements |  |  |
| CPU |  | 2.8GHz or better |  |  |
| RAM |  | 8 GB or better |  |  |
| HDD |  | 500GB or better |  |  |
| Network |  | 100Mbps |  |  |
| Database |  | SQL Server 2012 Express or better |  |  |
| Accessories |  | DVD Writer |  |  |
|  |  | Monitor 19" or better |  |  |
|  |  | Any required accessory not specifically referred to install/use the equipment |  |  |
| Item Number: 14. EACS Client PC |  |  |  |  |
| DESCRIPTION |  |  | Bidder's Response | Page No. |
| Features |  |  |  |  |
| OS |  | Windows 7 Professional (64 bit) or better |  |  |
| Processor |  | Intel® Core™ i5 or better |  |  |
| Miscellaneous |  | Branded unit |  | - |
|  |  | Must complied to EACS client software requirements |  |  |
| CPU |  | 3.1 GHz or better |  |  |
| RAM |  | 8 GB or better |  |  |
| HDD |  | 500GB or better. |  |  |
| Network |  | 100Mbps |  |  |
| Accessories |  | DVD Writer |  |  |
|  |  | Monitor 19" or better |  |  |
|  |  | Any required accessory not specifically referred to install/use the equipment |  |  |

24. NURSE CALL SYSTEM SPECIFICATION

24.1 SYSTEM DESIGN

The system shall be designed taking into account following specification, tender drawing and the client requirement by specialist contractor with experience in the trade to provide a reliable emergency call system.

The user calls for assistance by activating a ceiling pull, standard call point. A confidence light on the calling device illuminates to reassure the user that the call has been registered. At the system’s indicator panel-Nurse Control Panel (s), an indicator light illuminates and a buzzer sounds to inform staff that someone is in need of assistance. Relevant over door lights (if available) also operate (as fitted) to provide additional visual indication of the call. A member of staff visits the calling room to assist the user and resets the calling device to return the system to normal. The following shows sample items for reference.

The master reset button of system’s indicator panel-Nurse Control Panel should be able to enable or disable as this facility allows standard calls to be globally cancelled without the source of the call being investigated. The “Mute” button allows any standard calls on the system to be silenced but it leaves relevant indicator light(s) lit. Although a new call from a different call point will re-activate the sounder.

Exact location of call points & remote indicators, etc. shall be proposed by architect. The positions shown are suggested locations in areas as shown in the drawings.

24.2 SYSTEM PERFORMANCE CRITERIA

The system performance criteria shall follow international agreed standards and local regulations.  They shall be, but not be limited, to the following:

The system performance criteria shall follow international agreed standards and local regulations.  They shall be, but not be limited, to the following:

- Test call registering of each call point in Nurse Control Panel

- Test Visual and audible alert generate at Nurse Control Panel by each call point

- Test call resetting of each call point

- Test remote indicator function

24.3 GENERAL REQUIREMENT OF NURSE CALL SYSTEM EQUIPMENT

General

All equipment to be supplied under this specification shall be new and the current model of a standard product of a Manufacturer of record.  A Manufacturer of record shall be defined as a company whose main occupation is the manufacture for sale of the items of equipment supplied.

- Maintains a factory production line for the item submitted.

- Maintains a stock of replacement parts for the item submitted.

- Maintains engineering drawings, specifications, and operating manuals and for the items submitted.

- Has published and distributed descriptive literature and equipment specifications on the items of equipment submitted at least 30 days prior to the tender issue.

Specifications of equipment as set forth in this specification are minimum requirements, unless otherwise stated, and shall not be construed as limiting the overall quality, quantity or performance characteristics of items furnished in the Nurse Call system.  When the Contractor furnishes an item of equipment for which there is a specification contained herein, the item of equipment shall meet or exceed the specification for that item of equipment.

The total nurse call system shall be installed so that the combination of equipment actually employed does not produce any undesirable visual or aural effects such as signal distortions, noise pulses, glitches, hum bars, transients, ghosting, etc.

All trunk, branches and interconnecting cables and unused ports/taps shall be terminated.

24.4 REGULATIONS AND CODE OF PRACTICE

It shall be the Contractor’s responsibilities to ensure that the whole nurse call system shall comply with all statutory, regulations and requirements of all authorities having jurisdiction over the work.

24.5 TESTING

The Contractor shall make all the necessary setting of the equipment after installation. The call registering, resetting shall be tested in each call point to suit the usage. All settings shall be clearly marked upon final adjustments.

The contractor shall carry out performance tests in the presence of the Engineer with prior approved test methodology before handling over the system.

24.6 ITEM SPECIFICATION

| Item Number : 2 . Emergency Mater Panel (Nurse Station Panel) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DESCRIPTION |  |  |  |  |  |  | Bidder's Response |  | Page No. |  |
| Make |  |  |  |  |  |  |  |  |  |  |
| Model |  |  |  |  |  |  |  |  |  |  |
| Country of origin |  |  |  |  |  |  |  |  |  |  |
| Features |  |  |  |  |  |  |  |  |  |  |
| Zone capacities (Number of zones supported by a single panel panel) |  |  | 10 |  | Available |  |  |  |  |  |
|  |  |  | 20 |  | Available |  |  |  |  |  |
|  |  |  | 30 or better |  | Available |  |  |  |  |  |
| Availability of indicator light to inform an activation of call button |  |  |  |  | Available |  |  |  |  |  |
| Possibility of observe all active calls simultaneously |  |  |  |  | Possible |  |  |  |  |  |
| Ability to identify bed numbers of call points activated simultaneously |  |  |  |  | Possible |  |  |  |  |  |
| Availability of buzzer sounds to inform an activation of call button |  |  |  |  | Available |  |  |  |  |  |
| Buzzer sound level |  |  |  |  | 60dB/A or better |  |  |  |  |  |
| Simultaneous call notification (Any number of call button activations notify on the panel) |  |  |  |  | Available |  |  |  |  |  |
| Methods of reset - Reset key or Reset button |  |  |  |  | Available |  |  |  |  |  |
| Master reset button(calls to be globally cancelled) |  |  |  |  | Available |  |  |  |  |  |
| Master reset button Enable/Disable facility |  |  |  |  | Available |  |  |  |  |  |
| Mute buttons |  |  |  |  | Available |  |  |  |  |  |
| Mute button silence calls but it leaves relevant indicator light(s) lit |  |  |  |  | Available |  |  |  |  |  |
| Mute button Enable/Disable facility |  |  |  |  | Available |  |  |  |  |  |
| Muted panel re-activate sound when a new call is received |  |  |  |  | Available |  |  |  |  |  |
| Battery backup with charging |  |  |  |  | 2 hours or better |  |  |  |  |  |
| Supply voltage |  |  |  |  | 230V AC |  |  |  |  |  |
| Operating Voltage |  |  |  |  | 12V DC |  |  |  |  |  |
| System Type |  |  |  |  | Wired zones |  |  |  |  |  |
| Accessories |  |  |  |  | Any required accessory not specifically referred to install/use the equipment |  |  |  |  |  |
| Item Number : 4. Button Reset Emergency Call Point without tail call lead |  |  |  |  |  |  |  |  |  |  |
| DESCRIPTION |  |  |  |  |  |  | Bidder's Response |  | Page No. |  |
| Make |  |  |  |  |  |  |  |  |  |  |
| Model |  |  |  |  |  |  |  |  |  |  |
| Country of origin |  |  |  |  |  |  |  |  |  |  |
| Features |  |  |  |  |  |  |  |  |  |  |
| Powering |  |  |  |  | By Master panel |  |  |  |  |  |
| confidence light (Availability of light on the calling device which illuminates to reassure the user that the call has been registered in master panel) |  |  |  |  | Available |  |  |  |  |  |
| Reset Method |  |  |  |  | Button Reset |  |  |  |  |  |
| Remote socket for tail call lead |  |  |  |  | Available |  |  |  |  |  |
| Tail call lead |  |  |  |  | Not available |  |  |  |  |  |
| Calling method |  |  |  |  | Button call point |  |  |  |  |  |
| Size |  |  |  |  | Standard switch box size, compact |  |  |  |  |  |
| Accessories |  |  |  |  | Any required accessory not specifically referred to install/use the equipment |  |  |  |  |  |
| Item Number : 5. Button Reset Emergency Call Point with tail call lead |  |  |  |  |  |  |  |  |  |  |
| DESCRIPTION |  |  |  |  |  |  | Bidder's Response |  | Page No. |  |
| Make |  |  |  |  |  |  |  |  |  |  |
| Model |  |  |  |  |  |  |  |  |  |  |
| Country of origin |  |  |  |  |  |  |  |  |  |  |
| Features |  |  |  |  |  |  |  |  |  |  |
| Powering |  |  |  |  | By Master panel |  |  |  |  |  |
| confidence light (Availability of light on the calling device which illuminates to reassure the user that the call has been registered in master panel) |  |  |  |  | Available |  |  |  |  |  |
| Reset Method |  |  |  |  | Button Reset |  |  |  |  |  |
| Remote socket for tail call lead |  |  |  |  | Available |  |  |  |  |  |
| Tail call lead |  |  | Availability |  | Available |  |  |  |  |  |
|  |  |  | Length |  | 1.8m (6ft) |  |  |  |  |  |
| Calling method |  |  |  |  | Button call point or removing tail call lead |  |  |  |  |  |
| Size |  |  |  |  | Standard switch box size, compact |  |  |  |  |  |
| Accessories |  |  |  |  | Any required accessory not specifically referred to install/use the equipment |  |  |  |  |  |
| Item Number : 6. Button Reset Emergency Call Point with ceiling pull code |  |  |  |  |  |  |  |  |
| DESCRIPTION |  |  |  |  | Bidder's Response |  | Page No. |  |
| Make |  |  |  |  |  |  |  |  |
| Model |  |  |  |  |  |  |  |  |
| Country of origin |  |  |  |  |  |  |  |  |
| Features |  |  |  |  |  |  |  |  |
| Powering |  |  | By Master panel |  |  |  |  |  |
| confidence light (Availability of light on the calling device which illuminates to reassure the user that the call has been registered in master panel) |  |  | Available |  |  |  |  |  |
| Reset Method |  |  | Button Reset. |  |  |  |  |
| Remote socket for tail call lead |  |  | Not Available. |  |  |  |  |
| Tail call lead | Availability |  | Not Available |  |  |  |  |  |
| Calling method |  |  | Pull code |  |  |  |  |  |
| Size |  |  | Standard switch box size, compact |  |  |  |  |  |
| Accessories |  |  | Any required accessory not specifically referred to install/use the equipment |  |  |  |  |  |
| Features |  |  |  |  |  |  |  |  |
| Item Number : 7. Over Door Indicator (Remote Indicator) |  |  |  |  |  |  |  |  |
| DESCRIPTION |  |  |  |  | Bidder's Response |  | Page No. |  |
| Make |  |  |  |  |  |  |  |  |
| Model |  |  |  |  |  |  |  |  |
| Country of origin |  |  |  |  |  |  |  |  |
| Features |  |  |  |  |  |  |  |  |
| Indication |  |  | Light Illumination |  |  |  |  |  |
| Size |  |  | Standard switch box size, compact |  |  |  |  |  |
| Accessories |  |  | Any required accessory not specifically referred to install/use the equipment |  |  |  |  |  |

25. PRIVATE AUTOMATIC BRANCH EXCHANGE (PABX) SPECIFICATION

25.1 Scope of work

The work to be carried out under this tender specification shall consist of the supply, delivery to site, installation, testing, commission, handover in approved work order and maintenance during the defects liability of period of a proposed digital private automatic branch exchange (PABX) in accordance to the specification, supplementary notes, condition of contract, drawing attached herewith.

Cabling and any necessary trunking or cable trays from the Telekom main distribution frame to the PABX room shall be included in the tender price.

Tenderer shall liaison with relevant Local Telecommunication Authority, for lines application, testing and commissioning of the incoming lines to ensure the PABX system is fully functional in accordance to the works schedule.

Tenderer shall provide basic operation and maintenance training of the PABX system, digital phones, call billing system and Administration Tools to the company staff and company in-house maintenance team.

25.2 PABX system in general

The proposed PABX shall be fully digital and adhere to ITU-T recommendations for A-Law PCM switching.

The proposed PABX system shall use the same hardware and software across all line size and modular in design. Expansion shall only involve adding of cards and shelves or line trunk units in the existing cabinet. PABX system that uses different type of cards in different shall not be consider at all.

The proposed PABX system shall be have ‘Universal Port Architecture, design to allow flexible system configuration and maximum utilization of all available card slots.

The proposed PABX shall be a fully non-blocking system. The traffic flow of the proposed PABX system shall be 1 Erlang per port. The number of ports supported shall be met by the same number of time slots in the PABX switching matrix.

The system shall facilitate expansion from the initial proposed capacity to the maximum capacity of 5,000 users by only addition of cards and shelves in the existing cabinet of the offered PABX.

The proposed PABX system shall support the same features and applications across all the line sizes without having to upgrade to the next higher model. The only cost that will incur in the future shall due to the expansion of present capacity only. PABX system that involve changing of whole system and cards for expansion from the present model to the next higher model shall not be considered at all. The proposed PABX system shall support the following features without any software upgrade:

•	Normal PABX features

•	Networking

•	IP Telephony

The ISDN primary rate interface (PRI) shall be supported as incoming to the proposed PABX system. The software needed for ISDN applications shall be a standard package of the proposed PABX system and shall not incur any cost. The PABX system shall support both: -

• 	Decadic pulse and dual tone multi-frequency DTMF) based analogue/single line extension telephone sets

• 	2-wire digital extension telephone sets using ITU-TU interface signaling protocol in any combination

• 	Single line telephone set with RJ11 data port built-in.   These single line phones shall be in either one line or two lines.

The proposed PABX system shall be able to connect to 100% digital telephone sets up to its maximum capacity.

The proposed PABX system shall be able to restart automatically without human intervention when the external AC power supply is resumed after complete power failure, where backup batteries are also depleted.

Tenderer shall supply a modem together with the proposed PABX system for automatic system failure alert or remote maintenance purposes.

The proposed PABX system shall support multi-signaling protocol such as MFC R2, DPNSS, Q-sig and ISDN on digital 2Mbps link.

The proposed PABX system shall support multi-carriers. The communication links shall be bi-directional on any of the 64kbps channel.

25.3 SYSTEM HARDWARE

The designed/architecture of the proposed PABX system must meet the following requirement: -

a.	Client/Server model using LAN technology

b.	Standard market components such as Intel processor

c.	No traffic saturation whatever the number of users

d.	Common bus absence, a problem of one link does not interfere with the other links.

e.	Decentralized functions on all interfaces; switching, tone detection, conference.

f.	Decentralized power supply on all boards. Modules that are require power supply will not be considered.

The tenderer shall supply external rectifier as charger to the backup batteries and to convert the power supply from AC to DC.

The proposed PABX system shall be placed in an air-conditioned PABX room. The ambient condition of the PABX room shall be as follows to ensure optimum system performance.

Room temperature: 16 - 40°C	    Absolute humidity :6 - 18 g H2O/m2     	   Relative humidity: 20 - 70%

The proposed PABX system shall be ventilated by convection air flow. No cooling fans shall be used in any part of the PABX cabinets.

The proposed PABX system shall use a same set of line, trunk and other interface cards across all the line sizes or models within the same family. The initial investment shall be protected when proposed PABX system is expanded later.

The analogue extension cards of the proposed PABX system shall have 32 circuits each and in the form of 2-wire connection.

The digital extension cards of the proposed PABX system shall have 32 circuits each and in the form of 2-wire connection.

The analogue trunk cards of the proposed PABX system shall have 8 circuits each.

The module that houses all the line cards must be based on universal card slots with minimum 14 slots per cabinet.

The digital extension card must not only support the digital telephone but also the DECT base stations. Tenderer shall supply one lot of high-quality maintenance free sealed lead acid batteries with battery racks for 4 hours power back-up together with the proposed PABX system. These batteries shall be connected to the PABX charger. Tenderer shall submit some battery data sheet together with the submission.

The proposed PABX system shall come with a dump terminal as system administration and maintenance terminal.

25.4 SYSTEM SOFTWARE

The proposed PABX system shall use the Unix Chorus real time micro-kernel open operating system. The operating system shall control the execution of the system programs and administration of the PABX resources.

The software is structured in three (3) layers:

a.	The Unix Chorus real time micro-kernel supervises the other two layers

b.	The interface layer (APIs) allows the applications to communicate with the CPU and guarantees real time processing.

c.	The application layer with the real time applications servers and the Unix applications servers

The proposed PABX system shall have uniform system software for all the line size models within the same PABX family.

The system software shall be stored in a hard disk. The system software can be back-up in diskettes.

25.5 SYSTEM CAPACITY

The proposed PABX system shall be equipped with the following capacity: -

Description 			 			      	          Capacity

The number of C.O. lines					10

The number of analogue extensions				250

The number of digital extensions				5

The number of Screen based attendant consoles		1

The power failure transfer unit0					-

The music on hold facility					1

Duplicated CPU for Redundancy					1

The following telephone sets shall be supplied together with the PABX system: - X Number of single line phone for analogue extensions.

X Number of 2-wire digital phone with display, programmable feature buttons and semi-handsfree. X Number of 2-wire digital phone with display, programmable feature buttons and full-handsfree.

25.6 NUMBERING PLAN

The proposed PABX system shall variably numbering scheme where a combination of extension numbers from 1 digit to 6 digits is supported.

The proposed PABX system shall have a flexible numbering plan. Both closed and open numbering plan shall be supported.

25.7 PABX FEATURES AND FACILITIES

25.7.1 Alternating between two parties

The proposed PABX system shall allow a user to switch back and forth between 2 connections either internal or external as often as possible. During this process, one party is connected to the user while the other is being on hold and provide with system music-on-hold.

25.7.2 Authorization code and password for call billing identification.

The proposed PABX system shall be able to request the users to enter an authorization code or a password via the keypad before making a call. The code shall be captured by the call detail recording system together with the number dialed to billing identification purposes.

25.7.3 Automatic Ringback for Transferred Unanswered Calls

Incoming calls transferred by an extension to the destination extensions shall ring back automatically at the extension where the calls are transferred if these calls are not answered by the destination extensions within a period of time. This feature shall be applicable to all PABX extensions including the attendant console.

25.7.4 Call Back - Busy and No Answer

An extension calling a busy extension or an extension with no answer shall be able to enter a code for back request and as soon as the busy extension is free or the no answer extension is used once, both the calling extension and destination extension are automatically rung and connected upon answering.

25.7.5 Call Forward

This service feature shall allow all calls destined for an extension to be forwarded to another extension or to the PABX operator regardless of the state of the extension, whether it is busy or idle.

25.7.6 Call Hold

This feature shall enable an extension user to hold an ongoing call and free his line to initiate another call or request for a service feature.

25.7.7 Call Park

This feature shall enable an extension user to park his existing call and retrieve the call from any other telephone by dialing a pre-arranged code.

25.7.8 Call Pick-up

Incoming calls to an extension in a group of extensions with call pick-up facility shall be able to be picked up by any extension within the same group by just dialing a code. There shall be no limit for the number of analog extensions per group or 25 digital extensions per group.

25.7.9 Call Tracing

This feature shall print out the number of a caller on a printer for logging purpose.

25.7.10 Call Transfer

This feature shall permit an extension user to transfer an existing call to another extension without the assistance of the PABX operator.

25.7.11 Camp-on

This feature shall enable to calling extension that calls a busy extension to hold the call in a special waiting mode and send a comp-on tone indication to the busy extension. When the busy extension becomes idle, it is automatically rung and connected to the waiting trunk call.

25.7.11 Class of Service

This service feature permits all extensions to be assigned a class of service in accordance with the degree of feature usage desired. The proposed PABX system shall be able to provide class of service to all its users. 16 group of class of service shall be possible. Each user shall have 2 class of service. The class of service shall be switchovered by attendant console or by entering a password (12 digits maximum) by the user on the telephone set or automatically at predefined time.

25.7.12 Day/Night Class of Service

This feature shall enable any extension to alternate between two different class of service - one for day and another for night. The PABX system shall be programmed in such a way that the class of service of extension will change automatically when night service is activated by the PABX operator.

25.7.13 Conference - 3 parties

This feature shall allow an extension user to add another extension user of the same PABX

system to an existing connection for a 3-party conference.

25.7.14 Decadic Pulse and DTMF Dialing

The proposed PABX system shall support telephone sets with decadic and DTMF dialing.

25.7.15 Digit Translation

The proposed PABX system shall be able to delete or insert digits from the string of digits dialed by the users. The PABX system shall convert up to 6 digits.

25.7.16 Direct Digital Interface

This proposed PABX system shall be able to be connect to private or public 2Mbps network. The transmission medium shall be twisted copper pair.

25.7.17 Direct Inward Dialing

This feature shall enable incoming calls to reach the extension without operator assistance. The calls shall dial 3 digit or 4-digit prefix allocated by Telekom Malaysia and follow by the

4 digit or 3-digit extension number they wish to reach.

25.7.18 DISA

The proposed PABX shall enable the user to dial to the PABX system to obtain a connection to dial out to another destination using normal CO trunks, tie trunks or leased lines. This feature shall be able to be protected by a password to prevent unauthorized usage of the facility. In the event of PABX dials out using CO lines, the proposed PABX system shall be able to drop the connection immediately upon termination of call to avoid excessive billing by Telekom Malaysia. The user shall pay only local call charges for the call to PABX and the rest of the call charges shall be billed to the PABX system.

25.7.19 Distinctive Ringing

The PABX system shall be able to have distinctive ringing tones for internal and external calls.

25.7.20 Display

The digital telephone set with display shall have the flexibility to display one of the following modes:

• 	The calling number and name of caller (internal calls and external calls if call line identification is possible).

• 	The calling number only (internal calls and external calls if call line identification is possible).

• 	The calling name only (internal calls and external calls if call line identification is possible).

25.7.21 Display During Calls

The calling party’s number shall be displayed at digital telephone set being reached with display together with the ringing tone. In case of incoming line without call line identification, only incoming calls are displayed. As for internal calls, the name and number of the calling extension shall be displayed.

25.7.22 Display During Dialing

The proposed PABX system shall allow the number being dialed to be displayed at digital telephone set with display. In case of internal calls, the name of the destination extension shall also be displayed throughout the conversation.

25.7.23 Do Not Disturb

The extension user shall be able to enter a code from his/her telephone set to prevent incoming calls. During this time, outgoing calls are still possible from this extension. However, the attendant console and urgent calls shall override this do not disturb status.

25.7.24 Howler Tone

The proposed PABX system shall send howler tone to an extension which remains in an off-hook state for a pre-assigned duration or to an extension which has not replaced the handset properly after finishing a call and alert the user to replace the handset properly.

25.7.25 Hotline Service

This feature shall allow an extension to call another pre-assigned extension by merely lifting the handset. There shall be two types of hotlines: immediate and timed delay. For immediate hotline, the predetermined extension shall be immediately rung by lifting of the handset of the hotline phone. For timed delay hotline service, the predetermined extension shall be rung after the time out delay by lifting of the handset of the hotline phone.

25.7.26 Music on Hold

This feature shall provide music to a party who is being on hold under conditions such as consultation hold, call transfer, etc.

25.7.27 Night Service

The proposed PABX system shall direct all incoming calls to a pre-arranged extension, a group of extensions or a bell for attention after working hour.

25.7.28 Number Redial

The extension user shall be able to store any internal numbers up to 6 digits or external numbers up to 22 digits for subsequent redial purposes.

25.7.29 On-hook Dialing

The proposed PABX system shall allowed all users with digital telephone sets to originate an internal or external call by dialing the number straight away with the handset on-hook and without activating the speaker button.

25.7.30 Password protection for administration extension

The proposed PABX system shall enable the company administration staff to lock their phones whenever required to prevent unauthorized staff from making any long-distance calls.

25.7.31 Power Failure Transfer

The PABX system shall be equipped with the power failure transfer unit to switch over the incoming lines to some pre-determined single line telephone sets in the event of complete power failure to enable the users to communicate with outside world.

25.7.32 Speed Dial - System

The proposed PABX system shall support 1,000 speed dial numbers which are accessible by all PABX users. Each speed dial number shall be up to 22 digits maximum. These speed dial numbers shall be divided into system list (accessible by everybody) and department list (accessible by users in that particular department only). The numbers for the system speed dial lists shall be programmed by the system administration and maintenance terminal.

25.7.33 Speed Dial - Individual

Besides the system speed dial list, the proposed PABX system shall have individual speed dial list for each user. These individual speed dial lists shall be maintained by the user himself/herself. Each individual speed dial list shall have 10 numbers maximum and each number shall be up to 22 digits long.

25.7.34 Timed reminder service

The proposed PABX system shall allow an extension user to enter a time from his/her telephone set for automatic ring back at the pre-set time and deliver a reminder message. The system shall support 1 time reminder per analog extension and 20-time reminders per digital extension.

25.8. PC BASED ATTENDANT CONSOLE

The proposed PABX system shall be equipped with attendant console with Handset and Headset and utilized the PC monitor only.

In the event of the failure of the PC monitor, the attendant console must still operate under normal circumstances except without display.

The attendant console shall be connected to a digital extension of the PABX system using a 8-wire connection.

The monitor of the attendant console shall display the day, date, time, internal and external call queue counter, calling extension, call process and the status of the extensions. Attendant consoles with LED display will not be considered as it will not display sufficient information to the operators and the display will be difficult to see in dim lighting conditions.

When the operators are free, the attendant consoles shall generate audible and visual call indication whenever there are incoming calls to alert the operators. The loudness of the call indication shall be adjustable.

When the operators are engaged with a call, the attendant consoles shall generate only visual indication whenever there are incoming calls to alert the operators.

The console shall be reached by the normal operator extension i.e., “0” or a personal extension number. The console shall have a counter for queuing trunk calls and internal calls.

The console shall have separate buttons to answer internal, external and personal calls. These call answer buttons shall allow operator to toggle between internal, external and personal calls. While answering a call, the other party shall be put on hold automatically.

The console shall incorporate the functions and facilities for business environment.

The attendant console shall be able to be connected to a tape recorder for recording of conversations. The attendant consoles shall be able to be connected to headset and handset.

The attendant console shall be able to transfer all calls in blind transfer mode or supervised mode.

All transferred calls that are not answered shall ring at the attendant consoles again after time-out factor.

25.8.1 Console Facilities

25.8.1.1 Camp-On with Tone Indication

This feature shall allow an operator to hold an incoming call in a specific waiting mode when the destination extension is busy. The operator shall send a camp-on tone indication to the busy destination extension. When the busy extension becomes idle, it is automatically rung and connected to the waiting party. Camp-on warning tone shall only be heard by the internal extension. Music-on-hold shall be provided to the waiting party.

25.8.1.2 Operator Override

This feature shall allow the operator to enter a busy trunk connection by operating the appropriate key and keying the trunk number. A warning tone shall be heard by the connected parties, after which the connected parties and operator will be connected in three-way connection.

25.8.1.3 Call Number Display

This feature shall allow the called extension number to be displayed on the console when a call is answered by the attendant operator.

25.8.1.4 Call Processing Indication

The screen shall provide indications to the operator relating the status of calls being processed.

25.8.1.5 Call Queuing

Calls directed to the console shall be placed in a ‘First-in/First-out’ queue. The operator may answer these calls in order of the arrival of the call by depressing the ‘Answer’ key.

25.8.1.6 Call Waiting Indicator

When the total number of calls waiting in queue for operator processing exceed a preset number of calls (e.g., 4 calls), this indicator shall flash at the operator console.

25.8.1.7 Display of Extension Information

Extensions calling or called by the operator will be identified by extension number, class of service and tenant number on the console display.

25.8.1.8 Individual Operator Access

The system shall be able to assign an individual number to each operator console in the system and allow the extension users to gain access to the specific operator console by dialing the assigned individual number.

25.8.1.9 Individual Trunk Access

This feature shall allow an operator to access individual trunks by dialing a access code.

25.8.1.10 Incoming Central Office Call to Tie Line Connection

This feature shall permit an operator to connect an incoming exchange call to an extension of a distance PABX via a tie line.

25.8.1.11 Lamp Check

Each operator console shall be equipped with a key which illuminates all LED’s and sounds an audible signal to the console audible simultaneously, allowing the operator to confirm proper operation of each indicator.

25.8.1.12 Non-Delayed Operation

This feature shall allow the operator to complete dialing of all types of calls (extension to trunk, trunk to trunk, trunk to extension) while the calling party holds on the line. The held calling party is then automatically connected to the called party.

25.8.1.13 Passing a Dial Tone/external trunk

The PABX operator shall be able to pass a dial tone to a restricted extension user to enable the user to make a call.

25.8.1.14 Time-out for dial tone / external trunk extended

The dial tone / external trunk extended by the operator to a user shall be clear down automatically if it is not used by the user within a certain period of time.

25.8.1.15 Class-of-service changeover on extending of dial tone/external trunk

The user shall receive a class-of-service which is normally higher than his/her normal class-of-service for the time the dial tone/external trunk is extended to the user.

25.8.1.16 Splitting

This feature shall allow the PABX operator to confer privately with one party on a operator- handled connection without the other party overhearing it.

25.8.1.17 Text messaging

The system's telephone application will enable the operator on transfer call status to send a short text message to a selected internal subscriber equipped with a terminal with a display. The operator will have the option of sending the message immediately onto the display panel of the subscriber if the line is engaged, or sending it to a text mailbox linked to the terminal, whether the called party is free or not. To facilitate the operation of this service, the operator should have the choice of several types of messages:

• 	Pre-programmed messages to answer most common cases (example: call back the switchboard, a visitor is waiting for you in reception etc.),

• 	Pre-programmed messages to be completed (example: call back number XYZ)

• 	Free messages to be composed entirely by the operator.

The tender will describe clearly all the characteristics of the service and the size of message, which can be sent in the various communication positions.

25.9 DIGITAL TELEPHONE

The proposed PABX system shall support digital telephone set. The proposed PABX system shall be able to support 100% full digital telephone connection.

The digital telephone sets shall have the programmable one touch button for the following features:

25.9.1 Call back - busy / no answer

It shall be able to initiate callback to a dialed station, irrespective of whether the called party is busy or receive no answer.

The connection is set up as soon as the called party cradles the handset or returns to his desk and uses the telephone.

25.9.2 Number Redial

It shall be possible to store a dialed internal or external number and dial it again later.

25.9.3 Call Forwarding

It shall be possible to reroute immediately all incoming calls to another telephone or the

Voice Mail Service.

A preset call forwarding tot a specific destination (such as a voice mailbox) or variable call forwarding to a programmable station is possible. Once call forwarding has been activated, it shall be able to transfer to another station by means of the “follow me’ facility.

25.9.4 Call Pick-up

It shall be able to pick-up a call which is ringing at another station within the same group by just pressing the call pick-up key at any telephone within the group.

25.9.5 Speed Calling - System

It shall be able to access to access centralized speed calling lists containing internal and external numbers which is stored into the PABX system. Tenderers shall state down the maximum speed calling numbers available in the system.

25.9.6 Speed Calling - Individual

Besides centralized speed dialing, each user shall be able to enter individual sped calling destinations for internal and external numbers. Each user is able to access to an individual speed calling list.  Tenderers shall state down the maximum individual speed calling numbers available in the system.

25.9.7 Second Call

The digital telephone set shall be able to receive a second call even if he is engaging on one line. There shall be a “second call” indicator button on the phone to signal the user and he is able to put the first caller on hold and take the second call if he wishes to.

25.9.8 Volume Control

The digital telephone shall have electronic “+” and “-” push buttons to control the loudness of receiving signal of the loudspeaker or handset earpiece.

25.9.9 Variable Ringing Tone

The users shall be able to loudness, frequency and pitch of their digital telephone set to set a unique ringing tone for their telephone set.

25.9.10 Adjustable Display Darkness

The digital telephone sets shall be able to adjust the darkness of the display by using the electronic “+” and “-” push buttons.

Tenderers shall purpose the following type of digital telephone sets together with this tender.

Executive Level Telephone Set complete with all the following capabilities: -

• 	2x20 characters display

• 	Display contrast adjustment

• 	Five contextual keys linked to the display, providing telephone services

• 	Alphabetic keyboard

• 	Hands-free and loud speaker

• 	Handset volume control

• 	18 programmable keys

• 	Personal repertory: 40 names

Options:

Analogue Z 600 Ohm interfaces, with power feeding and ringing generator

60 additional programmable keys

Management level Telephone Set complete with all the following capabilities: -

• 	1x20 characters display

• 	Display contrast adjustment

• 	Alphabetic keyboard

• 	Hands-free and loud speaker

• 	Handset volume control

• 	6 programmable keys

• 	Personal repertory: 15 names

Options:

Analogue Z 600 Ohms interface, with power feeding and ringing generator

60 additional programmable keys

Standard User Telephone Set complete with all the following capabilities: -

• 	1x20 characters display

• 	Display contrast adjustment

• 	Loud speaker

• 	2 programmable keys

• 	Personal Repertory: 15 names

25.10 SINGLE LINE TELEPHONE SET

Tenderer shall provide single line telephone sets together with the tender.

• 	Message waiting light

• 	Redial Key

• 	Flash Key

• 	Parallel Data Port

25.10.1 Main Distribution Frame

The tenderer shall provide main distribution frame for equipment side only together with the proposed PABX system.

The terminal block shall be vertical mounting connector type for ease of installation and maintenance.

All terminal blocks for the exchange lines and extension lines shall be equipped with gas discharge lightning arrestors.

Tenderer shall also provide power failure transfer circuits together with the main distribution frame.

25.11 EARTHING

The PABX earthing shall be of 1 ohm or less. The cost of installation of the PABX equipment shall include the cost of providing a good earthing for the equipment.

25.12 TECHNICAL SUPPORT STAFF

The tenderer shall provide a list of their technical support staff together with their working experience on PABX system.

Tenderer’s technical support staff shall be trained in the principal’s regional office on PABX system. Tenderer shall submit a copy of the certificate of training of the staff together with the tender submission.

Tenderer shall indicate the location of their nearest front line support office, branch office and dealer’s office in relation to the proposed site of the PABX. The names and experience of the technical support staff stationed there shall be provided.

25.13 WARRANTY

Tenderer shall provide 12 months full warranty on the PABX and all associated equipment from the date of successful commissioning against any manufacturing defects.

25.14 TRAINING

Tenderer shall provide training for the users and staff prior to commissioning of the PABX to ensure that they are competent enough to use the telephones and features.

26. TELEPHONE SYSTEM SPECIFICATION

26.1 GENERAL

The following specification covers the supply, delivery, installation, testing and commissioning of a complete Telephone System including maintenance during the defects liability period. All work pertaining to the system shall be in accordance with these specifications and shall meet all applicable Rules & Regulations of the local telecommunication authority.

The specifications and drawings are intended to provide the minimum basic performance and characteristics for the supply and installation of a complete system and the required standards of workmanship and materials in the design, manufacture, supply, installation, testing and commissioning of the system.

System provided shall be complete and operable, and shall include the required accessories, fastenings and supports. One coat of primer shall be applied for all fastenings and supports.

26.2 TELEPHONE WIRING AND INSTALLATION

The entire telephone wiring installation, as shown on the relevant drawings accompanying this document, shall be supplied, installed and commissioned by the Contractor who shall also be a Registered Contractor with the local telecommunication authority.  If the contractor is not registered with the local telecommunication authority, he shall then obtain the services of a Registered Contractor and submit the name of such contractor to the Consulting Engineer for approval prior to engaging the services of the said contractor.  In the event of the contractor engaging the services of an approved Registered Contractor, he shall be fully responsible for all works undertaken by such Registered Contractor, including all terms and conditions stated under this Contract.

The entire telephone wiring installation shall include all accessories necessary for the completion of the works in every respect and to the satisfaction of the local telecommunication authority, whether such be mentioned in this specification and the drawings or not.

The telephone under floor trunking shall within the building shall be carried out in concealed, rigid PVC under floor trunking of gauges and type approved by the local telecommunication authority.  The trunking runs shall be laid in floor screeds below floor finishes. Where possible, the Contractor shall closely liaise and arrange for chases of suitable depths and widths to be cast in the floor screeds to accommodate the trunking, the final concreting of chases shall be undertaken under approval from the Consulting Engineer and local telecommunication authority.

Telephone floor trunking shall, as far as possible, be supplied in lengths to suit the trunking runs. Where joints are unavoidable the joints shall be coated with an approved jointing compound during assembly and be made watertight. All joints shall be so constructed that cables can be conveniently drawn through without damage.

A piece of suitably flexible and strong draw-in-multi-strand wire shall be left in every section of the underfloor telephone trunking between adjoining junction boxes. These draw-in wires are for the running of future telephone cables.

Where riser ducts are used in the building for telephone cabling the scope shall include perforated cable tray covering the whole wide of the riser ducts.

Distribution boxes used outside riser enclosure shall be made of mild steel material 16 SWG minimum thicknesses and fitted with locks.  Those distribution boxes used inside locked riser enclosure shall be made of mild steel and fitted with clipped-on-covers.

The junction boxes must be watertight, made of stainless steel with durable screw-on covers of 10 SWG thickness and flush with the floor covering.  Telephone outlet box may be round or square as indicated and the outlet hole 6mm diameter in which rubber grommet shall be fitted.  Where building structure prohibits the use of trunking of more than 25mm depth, then the width of the trunking shall be increased proportionately.

Telephone outlet and junction boxes shall be of molded type and type approved by the Consulting Engineer and local telecommunication authority. The boxes shall be recessed in the floors and provided with removable, non-corrodible metal covers (metal covers to be flush with floor finishes.

A gasket shall be provided around the end of each junction box to prevent seepage of water into the box when the cover has been screwed in position. The screws used shall be of non-corrosive type (preferably of brass) and countersunk so that their heads do not protrude above the finished floor levels when installed.

The junction boxes are to be supplied in terminal though way, tee-off or intersection patterns as required on the drawings.  The opening where trunking enters each box shall be filled smooth so that the PVC sheath of the telephone cables will not be damaged during installation.

Cable terminal unit used for telephone risers shall be of the galvanized type and generally conform to the requirements for cable trays.

All necessary cable trays used for risers shall be of the galvanized type and generally conform to the requirements for cable trays.

All materials used for wiring must be approved by the local telecommunication authority.   Internal telephone cables shall comprise tinned, annealed copper conductors, PVC insulated and PVC sheathed with Grey/Black color code of conductors according to local telecommunication authority Specification.

26.3 TELEPHONE MANHOLE AND PIT

Telephone manholes and pits shall be constructed according to local telecommunication authority requirements. The manhole and pit shall be of waterproof construction.

If the site selected for a manhole be encroached upon by any obstruction, as for instance, a pipe main, Contractor shall arch the walls round such obstruction, or make other arrangement as may be required by the Engineer.

Conduits shall enter manholes and pits at such a depth to ensure a clearance of at least 450mm between the top of the barrel of the uppermost conduits and the underside of the roof of the manhole or pit.

Where the duct capacity of any proposed manhole is not fully utilized the space shall be fitted with dummy ducts for future duct growth.  The dummy ducts shall be sealed with 13mm cement mortar inside the chamber wall.

To ensure that cables can easily be housed in manholes and pits with a minimum of bending, the conduits should be splayed over the last length to enter the manhole and pit equally on either side. The manhole and pit shall be constructed throughout of Class ‘B’ concrete.

26.4 EARTHING

All necessary earthing requirements for the whole installation should be included in the cost.

26.5 TESTING AND COMMISSIONING

The contractor shall liaise with the local telecommunication authority and be responsible for getting the installation tested and approved.

27. SOLAR PANEL SYSTEM

Design, supply and complete installation of Solar PV, according to Utility Regulatory Authority Regulations and Guidelines with a minimum capacity of 50Kw. Please refer to detailed drawing for further information.