Republic of Maldives

Request for Bids

GRID-UPGRADING IN SELECTED ISLANDS IN THE MALDIVES

_______________________________

RFB No: MV-MEE-266363-CW-RFB

Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) Project

Issued on: March 16, 2022

Issued by:

Ministry of Finance

Republic of Maldives

# Standard Procurement Document

# Table of Contents

PART 1 – Bidding Procedures	3

Section I - Instructions to Bidders	6

Section II - Bid Data Sheet (BDS)	31

Section III - Evaluation and Qualification Criteria	37

Section IV - Bidding Forms	49

Section V - Eligible Countries	145

Section VI - Fraud and Corruption	147

PART 2 –Works’ Requirements	149

Section VII - Works’ Requirements	151

PART 3 – Conditions of Contract and Contract Forms	298

Section VIII - General Conditions (GC)	299

Section IX - Particular Conditions	301

Section X - Contract Forms	351

PART 1 – Bidding Procedures

Section I - Instructions to Bidders

Contents

A.	General	6

1.	Scope of Bid	6

2.	Source of Funds	7

3.	Fraud and Corruption	7

4.	Eligible Bidders	7

5.	Eligible Materials, Equipment, and Services	10

B.	Contents of Bidding Document	10

6.	Sections of Bidding Document	10

7.	Clarification of Bidding Document, Site Visit, Pre-Bid Meeting	11

8.	Amendment of Bidding Document	12

C.	Preparation of Bids	12

9.	Cost of Bidding	12

10.	Language of Bid	12

11.	Documents Comprising the Bid	12

12.	Letter of Bid and Schedules	13

13.	Alternative Bids	13

14.	Bid Prices and Discounts	14

15.	Currencies of Bid and Payment	15

16.	Documents Comprising the Technical Proposal	15

17.	Documents Establishing the Eligibility and Qualifications of the Bidder	15

18.	Period of Validity of Bids	15

19.	Bid Security	16

20.	Format and Signing of Bid	18

D.	Submission and Opening of Bids	18

21.	Sealing and Marking of Bids	18

22.	Deadline for Submission of Bids	19

23.	Late Bids	19

24.	Withdrawal, Substitution, and Modification of Bids	19

25.	Bid Opening	20

E.	Evaluation and Comparison of Bids	21

26.	Confidentiality	21

27.	Clarification of Bids	21

28.	Deviations, Reservations, and Omissions	22

29.	Determination of Responsiveness	22

30.	Nonmaterial Nonconformities	22

31.	Correction of Arithmetical Errors	23

32.	Conversion to Single Currency	23

33.	Margin of Preference	24

34.	Subcontractors	24

35.	Evaluation of Bids	24

36.	Comparison of Bids	25

37.	Abnormally Low Bids	25

38.	Unbalanced or Front Loaded Bids	26

39.	Qualifications of the Bidder	26

40.	Most Advantageous Bid	26

41.	Employer’s Right to Accept Any Bid, and to Reject Any or All Bids	27

42.	Standstill Period	27

43.	Notification of Intention to Award	27

F.	Award of Contract	27

44.	Award Criteria	27

45.	Notification of Award	27

46.	Debriefing by the Employer	28

47.	Signing of Contract	29

48.	Performance Security	29

49.	Procurement Related Complaint	30

| Section I - Instructions to Bidders |  |
| --- | --- |
|  | General |
| Scope of Bid | In connection with the Specific Procurement Notice – Request for Bids (RFB), specified in the Bid Data Sheet (BDS), the Employer, as specified in the BDS, issues this Bidding document for the provision of Works as specified in Section VII, Works’ Requirements. The name, identification, and number of lots (contracts) of this RFB are specified in the BDS. |
|  | Throughout this bidding document: the term “in writing” means communicated in written form (e.g. by mail, e-mail, fax, including, if specified in the BDS, distributed or received through electronic-procurement system used by the Employer) with proof of receipt; if the context so requires, “singular” means “plural’ and vice versa; “Day” means calendar day, unless otherwise specified as a “Business Day.” A “Business Day” is any day that is a working day of the Borrower. It excludes the Borrower’s official public holidays; “ES” means environmental and social (including Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH)); “Sexual Exploitation and Abuse” “(SEA)” means the following: Sexual Exploitation is defined as any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another. Sexual Abuse is defined as the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions; “Sexual Harassment” “(SH)” is defined as unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature by the Contractor’s Personnel with other Contractor’s or Employer’s Personnel; “Contractor’s Personnel” is as defined in Sub-Clause 1.1.17 of the General Conditions; and “Employer’s Personnel” is as defined in Sub-Clause 1.1.33 of the General Conditions. A non-exhaustive list of (i) behaviors which constitute SEA and (ii) behaviors which constitute SH is attached to the Code of Conduct form in Section IV. |
| Source of Funds | The Borrower or Recipient (hereinafter called “Borrower”) specified in the BDS has received or has applied for financing (hereinafter called “funds”) from the International Bank for Reconstruction and Development or the International Development Association (hereinafter called “the Bank”) in an amount specified in the BDS, toward the project named in the BDS. The Borrower intends to apply a portion of the funds to eligible payments under the contract(s) for which this Bidding document is issued. |
|  | Payment by the Bank will be made only at the request of the Borrower and upon approval by the Bank, and will be subject, in all respects, to the terms and conditions of the Loan (or other financing) Agreement. The Loan (or other financing) Agreement prohibits a withdrawal from the loan account for the purpose of any payment to persons or entities, or for any import of goods, equipment, plant, or materials, if such payment or import is prohibited by a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations. No party other than the Borrower shall derive any rights from the Loan (or other financing) Agreement or have any claim to the proceeds of the Loan (or other financing). |
| Fraud and Corruption | The Bank requires compliance with the Bank’s Anti-Corruption Guidelines and its prevailing sanctions policies and procedures as set forth in the WBG’s Sanctions Framework, as set forth in Section VI. In further pursuance of this policy, Bidders shall permit and shall cause their agents (where declared or not), subcontractors, subconsultants, service providers, suppliers, and personnel, to permit the Bank to inspect all accounts, records and other documents relating to any initial selection process, prequalification process, bid submission, proposal submission, and contract performance (in the case of award), and to have them audited by auditors appointed by the Bank. |
| Eligible Bidders | A Bidder may be a firm that is a private entity, a state-owned enterprise or institution subject to ITB 4.6 or any combination of such entities in the form of a joint venture (JV) under an existing agreement or with the intent to enter into such an agreement supported by a letter of intent. In the case of a joint venture, all members shall be jointly and severally liable for the execution of the entire Contract in accordance with the Contract terms. The JV shall nominate a Representative who shall have the authority to conduct all business for and on behalf of any and all the members of the JV during the Bidding process and, in the event the JV is awarded the Contract, during contract execution. Unless specified in the BDS, there is no limit on the number of members in a JV. |
|  | A Bidder shall not have a conflict of interest. Any Bidder found to have a conflict of interest shall be disqualified. A Bidder may be considered to have a conflict of interest for the purpose of this Bidding process, if the Bidder: - directly or indirectly controls, is controlled by or is under common control with another Bidder; or - receives or has received any direct or indirect subsidy from another Bidder; or - has the same legal representative as another Bidder; or - has a relationship with another Bidder, directly or through common third parties, that puts it in a position to influence the Bid of another Bidder, or influence the decisions of the Employer regarding this Bidding process; or - or any of its affiliates participated as a consultant in the preparation of the design or technical specifications of the works that are the subject of the Bid; or - or any of its affiliates has been hired (or is proposed to be hired) by the Employer or Borrower as Engineer for the Contract implementation; or - would be providing goods, works, or non-consulting services resulting from or directly related to consulting services for the preparation or implementation of the project specified in the BDS ITB 2.1 that it provided or were provided by any affiliate that directly or indirectly controls, is controlled by, or is under common control with that firm; or - has a close business or family relationship with a professional staff of the Borrower (or of the project implementing agency, or of a recipient of a part of the loan) who: (i) are directly or indirectly involved in the preparation of the Bidding document or specifications of the Contract, and/or the Bid evaluation process of such Contract; or (ii) would be involved in the implementation or supervision of such Contract unless the conflict stemming from such relationship has been resolved in a manner acceptable to the Bank throughout the Bidding process and execution of the Contract. |
|  | A firm that is a Bidder (either individually or as a JV member) shall not participate in more than one Bid, except for permitted alternative Bids. This includes participation as a subcontractor in other Bids. Such participation shall result in the disqualification of all Bids in which the firm is involved. A firm that is not a Bidder or a JV member may participate as a subcontractor in more than one Bid. A Bidder may have the nationality of any country, subject to the restrictions pursuant to ITB 4.8. A Bidder shall be deemed to have the nationality of a country if the Bidder is constituted, incorporated or registered in and operates in conformity with the provisions of the laws of that country, as evidenced by its articles of incorporation (or equivalent documents of constitution or association) and its registration documents, as the case may be. This criterion also shall apply to the determination of the nationality of proposed subcontractors or subconsultants for any part of the Contract including related Services. |
|  | A Bidder that has been sanctioned by the Bank, pursuant to the Bank’s Anti-Corruption Guidelines, and in accordance with its prevailing sanctions policies and procedures as set forth in the World Bank Group’s Sanctions Framework, as described in Section VI paragraph 2.2 d. shall be ineligible to be prequalified for, initially selected for, bid for, propose for, or be awarded a Bank-financed contract or benefit from a Bank-financed contract, financially or otherwise, during such period of time as the Bank shall have determined. The list of debarred firms and individuals is available at the electronic address specified in the BDS. |
|  | Bidders that are state-owned enterprises or institutions in the Employer’s Country may be eligible to compete and be awarded a Contract(s) only if they can establish, in a manner acceptable to the Bank, that they (i) are legally and financially autonomous (ii) operate under commercial law, and (iii) are not under supervision of the Employer. A Bidder shall not be under suspension from bidding by the Employer as the result of the operation of a Bid–Securing or Proposal-Securing Declaration. Firms and individuals may be ineligible if so indicated in Section V and (a) as a matter of law or official regulations, the Borrower’s country prohibits commercial relations with that country, provided that the Bank is satisfied that such exclusion does not preclude effective competition for the supply of goods or the contracting of works or services required; or (b) by an act of compliance with a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations, the Borrower’s country prohibits any import of goods or contracting of works or services from that country, or any payments to any country, person, or entity in that country. When the Works are implemented across jurisdictional boundaries (and more than one country is a Borrower, and is involved in the procurement), then exclusion of a firm or individual on the basis of ITB 4.8 (a) above by any country may be applied to that procurement across other countries involved, if the Bank and the Borrowers involved in the procurement agree. A Bidder shall provide such documentary evidence of eligibility satisfactory to the Employer, as the Employer shall reasonably request. A firm that is under a sanction of debarment by the Borrower from being awarded a contract is eligible to participate in this procurement, unless the Bank, at the Borrower’s request, is satisfied that the debarment; (a) relates to fraud or corruption, and (b) followed a judicial or administrative proceeding that afforded the firm adequate due process. |
| Eligible Materials, Equipment, and Services | The materials, equipment and services to be supplied under the Contract and financed by the Bank may have their origin in any country subject to the restrictions specified in Section V, Eligible Countries, and all expenditures under the Contract will not contravene such restrictions. At the Employer’s request, Bidders may be required to provide evidence of the origin of materials, equipment and services. |
|  | Contents of Bidding Document |
| Sections of Bidding Document | The Bidding document consists of Parts 1, 2, and 3, which includes all the sections specified below, and which should be read in conjunction with any Addenda issued in accordance with ITB 8. PART 1 Bidding Procedures - Section I - Instructions to Bidders (ITB) - Section II - Bid Data Sheet (BDS) - Section III - Evaluation and Qualification Criteria - Section IV - Bidding Forms - Section V - Eligible Countries - Section VI - Fraud and Corruption PART 2 Works Requirements - Section VII - Works’ Requirements PART 3 Conditions of Contract and Contract Forms - Section VIII - General Conditions (GC) - Section IX - Particular Conditions (PC) - Section X - Contract Forms |
|  | The Specific Procurement Notice - Request for Bids (RFB) issued by the Employer is not part of the Bidding document. |
|  | Unless obtained directly from the Employer, the Employer is not responsible for the completeness of the Bidding document, responses to requests for clarification, the minutes of the pre-Bid meeting (if any), or Addenda to the Bidding document in accordance with ITB 8. In case of any contradiction, documents obtained directly from the Employer shall prevail. |
|  | The Bidder is expected to examine all instructions, forms, terms, and specifications in the Bidding document and to furnish with its Bid all information and documentation as is required by the Bidding document. |
| Clarification of Bidding Document, Site Visit, Pre-Bid Meeting | A Bidder requiring any clarification of the Bidding document shall contact the Employer in writing at the Employer’s address specified in the BDS or raise its enquiries during the pre-Bid meeting if provided for in accordance with ITB 7.4. The Employer will respond in writing to any request for clarification, provided that such request is received prior to the deadline for submission of Bids within a period specified in the BDS. The Employer shall forward copies of its response to all Bidders who have acquired the Bidding document in accordance with ITB 6.3, including a description of the inquiry but without identifying its source. If so specified in the BDS, the Employer shall also promptly publish its response at the web page identified in the BDS. Should the clarification result in changes to the essential elements of the Bidding document, the Employer shall amend the Bidding document following the procedure under ITB 8 and ITB 22.2. |
|  | The Bidder is advised to visit and examine the Site of Works and its surroundings and obtain for itself on its own responsibility all information that may be necessary for preparing the Bid and entering into a contract for construction of the Works. The costs of visiting the Site shall be at the Bidder’s own expense. |
|  | The Bidder and any of its personnel or agents will be granted permission by the Employer to enter upon its premises and lands for the purpose of such visit, but only upon the express condition that the Bidder, its personnel, and agents will release and indemnify the Employer and its personnel and agents from and against all liability in respect thereof, and will be responsible for death or personal injury, loss of or damage to property, and any other loss, damage, costs, and expenses incurred as a result of the inspection. |
|  | If so specified in the BDS, the Bidder’s designated representative is invited to attend a pre-Bid meeting and/or a Site of Works visit. The purpose of the meeting will be to clarify issues and to answer questions on any matter that may be raised at that stage. |
|  | The Bidder is requested to submit any questions in writing, to reach the Employer not later than one week before the meeting. |
|  | Minutes of the pre-Bid meeting, if applicable, including the text of the questions asked by Bidders, without identifying the source, and the responses given, together with any responses prepared after the meeting, will be transmitted promptly to all Bidders who have acquired the Bidding document in accordance with ITB 6.3. If so specified in the BDS, the Employer shall also promptly publish the Minutes of the pre-Bid meeting at the web page identified in the BDS. Any modification to the Bidding document that may become necessary as a result of the pre-Bid meeting shall be made by the Employer exclusively through the issue of an Addendum pursuant to ITB 8 and not through the minutes of the pre-Bid meeting. Nonattendance at the pre-Bid meeting will not be a cause for disqualification of a Bidder. |
| Amendment of Bidding Document | At any time prior to the deadline for submission of Bids, the Employer may amend the Bidding document by issuing addenda. |
|  | Any addendum issued shall be part of the Bidding document and shall be communicated in writing to all who have obtained the Bidding document from the Employer in accordance with ITB 6.3. The Employer shall also promptly publish the addendum on the Employer’s web page in accordance with ITB 7.1. |
|  | To give Bidders reasonable time in which to take an addendum into account in preparing their Bids, the Employer should extend the deadline for the submission of Bids, pursuant to ITB 22.2. |
|  | Preparation of Bids |
| Cost of Bidding | The Bidder shall bear all costs associated with the preparation and submission of its Bid, and the Employer shall not be responsible or liable for those costs, regardless of the conduct or outcome of the Bidding process. |
| Language of Bid | The Bid, as well as all correspondence and documents relating to the Bid exchanged by the Bidder and the Employer, shall be written in the language specified in the BDS. Supporting documents and printed literature that are part of the Bid may be in another language provided they are accompanied by an accurate translation of the relevant passages in the language specified in the BDS, in which case, for purposes of interpretation of the Bid, such translation shall govern. |
| Documents Comprising the Bid | The Bid shall comprise the following: - Letter of Bid prepared in accordance with ITB 12; - Schedules including priced Bill of Quantities, completed in accordance with ITB 12 and ITB 14; - Bid Security or Bid-Securing Declaration, in accordance with ITB 19.1; - Alternative Bid, if permissible, in accordance with ITB 13; - Authorization: written confirmation authorizing the signatory of the Bid to commit the Bidder, in accordance with ITB 20.3; - Qualifications: documentary evidence in accordance with ITB 17 establishing the Bidder’s qualifications to perform the Contract if its Bid is accepted; - Conformity: a technical proposal in accordance with ITB 16; - any other document required in the BDS. In addition to the requirements under ITB 11.1, Bids submitted by a JV shall include a copy of the Joint Venture Agreement entered into by all members. Alternatively, a letter of intent to execute a Joint Venture Agreement in the event of a successful Bid shall be signed by all members and submitted with the Bid, together with a copy of the proposed Agreement. The Bidder shall furnish in the Letter of Bid information on commissions and gratuities, if any, paid or to be paid to agents or any other party relating to this Bid. The Bidder shall furnish in the Letter of Bid the names of three potential DAAB members and attach their curriculum vitae. The list of potential DAAB members proposed by the Employer (Contract Data 21.1) and by the Bidder (Letter of Bid) shall be subject to Bank’s No-objection. |
| Letter of Bid and Schedules | The Letter of Bid and Schedules, including the Bill of Quantities, shall be prepared using the relevant forms furnished in Section IV, Bidding Forms. The forms must be completed without any alterations to the text, and no substitutes shall be accepted except as provided under ITB 20.3. All blank spaces shall be filled in with the information requested. |
| Alternative Bids | Unless otherwise specified in the BDS, alternative Bids shall not be considered. |
|  | When alternative times for completion are explicitly invited, a statement to that effect will be included in the BDS, and the method of evaluating different alternative times for completion will be described in Section III, Evaluation and Qualification Criteria. |
|  | Except as provided under ITB 13.4 below, Bidders wishing to offer technical alternatives to the requirements of the Bidding document must first price the Employer’s design as described in the Bidding document and shall further provide all information necessary for a complete evaluation of the alternative by the Employer, including drawings, design calculations, technical specifications, breakdown of prices, and proposed construction methodology and other relevant details. Only the technical alternatives, if any, of the Bidder with the Most Advantageous Bid conforming to the basic technical requirements shall be considered by the Employer. |
|  | When specified in the BDS, Bidders are permitted to submit alternative technical solutions for specified parts of the Works, and such parts will be identified in the BDS, as will the method for their evaluating, and described in Section VII, Works’ Requirements. |
| Bid Prices and Discounts | The prices and discounts (including any price reduction) quoted by the Bidder in the Letter of Bid and in the Bill of Quantities shall conform to the requirements specified below. The Bidder shall fill in rates and prices for all items of the Works described in the Bill of Quantities. Items against which no rate or price is entered by the Bidder shall be deemed covered by the rates for other items in the Bill of Quantities and will not be paid for separately by the Employer. An item not listed in the priced Bill of Quantities shall be assumed to be not included in the Bid, and provided that the Bid is determined substantially responsive notwithstanding this omission, the average price of the item quoted by substantially responsive Bidders will be added to the Bid price and the equivalent total cost of the Bid so determined will be used for price comparison. |
|  | The price to be quoted in the Letter of Bid, in accordance with ITB 12.1, shall be the total price of the Bid, excluding any discounts offered. |
|  | The Bidder shall quote any discounts and the methodology for their application in the Letter of Bid, in accordance with ITB 12.1. |
|  | Unless otherwise specified in the BDS and the Conditions of Contract, the rates and prices quoted by the Bidder are subject to adjustment during the performance of the Contract in accordance with the provisions of the Conditions of Contract. In such a case, the Bidder shall furnish the indices and weightings for the price adjustment formulae in the Table of Adjustment Data and the Employer may require the Bidder to justify its proposed indices and weightings. |
|  | If, so specified in ITB 1.1, Bids are being invited for individual lots (contracts) or for any combination of lots (packages). Bidders wishing to offer discounts for the award of more than one Contract shall specify in their Bid the price reductions applicable to each package, or alternatively, to individual Contracts within the package. Discounts shall be submitted in accordance with ITB 14.4, provided the Bids for all lots (contracts) are opened at the same time. If, however, rated criteria is used in accordance with ITB 35.2, discounts on condition of award of more than one contract will not be used for Bid evaluation purpose. |
|  | All duties, taxes, and other levies payable by the Contractor under the Contract, or for any other cause, as of the date 28 days prior to the deadline for submission of Bids, shall be included in the rates and prices and the total Bid Price submitted by the Bidder. |
| Currencies of Bid and Payment | The currency (ies) of the Bid and the currency (ies) of payments shall be the same and shall be as specified in the BDS. Bidders may be required by the Employer to justify, to the Employer’s satisfaction, their local and foreign currency requirements, and to substantiate that the amounts included in the unit rates and prices and shown in the Table of Adjustment Data in the Appendix to Bid are reasonable, in which case a detailed breakdown of the foreign currency requirements shall be provided by Bidders. |
| Documents Comprising the Technical Proposal | The Bidder shall furnish a technical proposal including a statement of work methods, equipment, personnel, schedule and any other information as stipulated in Section IV, Bidding Forms, in sufficient detail to demonstrate the adequacy of the Bidder’s proposal to meet the work’s requirements and the completion time. |
| Documents Establishing the Eligibility and Qualifications of the Bidder | To establish Bidder’s eligibility in accordance with ITB 4, Bidders shall complete the Letter of Bid, included in Section IV, Bidding Forms. In accordance with Section III, Evaluation and Qualification Criteria, to establish its qualifications to perform the Contract the Bidder shall provide the information requested in the corresponding information sheets included in Section IV, Bidding Forms. |
|  | If a margin of preference applies as specified in accordance with ITB 33.1, domestic Bidders, individually or in joint ventures, applying for eligibility for domestic preference shall supply all information required to satisfy the criteria for eligibility specified in accordance with ITB 33.1. |
| Period of Validity of Bids | Bids shall remain valid until the date specified in the BDS or any extended date if amended by the Employer in accordance with ITB 8. A Bid that is not valid until the date specified in the BDS, or any extended date if amended by the Employer in accordance with ITB 8, shall be rejected by the Employer as nonresponsive. |
|  | In exceptional circumstances, prior to the date of expiration of the Bid validity, the Employer may request Bidders to extend the period of validity of their Bids. The request and the responses shall be made in writing. If a Bid Security is requested in accordance with ITB 19, it shall also be extended for twenty-eight (28) days beyond the extended date for bid validity. A Bidder may refuse the request without forfeiting its Bid security. A Bidder granting the request shall not be required or permitted to modify its Bid, except as provided in ITB 18.3. |
|  | If the award is delayed by a period exceeding fifty-six (56) days beyond the date of expiry of the Bid validity specified in accordance with ITB 18.1, the Contract price shall be determined as follows: - in the case of fixed price contracts, the Contract price shall be the Bid price adjusted by the factor specified in the BDS; - in the case of adjustable price contracts, no adjustment shall be made; or - in any case, Bid evaluation shall be based on the Bid price without taking into consideration the applicable correction from those indicated above. |
| Bid Security | The Bidder shall furnish as part of its Bid, either a Bid-Securing Declaration or a Bid Security as specified in the BDS, in original form and, in the case of a Bid Security, in the amount and currency specified in the BDS. |
|  | A Bid-Securing Declaration shall use the form included in Section IV, Bidding Forms. |
|  | If a Bid Security is specified pursuant to ITB 19.1, the Bid Security shall be a demand guarantee in any of the following forms at the Bidder’s option: - an unconditional guarantee issued by a bank or non-bank financial institution (such as an insurance, bonding or surety company); - an irrevocable letter of credit; - a cashier’s or certified check; or - another security specified in the BDS, - from a reputable source from an eligible country. If an unconditional guarantee is issued by a non-bank financial institution located outside the Employer’s Country, the issuing non-bank financial institution shall have a correspondent financial institution located in the Employer’s Country to make it enforceable unless the Employer has agreed in writing, prior to Bid submission, that a correspondent financial institution is not required. In the case of a bank guarantee, the Bid Security shall be submitted either using the Bid Security Form included in Section IV, Bidding Forms, or in another substantially similar format approved by the Employer prior to Bid submission. The Bid Security shall be valid for twenty-eight (28) days beyond the original date of expiry of the Bid validity, or beyond any extended date if requested under ITB 18.2. |
|  | If a Bid Security or Bid-Securing Declaration is specified pursuant to ITB 19.1, any Bid not accompanied by a substantially responsive Bid Security or Bid-Securing Declaration shall be rejected by the Employer as non-responsive. |
|  | If a Bid Security is specified pursuant to ITB 19.1, the Bid Security of unsuccessful Bidders shall be returned as promptly as possible upon the successful Bidder’s signing the Contract and furnishing the Performance Security and if required in the BDS, the Environmental and Social (ES) Performance Security pursuant to ITB 48. |
|  | The Bid Security of the successful Bidder shall be returned as promptly as possible once the successful Bidder has signed the Contract and furnished the required Performance Security, and if required in the BDS, the Environmental and Social (ES) Performance Security. |
|  | The Bid Security may be forfeited: - if a Bidder withdraws its Bid prior to the expiry date of the Bid validity specified by the Bidder on the Letter of Bid, or any extended date provided by the Bidder; or - if the successful Bidder fails to: #### (i) sign the Contract in accordance with ITB 47; or #### (ii) furnish a Performance Security and if required in the BDS, the Environmental and Social (ES) Performance Security in accordance with ITB 48. |
|  | The Bid Security or the Bid-Securing Declaration of a JV shall be in the name of the JV that submits the Bid. If the JV has not been legally constituted into a legally enforceable JV at the time of Bidding, the Bid Security or the Bid-Securing Declaration shall be in the names of all future members as named in the letter of intent referred to in ITB 4.1 and ITB 11.2. If a Bid Security is not required in the BDS, pursuant to ITB 19.1, and: - if a Bidder withdraws its Bid prior to the expiry date of the Bid validity specified by the Bidder on the Letter of Bid or any extended date provided by the Bidder; or - if the successful Bidder fails to: - sign the Contract in accordance with ITB 47; or - furnish a Performance Security and, if required in the BDS, the Environmental and Social (ES) Performance Security in accordance with ITB 48, - the Borrower may, if provided for in the BDS, declare the Bidder ineligible to be awarded a contract by the Employer for a period of time stated in the BDS. |
| Format and Signing of Bid | The Bidder shall prepare one original of the documents comprising the Bid as described in ITB 11 and clearly mark it “Original.” Alternative Bids, if permitted in accordance with ITB 13, shall be clearly marked “Alternative.” In addition, the Bidder shall submit copies of the Bid, in the number specified in the BDS and clearly mark them “Copy.” In the event of any discrepancy between the original and the copies, the original shall prevail. |
|  | Bidders shall mark as “CONFIDENTIAL” all information in their Bids which is confidential to their business. This may include proprietary information, trade secrets, or commercial or financially sensitive information. |
|  | The original and all copies of the Bid shall be typed or written in indelible ink and shall be signed by a person duly authorized to sign on behalf of the Bidder. This authorization shall consist of a written confirmation as specified in the BDS and shall be attached to the Bid. The name and position held by each person signing the authorization must be typed or printed below the signature. All pages of the Bid where entries or amendments have been made shall be signed or initialed by the person signing the Bid. |
|  | In case the Bidder is a JV, the Bid shall be signed by an authorized representative of the JV on behalf of the JV, and so as to be legally binding on all the members as evidenced by a power of attorney signed by their legally authorized representatives. |
|  | Any inter-lineation, erasures, or overwriting shall be valid only if they are signed or initialed by the person signing the Bid. |
|  | Submission and Opening of Bids |
| Sealing and Marking of Bids | The Bidder shall deliver the Bid in a single, sealed envelope (one-envelope Bidding process). Within the single envelope the Bidder shall place the following separate, sealed envelopes: - in an envelope marked “ORIGINAL”, all documents comprising the Bid, as described in ITB 11; and - in an envelope marked “COPIES”, all required copies of the Bid; and - if alternative Bids are permitted in accordance with ITB 13, and if relevant: - in an envelope marked “ORIGINAL –ALTERNATIVE BID”, the alternative Bid; and - in the envelope marked “COPIES- ALTERNATIVE BID”, all required copies of the alternative Bid. |
|  | The inner and outer envelopes shall: - bear the name and address of the Bidder; - be addressed to the Employer in accordance with ITB 22.1; - bear the specific identification of this Bidding process specified in accordance with BDS 1.1; and - bear a warning not to open before the time and date for Bid opening. |
|  | If all envelopes are not sealed and marked as required, the Employer will assume no responsibility for the misplacement or premature opening of the Bid. |
| Deadline for Submission of Bids | Bids must be received by the Employer at the address and no later than the date and time specified in the BDS. When so specified in the BDS, Bidders shall have the option of submitting their Bids electronically. Bidders submitting Bids electronically shall follow the electronic Bid submission procedures specified in the BDS. |
|  | The Employer may, at its discretion, extend the deadline for the submission of Bids by amending the Bidding document in accordance with ITB 8, in which case all rights and obligations of the Employer and Bidders previously subject to the deadline shall thereafter be subject to the deadline as extended. |
| Late Bids | The Employer shall not consider any Bid that arrives after the deadline for submission of Bids, in accordance with ITB 22. Any Bid received by the Employer after the deadline for submission of Bids shall be declared late, rejected, and returned unopened to the Bidder. |
| Withdrawal, Substitution, and Modification of Bids | A Bidder may withdraw, substitute, or modify its Bid after it has been submitted by sending a written notice, duly signed by an authorized representative, and shall include a copy of the authorization in accordance with ITB 20.3, (except that withdrawal notices do not require copies). The corresponding substitution or modification of the Bid must accompany the respective written notice. All notices must be: - prepared and submitted in accordance with ITB 20 and ITB 21 (except that withdrawals notices do not require copies), and in addition, the respective envelopes shall be clearly marked “Withdrawal,” “Substitution,” “Modification;” and - received by the Employer prior to the deadline prescribed for submission of Bids, in accordance with ITB 22. |
|  | Bids requested to be withdrawn in accordance with ITB 24.1 shall be returned unopened to the Bidders. |
|  | No Bid may be withdrawn, substituted, or modified in the interval between the deadline for submission of Bids and the date of expiry of Bid validity specified by the Bidder on the Letter of Bid or any extended date thereof. |
| Bid Opening | Except in the cases specified in ITB 23 and ITB 24.2, the Employer shall publicly open and read out in accordance with this ITB all Bids received by the deadline, at the date, time and place specified in the BDS, in the presence of Bidders` designated representatives and anyone who chooses to attend. Any specific electronic Bid opening procedures required if electronic Bidding is permitted in accordance with ITB 22.1, shall be as specified in the BDS. |
|  | First, envelopes marked “Withdrawal” shall be opened and read out and the envelope with the corresponding Bid shall not be opened but returned to the Bidder. No Bid withdrawal shall be permitted unless the corresponding withdrawal notice contains a valid authorization to request the withdrawal and is read out at Bid opening. Next, envelopes marked “Substitution” shall be opened and read out and exchanged with the corresponding Bid being substituted, and the substituted Bid shall not be opened, but returned to the Bidder. No Bid substitution shall be permitted unless the corresponding substitution notice contains a valid authorization to request the substitution and is read out at Bid opening. Next, envelopes marked “Modification” shall be opened and read out with the corresponding Bid. No Bid modification shall be permitted unless the corresponding modification notice contains a valid authorization to request the modification and is read out at Bid opening. |
|  | Next, all remaining envelopes shall be opened one at a time, reading out: the name of the Bidder and whether there is a modification; the total Bid Price, per lot (contract) if applicable, including any discounts and alternative Bids; the presence or absence of a Bid Security or Bid-Securing Declaration, if required; and any other details as the Employer may consider appropriate. Only Bids, alternative Bids and discounts that are opened and read out at Bid opening shall be considered further for evaluation. The Letter of Bid and the Bill of Quantities are to be initialed by representatives of the Employer attending Bid opening in the manner specified in the BDS. |
|  | The Employer shall neither discuss the merits of any Bid nor reject any Bid (except for late Bids, in accordance with ITB 23.1). The Employer shall prepare a record of the Bid opening that shall include, as a minimum: - the name of the Bidder and whether there is a withdrawal, substitution, or modification; - the Bid Price, per lot (contract) if applicable, including any discounts; - any alternative Bids; - the presence or absence of a Bid Security, if one was required. The Bidders’ representatives who are present shall be requested to sign the record. The omission of a Bidder’s signature on the record shall not invalidate the contents and effect of the record. A copy of the record shall be distributed to all Bidders. |
|  | Evaluation and Comparison of Bids |
| Confidentiality | Information relating to the evaluation of Bids and recommendation of contract award shall not be disclosed to Bidders or any other persons not officially concerned with the Bidding process until information on Intention to Award the Contract is transmitted to all Bidders in accordance with ITB 43. |
|  | Any effort by a Bidder to influence the Employer in the evaluation of the Bids or Contract award decisions may result in the rejection of its Bid. |
|  | Notwithstanding ITB 26.2, from the time of Bid opening to the time of Contract award, if a Bidder wishes to contact the Employer on any matter related to the Bidding process, it shall do so in writing. |
| Clarification of Bids | To assist in the examination, evaluation, and comparison of the Bids, and qualification of the Bidders, the Employer may, at its discretion, ask any Bidder for a clarification of its Bid, given a reasonable time for a response. Any clarification submitted by a Bidder that is not in response to a request by the Employer shall not be considered. The Employer’s request for clarification and the response shall be in writing. No change, including any voluntary increase or decrease, in the prices or substance of the Bid shall be sought, offered, or permitted, except to confirm the correction of arithmetic errors discovered by the Employer in the evaluation of the Bids, in accordance with ITB 31. |
|  | If a Bidder does not provide clarifications of its Bid by the date and time set in the Employer’s request for clarification, its Bid may be rejected. |
| Deviations, Reservations, and Omissions | During the evaluation of Bids, the following definitions apply: - “Deviation” is a departure from the requirements specified in the Bidding document; - “Reservation” is the setting of limiting conditions or withholding from complete acceptance of the requirements specified in the Bidding document; and - “Omission” is the failure to submit part or all of the information or documentation required in the Bidding document. |
| Determination of Responsiveness | The Employer’s determination of a Bid’s responsiveness is to be based on the contents of the Bid itself, as defined in ITB 11. |
|  | A substantially responsive Bid is one that meets the requirements of the Bidding document without material deviation, reservation, or omission. A material deviation, reservation, or omission is one that, |
|  | - if accepted, would: |
|  | #### (i) affect in any substantial way the scope, quality, or performance of the Works specified in the Contract; or |
|  | #### (ii) limit in any substantial way, inconsistent with the Bidding document, the Employer’s rights or the Bidder’s obligations under the proposed Contract; or |
|  | - if rectified, would unfairly affect the competitive position of other Bidders presenting substantially responsive Bids. |
|  | The Employer shall examine the technical aspects of the Bid submitted in accordance with ITB 16, in particular, to confirm that all requirements of Section VII, Works’ Requirements have been met without any material deviation, reservation or omission. |
|  | If a Bid is not substantially responsive to the requirements of the Bidding document, it shall be rejected by the Employer and may not subsequently be made responsive by correction of the material deviation, reservation, or omission. |
| Nonmaterial Nonconformities | Provided that a Bid is substantially responsive, the Employer may waive any nonconformities in the Bid. |
|  | Provided that a Bid is substantially responsive, the Employer may request that the Bidder submit the necessary information or documentation, within a reasonable period of time, to rectify nonmaterial nonconformities in the Bid related to documentation requirements. Requesting information or documentation on such nonconformities shall not be related to any aspect of the price of the Bid. Failure of the Bidder to comply with the request may result in the rejection of its Bid. |
|  | Provided that a Bid is substantially responsive, the Employer shall rectify quantifiable nonmaterial nonconformities related to the Bid Price. To this effect, the Bid Price shall be adjusted, for comparison purposes only to reflect the price of a missing or non-conforming item or component, by adding the average price of the item or component quoted by substantially responsive Bidders. If the price of the item or component cannot be derived from the price of other substantially responsive Bids, the Employer shall use its best estimate. |
| Correction of Arithmetical Errors | Provided that the Bid is substantially responsive, the Employer shall correct arithmetical errors on the following basis: - if there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price shall prevail, and the total price shall be corrected, unless in the opinion of the Employer there is an obvious misplacement of the decimal point in the unit price, in which case the total price as quoted shall govern and the unit price shall be corrected; - if there is an error in a total corresponding to the addition or subtraction of subtotals, the subtotals shall prevail and the total shall be corrected; and - if there is a discrepancy between words and figures, the amount in words shall prevail, unless the amount expressed in words is related to an arithmetic error, in which case the amount in figures shall prevail subject to (a) and (b) above. |
|  | Bidders shall be requested to accept correction of arithmetical errors. Failure to accept the correction in accordance with ITB 31.1, shall result in the rejection of the Bid. |
| Conversion to Single Currency | For evaluation and comparison purposes, the currency(ies) of the Bid shall be converted into a single currency as specified in the BDS. |
| Margin of Preference | Unless otherwise specified in the BDS, a margin of preference for domestic Bidders shall not apply. |
| Subcontractors | Unless otherwise stated in the BDS, the Employer does not intend to execute any specific elements of the Works by subcontractors selected in advance by the Employer. |
|  | Bidders may propose subcontracting up to the percentage of total value of contracts or the volume of works as specified in the BDS. Subcontractors proposed by the Bidder shall be fully qualified for their parts of the Works. |
|  | The subcontractor’s qualifications shall not be used by the Bidder to qualify for the Works unless their specialized parts of the Works were previously designated by the Employer in the BDS as can be met by subcontractors referred to hereafter as ‘Specialized Subcontractors’, in which case, the qualifications of the Specialized Subcontractors proposed by the Bidder may be added to the qualifications of the Bidder. |
| Evaluation of Bids | - Technical Evaluation The Employer shall evaluate the Bids using the criteria and methodologies listed in Section III, Evaluation and Qualification Criteria. If specified in the BDS, the Employer’s evaluation will be carried out by applying rated criteria that take into account technical factors, in addition to cost factors. An Evaluated Bid Score will be calculated for each responsive Bid using the formula, specified in Section III, Evaluation and Qualification Criteria. The scores to be given to technical factors and sub factors are specified in the BDS. The weight to be assigned for the Technical factors and cost is specified in the BDS. |
|  | - Financial Evaluation To evaluate a Bid, the Employer shall consider the following: |
|  | - the Bid price, excluding Provisional Sums and the provision, if any, for contingencies in the Summary Bill of Quantities, but including Daywork items, where priced competitively; - price adjustment for correction of arithmetic errors in accordance with ITB 31.1; - price adjustment due to discounts offered in accordance with ITB 14.4; - converting the amount resulting from applying (a) to (c) above, if relevant, to a single currency in accordance with ITB 32; - price adjustment due to quantifiable nonmaterial nonconformities in accordance with ITB 30.3; and - the additional evaluation factors specified in the BDS and Section III, Evaluation and Qualification Criteria. |
|  | The estimated effect of the price adjustment provisions of the Conditions of Contract, applied over the period of execution of the Contract, shall not be taken into account in Bid evaluation. |
|  | If this Bidding document allows Bidders to quote separate prices for different lots (contracts), the methodology to determine the lowest evaluated cost of the lot (contract) combinations, including any discounts offered in the Letter of Bid, is specified in Section III, Evaluation and Qualification Criteria. If, however, rated criteria is used in accordance with ITB 35.2, discounts on condition of award of more than one contract will not be used for Bid evaluation purpose. |
| Comparison of Bids | The Employer shall compare the evaluated costs of all substantially responsive Bids established in accordance with ITB 35.1 to determine the Bid that has the lowest evaluated cost. If ITB 35.2 is applicable, the Employer will determine the Bid with the highest combined technical and financial score in accordance with BDS 35.2. |
| Abnormally Low Bids | An Abnormally Low Bid is one where the Bid price, in combination with other elements of the Bid, appears so low that it raises material concerns as to the capability of the Bidder in regard to the Bidder’s ability to perform the Contract for the offered Bid Price. In the event of identification of a potentially Abnormally Low Bid, the Employer shall seek written clarifications from the Bidder, including detailed price analyses of its Bid price in relation to the subject matter of the contract, scope, proposed methodology, schedule, allocation of risks and responsibilities and any other requirements of the Bidding document. After evaluation of the price analyses, in the event that the Employer determines that the Bidder has failed to demonstrate its capability to perform the Contract for the offered Bid Price, the Employer shall reject the Bid. |
| Unbalanced or Front Loaded Bids | If the Bid that is evaluated as the lowest evaluated cost is, in the Employer’s opinion, seriously unbalanced or front loaded, the Employer may require the Bidder to provide written clarifications. Clarifications may include detailed price analyses to demonstrate the consistency of the Bid prices with the scope of works, proposed methodology, schedule and any other requirements of the Bidding document. After the evaluation of the information and detailed price analyses presented by the Bidder, the Employer may as appropriate: - accept the Bid; or - require that the total amount of the Performance Security be increased at the expense of the Bidder to a level not exceeding 20% of the Contract Price; or - reject the Bid. |
| Qualifications of the Bidder | The Employer shall determine to its satisfaction whether the eligible Bidder that is selected as having submitted the lowest evaluated cost and substantially responsive Bid, meets the qualifying criteria specified in Section III, Evaluation and Qualification Criteria. |
|  | The determination shall be based upon an examination of the documentary evidence of the Bidder’s qualifications submitted by the Bidder, pursuant to ITB 17. The determination shall not take into consideration the qualifications of other firms such as the Bidder’s subsidiaries, parent entities, affiliates, subcontractors (other than Specialized Subcontractors if permitted in the Bidding document), or any other firm(s) different from the Bidder. |
|  | Prior to Contract award, the Employer will verify that the successful Bidder (including each member of a JV) is not disqualified by the Bank due to noncompliance with contractual SEA/SH prevention and response obligations. The Employer will conduct the same verification for each subcontractor proposed by the successful Bidder. If any proposed subcontractor does not meet the requirement, the Employer will require the Bidder to propose a replacement subcontractor.. |
|  | An affirmative determination shall be a prerequisite for award of the Contract to the Bidder. A negative determination shall result in disqualification of the Bid, in which event the Employer shall proceed to the Bidder who offers a substantially responsive Bid with the next lowest evaluated cost to make a similar determination of that Bidder’s qualifications to perform satisfactorily. |
| Most Advantageous Bid | The Employer shall determine the Most Advantageous Bid. The Most Advantageous Bid is the Bid of the Bidder that meets the Qualification Criteria and whose Bid has been determined to be substantially responsive to the Bidding document and: - when rated criteria are used is the Bid with the highest combined technical and financial score; or - when rated criteria are not used, is the Bid with the lowest evaluated cost. |
| Employer’s Right to Accept Any Bid, and to Reject Any or All Bids | The Employer reserves the right to accept or reject any Bid and to annul the Bidding process and reject all Bids at any time prior to Contract Award, without thereby incurring any liability to Bidders. In case of annulment, all Bids submitted and specifically, Bid securities, shall be promptly returned to the Bidders. |
| Standstill Period | The Contract shall not be awarded earlier than the expiry of the Standstill Period. The Standstill Period shall be ten (10) Business Days unless extended in accordance with ITB 46. The Standstill Period commences the day after the date the Employer has transmitted to each Bidder the Notification of Intention to Award the Contract. Where only one Bid is submitted, or if this contract is in response to an emergency situation recognized by the Bank, the Standstill Period shall not apply. |
| Notification of Intention to Award | The Employer shall send to each Bidder the Notification of Intention to Award the Contract to the successful Bidder. The Notification of Intention to Award shall contain, at a minimum, the following information: - the name and address of the Bidder submitting the successful Bid; - the Contract price of the successful Bid; - the names of all Bidders who submitted Bids, and their Bid prices as readout, and as evaluated; - a statement of the reason(s) the Bid (of the unsuccessful Bidder to whom the notification is addressed) was unsuccessful, unless the price information in c) above already reveals the reason; - the expiry date of the Standstill Period; and - instructions on how to request a debriefing and/or submit a complaint during the standstill period; |
| Award of Contract |  |  |
| Award Criteria | Subject to ITB 41, the Employer shall award the Contract to the successful Bidder. This is the Bidder whose Bid has been determined to be the Most Advantageous Bid. |  |
| Notification of Award | Prior to the date of expiry of the bid validity, and upon expiry of the Standstill Period specified in ITB 42.1 or any extension thereof, and, upon satisfactorily addressing any complaint that has been filed within the Standstill Period, the Employer shall notify the successful Bidder, in writing, that its Bid has been accepted. The notification of award (hereinafter and in the Conditions of Contract and Contract Forms called the “Letter of Acceptance”) shall specify the sum that the Employer will pay the Contractor in consideration of the execution of the Contract (hereinafter and in the Conditions of Contract and Contract Forms called “the Contract Price”). Within ten (10) Business Days after the date of transmission of the Letter of Acceptance, the Employer shall publish the Contract Award Notice which shall contain, at a minimum, the following information: - name and address of the Employer; - name and reference number of the contract being awarded, and the selection method used; - names of all Bidders that submitted Bids, and their Bid prices as read out at Bid opening, and as evaluated; - names of all Bidders whose Bids were rejected either as nonresponsive or as not meeting qualification criteria, or were not evaluated, with the reasons therefor; - the name of the successful Bidder, the final total contract price, the contract duration and a summary of its scope; and - successful Bidder’s Beneficial Ownership Disclosure Form, if specified in BDS ITB 47.1 The Contract Award Notice shall be published on the Employer’s website with free access if available, or in at least one newspaper of national circulation in the Employer’s Country, or in the official gazette. The Employer shall also publish the contract award notice in UNDB online. Until a formal Contract is prepared and executed, the Letter of Acceptance shall constitute a binding Contract. |  |
| Debriefing by the Employer | On receipt of the Employer’s Notification of Intention to Award referred to in ITB 43.1, an unsuccessful Bidder has three (3) Business Days to make a written request to the Employer for a debriefing. The Employer shall provide a debriefing to all unsuccessful Bidders whose request is received within this deadline. Where a request for debriefing is received within the deadline, the Employer shall provide a debriefing within five (5) Business Days, unless the Employer decides, for justifiable reasons, to provide the debriefing outside this timeframe. In that case, the standstill period shall automatically be extended until five (5) Business Days after such debriefing is provided. If more than one debriefing is so delayed, the standstill period shall not end earlier than five (5) Business Days after the last debriefing takes place. The Employer shall promptly inform, by the quickest means available, all Bidders of the extended standstill period. Where a request for debriefing is received by the Employer later than the three (3) -Business Day deadline, the Employer should provide the debriefing as soon as practicable, and normally no later than fifteen (15) Business Days from the date of publication of Public Notice of Award of contract. Requests for debriefing received outside the three (3)-day deadline shall not lead to extension of the standstill period. Debriefings of unsuccessful Bidders may be done in writing or verbally. The Bidder shall bear its own costs of attending such a debriefing meeting. |
| Signing of Contract | The Employer shall send to the successful Bidder the Letter of Acceptance including the Contract Agreement, and, if specified in the BDS, a request to submit the Beneficial Ownership Disclosure Form providing additional information on its beneficial ownership. The Beneficial Ownership Disclosure Form, if so requested, shall be submitted within eight (8) Business Days of receiving this request. |
|  | The successful Bidder shall sign, date and return to the Employer, the Contract Agreement within twenty-eight (28) days of its receipt. |
| Performance Security | Within twenty-eight (28) days of the receipt of the Letter of Acceptance from the Employer, the successful Bidder shall furnish the Performance Security and, if required in the BDS, the Environmental and Social (ES) Performance Security in accordance with the Conditions of Contract, subject to ITB 38.2 (b), using for that purpose the Performance Security and ES Performance Security Forms included in Section X, Contract Forms, or another form acceptable to the Employer. If the Performance Security furnished by the successful Bidder is in the form of a bond, it shall be issued by a bonding or insurance company that has been determined by the successful Bidder to be acceptable to the Employer. A foreign institution providing a bond shall have a correspondent financial institution located in the Employer’s Country, unless the Employer has agreed in writing that a correspondent financial institution is not required. |
|  | Failure of the successful Bidder to submit the above-mentioned Performance Security and, if required in the BDS, the Environmental and Social (ES) Performance Security, or sign the Contract shall constitute sufficient grounds for the annulment of the award and forfeiture of the Bid Security. In that event the Employer may award the Contract to the Bidder offering the next Most Advantageous Bid. |
| Procurement Related Complaint | The procedures for making a Procurement-related Complaint are as specified in the BDS. |

| Section II - Bid Data Sheet (BDS) The following specific data for the Works to be procured shall complement, supplement, or amend the provisions in the Instructions to Bidders (ITB). Whenever there is a conflict, the provisions herein shall prevail over those in ITB. |  |
| --- | --- |
| A. General |  |
| ITB 1.1 | The reference number of the Request for Bids (RFB) is: MV-MEE-266363-CW-RFB The Employer is: Ministry of Environment, Climate Change and Technology, Green Building Republic of Maldives The name of the RFB is: GRID-UPGRADING IN SELECTED ISLANDS IN THE MALDIVES The number and identification of lots (contracts) comprising this RFB is: - LOT ONE: Grid-Upgrading in Addu City mainland, Addu City Hulhumeedhoo, Fuvamulah City, and GDh. Thinadhoo. - LOT TWO: Grid-Upgrading in B. Eydhafushi, Lh. Hinnavaru, Kulhudhuffushi City. - LOT THREE: Grid-Upgrading in L. Fonadhoo, interconnected network of L. Isdhoo, Kalaidhoo and Dhanbidhoo, L. Maabaidhoo, L. Kunahandhoo, L. Hithadhoo and Sh. Funadhoo. |
| ITB 2.1 | The Borrower is: Government of the Republic of Maldives Financing Agreement amount: USD 107 Million The name of the Project is: Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) Project |

| ITB 4.1 | Maximum number of members in the JV shall be: Three (03) |
| --- | --- |
| ITB 4.5 | A list of debarred firms and individuals is available on the Bank’s external website: http://www.worldbank.org/debarr |
| B. Contents of Bidding Document |  |
| ITB 7.1 | For Clarification of Bid purposes only, the Employer’s address is: National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives Tel: (+960) 3349102 E-Mail: ibrahim.aflah@finance.gov.mv Copy to: tender@finance.gov.mv Requests for clarification should be received by the Employer no later than: 28 days prior to Bid submission date. Web page: https://www.finance.gov.mv/tenders |
| ITB 7.4 | A Pre-Bid meeting shall take place at the following date, time and place: Date: April 06, 2022 Time: 10:00 AM Male’ Time Duration: 2 Hours Maximum Place: Employer will organize an ONLINE VIDEO CONFERENCE MEETING for the Pre-Bid meeting. Bidder must send by email clarifications they intend to ask in the Pre-Bid meeting by March 30, 2022, 01:00 PM Male’ Time. All registered Bidders will receive an email with the link to join the meeting Three (3) Days before the meeting. Only Two (2) representatives from each Bidder shall join the meeting. The Employer shall not be responsible for any interruptions or disconnections during the Online Video Conference Meeting. A site visit conducted by the Employer will not be organized. |

| C. Preparation of Bids |  |
| --- | --- |
| ITB 10.1 | The language of the Bid is: English All correspondence exchange shall be in English language. Language for translation of supporting documents and printed literature is English language. |
| ITB 11.1 (h) | The Bidder shall submit the following additional documents in its Bid: Code of Conduct for Contractor’s Personnel (ES) The Bidder shall submit its Code of Conduct that will apply to Contractor’s Personnel (as defined in Sub-Clause 1.1.17 of the General Conditions of Contract), to ensure compliance with the Contractor’s Environmental and Social (ES) obligations under the Contract. The Bidder shall use for this purpose the Code of Conduct form provided in Section IV. No substantial modifications shall be made to this form, except that the Bidder may introduce additional requirements, including as necessary to consider specific Contract issues/risks. |
| ITB 13.1 | Alternative Bids shall not be considered. |
| ITB 13.2 | Alternative times for completion shall not be permitted. |
| ITB 13.4 | Alternative technical solutions shall not be permitted. |
| ITB 14.5 | The prices quoted by the Bidder shall be: Fixed |
| ITB 15.1 | The unit rates and prices shall be quoted by the Bidder in the Bill of Quantities separately in the following currencies: (i) for those inputs to the Works that the Bidder expects to supply from within the Employer’s Country, in Maldivian Rufiyaa, and further referred to as “the local currency”; and (ii) for those inputs to the Works that the Bidder expects to supply from outside the Employer’s Country (referred to as “the foreign currency requirements”), in up to any Three (3) foreign currencies. Under MMA Monetary Regulation Section 5. any payment to local contractors will be made in the local currency. |
| ITB 18.1 | The Bid shall be valid until: August 31, 2022 |
| ITB 18.3 (a) | The Bid price shall be adjusted by the following factor(s): SOFR+1 for foreign currency |

| ITB 19.1 | A Bid Security shall be required in its original form. The amount and currency of the Bid Security shall be: Lot One: USD 300,000.00 Lot Two: USD 90,000.00 Lot Three: USD 100,000.00 The Beneficiary Address of the Bid Security shall be: Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives |
| --- | --- |
| ITB 19.3 | The Bid Security shall be unconditional guarantee issued by a reputable bank valid for TWENTY-EIGHT (28) Days beyond the original date of expiry of the Bid validity, or beyond any extended date if requested under ITB 18.2. |
| ITB 20.1 | In addition to the original of the Bid, the number of copies is: One (1) digital copy on a DVD or CD. The type of optical disk that should be used is DVD-R or CD-R. Any discrepancies between the hard copies and the DVD/CD, the original-hardcopy shall prevail. |
| ITB 20.3 | The written confirmation of authorization to sign on behalf of the Bidder shall consist of: Power of Attorney effective for the duration of the proposal validity, signed by legally authorized signatory(ies) of the bidder or all of the partners to a JV. Electronic Signature on Original Bid Document shall not be acceptable. |
| D. Submission and Opening of Bids |  |
| ITB 22.1 | For Bid submission purposes only, the Employer’s address is: National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives The deadline for Bid submission is: Date: June 01, 2022 Time: 01:00 PM Male’ Time Bidders shall not have the option of submitting their Bids electronically. |

| ITB 25.1 | The Bid opening shall take place at: National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives Date: June 01, 2022 Time: 01:00 PM Male’ Time |
| --- | --- |
| ITB 25.6 | The Letter of Bid and Price Schedules shall be initialed by Two (2) representatives of the Employer conducting Bid opening. |
| E. Evaluation, and Comparison of Bids |  |
| ITB 32.1 | The currency that shall be used for Bid evaluation and comparison purposes to convert (at the selling exchange rate) all Bid prices expressed in various currencies into a single currency is: United States Dollars The source of exchange rate shall be: Maldives Monetary Authority www.mma.gov.mv The date for the exchange rate shall be: May 18, 2022 |
| ITB 33.1 | A margin of domestic preference shall not apply. |
| ITB 34.1 | At this time the Employer does not intend to execute certain specific parts of the Works by subcontractors selected in advance. |
| ITB 34.2 | Contractor’s proposed subcontracting: Maximum percentage of subcontracting permitted is: Thirty-Five (35) Percent of the total contract amount. Bidders planning to subcontract more than 10% of total contract amount shall specify, in the Letter of Bid, the activity (ies) or parts of the Works to be subcontracted along with complete details of the subcontractors and their qualification and experience. Sub-contractors ‘qualification and experience will not be considered for evaluation of the Bidder. The Bidder on its own (without considering the qualification and experience of the sub-contractor) should meet the qualification criteria. |
| F. Award of Contract |  |
| ITB 47.1 | The successful Bidder shall not submit the Beneficial Ownership Disclosure Form. |
| ITB 48.1 and 48.2 | The successful Bidder shall be required to submit an Environmental and Social (ES) Performance Security. |
| ITB 49.1 | The procedures for making a Procurement-related Complaint are detailed in the “Procurement Regulations for IPF Borrowers (Annex III).” If a Bidder wishes to make a Procurement-related Complaint, the Bidder shall submit its complaint following these procedures, In Writing (by the quickest means available, such as by email), to: Ms.Fathimath Rishfa Ahmed Chief Procurement Executive National Tender Ministry of Finance Ameenee Magu, Maafannu, Male’, 20379 Republic of Maldives Tel: (+960) 3349102 E-Mail: ibrahim.aflah@finance.gov.mv Copy to: tender@finance.gov.mv In summary, a Procurement-related Complaint may challenge any of the following: - the terms of the Bidding Documents; and - the Employer’s decision to award the contract. |

Section III - Evaluation and Qualification Criteria

This section contains all the criteria that the Employer shall use to evaluate Bids and qualify Bidders. No other factors, methods or criteria shall be used other than specified in this Bidding document. The Bidder shall provide all the information requested in the forms included in Section IV, Bidding Forms.

Wherever a Bidder is required to state a monetary amount, Bidders should indicate the USD equivalent using the rate of exchange determined as follows:

- For construction turnover or financial data required for each year - Exchange rate prevailing on the last day of the respective calendar year (in which the amounts for that year is to be converted) was originally established.

- Value of single contract - Exchange rate prevailing on the date of the contract.

Exchange rates shall be taken from the publicly available source identified in the ITB 32.1. Any error in determining the exchange rates in the Bid may be corrected by the Employer.

- Technical and Financial Evaluation

- Evaluation of Technical Proposal

Assessment of adequacy of Technical Proposal with Requirements in accordance with ITB 35.1.

1.1 Techinical Proposal Scoring Methology: Not Applicable

- 1.2 Sustainable Procurement: Not Applicable

1.3 Alternative Technical Solutions for specified parts of the Works: Not Applicable

Financial Evaluation

2.1 Margin of Preference:  Not Applicable

2.2 Criteria for Financial Evaluation

In addition to the criteria listed in ITB 35.3 (a) – (e) the following criteria shall apply:

#### Time Schedule : None

#### Life Cycle Costs : None

- Combined Evaluation

Not Applicable

- Multiple Contracts

If permitted under ITB 35.5, will be evaluated as follows:

#### Award Criteria for Multiple Contracts [ITB 35.5]:

Lots

Bidders have the option to Bid for any one or more lots. Bids will be evaluated lot-wise, consider discounts offered, if any, after considering all possible combinations of lots, the contract(s) will be awarded to the Bidder or Bidders offering the lowest evaluated cost to the Employer for combined lots, subject to the selected Bidder(s) meeting the required qualification criteria for lot or combination of lots as the case may be.

#### Qualification Criteria for Multiple Contracts

The criteria for qualification is aggregate minimum requirement for respective lots as specified under items 3.1 and 3.2.

- Specialized Subcontractors

Not Applicable

- Qualification

| Eligibility and Qualification Criteria |  |  | Compliance Requirements |  |  |  | Documentation |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | Subject | Requirement | Single Entity | Joint Venture (existing or intended) |  |  | Submission Requirements |
|  |  |  |  | All Members Combined | Each Member | One Member |  |
| 1. Eligibility |  |  |  |  |  |  |  |
| 1.1 | Nationality | Nationality in accordance with ITB 4.4 | Must meet requirement | N/A | Must meet requirement | N/A | Forms ELI – 1.1 and 1.2, with attachments |
| 1.2 | Conflict of Interest | No conflicts of interest in accordance with ITB 4.2 | Must meet requirement | N/A | Must meet requirement | N/A | Letter of Bid |
| 1.3 | Bank Eligibility | Not having been declared ineligible by the Bank, as described in ITB 4.5. | Must meet requirement | N/A | Must meet requirement | N/A | Letter of Bid |
| 1.4 | State- owned Enterprise or Institution of the Borrower country | Meets conditions of ITB 4.6 | Must meet requirement | N/A | Must meet requirement | N/A | Forms ELI – 1.1 and 1.2, with attachments |
| 1.5 | United Nations resolution or Borrower’s country law | Not having been excluded as a result of prohibition in the Borrower’s country laws or official regulations against commercial relations with the Bidder’s country, or by an act of compliance with UN Security Council resolution, both in accordance with ITB 4.8 and Section V. | Must meet requirement | N/A | Must meet requirement | N/A | Forms ELI – 1.1 and 1.2, with attachments |
| 2. Historical Contract Non-Performance |  |  |  |  |  |  |  |
| 2.1 | History of Non-Performing Contracts | Non-performance of a contract did not occur as a result of contractor default since 1st January 2017. | Must meet requirement | N/A | Must meet requirement | N/A | Form CON-2 |
| 2.2 | Suspension Based on Execution of Bid/Proposal Securing Declaration by the Employer | Not under suspension based on-execution of a Bid/Proposal Securing Declaration pursuant to ITB 4.7 and ITB 19.9 | Must meet requirement | N/A | Must meet requirement | N/A | Letter of Bid |
| 2.3 | Pending Litigation | Bidder’s financial position and prospective long-term profitability still sound according to criteria established in 3.1 below and assuming that all pending litigation will be resolved against the Bidder. | Must meet requirement | N/A | Must meet requirement | N/A | Form CON – 2 |
| 2.4 | Litigation History | No consistent history of court/arbitral award decisions against the Bidder since 1st January 2017. | Must meet requirement | N/A | Must meet requirement | N/A | Form CON – 2 |
| 2.5 | Declaration: Environmental and Social (ES) past performance | Declare any civil work contracts that have been suspended or terminated and/or performance security called by an employer for reasons of breach of environmental, or social (including Sexual Exploitation, and Abuse) contractual obligations in the past Five (5) years. | Must make the declaration. | N/A | Each must make the declaration. | N/A | Form CON-3 ES Performance Declaration |
| 2.6 | Bank’s SEA and/or SH Disqualification | At the time of Contract Award, not subject to disqualification by the Bank for non-compliance with SEA/ SH obligations | Must meet requirement (including each subcontractor proposed by the Bidder) | N/A | Must meet requirement (including each subcontractor proposed by the Bidder) | N/A | Letter of Bid, Form CON-4 |

| Eligibility and Qualification Criteria |  |  | Compliance Requirements |  |  |  | Documentation |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | Subject | Requirement | Single Entity | Joint Venture (existing or intended) |  |  | Submission Requirements |
|  |  |  |  | All Members Combined | Each Member | One Member |  |
| 3. Financial Situation and Performance |  |  |  |  |  |  |  |
| 3.1 | Financial Capabilities | (i) The Bidder shall demonstrate that it has access to, or has available, liquid assets, unencumbered real assets, lines of credit, and other financial means (independent of any contractual advance payment) sufficient to meet the construction cash flow requirements estimated as per the following for the subject contract(s) net of the Bidder’s other commitments: Lot 1: USD 4 Million Lot 2: USD 1.2 Million Lot 3: USD 1.4 Million Bidders Bidding for multiple lots will be evaluated based on combination of lots (Refer Section III, B.) | Must meet requirement | Must meet requirement | Must meet at least Five (5) percent of the requirement | Must meet at least Fifty (50) percent of the requirement | Form FIN – 3.1, 3.3 & 3.4, with attachments Only the qualifications of the Bidder shall be considered. Qualifications of other firms, including the Bidder’s subsidiaries, parent entities, affiliates, subcontractors or any other firm(s) different from the Bidder SHALL NOT be considered. Line of Credit (LOC) shall be specific to the Bid/Lot or if a general LOC is presented it shall include up to date details such as remaining balance as of January 2022. |
|  |  | (ii) The Bidders shall also demonstrate, to the satisfaction of the Employer, that it has adequate sources of finance to meet the cash flow requirements on works currently in progress and for future contract commitments. | Must meet requirement | Must meet requirement | N/A | N/A |  |
|  |  | (iii) The Auditor’s Report independently audited and certified (with Financial Statements and Notes to Financial Statements) or, if not required by the laws of the Bidder’s country, other reports and/or financial statements acceptable to the Employer, for the years 2018, 2019 and 2020 shall be submitted and must demonstrate the current soundness of the Bidder’s financial position and indicate its prospective long-term profitability. | Must meet requirement Consolidated Financial Statements WILL NOT be Accepted. | N/A | Must meet requirement Consolidated Financial Statements WILL NOT be Accepted. | N/A |  |
| 3.2 | Average Annual Construction Turnover | Minimum average annual construction turnover as follows, calculated as total certified payments received for contracts in progress and/or completed within the years 2018, 2019 and 2020, divided by Three (3). Lot 1: USD 20 Million Lot 2: USD 6 Million Lot 3: USD 7 Million | Must meet requirement | Must meet requirement | Must meet at least Five (5) percent of the requirement | Must meet at least Fifty (50) percent of the requirement | Form FIN – 3.2 Only the qualifications of the Bidder shall be considered. Qualifications of other firms, including the Bidder’s subsidiaries, parent entities, affiliates, subcontractors or any other firm(s) different from the Bidder SHALL NOT be considered. |

| Eligibility and Qualification Criteria |  |  |  | Compliance Requirements |  |  |  | Documentation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. | Subject |  | Requirement | Single Entity | Joint Venture (existing or intended) |  |  | Submission Requirements |
|  |  |  |  |  | All Members Combined | Each Member | One Member |  |
| 4. Experience |  |  |  |  |  |  |  |  |
| 4.1(a) |  | General Construction Experience | Experience under construction contracts in the role of prime contractor, JV member, Subcontractor, or management contractor for at least the last Five (5) years, starting 1st January 2017. | Must meet requirement | N/A | Must meet requirement | N/A | Form EXP – 4.1 Only the qualifications of the Bidder shall be considered. Qualifications of other firms, including the Bidder’s subsidiaries, parent entities, affiliates, subcontractors or any other firm(s) different from the Bidder SHALL NOT be considered. |
| 4.2(a) |  | Specific Construction & Contract Management Experience | (i) A minimum number of similar contracts that have been satisfactorily and substantially completed as a prime contractor, joint venture member, management contractor or Subcontractor between 1st January 2017 and bid submission deadline as specified below. - Minimum three (3) projects including both low voltage (<400V) and medium voltage (6-33kV) underground distribution cable installations with cumulative length not lower than 30 km for Lot 1 and 10 km for Lo2 and 3; and - Minimum two (2) projects inclusive of substation automation works (Substation automation: including supply, installation and commissioning of intelligent electronic devices (IED), such as per IEC 61850) | Must meet requirement | N/A | N/A | Must meet requirement | Form EXP 4.2(a) [Bidder must submit copy of the original documents to prove completion of the works (Operational Acceptance Certificate OR Completion Certificate OR Completion Letter, etc. which should be in the Bidder’s name] Only the qualifications of the Bidder shall be considered. Qualifications of other firms, including the Bidder’s subsidiaries, parent entities, affiliates, subcontractors or any other firm(s) different from the Bidder SHALL NOT be considered. |
|  |  |  | (ii) Minimum two (2) project inclusive of substation automation works. | Must meet requirement | N/A | N/A | Must meet requirement |  |
| 4.2(b) |  | Specific Experience in managing ES aspects | For the contracts in 4.2 (a) above and/or any other contracts [substantially completed and under implementation] as prime contractor, joint venture member, or Subcontractor between 1st January 2017 and Bid submission deadline, experience in managing ES risks and impacts in the following aspect(s): Preparation or implementation of project specific ESIA or ESMP or ESCP or other equivalent required by the law of the specific country. | Must meet requirements | Must meet requirement | N/A | N/A | Form EXP 4.2 (b) Only the qualifications of the Bidder shall be considered. Qualifications of other firms, including the Bidder’s subsidiaries, parent entities, affiliates, subcontractors or any other firm(s) different from the Bidder SHALL NOT be considered. [Bidder shall submit a supporting document stating the scope of ESIA/ESMP/ESCP specific works undertaken] |

5.	Contractor’s Representative and Key Personnel

The Bidder must demonstrate that it will have a suitably qualified Contractor’s Representative and suitably qualified (and in adequate numbers) Key Personnel, as described in the Specification.

The Bidder shall provide details of the Contractor’s Representative and Key Personnel and such other Key Personnel that the Bidder considers appropriate to perform the Contract, together with their academic qualifications and work experience. The Bidder shall complete the relevant Forms in Section IV, Bidding Forms.

6.	Equipment

The Bidder must demonstrate that it has access to the key equipment listed hereafter:

| Equipment Type and Characteristics | Minimum Number required |
| --- | --- |
| Lot 1 | 2 |
| Trenching equipment suitable for medium voltage trench profiles |  |
| Lot 2 |  |
| Trenching equipment suitable for medium voltage trench profiles | 2 |
| Lot 3 |  |
| Trenching equipment suitable for medium voltage trench profiles | 2 |

The Bidder shall provide further details of proposed items of equipment using Form EQU in Section IV, Bidding Forms.

Section IV - Bidding Forms

Table of Forms

Letter of Bid	49

Appendix to Bid	53

Schedule of Cost Indexation	53

Not Applicable	53

Table B.  Foreign Currency (FC)	53

Not Applicable	53

Table C.  Summary of Payment Currencies	54

Bill of Quantities	55

Bill No. 1:  General Items – Lot 1	57

Bill No. 2:  Electrical Works – Lot 1	58

Daywork Schedule – Lot 1	66

Daywork Summary – Lot 1	68

Grand Summary – Lot 1	69

Bill No. 1:  General Items – Lot 2	70

Bill No. 2:  Electrical Works – Lot 2	71

Daywork Schedule – Lot 2	77

Daywork Summary – Lot 2	79

Grand Summary – Lot 2	80

Bill No. 1:  General Items – Lot 3	81

Bill No. 2:  Electrical Works – Lot 3	82

Daywork Schedule – Lot 3	98

Daywork Summary – Lot 3	100

Grand Summary – Lot 3	101

Technical Proposal	103

Form TECH- 1: Site Organization	104

Form TECH- 2: Method Statement	105

Form TECH- 3: Schedule	107

Code of Conduct for Contractor’s Personnel (ES) Form	108

Form TECH- 6: Materials	112

Form EQU: Equipment	112

Form PER -1	114

Form PER-2:	116

Bidders Qualification without prequalification	118

Form ELI -1.1	119

Form ELI -1.2	120

Form CON – 2	121

Form CON – 3	123

Form CON – 4	125

Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment Performance Declaration	125

Form FIN – 3.1:	127

Form FIN – 3.2:	129

Form FIN – 3.3:	130

Form FIN – 3.4:	131

Form EXP - 4.1	132

Form EXP - 4.2(a)	133

Form of Bid Security - Demand Guarantee	136

Letter of Bid

[The Bidder must prepare the Letter of Bid on stationery with its letterhead clearly showing the Bidder’s complete name and address.]

Note:  All italicized text in brackets is for use in preparing this form and shall be deleted from the final products.

Date of this Bid submission: [insert date (as day, month and year) of Bid submission]

Request for Bid No.: [insert identification]

To:	Ms. Fathimath Rishfa Ahmed

National Tender,

Ministry of Finance

Ameenee Magu,

Male’, 20379

Republic of Maldives

GRID-UPGRADING IN SELECTED ISLANDS IN THE MALDIVES

[delete as appropriate if bidding for separate Lots]:

Lot 1: Grid-Upgrading in Addu City mainland, Addu City Hulhumeedhoo, Fuvamulah City, and GDh. Thinadhoo

Lot 2: Grid-Upgrading in B. Eydhafushi, Lh. Hinnavaru, Kulhudhuffushi City

Lot 3: Grid-Upgrading in L. Fonadhoo, interconnected network of L. Isdhoo, L. Kalaidhoo and L. Dhabidhoo, L. Maabaidhoo, L. Kunahandhoo, L. Hithadhoo and Sh. Funadhoo

We, the undersigned, declare that:

- No reservations: We have examined and have no reservations to the Bidding document, including Addenda issued in accordance with ITB 8;

- Eligibility: We meet the eligibility requirements and have no conflict of interest in accordance with ITB 4;

- Bid-Securing Declaration: We have not been suspended nor declared ineligible by the Employer based on execution of a Bid-Securing or Proposal-Securing Declaration in the Employer’s Country in accordance with ITB 4.7;

- Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment (SH): [select the appropriate option from (i) to (v) below and delete the others].

We [where JV, insert: “including any of our JV members”], and any of our subcontractors:

- [have not been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.]

- [are subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.]

- [had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations. An arbitral award on the disqualification case has been made in our favor.]

- [had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations for a period of two years. We have subsequently provided and demonstrated that we have adequate capacity and commitment to comply with SEA and SH prevention and response obligations.]

- [had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations for a period of two years. We have attached documents demonstrating that we have adequate capacity and commitment to comply with SEA and SH prevention and response obligations.]

- Conformity: We offer to execute in conformity with the Bidding document and in accordance with the implementation and completion specified in the construction schedule, the following Works: [insert a brief description of the Works];

;

- Bid Price: The total price of our Bid, excluding any discounts offered in item (f) below is: [Insert one of the options below as appropriate]

Option 1, in case of one lot:  Total price is: [insert the total price of the Bid in words and figures, indicating the various amounts and the respective currencies];

Or

Option 2, in case of multiple lots: (a) Total price of each lot [insert the total price of each lot in words and figures, indicating the various amounts and the respective currencies]; and (b) Total price of all lots (sum of all lots) [insert the total price of all lots in words and figures, indicating the various amounts and the respective currencies];

- Discounts: The discounts offered and the methodology for their application are:

(i) The discounts offered are: [Specify in detail each discount offered.]

(ii) The exact method of calculations to determine the net price after application of discounts is shown below: [Specify in detail the method that shall be used to apply the discounts];

- Bid Validity: Our Bid shall be valid until SEPTEMBER 22, 2022 in accordance with ITB 18.1, and it shall remain binding upon us and may be accepted at any time before the expiration of that period;

- Performance Security If our Bid is accepted, we commit to obtain a Performance Security and an Environmental and Social (ES) Performance Security, in accordance with the Bidding document;

- One Bid Per Bidder: We are not submitting any other Bid(s) as an individual Bidder, and we are not participating in any other Bid(s) as a Joint Venture member or as a subcontractor, and meet the requirements of ITB 4.3, other than alternative Bids submitted in accordance with ITB 13;

- Suspension and Debarment: We, along with any of our subcontractors, suppliers, consultants, manufacturers, or service providers for any part of the contract, are not subject to, and not controlled by any entity or individual that is subject to, a temporary suspension or a debarment imposed by the World Bank Group or a debarment imposed by the World Bank Group in accordance with the Agreement for Mutual Enforcement of Debarment Decisions between the World Bank and other development banks. Further, we are not ineligible under the Employer’s Country laws or official regulations or pursuant to a decision of the United Nations Security Council;

- State-owned enterprise or institution: [select the appropriate option and delete the other] [We are not a state-owned enterprise or institution] / [We are a state-owned enterprise or institution but meet the requirements of ITB 4.6];

- Commissions, gratuities, fees: We have paid, or will pay the following commissions, gratuities, or fees with respect to the Bidding process or execution of the Contract: [insert complete name of each Recipient, its full address, the reason for which each commission or gratuity was paid and the amount and currency of each such commission or gratuity]

| Name of Recipient | Address | Reason | Amount |
| --- | --- | --- | --- |

(If none has been paid or is to be paid, indicate “none.”)

- Binding Contract: We understand that this Bid, together with your written acceptance thereof included in your Letter of Acceptance, shall constitute a binding contract between us, until a formal contract is prepared and executed;

- Not Bound to Accept: We understand that you are not bound to accept the lowest evaluated cost Bid, the Most Advantageous Bid or any other Bid that you may receive;

- Fraud and Corruption: We hereby certify that we have taken steps to ensure that no person acting for us or on our behalf engages in any type of Fraud and Corruption;

- Potential DAAB Members: We hereby propose the following three persons, whose curriculum vitae are attached, as potential DAAB members:

| Name | Address |
| --- | --- |
| - ……...... |  |
| - ……….. |  |
| - ……… |  |

Name of the Bidder: *[insert name of the Bidder]

Name of the person duly authorized to sign the Bid on behalf of the Bidder: **[insert complete name of person duly authorized to sign the Bid]

Title of the person signing the Bid: [insert complete title of the person signing the Bid]

Signature of the person named above: [insert signature of person whose name and capacity are shown above]

Date signed [insert date of signing] day of [insert month], [insert year]

Date signed ________________________________ day of _______________________, _____

*: In the case of the Bid submitted by joint venture specify the name of the Joint Venture as Bidder

**: Person signing the Bid shall have the power of attorney given by the Bidder to be attached with the Bid

Appendix to Bid

Schedule of Cost Indexation

Not Applicable

Table of Adjustment Data

Not Applicable

Table B.  Foreign Currency (FC)

Not Applicable

Table C.  Summary of Payment Currencies

Table:  Alternative B

To be used only with Alternative B Prices directly quoted in the currencies of payment.  (ITB 15.1)

Summary of currencies of the Bid for                                          [insert name of Section of the Works]

| Name of currency | Amounts payable |
| --- | --- |
| Local currency: |  |
| Foreign currency #1: |  |
| Foreign currency #2: |  |
| Foreign currency #3: |  |
| Provisional sums expressed in local currency ____________________________________ | [To be entered by the Employer] |

Bill of Quantities

A.  Preamble

      - The Bill of Quantities shall be read in conjunction with the Instructions to Bidders, General and Particular Conditions, Technical Specifications, and Drawings.

      - The quantities given in the Bill of Quantities are estimated and provisional, and are given to provide a common basis for bidding.  The basis of payment will be the actual quantities of work ordered and carried out, as measured by the Contractor and verified by the Engineer and valued at the rates and prices bid in the priced Bill of Quantities, where applicable, and otherwise at such rates and prices as the Engineer may fix within the terms of the Contract.

      - The rates and prices bid in the priced Bill of Quantities shall, except insofar as it is otherwise provided under the Contract, include all Constructional Plant, labour, supervision, materials, erection, maintenance, insurance, profit, taxes, and duties, together with all general risks, liabilities, and obligations set out or implied in the Contract.

      - A rate or price shall be entered against each item in the priced Bill of Quantities, whether quantities are stated or not.  The cost of Items against which the Contractor has failed to enter a rate or price shall be deemed to be covered by other rates and prices entered in the Bill of Quantities.

      - The whole cost of complying with the provisions of the Contract shall be included in the Items provided in the priced Bill of Quantities, and where no Items are provided, the cost shall be deemed to be distributed among the rates and prices entered for the related Items of Work.

      - General directions and descriptions of work and materials are not necessarily repeated nor summarized in the Bill of Quantities.  References to the relevant sections of the Contract documentation shall be made before entering prices against each item in the priced Bill of Quantities.

      - Provisional Sums included and so designated in the Bill of Quantities shall be expended in whole or in part at the direction and discretion of the Engineer in accordance with Sub-Clauses 13.4 and 13.5 of the General Conditions except with respect to DAAB Fees and Expenses for which no instruction will be required from the Engineer.

      - The method of measurement of completed work for payment shall be in accordance with Standard Method of Measurement of the U.K. Institution of Civil Engineers.

B.  Work Items

1.	The Bill of Quantities usually contains the following part Bills, which have been grouped according to the nature or timing of the work:

Bill No. 1—General Items;

Bill No. 2—Bill of Quantities;

Daywork Schedule; and

Summary Bill of Quantities.

2.	If BDS-ITB 15.1 (a) applies, Bidders shall price the Bill of Quantities in local currency only and shall indicate in the Appendix to Bid the percentage expected for payment in foreign currency or currencies. If BDS-ITB 15.1 (b) applies Bidders shall price the Bill of Quantities in the applicable currency or currencies.

## Bill of Quantities

Bill No. 1:  General Items – Lot 1

| Bill No. 1.1: General Items – Lot 1 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description/Type | Type | Unit | Quantity | Rate | Amount |  |  |  |
|  |  |  |  |  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| 1.0 | Site investigation |  |  |  |  |  |  |  |  |
| 1.01 |  | Soil temperature, electrical and thermal resistivity | Islands | 4 |  |  |  |  |  |
| 1.02 |  | Route confirmation, including underground and concealed services survey | Islands with cable installation | 4 |  |  |  |  |  |
| 1.03 |  | Verification of suitability of MV configuration | Islands with MV works | 4 |  |  |  |  |  |
| 2.0 | Design confirmation |  |  |  |  |  |  |  |  |
| 2.01 |  | Power systems studies | Islands with MV works | 3 |  |  |  |  |  |
| 2.02 |  | MV Protection study | Islands with MV works | 4 |  |  |  |  |  |
| 2.03 |  | MV Earthing study | Islands with MV works | 4 |  |  |  |  |  |
| 2.04 |  | MV Cable sizing report | Islands with MV works | 4 |  |  |  |  |  |
| 2.05 |  | LV protection report | Islands with LV works | - |  |  |  |  |  |
| 2.06 |  | LV cable sizing and earthing report | Islands with LV works | - |  |  |  |  |  |
| 2.07 |  | Communications design report | Islands | 4 |  |  |  |  |  |
| 2.08 | For construction drawings: | Drawings and installation specifications | Islands | 4 |  |  |  |  |  |
| 2.09 | GIS mapping | Final route map in GIS format | Islands with cable installation | 4 |  |  |  |  |  |
| 3.0 | As-built drawings |  |  |  |  |  |  |  |  |
| 3.01 |  | Drawings | Islands | 4 |  |  |  |  |  |
| 3.02 | Manuals and procedures documentation | All | Islands | 4 |  |  |  |  |  |
| 3.03 | Training & Capacity Building | All | Islands | 4 |  |  |  |  |  |
| 4.0 | Environmental & Social tasks |  |  |  |  |  |  |  |  |
| 4.01 |  | Implementation of Environmental and Social Code of Practice (ESCP) | Islands | 4 |  |  |  |  |  |
| 4.02 |  | Transfer of Construction waste to Thilafushi during demobilization | Islands | 4 |  |  |  |  |  |
| 4.03 |  | Procuring of safety signs, barricade tape and project site boards for each island | Islands | 4 |  |  |  |  |  |
| 4.04 |  | Procuring Personal Protective Equipment for workforce as per the ESCP | Islands | 4 |  |  |  |  |  |
| 4.05 |  | Health and Safety Toolbox training to construction workforce prior to commencement and weekly thereafter as per ESCP | Islands | 4 |  |  |  |  |  |
| 4.06 |  | Excavation protection sloping/shoring/shielding method approved by engineer as per the ESCP | Islands | 4 |  |  |  |  |  |
| 4.07 |  | Briefing session on Code of conduct of workforce prior to commencement of work | Islands | 4 |  |  |  |  |  |
| 4.08 |  | Development of Occupation Health Safety Management Plan for the project | Document | 1 |  |  |  |  |  |
| 4.09 |  | Updating of ESCP | Document | 1 |  |  |  |  |  |
| Total for Bill No. 1.1 (carried forward to Grand Summary – Lot 1, p. …………) |  |  |  |  |  |  |  |  |  |

Bill No. 2:  Electrical Works – Lot 1

| Bill No. 2a: ADDU CITY MAIN LAND |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | 1 |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | 40,000 |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | 1,200 |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 2,040 |  |  |  | L |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building (This is only needed for new substations) - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 6 |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | 5 |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | 5 |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | 5 |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 5 |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |
| Total for Bill No.2a (carried forward to Grand Summary – Lot 1, p...................) |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2b: ADDU CITY- HULHUMEEDHOO |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |
|  |  |  |  |  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | 2 |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | 21,000 |  |  |  |  |  |
|  |  | 70 mm2 | Meter | - |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 2 |  |  | 9 |  |  |
| 3.02 |  | Outdoor substation civil works Includes all related equipment and installation requirements, not limited to: fencing, foundations, earthing, ducting, cable entries, security, lighting | Unit | 1 |  |  |  |  |  |
| 3.03 |  | RMU-4 way | Unit | 2 |  |  |  |  |  |
| 3.04 |  | RMU-3 way | Unit | 7 |  |  |  |  |  |
| 3.05 |  | 800 kVA transformer | Unit | 2 |  |  |  |  |  |
| 3.06 |  | 500 kVA transformer | Unit | 7 |  |  |  |  |  |
| 3.07 |  | LV DB | Unit | - |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |
| Total for Bill 2b. (carried forward to Grand Summary – Lot 1, p..................) |  |  |  |  |  |  |  |  |  |

| Bill No. 2c: FUVAHMULAH CITY |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |
|  |  |  |  |  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 850 |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 2c (carried forward to Grand Summary – Lot 1, p. ……) |  |  |  |  |  |  |  |  |  |

| Bill No. 2d: GDh. THINADHOO |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |
|  |  |  |  |  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | 2 |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | 6,500 |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 620 |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 4 |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | - |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | 8 |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | 8 |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 8 |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  |  | - |  |  |  |  |  |
| Total for Bill No. 2d (carried forward to Grand Summary – Lot 1, p. ……….) |  |  |  |  |  |  |  |  |  |

Daywork Schedule – Lot 1

General

Reference should be made to Sub-Clause 13.5 of the General Conditions. Work shall not be executed on a daywork basis except by written order of the Engineer. Bidders shall enter rates for daywork items in the Schedules, which rates shall apply to any quantity of daywork ordered by the Engineer.  Nominal quantities have been indicated against each item of daywork, and the extended total for Daywork shall be carried forward as a Provisional Sum to the Summary Total Bid Amount.

Daywork Labour

The Contractor shall be entitled to payment in respect of the total time that labour is employed on daywork, calculated at the rates entered by the Contractor in the Schedule of Daywork Rates:  1. Labour, together with an additional percentage payment on rates representing the Contractor’s profit, overheads, etc.

Daywork Materials

The Contractor shall be entitled to payment in respect of materials used for daywork (except for materials for which the cost is included in the percentage addition to labour costs as detailed heretofore), at the rates entered by the Contractor in the Schedule of Daywork Rates: 2. Materials, together with an additional percentage payment on the rates to cover overhead charges and profit etc.

Daywork Contractor’s Equipment

The Contractor shall be entitled to payments in respect of Contractor’s Equipment already on Site and employed on daywork at the rental rates entered by the Contractor in the Schedule of Daywork Rates:  3. Contractor’s Equipment.  Said rates shall be deemed to include due and complete allowance for depreciation, interest, indemnity, and insurance, repairs, maintenance, supplies, fuel, lubricants, and other consumables, and all overhead, profit, and administrative costs related to the use of such equipment. The cost of drivers, operators, and assistants will be paid for separately as described under the section on Daywork Labour.

| Schedule of Daywork Rates: 1. Labour – Lot 1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item no. | Description | Unit | Nominal quantity | Rate a | Extended amount |
| 1 | unqualified labourer | Day | 10 |  |  |
| 2 | trainee or apprentice electrician | Day | 10 |  |  |
| 3 | qualified electrician, low voltage | Day | 10 |  |  |
| 4 | qualified electrician, medium voltage | Day | 10 |  |  |
| 5 | Site supervisor | Day | 10 |  |  |
| 6 | Per-diem (including accommodation) for non-resident staff | Day | 10 |  |  |
| Total for Daywork: Labour (carried forward to Daywork Summary, p. ……) |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |  |

| Schedule of Daywork Rates: 2. Materials – Lot 1 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description | Unit | Nominal quantity | Rate a | Extended amount |  |
| 1 | Concrete | m3 | 5 |  |  |  |
| 2 | Reinstate concrete road following trenching for cable route | m | 100 |  |  |  |
| 3 | Reinstate unpaved road following trenching for cable route | m | 100 |  |  |  |
| Total for Daywork: Materials (carried forward to Daywork Summary, p. ……) |  |  |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |  |  |  |  |

| Schedule of Daywork Rates: 3. Contractor’s Equipment – Lot 1 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description | Nominal quantity (hours) | Basic hourly rental rate a | Extended amount |  |
| 1 | Excavator | 10 |  |  |  |
| 2 | Cable drum roller | 5 |  |  |  |
| 3 | Rigid 2 or 3 axle truck | 20 |  |  |  |
| Total for Daywork: Contractor’s Equipment (carried forward to Daywork Summary, p. …..) |  |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |

Daywork Summary – Lot 1

| Details | Page | Amount (MVR) | % Foreign |
| --- | --- | --- | --- |
| 1. Total for Daywork: Labour |  |  |  |
| 2. Total for Daywork: Materials |  |  |  |
| 3. Total for Daywork: Contractor’s Equipment |  |  |  |
| Total for Daywork (Provisional Sum) (carried forward to Grand Summary, p. ……) |  |  |  |

Grand Summary – Lot 1

| General Summary | Page | Amount |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| Bill No. 1: General Items – Lot 1 |  |  |  |  |  |
| Bill No. 2: Electrical Works – Lot 1 |  |  |  |  |  |
| Bill No. 2 a - Addu City Mainland |  |  |  |  |  |
| Bill No. 2 b - Addu City Hulhumeedhoo |  |  |  |  |  |
| Bill No. 2 c - Fuvamulah City |  |  |  |  |  |
| Bill No. 2 d - GDh. Thinadhoo |  |  |  |  |  |
| Subtotal of Bills - Lot 1 (in case of multiple lots carried forward to Grand Summary – Multiple Lots) | (A) |  |  |  |  |
| Total for Daywork (Provisional Sum) * | (B) |  |  |  |  |
| Total of Bills Plus Provisional Sums (A + B) i | (D) |  |  |  |  |
| Add Provisional Sum for Contingency Allowance [Two (2) percent of the Subtotal of Bills (A)] ii | (E) | [sum] | [sum] | [sum] | [sum] |
| Bid Price (D + E) (Carried forward to Letter of Bid) | (F) |  |  |  |  |

i) All Provisional Sums are to be expended in whole or in part at the direction and discretion of the Engineer in accordance with Sub-Clauses 13.4 and 13.5 of the General Conditions except with respect to DAAB Fees and Expenses for which Sub-Clause 13.4 of the Particular Conditions – Part B shall apply.

ii) To be entered by the Employer.

* For evaluation purposes, Provisional Sum, other than Daywork will be excluded

Bill No. 1:  General Items – Lot 2

| Bill No. 1.2: General Items -Lot 2 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description | Type | Unit | Quantity | Rate | Amount |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| 1.0 | Site investigation |  |  |  |  |  |  |  |  |  |
| 1.01 |  | Soil temperature, electrical and thermal resistivity | Islands | 3 |  |  |  |  |  |  |
| 1.02 |  | Route confirmation, including underground and concealed services survey | Islands with cable installation | 3 |  |  |  |  |  |  |
| 1.03 |  | Verification of suitability of MV configuration | Islands with MV works | 3 |  |  |  |  |  |  |
| 2.0 | Design confirmation |  |  |  |  |  |  |  |  |  |
| 2.01 |  | Power systems studies | Islands with MV works | 3 |  |  |  |  |  |  |
| 2.02 |  | MV Protection study | Islands with MV works | 3 |  |  |  |  |  |  |
| 2.03 |  | MV Earthing study | Islands with MV works | 3 |  |  |  |  |  |  |
| 2.04 |  | MV Cable sizing report | Islands with MV works | 3 |  |  |  |  |  |  |
| 2.05 |  | LV protection report | Islands with LV works | - |  |  |  |  |  |  |
| 2.06 |  | LV cable sizing and earthing report | Islands with LV works | - |  |  |  |  |  |  |
| 2.07 |  | Communications design report | Islands | 3 |  |  |  |  |  |  |
| 2.08 | For construction drawings | Drawings and installation specifications | Islands | 3 |  |  |  |  |  |  |
| 2.09 | GIS mapping | Final route map in GIS format | Islands with cable installation | 3 |  |  |  |  |  |  |
| 3.0 | As-built drawings |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Drawings | Islands | 3 |  |  |  |  |  |  |
| 3.02 | Manuals and procedures documentation | All | Islands | 3 |  |  |  |  |  |  |
| 3.03 | Training & Capacity Building | All | Islands | 3 |  |  |  |  |  |  |
| 4.0 | Environmental & Social tasks |  |  |  |  |  |  |  |  |  |
| 4.01 |  | Implementation of Environmental and Social Code of Practice (ESCP) | Islands | 4 |  |  |  |  |  |  |
| 4.02 |  | Transfer of Construction waste to Thilafushi during demobilization | Islands | 4 |  |  |  |  |  |  |
| 4.03 |  | Procuring of safety signs, barricade tape and project site boards for each island | Islands | 4 |  |  |  |  |  |  |
| 4.04 |  | Procuring Personal Protective Equipment for workforce as per the ESCP | Islands | 4 |  |  |  |  |  |  |
| 4.05 |  | Health and Safety Toolbox training to construction workforce prior to commencement and weekly thereafter as per ESCP | Islands | 4 |  |  |  |  |  |  |
| 4.06 |  | Excavation protection sloping/shoring/shielding method approved by engineer as per the ESCP | Islands | 4 |  |  |  |  |  |  |
| 4.07 |  | Briefing session on Code of conduct of workforce prior to commencement of work | Islands | 4 |  |  |  |  |  |  |
| 4.08 |  | Development of Occupation Health Safety Management Plan for the project | Document | 1 |  |  |  |  |  |  |
| 4.09 |  | Updating of ESCP | Document | 1 |  |  |  |  |  |  |
| Total for Bill No. 1.2: General Items -Lot 2 (carried forward to Grand Summary – Lot 2, p. ….) |  |  |  |  |  |  |  |  |  |  |

Bill No. 2:  Electrical Works – Lot 2

| Bill No. 2e: B. EYDHAFUSHI |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | 2,800 |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 600 |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 5 |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | 5 |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | 5 |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 5 |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | 585 |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | 608 |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 2e (carried forward to Grand Summary – Lot 2, p. ……) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2f: Lh. HINNAVARU |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |
|  |  |  |  |  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | 2 |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | 1 |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | 2,600 |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 1,000 |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 5 |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | 5 |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | - |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | 5 |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 5 |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | 152 |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | 279 |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | 292 |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | 457 |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |
| Total for Bill No. 2f. (carried forward to Grand Summary – Lot 2, p. ……) |  |  |  |  |  |  |  |  |  |

| Bill No. 2g: KULHUDHUFUSHI CITY |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | 16,500 |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | 0 |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | - |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 2g (carried forward to Grand Summary – Lot 2, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

Daywork Schedule – Lot 2

General

Reference should be made to Sub-Clause 13.5 of the General Conditions. Work shall not be executed on a daywork basis except by written order of the Engineer. Bidders shall enter rates for daywork items in the Schedules, which rates shall apply to any quantity of daywork ordered by the Engineer.  Nominal quantities have been indicated against each item of daywork, and the extended total for Daywork shall be carried forward as a Provisional Sum to the Summary Total Bid Amount.

Daywork Labour

The Contractor shall be entitled to payment in respect of the total time that labour is employed on daywork, calculated at the rates entered by the Contractor in the Schedule of Daywork Rates:  1. Labour, together with an additional percentage payment on rates representing the Contractor’s profit, overheads, etc.

Daywork Materials

The Contractor shall be entitled to payment in respect of materials used for daywork (except for materials for which the cost is included in the percentage addition to labour costs as detailed heretofore), at the rates entered by the Contractor in the Schedule of Daywork Rates: 2. Materials, together with an additional percentage payment on the rates to cover overhead charges and profit etc.

Daywork Contractor’s Equipment

The Contractor shall be entitled to payments in respect of Contractor’s Equipment already on Site and employed on daywork at the rental rates entered by the Contractor in the Schedule of Daywork Rates:  3. Contractor’s Equipment.  Said rates shall be deemed to include due and complete allowance for depreciation, interest, indemnity, and insurance, repairs, maintenance, supplies, fuel, lubricants, and other consumables, and all overhead, profit, and administrative costs related to the use of such equipment. The cost of drivers, operators, and assistants will be paid for separately as described under the section on Daywork Labour.

| Schedule of Daywork Rates: 1. Labour – Lot 2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item no. | Description | Unit | Nominal quantity | Rate a | Extended amount |
| 1 | unqualified labourer | Day | 10 |  |  |
| 2 | trainee or apprentice electrician | Day | 10 |  |  |
| 3 | qualified electrician, low voltage | Day | 10 |  |  |
| 4 | qualified electrician, medium voltage | Day | 10 |  |  |
| 5 | Site supervisor | Day | 10 |  |  |
| 6 | Per-diem (including accommodation) for non-resident staff | Day | 10 |  |  |
| Total for Daywork: Labour (carried forward to Daywork Summary, p. ……) |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |  |

| Schedule of Daywork Rates: 2. Materials – Lot 2 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description | Unit | Nominal quantity | Rate a | Extended amount |  |
| 1 | Concrete | m3 | 5 |  |  |  |
| 2 | Reinstate concrete road following trenching for cable route | m | 100 |  |  |  |
| 3 | Reinstate unpaved road following trenching for cable route | m | 100 |  |  |  |
| Total for Daywork: Materials (carried forward to Daywork Summary, p. ……) |  |  |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |  |  |  |  |

| Schedule of Daywork Rates: 3. Contractor’s Equipment – Lot 2 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item no. | Description | Nominal quantity (hours) | Basic hourly rental rate a | Extended amount |
| 1 | Excavator | 10 |  |  |
| 2 | Cable drum roller | 5 |  |  |
| 3 | Rigid 2 or 3 axle truck | 20 |  |  |
| Total for Daywork: Contractor’s Equipment (carried forward to Daywork Summary, p. ……) |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |

Daywork Summary – Lot 2

| Details | Page | Amount (MVR) | % Foreign |
| --- | --- | --- | --- |
| 1. Total for Daywork: Labour |  |  |  |
| 2. Total for Daywork: Materials |  |  |  |
| 3. Total for Daywork: Contractor’s Equipment |  |  |  |
| Total for Daywork (Provisional Sum) (carried forward to Grand Summary, p. ……) |  |  |  |

Grand Summary – Lot 2

| General Summary | Page | Amount |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| Bill No. 1: General Items – Lot 2 |  |  |  |  |  |
| Bill No. 2: Electrical Works – Lot 2 |  |  |  |  |  |
| Bill No. 2 e – B. Eydhafushi |  |  |  |  |  |
| Bill No. 2 f – Lh. Hinnavaru |  |  |  |  |  |
| Bill No. 2 g – Kulhudhuffushi City |  |  |  |  |  |
| Subtotal of Bills Lot 2 (in case of multiple lots carried forward to Grand Summary – Multiple Lots) | (A) |  |  |  |  |
| Total for Daywork (Provisional Sum) * | (B) |  |  |  |  |
| Total of Bills Plus Provisional Sums (A + B) i | (D) |  |  |  |  |
| Add Provisional Sum for Contingency Allowance [2 percent of Subtotals of Bills (A)] ii | (E) | [sum] | [sum] | [sum] | [sum] |
| Bid Price (D + E) (Carried forward to Letter of Bid) | (F) |  |  |  |  |

i) All Provisional Sums are to be expended in whole or in part at the direction and discretion of the Engineer in accordance with Sub-Clauses 13.4 and 13.5 of the General Conditions except with respect to DAAB Fees and Expenses for which Sub-Clause 13.4 of the Particular Conditions – Part B shall apply.

ii) To be entered by the Employer.

* For evaluation purposes, Provisional Sum, other than Daywork will be excluded

Bill No. 1:  General Items – Lot 3

| Bill No. 1.3: General Items – Lot 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Site investigation |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | Soil temperature, electrical and thermal resistivity | Islands | 8 |  |  |  |  |  |  |  |  |  |
| 1.02 |  | Route confirmation, including underground and concealed services survey | Islands with cable installation | 7 |  |  |  |  |  |  |  |  |  |
| 1.03 |  | Verification of suitability of MV configuration | Islands with MV works | 5 |  |  |  |  |  |  |  |  |  |
| 2.0 | Design confirmation |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | Power systems studies | Islands with MV works | 5 |  |  |  |  |  |  |  |  |  |
| 2.02 |  | MV Protection study | Islands with MV works | 5 |  |  |  |  |  |  |  |  |  |
| 2.03 |  | MV Earthing study | Islands with MV works | 5 |  |  |  |  |  |  |  |  |  |
| 2.04 |  | MV Cable sizing report | Islands with MV works | 5 |  |  |  |  |  |  |  |  |  |
| 2.05 |  | LV protection report | Islands with LV works | 3 |  |  |  |  |  |  |  |  |  |
| 2.06 |  | LV cable sizing and earthing report | Islands with LV works | 3 |  |  |  |  |  |  |  |  |  |
| 2.07 |  | Communications design report | Islands | 8 |  |  |  |  |  |  |  |  |  |
| 2.08 | For construction drawings | Drawings and installation specifications | Islands | 8 |  |  |  |  |  |  |  |  |  |
| 2.09 | GIS mapping | Final route map in GIS format | Islands with cable installation | 7 |  |  |  |  |  |  |  |  |  |
| 3.0 | As-built drawings |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Drawings | Islands | 8 |  |  |  |  |  |  |  |  |  |
| 3.02 | Manuals and procedures documentation | All | Islands | 8 |  |  |  |  |  |  |  |  |  |
| 3.03 | Training & Capacity Building | All | Islands | 8 |  |  |  |  |  |  |  |  |  |
| 4.0 | Environmental & Social tasks |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | Implementation of Environmental and Social Code of Practice (ESCP) | Islands | 4 |  |  |  |  |  |  |  |  |  |
| 4.02 |  | Transfer of Construction waste to Thilafushi during demobilization | Islands | 4 |  |  |  |  |  |  |  |  |  |
| 4.03 |  | Procuring of safety signs, barricade tape and project site boards for each island | Islands | 4 |  |  |  |  |  |  |  |  |  |
| 4.04 |  | Procuring Personal Protective Equipment for workforce as per the ESCP | Islands | 4 |  |  |  |  |  |  |  |  |  |
| 4.05 |  | Health and Safety Toolbox training to construction workforce prior to commencement and weekly thereafter as per ESCP | Islands | 4 |  |  |  |  |  |  |  |  |  |
| 4.06 |  | Excavation protection sloping/shoring/shielding method approved by engineer as per the ESCP | Islands | 4 |  |  |  |  |  |  |  |  |  |
| 4.07 |  | Briefing session on Code of conduct of workforce prior to commencement of work | Islands | 4 |  |  |  |  |  |  |  |  |  |
| 4.08 |  | Development of Occupation Health Safety Management Plan for the project | Document | 1 |  |  |  |  |  |  |  |  |  |
| 4.09 |  | Updating of ESCP | Document | 1 |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 1.3: General Items – Lot 3 (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

Bill No. 2:  Electrical Works – Lot 3

| Bill No. 2h – L. FONADHOO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 4,100 |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 2h (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2i – L. ISDHOO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 7,400 |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 3 |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | 3 |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 3 |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 2i (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2j – L. KALAIDHOO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 3,200 |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 2 |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 2j (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2k – L. DHANBIDHOO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 1 |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipemnt and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |  |  |  |
| Total for Bill No.2l (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2 l – L. MAABAIDHOO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit |  |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | - |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | 1,954 |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | 448 |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | 231 |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | 1,673 |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | 1,508 |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | 853 |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | 22 |  |  |  |  |  |  |  |  |  |
| Total for Bill No.2l (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2m– L. KUNA HANDHOO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | - |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | 1,058 |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | 1,067 |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | 2,405 |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | 2,645 |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | 3,274 |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | 506 |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | 786 |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | 21 |  |  |  |  |  |  |  |  |  |
| Total for Bill No.2m (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2n – L. HITHADHOO |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Local Currency |  | Foreign Currency 1 |  | Foreign Currency 2 |  | Foreign Currency 3 |  |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.01 |  | 3500 kVA | Unit | - |  |  |  |  |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | - |  |  |  |  |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | - |  |  |  |  |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | 4,181 |  |  |  |  |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | 2,181 |  |  |  |  |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | 2,629 |  |  |  |  |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | 793 |  |  |  |  |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | 195 |  |  |  |  |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |  |  |  |  |
| Total for Bill No. 2n (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Bill No. 2o – SH. FUNADHOO |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description- refer Employer Requirements for full detail | Type | Unit | Quantity | Rate | Amount |  |  |  |
|  |  |  |  |  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| 1.0 | Step-up transformer at power station, including installation and connection requirements |  |  |  |  |  |  |  |  |
| 1.01 |  | 2500 kVA | Unit | 2 |  |  |  |  |  |
| 1.02 | MV switchgear at the power station, including installation and connection requirements | As per Employer Requirements, Appendix B | Unit | 1 |  |  |  |  |  |
| 2.0 | MV cable and FO cable (equal quantity of each) - Replace existing cable or new cable Includes all related equipment and installation requirements, not limited to: electrical cable, fibre optic cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 2.01 |  | 185 mm2 | Meter | - |  |  |  |  |  |
| 2.02 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 2.03 |  | 120 mm2 | Meter | - |  |  |  |  |  |
| 2.04 |  | 70 mm2 | Meter | 3,522 |  |  |  |  |  |
| 3.0 | Substation Includes all equipment and installation requirements, not limited to building, RMU, transformer, LV board, earthing, circuit breakers, testing and certification |  |  |  |  |  |  |  |  |
| 3.01 |  | Building - specifications as per Employer Requirements Includes all related equipment and installation requirements, not limited to: foundations, earthing, ducting, cable entries, security, lighting | Unit | 3 |  |  |  |  |  |
| 3.02 |  | RMU-4 way | Unit | - |  |  |  |  |  |
| 3.03 |  | RMU-3 way | Unit | 3 |  |  |  |  |  |
| 3.04 |  | 800 kVA transformer | Unit | 3 |  |  |  |  |  |
| 3.05 |  | 500 kVA transformer | Unit | - |  |  |  |  |  |
| 3.06 |  | LV DB | Unit | 3 |  |  |  |  |  |
| 4.0 | LV distribution cable - replace existing Includes all related equipment and installation requirements, not limited to: electrical cable, conduits, mechanical protection, marker tape, trenching, special fill materials, compaction, marker posts, terminations, test and certification. |  |  |  |  |  |  |  |  |
| 4.01 |  | 300 mm2 | Meter | - |  |  |  |  |  |
| 4.02 |  | 240 mm2 | Meter | - |  |  |  |  |  |
| 4.03 |  | 185 mm2 | Meter | - |  |  |  |  |  |
| 4.04 |  | 150 mm2 | Meter | - |  |  |  |  |  |
| 4.05 |  | 120 mm2 | Meter | - |  |  |  |  |  |
| 4.06 |  | 95 mm2 | Meter | 132 |  |  |  |  |  |
| 4.07 |  | 70 mm2 | Meter | 338 |  |  |  |  |  |
| 4.08 |  | 50 mm2 | Meter | - |  |  |  |  |  |
| 4.09 |  | 35 mm2 | Meter | 128 |  |  |  |  |  |
| 4.10 |  | 25 mm2 | Meter | - |  |  |  |  |  |
| 4.11 |  | 16 mm2 | Meter | - |  |  |  |  |  |
| 5.0 | Low voltage distribution box including all related equipment and installation requirements not limited to: structure / mounting, earthing, connections, fuses and fuse holders, terminations, test and certifications. |  | Unit | - |  |  |  |  |  |
| Total for Bill No.2o (carried forward to Grand Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |  |  |

Daywork Schedule – Lot 3

General

Reference should be made to Sub-Clause 13.5 of the General Conditions. Work shall not be executed on a daywork basis except by written order of the Engineer. Bidders shall enter rates for daywork items in the Schedules, which rates shall apply to any quantity of daywork ordered by the Engineer.  Nominal quantities have been indicated against each item of daywork, and the extended total for Daywork shall be carried forward as a Provisional Sum to the Summary Total Bid Amount.

Daywork Labour

The Contractor shall be entitled to payment in respect of the total time that labour is employed on daywork, calculated at the rates entered by the Contractor in the Schedule of Daywork Rates:  1. Labour, together with an additional percentage payment on rates representing the Contractor’s profit, overheads, etc.

Daywork Materials

The Contractor shall be entitled to payment in respect of materials used for daywork (except for materials for which the cost is included in the percentage addition to labour costs as detailed heretofore), at the rates entered by the Contractor in the Schedule of Daywork Rates: 2. Materials, together with an additional percentage payment on the rates to cover overhead charges and profit etc.

Daywork Contractor’s Equipment

The Contractor shall be entitled to payments in respect of Contractor’s Equipment already on Site and employed on daywork at the rental rates entered by the Contractor in the Schedule of Daywork Rates:  3. Contractor’s Equipment.  Said rates shall be deemed to include due and complete allowance for depreciation, interest, indemnity, and insurance, repairs, maintenance, supplies, fuel, lubricants, and other consumables, and all overhead, profit, and administrative costs related to the use of such equipment. The cost of drivers, operators, and assistants will be paid for separately as described under the section on Daywork Labour.

| Schedule of Daywork Rates: 1. Labour – Lot 3 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item no. | Description | Unit | Nominal quantity | Rate a | Extended amount |
| 1 | unqualified labourer | Day | 10 |  |  |
| 2 | trainee or apprentice electrician | Day | 10 |  |  |
| 3 | qualified electrician, low voltage | Day | 10 |  |  |
| 4 | qualified electrician, medium voltage | Day | 10 |  |  |
| 5 | Site supervisor | Day | 10 |  |  |
| 6 | Per-diem (including accommodation) for non-resident staff | Day | 10 |  |  |
| Total for Daywork: Labour (carried forward to Daywork Summary – Lot 3, p. …….) |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |  |

| Schedule of Daywork Rates: 2. Materials – Lot 3 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description | Unit | Nominal quantity | Rate a | Extended amount |  |
| 1 | Concrete | m3 | 5 |  |  |  |
| 2 | Reinstate concrete road following trenching for cable route | m | 100 |  |  |  |
| 3 | Reinstate unpaved road following trenching for cable route | m | 100 |  |  |  |
| Total for Daywork: Materials (carried forward to Daywork Summary – Lot 3, p. …….) |  |  |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |  |  |  |  |

| Schedule of Daywork Rates: 3. Contractor’s Equipment – Lot 3 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item no. | Description | Nominal quantity (hours) | Basic hourly rental rate a | Extended amount |  |
| 1 | Excavator | 10 |  |  |  |
| 2 | Cable drum roller | 5 |  |  |  |
| 3 | Rigid 2 or 3 axle truck | 20 |  |  |  |
| Total for Daywork: Contractor’s Equipment (carried forward to Daywork Summary – Lot 3, p. …….) |  |  |  |  |  |  |
| a. To be entered by the Bidder. |  |  |  |  |

Daywork Summary – Lot 3

| Details | Page | Amount (MVR) | % Foreign |
| --- | --- | --- | --- |
| 1. Total for Daywork: Labour |  |  |  |
| 2. Total for Daywork: Materials |  |  |  |
| 3. Total for Daywork: Contractor’s Equipment |  |  |  |
| Total for Daywork (Provisional Sum) (carried forward to Grand Summary, p. …….) |  |  |  |

Grand Summary – Lot 3

| General Summary | Page | Amount |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| Bill No. 1: General Items – Lot 3 |  |  |  |  |  |
| Bill No. 2: Electrical Works – Lot 3 |  |  |  |  |  |
| Bill No. 2 h – L. Fonadhoo |  |  |  |  |  |
| Bill No. 2 i – L. Isdhoo |  |  |  |  |  |
| Bill No. 2 j – L. Kalaidhoo |  |  |  |  |  |
| Bill No. 2 k – L. Dhanbidhoo |  |  |  |  |  |
| Bill No. 2 l– L. Maabaidhoo |  |  |  |  |  |
| Bill No. 2 m – L. Kunahandhoo |  |  |  |  |  |
| Bill No. 2 n – L. Hithadhoo |  |  |  |  |  |
| Bill No. 2 o – Sh. Funadhoo |  |  |  |  |  |
| Subtotal of Bills Lot 3 (in case of multiple lots carried forward to Grand Summary – Multiple Lots) | (A) |  |  |  |  |
| Total for Daywork (Provisional Sum) * | (B) |  |  |  |  |
| Specified Provisional Sums included in subtotal of bills ii | (C) |  |  |  |  |
| Total of Bills Plus Provisional Sums (A + B + C) i | (D) |  |  |  |  |
| Add Provisional Sum for Contingency [2 percent of the Subtotal of Bills (A)] ii | (E) | [sum] | [sum] | [sum] | [sum] |
| Bid Price (D + E) (Carried forward to Letter of Bid) | (F) |  |  |  |  |

i) All Provisional Sums are to be expended in whole or in part at the direction and discretion of the Engineer in accordance with Sub-Clauses 13.4 and 13.5 of the General Conditions except with respect to DAAB Fees and Expenses for which Sub-Clause 13.4 of the Particular Conditions – Part B shall apply.

ii) To be entered by the Employer.

* For evaluation purposes, Provisional Sum, other than Daywork will be excluded

Grand Summary – Multiple Lots

Contract Name:

Contract No.:

| Grand Summary | Page | Amount |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Local Currency | Foreign Currency 1 | Foreign Currency 2 | Foreign Currency 3 |
| Grand Summary Lot 1 |  |  |  |  |  |
| Grand Summary Lot 2 |  |  |  |  |  |
| Grand Summary Lot 3 |  |  |  |  |  |
| Subtotal of Bills (Lot1+Lot2+Lot3) | (A) |  |  |  |  |
| Total for Daywork (Provisional Sum) * | (B) |  |  |  |  |
| Total of Bills Plus Provisional Sums (A + B ) i | (D) |  |  |  |  |
| Add Provisional Sum for Contingency Allowance (if any) ii | (E) | [sum] | [sum] | [sum] | [sum] |
| Bid Price (D + E) (Carried forward to Letter of Bid) | (F) |  |  |  |  |
| i) All Provisional Sums are to be expended in whole or in part at the direction and discretion of the Engineer in accordance with Sub-Clauses 13.4 and 13.5 of the General Conditions except with respect to DAAB Fees and Expenses for which Sub-Clause 13.4 of the Particular Conditions – Part B shall apply. ii) To be entered by the Employer. * For evaluation purposes, Provisional Sum, other than Daywork will be excluded |  |  |  |  |  |  |  |

Technical Proposal

- Site Organization

- Method Statement

- Mobilization Schedule

- Code of Conduct for Contractor’s Personnel (ES)

- Materials

- Equipment

- Key Personnel Schedule

- Others

Form TECH- 1: Site Organization

Bidders should provide the details of their proposed site organization, which must address the following points. The format and structure of this form is not specified.

Please provide a high-level description on a stage by stage basis, aligned with the mobilization and construction schedule, of the proposed site organization, including laydown of parts and equipment, site security, and any temporary facilities or buildings. Please include sketches of site organization where necessary.

In particular, site organization should highlight capacity for:

- Sensitivity to the needs and impact on the local island community;

- Required laydown areas;

- Delivery of equipment, and its storage and security on site, including materials receiving and quality control;

- Safe work methods;

- Access and egress for emergencies;

- Any provisions for securing the site in the event of natural disasters; and

- Efficient workflow and movement along roads, including traffic management, minimizing impact to community.

Required to attach:

☐General description of site organization, addressing above points.

☐Sample work method statement for:

- Trenching; and

- Commissioning substation.

Form TECH- 2: Method Statement

Bidders should provide the details of their proposed method for carrying out the contract, which must address the following points. The format and structure of this form is not specified.

Provide a method statement for each of the following:

- Carrying out the required design services, including;

  - Software held by the Bidder or its proposed subcontractors for undertaking the required studies;

  - Plan for value engineering during the design phase, to ensure optimal equipment selection and identify opportunities for more efficient implementation of network upgrades; and

  - Submission and document management and clarification processes.

- Overall project logistics, demonstrating how works on successive islands projects will be staged and coordinated. Also demonstrating how the sea and land transport requirements for the islands will be met;

- FAT plan for major equipment;

- Installation works process, including staffing, team structures, accommodation and provisions for any non-local workers considering any limitations of local facilities and services;

- Construction workflow for cable installation, substation, and switchyard installation;

- Process for grid connection / cut-overs, including management of shutdowns and their likely duration;

- Carrying out site inspection and test for the project. Please include a sample medium voltage test plan. Corresponding MV test equipment should be specified in the ‘Contractor’s Equipment’ Form; and

- Capacity building and training, including details of proposed involvement of relevant local personnel in the planning, design, and construction of the plant, expected training modes, number and duration of training sessions, and documentation to be delivered.

Required to attach:

☐Method statement for carrying out design services (max. 1 page)

☐Method statement for logistics (max. 1 page)

☐Sample FAT plan (e.g., from previous project – no page limit)

☐Method statement for installation, including workflow and team structures (max. 4 pages)

☐Sample MV test plans (e.g., from previous project – no page limit)

☐Description of training and capacity building. State number and duration of sessions. State type of training delivery.

Form TECH- 3: Schedule

Bidders shall provide a statement stipulating that their time to completion complies with the Bid Data Sheet and Employer’s Requirements.

Bidders shall provide a Gantt Chart for project delivery, which shall include, at a minimum:

- Design submission milestones;

- Placement of procurement orders for major equipment;

- FAT dates for major equipment;

- Shipment and delivery dates for major equipment;

- Site work dates for each island (with identification of work teams); and

- Preliminary commissioning dates for each island.

The Gantt Chart shall show schedule in Calendar days from contract effectiveness date.

Required to attach:

☐Statement of Time to Completion

☐Gantt chart addressing above requirements

In accordance with the Particular Conditions, Sub-Clause 4.1, the Contractor shall not carry out mobilization to Site unless the Engineer gives consent that appropriate measures are in place to address environmental and social risks and impacts, which as a minimum shall include applying the Code of Conduct for Contractor’s Personnel, submitted as part of the Bid and agreed as part of the Contract.

The construction schedule shall include the following key milestones:

- No-objection to the Contractor’s ESCP, in accordance with the Particular Conditions – Special provisions Sub-Clause 4.1.

- Constitution of the DAAB

Note to the Bidder:

The minimum content of the Code of Conduct form as set out by the Employer shall not be substantially modified. However, the Bidder may add requirements as appropriate, including to take into account Contract-specific issues/risks.

The Bidder shall initial and submit the Code of Conduct form as part of its bid.

Code of Conduct for Contractor’s Personnel (ES) Form

CODE OF CONDUCT FOR CONTRACTOR’S PERSONNEL

We are the Contractor, [enter name of Contractor].  We have signed a contract with [enter name of Employer] for [enter description of the Works]. These Works will be carried out at [enter the Site and other locations where the Works will be carried out]. Our contract requires us to implement measures to address environmental and social risks related to the Works, including the risks of sexual exploitation, sexual abuse and sexual harassment.

This Code of Conduct is part of our measures to deal with environmental and social risks related to the Works.  It applies to all our staff, labourers and other employees at the Works Site or other places where the Works are being carried out.  It also applies to the personnel of each subcontractor and any other personnel assisting us in the execution of the Works.  All such persons are referred to as “Contractor’s Personnel” and are subject to this Code of Conduct.

This Code of Conduct identifies the behavior that we require from all Contractor’s Personnel.

Our workplace is an environment where unsafe, offensive, abusive or violent behavior will not be tolerated and where all persons should feel comfortable raising issues or concerns without fear of retaliation.

REQUIRED CONDUCT

Contractor’s Personnel shall:

- carry out his/her duties competently and diligently;

- comply with this Code of Conduct and all applicable laws, regulations and other requirements, including requirements to protect the health, safety and well-being of other Contractor’s Personnel and any other person;

- maintain a safe working environment including by:

  - ensuring that workplaces, machinery, equipment and processes under each person’s control are safe and without risk to health;

  - wearing required personal protective equipment;

  - using appropriate measures relating to chemical, physical and biological substances and agents; and

  - following applicable emergency operating procedures.

- report work situations that he/she believes are not safe or healthy and remove himself/herself from a work situation which he/she reasonably believes presents an imminent and serious danger to his/her life or health;

- treat other people with respect, and not discriminate against specific groups such as women, people with disabilities, migrant workers or children;

- not engage in Sexual Harassment, which means unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature with other Contractor’s or Employer’s Personnel;

- not engage in Sexual Exploitation, which means any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another;

- not engage in Sexual Abuse, which means the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions;

- not engage in any form of sexual activity with individuals under the age of 18, except in case of pre-existing marriage;

- complete relevant training courses that will be provided related to the environmental and social aspects of the Contract, including on health and safety matters, Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH);

- undertake all project activities as per Environmental and Social Code of Practice (Appendix D) developed for the project;

- have a valid work permit to undertake project activities for the project duration;

- report violations of this Code of Conduct; and

- not retaliate against any person who reports violations of this Code of Conduct, whether to us or the Employer, or who makes use of the grievance mechanism for Contractor’s Personnel or the project’s Grievance Redress Mechanism.

RAISING CONCERNS

If any person observes behavior that he/she believes may represent a violation of this Code of Conduct, or that otherwise concerns him/her, he/she should raise the issue promptly. This can be done in either of the following ways:

- Contact [enter name of the Contractor’s Social Expert with relevant experience in handling sexual exploitation, sexual abuse and sexual harassment cases, or if such person is not required under the Contract, another individual designated by the Contractor to handle these matters] in writing at this address [   ] or by telephone at [   ] or in person at [   ]; or

- Call [  ]  to reach the Contractor’s hotline (if any) and leave a message.

The person’s identity will be kept confidential, unless reporting of allegations is mandated by the country law. Anonymous complaints or allegations may also be submitted and will be given all due and appropriate consideration. We take seriously all reports of possible misconduct and will investigate and take appropriate action. We will provide warm referrals to service providers that may help support the person who experienced the alleged incident, as appropriate.

There will be no retaliation against any person who raises a concern in good faith about any behavior prohibited by this Code of Conduct.  Such retaliation would be a violation of this Code of Conduct.

CONSEQUENCES OF VIOLATING THE CODE OF CONDUCT

Any violation of this Code of Conduct by Contractor’s Personnel may result in serious consequences, up to and including termination and possible referral to legal authorities.

FOR CONTRACTOR’S PERSONNEL:

I have received a copy of this Code of Conduct written in a language that I comprehend.  I understand that if I have any questions about this Code of Conduct, I can contact [enter name of Contractor’s contact person(s) with relevant experience] requesting an explanation.

Name of Contractor’s Personnel: [insert name]

Signature: __________________________________________________________

Date: (day month year): _______________________________________________

Countersignature of authorized representative of the Contractor:

Signature: ________________________________________________________

Date: (day month year): ______________________________________________

ATTACHMENT 1: Behaviors constituting Sexual Exploitation and Abuse (SEA) and behaviors and behaviors constituting Sexual Harassment (SH)

ATTACHMENT 1 TO THE CODE OF CONDUCT FORM

BEHAVIORS CONSTITUTING SEXUAL EXPLOITATION AND ABUSE (SEA) AND BEHAVIORS CONSTITUTING SEXUAL HARASSMENT (SH)

The following non-exhaustive list is intended to illustrate types of prohibited behaviors.

- Examples of sexual exploitation and abuse include, but are not limited to:

- A Contractor’s Personnel tells a member of the community that he/she can get them jobs related to the work site (e.g. cooking and cleaning) in exchange for sex.

- A Contractor’s Personnel that is connecting electricity input to households says that he can connect women headed households to the grid in exchange for sex.

- A Contractor’s Personnel rapes, or otherwise sexually assaults a member of the community.

- A Contractor’s Personnel denies a person access to the Site unless he/she performs a sexual favor.

- A Contractor’s Personnel tells a person applying for employment under the Contract that he/she will only hire him/her if he/she has sex with him/her.

- Examples of sexual harassment in a work context

- Contractor’s Personnel comment on the appearance of another Contractor’s Personnel (either positive or negative) and sexual desirability.

- When a Contractor’s Personnel complains about comments made by another Contractor’s Personnel on his/her appearance, the other Contractor’s Personnel comment that he/she is “asking for it” because of how he/she dresses.

- Unwelcome touching of a Contractor’s or Employer’s Personnel by another Contractor’s Personnel.

- A Contractor’s Personnel tells another Contractor’s Personnel that he/she will get him/her a salary raise, or promotion if he/she sends him/her naked photographs of himself/herself.

Form TECH- 6: Materials

Bidders should provide the details of their proposed Materials, which must address the following points.

- A plain English summary of the components, certifications / standards compliance, and planned installation;

- Details of any areas of minor non-conformity with the Employer Requirements. Only minor non-conformities identified at this stage may be considered as exceptions to the Employer Requirements in the contract, should the bidder be successful;

- All Original Equipment Manufacturer (OEM) warranty terms, conditions and warranted levels;

- Specifications (full data sheets and certifications) of major materials. Major materials include RMUs, switchboards, cables, transformers. Employer may request data sheets of other equipment during evaluation;

- Summary of the communications equipment to be installed; and

- Dimensioned concept drawings (plan and elevation view) of the typical physical layout for substations.

Required to attach:

☐ Plain English summary of the equipment (max. 1 page)

☐ Details of any minor non-conformities.  A general declaration of compliance for each major equipment, and an undertaking to replace if necessary to achieve compliance at no financial cost or time cost to the project.

☐ Equipment data sheet for all major materials. Major material comprises (and data sheets should be attached in this order):

- Transformers, RMU, switchgear, MV cables, LV cables.

☐ Available certificates of conformance with standards as per the Employer Requirements for all major materials.

☐ Statement by the Bidder acknowledging and committing to undertake the vendor verification requirements as per the Employer Requirements, Appendix A, Section 10.1

☐ Warranty terms for all major materials

☐ Description of proposed communications (max 1 page)

☐ Dimensioned drawings of typical substation

| Declaration: We hereby declare that all proposed materials are 100% in compliance with Employer’s Requirements. Any major/minor non-compliances if found at any stage, shall be resolved to the satisfaction of employer at no additional cost. |  |
| --- | --- |
| Name: | Signature: |

Form EQU: Equipment

The Bidder shall provide adequate information to demonstrate clearly that it has the capability to meet the requirements for the key equipment listed in Section III, Evaluation and Qualification Criteria. A separate Form shall be prepared for each item of equipment listed, or for alternative equipment proposed by the Bidder.

| Item of equipment |  |  |
| --- | --- | --- |
| Equipment information | Name of manufacturer | Model and power rating |
|  | Capacity | Year of manufacture |
| Current status | Current location |  |
|  | Details of current commitments |  |
| Source | Indicate source of the equipment o Owned o Rented o Leased o Specially manufactured |  |

Omit the following information for equipment owned by the Bidder.

| Owner | Name of owner |  |
| --- | --- | --- |
|  | Address of owner |  |
|  | Telephone | Contact name and title |
|  | Fax | Telex |
| Agreements | Details of rental / lease / manufacture agreements specific to the project |  |

Form PER -1

Contractor’s Representative and Key Personnel

Schedule

Bidders should provide the names and details of the suitably qualified Contractor’s Representative and Key Personnel to perform the Contract. The data on their experience should be supplied using the Form PER-2 below for each candidate.

Contractor’ Representative and Key Personnel

| - 1. | Title of position: Contractor’s Representative |  |
| --- | --- | --- |
|  | Name of candidate: |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| - 2. | Title of position: Environmental & Social Safeguards Officer |  |
|  | Name of candidate: |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| - 5. | Title of position: Site supervisors |  |
|  | Name of candidate |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| - 5. | Title of position: Logistics manager |  |
|  | Name of candidate |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| - 5. | Title of position: Electrical supervisor |  |
|  | Name of candidate |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| - 5. | Title of position: electricians, with HV cable jointing training |  |
|  | Name of candidate |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |
| - 5. | Title of position: Communications technician |  |
|  | Name of candidate |  |
|  | Duration of appointment: | [insert the whole period (start and end dates) for which this position will be engaged] |
|  | Time commitment: for this position: | [insert the number of days/week/months/ that has been scheduled for this position] |
|  | Expected time schedule for this position: | [insert the expected time schedule for this position (e.g. attach high level Gantt chart] |

Form PER-2:

Resume and Declaration

Contractor’s Representative and Key Personnel

Name of Bidder

| Position [#1]: [title of position from Form PER-1] |  |  |
| --- | --- | --- |
| Personnel information | Name: | Date of birth: |
|  | Address: | E-mail: |
|  | Professional qualifications: |  |
|  | Academic qualifications: |  |
|  | Language proficiency: [language and levels of speaking, reading and writing skills] |  |
| Details |  |  |
|  | Address of employer: |  |
|  | Telephone: | Contact (manager / personnel officer): |
|  | Fax: |  |
|  | Job title: | Years with present employer: |

Summarize professional experience in reverse chronological order. Indicate particular technical and managerial experience relevant to the project.

| Project | Role | Duration of involvement | Relevant experience |
| --- | --- | --- | --- |
| [main project details] | [role and responsibilities on the project] | [time in role] | [describe the experience relevant to this position] |

Declaration

I, the undersigned [insert either “Contractor’s Representative” or “Key Personnel” as applicable], certify that to the best of my knowledge and belief, the information contained in this Form PER-2 correctly describes myself, my qualifications and my experience.

I confirm that I am available as certified in the following table and throughout the expected time schedule for this position as provided in the Bid:

| Commitment | Details |
| --- | --- |
| Commitment to duration of contract: | [insert period (start and end dates) for which this Contractor’s Representative or Key Personnel is available to work on this contract] |
| Time commitment: | [insert period (start and end dates) for which this Contractor’s Representative or Key Personnel is available to work on this contract] |

I understand that any misrepresentation or omission in this Form may:

- be taken into consideration during Bid evaluation;

- result in my disqualification from participating in the Bid

- result in my dismissal from the contract.

Name of Contractor’s Representative or Key Personnel: [insert name]

Signature: __________________________________________________________

Date: (day month year): _______________________________________________

Countersignature of authorized representative of the Bidder:

Signature: ________________________________________________________

Date: (day month year): ______________________________________________

Bidders Qualification without prequalification

To establish its qualifications to perform the contract in accordance with Section III, Evaluation and Qualification Criteria the Bidder shall provide the information requested in the corresponding Information Sheets included hereunder.

Form ELI -1.1

Bidder Information Form

Date: _________________
RFB No. and title: _________________
Page __________of _______________pages

Bidder's name

In case of Joint Venture (JV), name of each member:

Bidder's actual or intended country of registration: [indicate country of Constitution]

Bidder's actual or intended year of incorporation:

Bidder's legal address [in country of registration]:

Bidder's authorized representative information Name: _____________________________________ Address: ___________________________________ Telephone/Fax numbers: _______________________ E-mail address: ______________________________

1. Attached are copies of original documents of  Articles of Incorporation (or equivalent documents of constitution or association), and/or documents of registration of the legal entity named above, in accordance with ITB 4.4  In case of JV, letter of intent to form JV or JV agreement, in accordance with ITB 4.1  In case of state-owned enterprise or institution, in accordance with ITB 4.6, documents establishing: - Legal and financial autonomy - Operation under commercial law - Establishing that the Bidder is not under the supervision of the Employer 2. Included are the organizational chart, a list of Board of Directors, and the beneficial ownership. [If required under BDS ITB 47.1, the successful Bidder shall provide additional information on beneficial ownership, using the Beneficial Ownership Disclosure Form.]

Form ELI -1.2

Bidder's JV Information Form
(to be completed for each member of Bidder’s JV)

Date: _______________
RFB No. and title: __________________
Page _______________ of ____________ pages

Bidder’s JV name:

JV member’s name:

JV member’s country of registration:

JV member’s year of constitution:

JV member’s legal address in country of constitution:

JV member’s authorized representative information Name: ____________________________________ Address: __________________________________ Telephone/Fax numbers: _____________________ E-mail address: _____________________________

1. Attached are copies of original documents of  Articles of Incorporation (or equivalent documents of constitution or association), and/or registration documents of the legal entity named above, in accordance with ITB 4.4.  In case of a state-owned enterprise or institution, documents establishing legal and financial autonomy, operation in accordance with commercial law, and that they are not under the supervision of the Employer, in accordance with ITB 4.6. 2. Included are the organizational chart, a list of Board of Directors, and the beneficial ownership. [If required under BDS ITB 47.1, the successful Bidder shall provide additional information on beneficial ownership for each JV member using the Beneficial Ownership Disclosure Form.]

Form CON – 2

Historical Contract Non-Performance, Pending Litigation and Litigation History

Bidder’s Name: ________________
Date: ______________________
JV Member’s Name_________________________
RFB No. and title: ___________________________
Page _______________of ______________pages

| Non-Performed Contracts in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
| --- | --- | --- | --- |
|  Contract non-performance did not occur since 1st January [insert year] specified in Section III, Evaluation and Qualification Criteria, Sub-Factor 2.1.  Contract(s) not performed since 1st January [insert year] specified in Section III, Evaluation and Qualification Criteria, requirement 2.1 |  |  |  |
| Year | Non- performed portion of contract | Contract Identification | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for nonperformance: [indicate main reason(s)] | [insert amount] |
| Pending Litigation, in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |
|  No pending litigation in accordance with Section III, Evaluation and Qualification Criteria, Sub-Factor 2.3. |  |  |  |
|  Pending litigation in accordance with Section III, Evaluation and Qualification Criteria, Sub-Factor 2.3 as indicated below. |  |  |  |

| Year of dispute |  | Amount in dispute (currency) |  | Contract Identification | Total Contract Amount (currency), USD Equivalent (exchange rate) |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Contract Identification: _________ Name of Employer: ____________ Address of Employer: __________ Matter in dispute: ______________ Party who initiated the dispute: ____ Status of dispute: ___________ |  |
|  |  |  |  | Contract Identification: Name of Employer: Address of Employer: Matter in dispute: Party who initiated the dispute: Status of dispute: |  |
| Litigation History in accordance with Section III, Evaluation and Qualification Criteria |  |  |  |  |  |
|  No Litigation History in accordance with Section III, Evaluation and Qualification Criteria, Sub-Factor 2.4.  Litigation History in accordance with Section III, Evaluation and Qualification Criteria, Sub-Factor 2.4 as indicated below. |  |  |  |  |  |
| Year of award | Outcome as percentage of Net Worth |  | Contract Identification |  | Total Contract Amount (currency), USD Equivalent (exchange rate) |
| [insert year] | [insert percentage] |  | Contract Identification: [indicate complete contract name, number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Matter in dispute: [indicate main issues in dispute] Party who initiated the dispute: [indicate “Employer” or “Contractor”] Reason(s) for Litigation and award decision [indicate main reason(s)] |  | [insert amount] |

Form CON – 3

Environmental and Social Performance Declaration

[The following table shall be filled in for the Bidder, each member of a Joint Venture and each Specialized Subcontractor]

Bidder’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member’s or Specialized Subcontractor’s Name: [insert full name]
RFB No. and title: [insert RFB number and title]
Page [insert page number] of [insert total number] pages

| Environmental and Social Performance Declaration in accordance with Section III, Qualification Criteria, and Requirements |  |  |  |
| --- | --- | --- | --- |
|  No suspension or termination of contract: An employer has not suspended or terminated a contract and/or called the performance security for a contract for reasons related to Environmental or Social (ES) performance since the date specified in Section III, Qualification Criteria, and Requirements, Sub-Factor 2.5.  Declaration of suspension or termination of contract: The following contract(s) has/have been suspended or terminated and/or Performance Security called by an employer(s) for reasons related to Environmental or Social (ES) performance since the date specified in Section III, Qualification Criteria, and Requirements, Sub-Factor 2.5. Details are described below: |  |  |  |
| Year | Suspended or terminated portion of contract | Contract Identification | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for suspension or termination: [indicate main reason(s) e.g. gender-based violence; sexual exploitation or sexual abuse breaches] | [insert amount] |
| [insert year] | [insert amount and percentage] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for suspension or termination: [indicate main reason(s)] | [insert amount] |
| … | … | [list all applicable contracts] | … |
| Performance Security called by an employer(s) for reasons related to ES performance |  |  |  |
| Year | Contract Identification |  | Total Contract Amount (current value, currency, exchange rate and US$ equivalent) |
| [insert year] | Contract Identification: [indicate complete contract name/ number, and any other identification] Name of Employer: [insert full name] Address of Employer: [insert street/city/country] Reason(s) for calling of performance security: [indicate main reason(s) e.g. for gender-based violence; sexual exploitation, or sexual abuse breaches] |  | [insert amount] |

Form CON – 4

Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment Performance Declaration

[The following table shall be filled in by the Bidder, each member of a Joint Venture and each subcontractor proposed by the Bidder]

Bidder’s Name: [insert full name]
Date: [insert day, month, year]
Joint Venture Member’s or Subcontractor’s Name: [insert full name]
RFB No. and title: [insert RFB number and title]
Page [insert page number] of [insert total number] pages

SEA and/or SH Declaration in accordance with Section III, Qualification Criteria, and Requirements

We:  (a) have not been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations  (b) are subject to disqualification by the Bank for non-compliance with SEA/ SH obligations  (c) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations. An arbitral award on the disqualification case has been made in our favor.  (d) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations for a period of two years. We have subsequently demonstrated that we have adequate capacity and commitment to comply with SEA/ SH obligations.  (e) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations for a period of two years. We have attached evidence demonstrating that we have adequate capacity and commitment to comply with SEA/ SH obligations.

[If (c) above is applicable, attach evidence of an arbitral award reversing the findings on the issues underlying the disqualification.]

[If (d) or ( e) above are applicable, provide the following information:]

Period of disqualification: From: _______________ To: ________________

If previously provided on another Bank financed works contract, details of evidence that demonstrated adequate capacity and commitment to comply with SEA/ SH obligations (as per (d) above) Name of Employer: ___________________________________________ Name of Project: _____________________________________ Contract description: _____________________________________________________ Brief summary of evidence provided: ________________________________________ ______________________________________________________________________ Contact Information: (Tel, email, name of contact person): _______________________ ______________________________________________________________________

As an alternative to the evidence under (d), other evidence demonstrating adequate capacity and commitment to comply with SEA/ SH obligations (as per (e) above) [attach details as appropriate].

Form FIN – 3.1:

Financial Situation and Performance

Bidder’s Name: ________________
Date: ______________________
JV Member’s Name_________________________
RFB No. and title: ___________________________
Page _______________of ______________pages

1. Financial data (Consolidated Figures WILL NOT be Accepted)

| Type of Financial information in (currency) | Historic information for year 2018, 2019 and 2020, |  |  |
| --- | --- | --- | --- |
|  | (amount in currency, currency, exchange rate*, USD equivalent) |  |  |
|  | 2018 | 2019 | 2020 |
| Statement of Financial Position (Information from Balance Sheet) |  |  |  |
| Total Assets (TA) |  |  |  |
| Total Liabilities (TL) |  |  |  |
| Total Equity/Net Worth (NW) |  |  |  |
| Current Assets (CA) |  |  |  |
| Current Liabilities (CL) |  |  |  |
| Working Capital (WC) (WC = CA – CL) |  |  |  |
| Information from Income Statement |  |  |  |
| Total Revenue (TR) |  |  |  |
| Profits Before Taxes (PBT) |  |  |  |
| Cash Flow Information |  |  |  |
| Cash Flow from Operating Activities |  |  |  |

*Refer to ITB 15 for the exchange rate

2. Financial documents

The Bidder and its parties shall provide copies of financial statements for 3 (Three) years pursuant Section III, Evaluation and Qualifications Criteria, Sub-factor 3.1. The financial statements shall:

(a) 	reflect the financial situation of the Bidder or in case of JV member, and not an affiliated entity (such as parent company or group member).

(b)	be independently audited or certified in accordance with local legislation.

(c)	be complete, including all notes to the financial statements.

(d)	correspond to accounting periods already completed and audited.

	Attached are copies of financial statements  for the 3 (Three) years required above; and complying with the requirements.

Form FIN – 3.2:

Average Annual Construction Turnover

Bidder’s Name: ________________
Date: ______________________
JV Member’s Name_________________________
RFB No. and title: ___________________________
Page _______________of ______________pages

|  |  | Annual turnover data (construction only) |  |  |
| --- | --- | --- | --- | --- |
| Year | Amount Currency |  | Exchange rate | USD equivalent |
| [indicate year] | [insert amount and indicate currency] |  |  |  |
| Average Annual Construction Turnover * |  |  |  |  |

* 	See Section III, Evaluation and Qualification Criteria, Sub-Factor 3.2.

Form FIN – 3.3:

Financial Resources

Specify proposed sources of financing, such as liquid assets, unencumbered real assets, lines of credit, and other financial means, net of current commitments, available to meet the total construction cash flow demands of the subject contract or contracts as specified in Section III, Evaluation and Qualification Criteria

| Financial Resources |  |  |
| --- | --- | --- |
| No. | Source of financing | Amount (US$ equivalent) |
| 1 | Line of credit |  |
| 2 | Unencumbered real assets |  |
| 3 | Liquid assets |  |
|  | (add as required) |  |

2. Supporting documents

The Bidder and its parties shall provide copies of documents as applicable from the following:

  (a) Letter for line of credit specific to the project

  (b) Letter for general line of credit with up to date details such as remaining balance as of January 2022

  (c) Independent auditor certificate/letter for unencumbered assets

Form FIN – 3.4:

Current Contract Commitments / Works in Progress

Bidders and each member to a JV should provide information on their current commitments on all contracts that have been awarded, or for which a letter of intent or acceptance has been received, or for contracts approaching completion, but for which an unqualified, full completion certificate has yet to be issued.

##### Current Contract Commitments

| ### No. | ### Name of Contract | ### Employer’s Contact Address, Tel, Fax | Value of Outstanding Work [Current US$ Equivalent] | Estimated Completion Date | Average Monthly Invoicing Over Last Six Months [US$/month)] |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
|  | (add as required) |  |  |  |  |

2. Supporting documents

The Bidder and its parties shall provide copies of documents for the following:

  (a) Auditor certificate/letter verifying details of current contract commitments (Even if no current contract commitments this shall be supported by the auditors certificate/letter)

Form EXP - 4.1

General Construction Experience

Bidder’s Name: ________________
Date: ______________________
JV Member’s Name_________________________
RFB No. and title: ___________________________
Page _______________of ______________pages

| Starting Year | Ending Year | Contract Identification | Role of Bidder |
| --- | --- | --- | --- |
|  |  | Contract name: ____________________ Brief Description of the Works performed by the Bidder: _____________________________ Amount of contract: ___________________ Name of Employer: ____________________ Address: _____________________________ |  |
|  |  | Contract name: _________________________ Brief Description of the Works performed by the Bidder: _____________________________ Amount of contract: ___________________ Name of Employer: ___________________ Address: _________________________ |  |
|  |  | Contract name: ________________________ Brief Description of the Works performed by the Bidder: __________________________ Amount of contract: ___________________ Name of Employer: ___________________ Address: _________________________ |  |

Form EXP - 4.2(a)

Specific Construction and Contract Management Experience

Bidder’s Name: ________________
Date: ______________________
JV Member’s Name_________________________
RFB No. and title: ___________________________
Page _______________of ______________pages

| Similar Contract No. | Information |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Contract Identification |  |  |  |  |  |
| Award date |  |  |  |  |  |
| Completion date |  |  |  |  |  |
| Role in Contract | Prime Contractor  |  | Member in JV  | Management Contractor  | Subcontractor  |
| Total Contract Amount |  |  |  | US$ |  |
| If member in a JV or Subcontractor, specify participation in total Contract amount |  |  |  |  |  |
| Employer's Name: |  |  |  |  |  |
| Address: Telephone/fax number E-mail: |  |  |  |  |  |

Form EXP - 4.2(a) (cont.)

Specific Construction and Contract Management Experience (cont.)

| Similar Contract No. | Information |
| --- | --- |
| Description of the similarity in accordance with Sub-Factor 4.2(a) of Section III: | [Project location, Cable installation type (Under-ground or overhead), Voltage level & grid capacity] |
| 1. Amount | [km of power distribution cables (MV, LV), no of substations and kVA ratings], km of fiber optic cables and substation automation works] |
| 2. Physical size of required works items |  |
| 3. Complexity |  |
| 4. Methods/Technology |  |
| 5. Construction rate for key activities |  |
| 6. Other Characteristics |  |

Form EXP - 4.2(b)

Specific Experience in Managing ES aspects

[The following table shall be filled in for contracts performed by the Bidder, and each member of a Joint Venture]

Bidder's Name: ________________
Date: ___________________
Bidder's JV Member Name: __________________
RFB No. and title: _____________________

Page __________________of ________________pages

Key Requirement no 1 in accordance with 4.2 (b):

Preparation or implementation of project specific ESIA or ESMP or ESCP

| Contract Identification |  |  |  |  |
| --- | --- | --- | --- | --- |
| Award date |  |  |  |  |
| Completion date |  |  |  |  |
| Role in Contract | Prime Contractor  | Member in JV  | Management Contractor  | Subcontractor  |
| Total Contract Amount |  |  | US$ |  |
| Details of relevant experience |  |  |  |  |

Form of Bid Security - Demand Guarantee

Beneficiary:  Ministry of Finance, Male’, Republic of Maldives

Request for Bids No: ________________________________________

Date:  __________________________

BID GUARANTEE No.: __________________________

Guarantor:  ________________________________________________

We have been informed that __________________________ (hereinafter called "the Applicant") has submitted or will submit to the Beneficiary its Bid (hereinafter called "the Bid") for the execution of ________________ under Request for Bids No. ___________ (“the RFB”).

Furthermore, we understand that, according to the Beneficiary’s conditions, Bids must be supported by a Bid guarantee.

At the request of the Applicant, we, as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________   (____________) upon receipt by us of the Beneficiary’s complying demand, supported by the Beneficiary’s statement, whether in the demand itself or a separate signed document accompanying or identifying the demand, stating that either the Applicant:

(a) 	has withdrawn its Bid prior to the Bid validity expiry date set forth in the Applicant’s Letter of Bid, or any extended date provided by the Applicant; or

(b) 	having been notified of the acceptance of its Bid by the Beneficiary prior to the expiry date of the Bid validity or any extension thereto provided by the Applicant, (i) has failed to execute the contract agreement, or (ii) has failed to furnish the Performance Security and, if required, the Environmental and Social (ES) Performance Security, in accordance with the Instructions to Bidders (“ITB”) of the Beneficiary’s Bidding document.

This guarantee will expire: (a) if the Applicant is the successful Bidder, upon our receipt of copies of the contract agreement signed by the Applicant and the Performance Security and, if required, the Environmental and Social (ES) Performance Security, issued to the Beneficiary in relation to such contract agreement; or (b) if the Applicant is not the successful Bidder, upon the earlier of (i) our receipt of a copy of the Beneficiary’s notification to the Applicant of the results of the Bidding process; or (ii) twenty-eight days after the expiry date of the Bid validity.

Consequently, any demand for payment under this guarantee must be received by us at the office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758.

_____________________________

[signature(s)]

Section V - Eligible Countries

Eligibility for the Provision of Goods, Works and Non-Consulting Services in 
Bank-Financed Procurement

In reference to ITB 4.8 and 5.1, for the information of the Bidders, at the present time firms, goods and services from the following countries are excluded from this Bidding process:

Under ITB 4.8 (a) and 5.1: None

Under ITB 4.8 (b) and 5.1: None

Section VI - Fraud and Corruption

- Purpose

  - The Bank’s Anti-Corruption Guidelines and this annex apply with respect to procurement under Bank Investment Project Financing operations.

- Requirements

- The Bank requires that Borrowers (including beneficiaries of Bank financing); bidders (applicants/proposers), consultants, contractors and suppliers; any sub-contractors, sub-consultants, service providers or suppliers; any agents (whether declared or not); and any of their personnel, observe the highest standard of ethics during the procurement process, selection and contract execution of Bank-financed contracts, and refrain from Fraud and Corruption.

- To this end, the Bank:

- Defines, for the purposes of this provision, the terms set forth below as follows:

- “corrupt practice” is the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party;

- “fraudulent practice” is any act or omission, including misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain financial or other benefit or to avoid an obligation;

- “collusive practice” is an arrangement between two or more parties designed to achieve an improper purpose, including to influence improperly the actions of another party;

- “coercive practice” is impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party;

- “obstructive practice” is:

- deliberately destroying, falsifying, altering, or concealing of evidence material to the investigation or making false statements to investigators in order to materially impede a Bank investigation into allegations of a corrupt, fraudulent, coercive, or collusive practice; and/or threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or

- acts intended to materially impede the exercise of the Bank’s inspection and audit rights provided for under paragraph 2.2 e. below.

- Rejects a proposal for award if the Bank determines that the firm or individual recommended for award, any of its personnel, or its agents, or its sub-consultants, sub-contractors, service providers, suppliers and/ or their employees, has, directly or indirectly, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices in competing for the contract in question;

- In addition to the legal remedies set out in the relevant Legal Agreement, may take other appropriate actions, including declaring misprocurement, if the Bank determines at any time that representatives of the Borrower or of a recipient of any part of the proceeds of the loan engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices during the procurement process, selection and/or execution of the contract in question,  without the Borrower having taken timely and appropriate action satisfactory to the Bank to address such practices when they occur, including by failing to inform the Bank in a timely manner at the time  they knew of the practices;

- Pursuant to the Banks Anti-Corruption Guidelines and in accordance with the Bank’s prevailing sanctions policies and procedures, may sanction a firm or individual, either indefinitely or for a stated period of time, including by publicly declaring such firm or individual ineligible (i) to be awarded or otherwise benefit from a Bank-financed contract, financially or in any other manner; (ii) to be a nominated sub-contractor, consultant, manufacturer or supplier, or service provider of an otherwise eligible firm being awarded a Bank-financed contract; and (iii) to receive the proceeds of any loan made by the Bank or otherwise to participate further in the preparation or implementation of any Bank-financed project;

- Requires that a clause be included in bidding/request for proposals documents and in contracts financed by a Bank loan, requiring (i) bidders (applicants/proposers), consultants, contractors, and suppliers: and their sub-contractors, sub-consultants, service providers, suppliers, agents, personnel, permit the Bank to inspect all accounts, records and other documents relating to the procurement process, selection and/or contract execution, and to have them audited by auditors appointed by the Bank.

PART 2 –Works’ Requirements

Section VII - Works’ Requirements

Country and Project Overview	152

General Requirements and Description of Works	153

Specifications	156

Division of Responsibilities Matrix	157

Engineering	159

Procurement	159

Construction	159

Commissioning	159

Operations and Maintenance	159

Battery Limits	160

Employer Provided Items	160

Permits, Certificates, Licenses, Registrations and Approvals	160

Equipment requirements	161

Quantity change management	161

Project Management and Delivery Requirements	161

Implementation Period	161

Appendix A – General technical requirements	164

Appendix B – Grid Infrastructure Requirements	200

Appendix C - Drawings	294

Appendix D - Environmental and Social (ES) requirements	295

Appendix E: Supplementary Information	297

# Description of the Works

## Country and Project Overview

The Republic of Maldives is a South Asian island country, located southwest of Sri Lanka and India. It is comprised of 1,192 coral islands grouped into 26 geographical atolls, spreading over an area of 115,300 km2 and occupying a total land area of 224 km2. Maldives is recognized as an upper middle-income economy by the World Bank (WB) with a GDP growth rate of 8.1% in 2018

Out of the total 1,192 islands, 187 are inhabited, 123 are self-contained tourist resorts and 128 are used for other industrial and commercial activities. The current population of Maldives is 543,088. The dispersed nature of the islands requires each island to have a separate power generation and distribution system. The powerhouses are operated mainly by three utility companies namely, State Electric Company Limited (STELCO), FENAKA Corporation Ltd. (FENAKA) and Male’ Water and Sewerage Company Pvt. Ltd. (MWSC).

Maldives achieved universal access to electricity in 2008, with 24 hours electricity service in all inhabited islands and resorts in the country. However, with no conventional fuel source, the country relies on imported diesel for electricity production and is seeking to overcome its economic and environmental burdens by adopting to renewable based power generation methods, specifically solar PV.

Renewable energy supportive policies and programs of the Maldivian Government has set PV growth on an upward trend over the past decade. The installed solar PV capacity has reached 21.52 MW in 2019 from 1.64MW in 2009. The National Strategic Action Plan (2019-2023) (SAP) sets targets to further increase the share of renewable energy by 20% compared to 2018 levels and in order to meet this target and beyond, the Ministry of Environment, Climate Change and Technology aims to increase the share of renewable energy to 70% of the national energy mix by 2030. Currently the energy from renewables make only 4% of the national energy mix and significant growth is anticipated for the Maldives energy sector with an approximate doubling of energy demand forecasted for many of the project islands over the next 10 years.

Developing renewable energy projects through private sector financing is an attractive way for Maldives to accelerate the development of renewable energy. Support from World Bank Group (WBG) has made tremendous contributions to improve the renewable energy investment climate in Maldives for the private sector. Through technical assistances and financial leverages delivered under the World Bank’s Accelerating Sustainable Private Investment in Renewable Energy (ASPIRE) project (ongoing since December 2014) two rounds of solar PV IPP bids with a total generation capacity of 6.5MW has been complete and PPA tariffs has reduced substantially for these two consecutive bids with the trend expected to continue. Prequalification of eligible bidders for the third phase of ASPIRE is ongoing which includes 11 MW of solar PV installations across various islands.

The current RE targets for Maldives require a high penetration of Variable Renewable Energy (VRE) in the island grids, thus modernizing and upgrading of the existing grid infrastructures are needed along with complementing technology options for energy storage. Building on the efforts of the ASPIRE initiative, during December 2020 WB has approved a second project, i.e. Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) project to further accelerate the energy transition occurring in Maldives and support a sustainable post COVID-19 recovery.

The development objective of the ARISE project is to increase the generation capacity from renewable energy sources and facilitate the integration of VRE in the mini grids of Maldives islands. The ARISE project includes a target of bringing in 36 MW new solar PV installations with an estimated cumulative 50MWh of Battery Energy Storage Systems (BESS), and grid infrastructure upgrades.

The works will draw on a mix of loan and grant financing mobilized under the ARISE project. The funding for the grid infrastructure component of ARISE is through a US$ 6.2 million International Development Association Grant and US$ 20 million Asian Infrastructure Investment Bank concessional loan. The grid infrastructure procurement covered by this request for quotation will support grids where solar PV is deployed under ASPIRE Phase III (11 MW) and first phase of ARISE (10 MW Floating PV and another 11-14 MW land-based PV installations).

## General Requirements and Description of Works

The works related to this Contract is for delivering grid infrastructure Works to support grid modernization, and the connection and integration of solar PV in the network on Fifteen (15) islands.

These islands have been packaged in to Three (3) Lots.

Lots 1: Addu City Mainland and Hulhumeedhoo, Fuvamulah City, and GDh.Thinadhoo

Addu City main land, Hulhumeedhoo, Fuvahmulah, Thinadhoo, require limited medium voltage (MV) network upgrades.

Lots 2: Eydhafushi, Hinnavaru, Kulhudhuffushi City

Kulhudhuffushi, require limited medium voltage (MV) network upgrades.

Hinnavaru and Eydhafushi are currently composed of LV circuits only. All MV elements, including transformers, communications, HMI/SCADA, fibres and all required components and miscellaneous are required to be provided for these two islands, along with connection of the new substations to the existing LV feeders.

Lots 3: L. Fonadhoo, interconnected network of L. Isdhoo, Kalaidhoo and Dhabidhoo, L. Maabaidhoo, L. Kunahandhoo and L. Hithadhoo, Sh. Funadhoo.

- L. Fonadhoo

- Sh. Funadhoo

- The planned interconnected network of L. Isdhoo, L. Kalaidhoo and L. Dhabidhoo.

- The remaining three islands (L. Maabaidhoo, L. Kunahandhoo and L. Hithadhoo) require LV network upgrades.

General:

There are four types of network modifications required.

- Installation of radial feeder to Solar Farm

- Installation of radial feeder and communications to solar farm and upgrade of associated distribution substation equipment at loop connection point

- Installation of a complete 11kV network, consisting of a switched main MV distribution loop and associated distribution substations and radial feeders to Solar Farms, and communications backbone.

- General grid upgrades (not associated with a specific solar PV interconnection):

  - Specified upgrades to the existing 11kV network, such supply and install, or replacement of conductors, substations, switchgear, transformers, boards or communications to modernise infrastructure and provide for capacity for future load growth.

  - Specified upgrades to the existing 400V network, such replacing conductors and distribution boxes, installing new feeder routes and reconnecting customers to provide for capacity for future load growth.

Standards and Codes:

The equipment installation and electrical works under the contract must be carried out in accordance with the latest revisions and amendments of relevant IEC standards as in force in Maldives. Furthermore, the installations must comply with the technical requirements prescribed by the Utility Regulatory Authority (URA) as well as any other laws or regulations of Maldives.

Further details are included in Section 1.3 Specifications.

Scope of Works

Scope of Project and requirements included in this section is to provide a general understanding of the nature of work to be delivered under the contract. Detailed specifications are included in Section 1.3 Specifications.

Medium Voltage Network:

- Network design and planning:

  - Site inspection to micro-site route and conduct soil testing.

  - Confirm selection of 11kV switchgear, 11kV feeder cables and all associated secondary equipment

  - Load flow studies, using solar generation and network loads provided by the Employer to confirm voltage profile is within allowable limits within modified regions of the 11kV network.

  - Fault level studies to identify fault levels throughout modified regions of the network. Maximum, minimum and projected ultimate fault levels must be considered for all fault and network switching scenarios.

  - Earthing studies, where applicable, to establish the earth philosophy of the medium voltage network and provide adequate earth fault detection for safe operation and management of the network.

  - Design of suitable feeder protection systems

  - Grading of radial feeder protection and main loop protection

  - Design a fibre optic backbone for each MV network to facilitate communication between all controllers, MV circuit breakers and switches, protection relays and further IEDs that participate in the power system.

  - Design and configure the connection of all communications devices associated with each radial feeder, protection and control, to the Fibre Optic communication backbone.

  - Develop and integrate a signal and IO tag database for each site to facilitate interfacing to each island’s power system SCADA.

  - Develop a construction procedure for each location to minimise network interruptions during construction and commissioning

  - Develop commissioning and test procedure for each modified region of the network.

- Civil works and installation of the Switchgear enclosures/ demountable buildings.

- Supply and install all equipment required to implement the design, as per the scope of work for each island

- Control and auxiliary supply for the 11 kV protection and metering system.

- Trenching and laying of 11 kV Cables

- Installation of earthing system

- Terminate and connect the 11kV feeder cables at each end

- Supply, install and commission fibre optic backbone for power system network communications on each island

- Provide routine test records verifying the results of Factory Acceptance Tests (FAT) for the MV Cables, MV switchgears and MV transformers.

- Commission the feeder ready for service. Commission tests shall include as a minimum:

  - IR test of install cables

  - CT ratio checks by primary injection

  - Protection trip checks by secondary injection, including confirmation of TCC at least three points

  - Step and touch potential test for equipment at each end of the radial feeder

  - Communications links – confirmation of operation and data transfer rates

Low Voltage Network:

- Network design and planning:

  - Confirm selection of feeder cable sizing for specified loading (to be provided by Employer) and prepare procurement specifications for cables, distribution boxes, and all associated equipment

  - Protection design for selection of LV MCBs, and coordination with MV protection system where applicable.

  - Earthing studies, where applicable, to specify earthing requirements for the safe operation and management of the network.

  - Develop a construction procedure for each location to minimise network interruptions during construction and commissioning

  - Develop commissioning and test procedure for each modified region of the network.

- Supply and install all equipment required to implement the design, as per the scope of work for each island

- Terminate and connect the LV feeder cables at each end

- Commission the feeder ready for service. Commission tests shall include as a minimum:

  - IR test of install cables

  - Step and touch potential test for equipment at each end of the radial feeder

## Specifications

Detailed specifications for this project are included in the following Appendices.

- Appendix A – General Requirements

  - This specifies the electrical standards applicable to all equipment, as well as general provisions for work practices, studies, document submission, and management of project, design, and quality.

- Appendix B – Grid infrastructure requirements:

  - This document provides details the work required on each island, as well as equipment specifications and requirements.

- Appendix C – Drawings

  - This contains limited drawings and related information on the sites, including maps and single line diagrams.  For detailed drawings, bidders are referred to the online data room.

- Appendix D – Environmental and Social Requirements:

  - This document specifies the Code of Practice that the Contractor must comply with.

- Appendix E – Supplementary information

  - Link directing to a data room with supplementary information is provided for information of bidders. The supplementary information has not been validated, may contain inaccuracies, and may change without notice. It is included to assist Bidders in evaluating their interest in the project and their proposed approach. The Bidder may not rely on the supplementary information in making their offer. Where supplementary information relates to particulars that may impact on the Bidders offer, the Bidder should make its own enquiries and satisfy itself as to the actual situation.

Where any conflict arises between this document, and the Appendices, or between any of the Appendices, the more onerous requirement shall apply unless otherwise agreed by the Employer.

## Division of Responsibilities Matrix

The following tables set out the division of responsibilities. Please note that where responsibility is not ‘Contractor’ Contractor’s inputs may still be required. Any requirements to deliver the project that are not explicitly listed below (or elsewhere in this Employer Requirements) are Contractor’s responsibility. This table shall be read in conjunction with Section 1.3 Specifications, which contains further information on the network elements that responsibilities apply to.

|  | Description | Employer | Utility | Contractor | Notes |
| --- | --- | --- | --- | --- | --- |
|  | Environment and social screening reports |  |  | Yes | To update |
|  | ESCP |  |  | Yes | To update |
|  | OHSMP |  |  | Yes |  |
|  | Land securing (Substations) |  | Yes |  |  |
|  | Site Survey |  |  | Yes |  |
|  | Geotechnical Survey |  |  | Yes (foundations) Optional (trenching) |  |
|  | Identification of underground service lines |  |  | Yes |  |
|  | Permits and licenses | Assist | Assist | Yes |  |
|  | Design, technical checks |  | Final Approvals | Yes |  |
|  | Inspection and test |  |  | Yes |  |
|  | MV and LV Design submission |  |  | Yes |  |
|  | Site Offices |  |  | Yes | If required |
|  | Contractors temporary site (Material storage) and site offices |  |  | Yes |  |
|  | Internet (temporary services) |  |  | Yes |  |
|  | Accommodation |  |  | Yes |  |
|  | Select Fill / Excavated Fill |  |  | Yes |  |
|  | Site Clearing, Grubbing |  |  | Yes | Minimal works |
|  | Internal Roads |  |  |  | N/A |
|  | Access Roads |  |  |  | N/A – use existing roads |
|  | Laydown |  | Assist | Yes |  |
|  | Site Grading, cut and fill |  |  |  | N/A |
|  | Site Preparation |  |  | Yes | Minimal works |
|  | Equipment shipping |  |  | Yes |  |
|  | Equipment land transport and cranage |  |  | Yes |  |
|  | Staff flights and land transport |  |  | Yes |  |
|  | Mobilisation & Demobilisation |  |  | Yes |  |
|  | Aggregate and Concrete |  |  | Yes |  |
|  | Trench bedding sand |  |  | Yes |  |
|  | Management Plans and documentation |  |  | Yes |  |
|  | OEM Equipment |  |  | Yes |  |
|  | Site surveying /pegging |  |  | Yes |  |
|  | Site clean-up |  |  | Yes |  |
|  | Labelling |  |  | Yes |  |
|  | As-Built drawings and documentation |  |  | Yes |  |
|  | Testing and Commissioning Reports |  |  | Yes |  |
|  | Spare Parts |  |  | Yes |  |
|  | Perimetral Fence |  |  |  | N/A |
|  | Steel Gates |  |  |  | N/A |
|  | Earthing and lightning protection |  |  | Yes |  |
|  | Install substations and transformers |  |  | Yes |  |
|  | Install and terminate feeder cables |  |  | Yes |  |
|  | Install and terminate fibre optic communications system |  |  | Yes |  |
|  | Switching |  | Assist | Yes |  |
|  | Commissioning |  |  | Yes |  |
|  | Procurement |  |  |  |  |
|  | Electrical Cabling |  |  | Yes |  |
|  | Substation RMUs |  |  | Yes |  |
|  | Substation transformers |  |  | Yes |  |
|  | Power station switchboards |  |  | Yes |  |
|  | Power station transformers |  |  | Yes |  |
|  | Fibre optic cable |  |  | Yes |  |
|  | Miscellaneous communications hardware |  |  | Yes |  |
|  | Miscellaneous electrical hardware |  |  | Yes |  |

## Engineering

The Contractor shall finalize design specifications of the Works in accordance with the Contract, including this Employer’s Requirements and the Specifications in Appendix sections.

## Procurement

The Contractor is to procure all items necessary for its scope of works. The Contractor is to provide a comprehensive Bill of Materials in its reporting to the Employer and detail the status of procurement and delivery within each report.

## Construction

The Contractor is required to carry out all construction activities (as per the division of responsibilities matrix) to prepare the site, install and connect the equipment, and ensure it is in a fit and sound state ready for energization. Construction planning and activities must give due consideration to the requirements of working on remote islands with limited resources.

Contractor is required to liaise with the Employer’s staff for connection and all necessary pre-commissioning tests of electrical and communications interfaces.

Contractor is required to coordinate with other trades or contractors (such as solar PV contractor and the electricity utility), who may be working on the same networks.

Further details on Construction requirements are included in the Technical Specifications.

## Commissioning

The Contractor shall prepare a comprehensive commissioning plan. In cooperation with the Employer, the Contractor shall liven the plant in accordance with the commissioning plan. The Contractor shall carry out necessary tests, including performance tests of equipment and provide a detailed commissioning report.

Further details on Commissioning requirements are included in the Specifications in Appendix sections.

## Operations and Maintenance

The Contractor shall provide comprehensive operations and maintenance manuals, procedures, data sheets, as-built drawings other information as required in the Specifications in Appendix sections.

The Utility is responsible for operation of the plant post commissioning. The Contractor must provide a comprehensive training program and 24/7 phone support to the Utility on each island for the first 12 months of operation. Phone support shall assist the Employer to diagnose and respond to faults and confirm correct operational procedures. Contractor may assume that Utility has existing expertise in LV distribution equipment and MV distribution equipment where similar equipment already exists on site. Training and support shall focus on automation, communications and control, along with resolution of issues specific to the installed equipment during the DLP.

## Battery Limits

The project battery limits are:

The scope of work on the Medium Voltage Network ends at

- Distribution / Consumer substations (SS-x): LV distribution boards (including LV distribution boards)

- Solar PV sites: HV Terminals of the RMU incomer isolation switch (excluding RMU and transformers)

- Powerhouses: LV Terminals of the Main Transformers (excluding LV distribution boards)

- BESS stations: HV Terminals of the RMU incomer isolation switch (excluding RMU and transformers)

The scope of work on the Low Voltage Network ends at

- Distribution / Consumer substations (SS-x): LV distribution boards (excluding LV distribution boards)

- Solar PV sites: N/A (scope of Solar PV contractor to connect to the network)

- Powerhouses: LV distribution boards

- BESS stations: N/A (scope of the BESS Contractor)

- LV feeders: Termination of the customer service main to distribution box (including re-termination)

## Employer Provided Items

The Employer shall provide any items or support as defined in the division of responsibilities matrix.

## Permits, Certificates, Licenses, Registrations and Approvals

The Contractor shall identify, make allowance for, and secure all necessary permits, certificates, licenses, registrations and approvals required for the project.

## Equipment requirements

Equipment requirements are as per the Bill of Quantities.

## Quantity change management

Changes in quantities of equipment to be installed under this contract, if required during design finalization and accepted by the Employer, or as initiated by the Employer, will be managed as follows:

Contractor shall design the Works. Through the design process, due to emerging details or request of the Employer, final quantities may change from this specification. Final quantities shall be subject to reasonable review by the Employer or its representative to ensure the design and quantities are fit-for purpose, sufficient and necessary.

Following issue of IFC design for all islands, the difference between the quantities in Bill of Quantities and IFC design quantities shall be multiplied by the unit rate for each item, then summed to determine the total price adjustment.

A Change Order shall be prepared and executed by both parties for the total price adjustment.

If further changes are made during construction, these shall be reassessed using the above procedure following issue of as-built, and a further Change Order executed for the additional total price adjustment.

## Project Management and Delivery Requirements

Detailed requirements for project management, including quality and safety management, design processes, testing and commissioning, meetings, and documentation are specified in Appendix A – General Requirements.

## Implementation Period

Grid infrastructure under this Contract will supplement the PV installations under ASPIRE Phase III and ARISE Phase I respectively. In order to reliably feed in the energy from these PV systems the grid infrastructure requirements are expected to be commissioned and in a fully functional state by the time the PV systems are interfaced with the grid. The implementation schedule is designed to support this requirement.

The Contract shall be completed within a 12-month period from Effectiveness.

Key dates in the implementation period are shown below.

| Milestone | Months from Effectiveness |
| --- | --- |
| E&S related screening & documentation - Updated ESSR - Updated ESCP - OHSMP | 2 |
| Design - preliminary (30%) – See Appendix A for details | 2 |
| Procurement – main equipment orders placed | 3 |
| Design – issued for construction | 5 |
| Vendor verification, factory quality assurance checks etc. | 3 |
| Cables, Transformer and MV Switch gear FAT completed | 8 |
| Site works commenced | 6 |
| Site works completed | 9 |
| Pre-commissioning complete | 10 |
| Completion date | 11 |
| Commissioning | 12 |

Contractor’s monthly reporting must clearly show progress against the above milestones. Any progress delays shall include a detailed explanation, schedule impact assessment, and plan to minimize any effect on subsequent milestones.

The Contractor’s workflow is expected to include multiple teams working in parallel across at least two islands at any time. Islands shall be commissioned progressively with the intent of minimizing disruption and optimizing the availability of works. It is expected that at most four (4) islands shall be commissioned per month. Thus, the first island shall be commissioned at least three (3) months before the last. The above dates for implementation apply for the last island.

The sequence of work shall be determined in cooperation with the Employer, with the objective of aligning individual island completion dates with the installation of other infrastructure (solar PV and BESS). The Employer shall advise the desired sequencing not more than 1 month from effectiveness. Contractor shall comply with this sequencing.

Contractor’s Representative and Key Personnel

| Item No. | Position/specialization | Relevant academic qualifications | Minimum years of relevant work experience |
| --- | --- | --- | --- |
| 1 | Contractor’s Representative | Engineering or project management degree or diploma | 15 years |
| 2 | Environmental & Social Safeguards Officer | First Degree in relevant field | 5 years |
| 3 | 1 x Site supervisors per site/island |  | 10 years |
| 4 | Logistics manager |  | 5 years |
| 5 | 1 x Electrical supervisor per site/island | Electrical engineering degree | 8 years |
| 6 | 2 x electricians, with HV cable jointing training | Electrial trade qualification, valid in Maldives) | 5 years |
| 7 | Communications technician |  | 5 years |

## Appendix A – General Technical Requirements

1.	Relationship to Other Parts of the Employer Requirements	165

2.	Language and Units	165

3.	Site requirements	166

4.	Reporting, documentation, and meetings	173

5.	Training and capacity building	183

6.	Environmental and social risk	183

7.	Equipment requirements	184

8.	Service conditions	184

9.	Civil and structural works requirements	185

10.	Quality control	186

11.	Warranty requirements	199

Relationship to Other Parts of the Employer Requirements

This part of the Employer Requirements (Appendix A –General), provides key technical requirements for implementation of the project. It shall be read in conjunction with other parts of the Employer’s Requirements.

In particular, note:

- Employer Requirements:

  - This document provides the necessary overview information on the project scope and general requirements. It also includes summary information on the island specific capacities and requirements.

- Appendix B –Grid Infrastructure specifications:

  - This document provides key technical and details of equipment and installation requirements on each island.

- Appendix C – – Drawings

  - This contains limited drawings and related information on the sites, including maps and single line diagrams.   For detailed drawings, bidders are referred to the online data room.

- Appendix D – Environmental and Social Requirements:

  - This document specifies the Code of Practice that the Contractor must comply with.

- Appendix E – Supplementary information:

  - Supplementary information is provided for information only. The supplementary information has not been validated, may contain inaccuracies, and may change without notice. It is included to assist Bidders in evaluating their interest in the project and their proposed approach. The Bidder may not rely on the supplementary information in making their offer. Where supplementary information relates to particulars that may impact on the Bidders offer, the Bidder should make its own enquiries and satisfy itself as to the actual situation.

Language and Units

  - Language:

The English language shall be used on all drawings and in all documents and wherever anything is required by the Contract, to be written, marked, printed or engraved.

Where noted (typically for operational procedures), documents shall also be produced in, or include, Dhivehi language.

  - Units of Measurement

Systeme International d’Unites (SI) units shall be used.

Site requirements

Specific limitations and requirements for work practices are included in the Environmental and Social Code of Practice (Appendix D). This section sets out general expectations for site works.

  - Work Practices

The Contractor will submit a set of work practices applicable to this project along with the general Health and Safety plan before site mobilization. The procedures will be subject to acceptance by the Employer. The procedures shall meet the following requirements.

    - Site Hours and Roster

The Contractor may work a rotation for all site-based personnel. Maldives Employment Act, including working hours, overtime rates, and consecutive days must be complied with.

    - Site Facilities and Temporary Services

As per division of responsibilities matrix. Contractor to note that any facilities noted in the division of responsibilities matrix are limited to that currently available at the power station area. If the Contractor requires additional facilities, then it shall make allowance for such.

    - Mobilization & Demobilization

Mobilization and demobilization shall include but not be limited to the following:

  - Supply, installation and maintenance of Contractor’s Site office and facilities;

  - Mobilization of all facilities, construction plant and personnel necessary for the Works; and

  - Demobilization of all facilities, Plant and Equipment and Contractor’s Personnel from Site, and the rehabilitation of all Temporary Work Sites to the approval of the Employer.

The Contractor shall be responsible for the mobilization of facilities, plant and equipment, and personnel.

    - Test energy

Test energy for initial pre-commissioning tests once equipment is connected to the grid will be provided free of charge by the Employer. Subsequent or repeat tests may be subject to electricity consumption charges at standard published tariffs.

    - Site Access and Vehicle Parking

The Contractor shall utilise only existing site access and vehicle parking areas, unless by prior approval by the Employer. The Contractor shall liaise with the Employer to ensure that access to the site and the daily business operations of the Employer, community members, and other contractors are not adversely affected.

    - Temporary sites, Laydown and Security

The contractor is required to obtain a designated temporary site from the island for storage of contractor’s materials, equipment’s and set up of site offices as necessary and this will be the primary areas of material storage for the contractor. In addition, the Contractor is permitted to use areas in the immediate vicinity of installations work sites for laydown or equipment storage as may be required for managing day works, subject to prior approvals from relevant stakeholders. Use of any other areas for laydown, storage, parking, or other such activities is generally not permitted, except by express consent of the Employer.

The Contractor shall be responsible for the security within the Site of Works.  The Contractor shall be responsible for inspection of any existing security fencing at the site and determining its fitness for purpose. The Contractor shall be responsible for any additional measures, or upgrades and maintenance to the security fencing for the duration of the Contract.

    - Site Clean Up

The Contractor shall make every effort to keep the Site of Works in a clean and tidy condition for the duration of the Works.  The Contractor shall, from time to time, and on completion of any area of the works or where directed by the Employer, remove rubbish, surplus materials or any other construction debris from such areas as may be attributable to the Work under the Contract and generally leave them in a satisfactory condition and to the approval of the Employer.

Upon completion of the Works, the Contractor shall remove all rubbish, debris, temporary earthworks or surplus materials from the site of the Works.  The site shall be left in a neat and tidy condition to the satisfaction of the Employer.

    - Site Control Measures

The Contractor shall provide for appropriate measures to manage and/or control traffic, water, dust and weed in and around the Site of Works.  Such measures shall be implemented during the entire duration of the Contract, and as specified in these Specifications, shown on the Drawings and/or as deemed necessary by the Contractor for performance of the Contract to the Employer’s satisfaction.

In the event of the Contractor failing to comply with its responsibilities under this Clause, the Employer may, without further notice, take such steps as it considers necessary, to provide for the safe passage and safety of traffic or to remove any obstruction or to repair damage, including, if it considers it necessary, the employment of workmen and watchmen to complete work and the cost thereof may be deducted from any monies due to the Contractor under the Contact.

    - Traffic and Exclusion Zones

The Contractor shall provide for continuous operation of normal traffic along all roads, pedestrian and vehicular access ways in and around the Site of Works or that are otherwise affected by the Works. The Contractor shall, where necessary, provide side tracks which shall be constructed, sign posted, and maintained to the satisfaction of the road owner and the Employer.

The Contractor shall erect and maintain exclusion zones beneath and adjacent to all work at heights and shall be responsible for the safety of all pedestrian and vehicular traffic within the Site of Works and any adjacent areas affected by them.  The Contractor shall provide for all necessary watchmen, lights, barriers, notices and signs, and shall provide and maintain the same to the satisfaction of the road owner and the Employer.

The Contractor shall not cause obstruction to any road, drain and/or watercourse and shall not break down or remove any gates or fences without prior approval of the Employer.  Where such obstructions or breakages cannot be avoided, the Contractor shall remove such obstruction or repair such breakages, to the satisfaction of the Employer, as soon as possible.

    - Site Meetings

The Contractor shall provide for its relevant staff to attend required meetings with the Employer at the project site or the Employer’s offices for the duration of the Contract. Consideration will be given to remote meetings (teleconference / videoconference) for instances where it can be shown that these will not affect the satisfactory outcomes of the meeting.

  - Miscellaneous Requirements

    - Organization and Communications Chart and Contactor’s Personnel Qualifications

Contractor shall provide an organization chart showing the key positions for project delivery. This shall include site management for each site, contractor’s representative, and lead roles for engineering, procurement, logistics, and safety at a minimum. Organization chart shall be accompanied by individual contact details, and a communications matrix that specifies who, from both the Contractor, Employer, and any other stakeholders, shall be included on any communications about the project, categorized by communications type (e.g. contract; engineering; site works; reporting; etc.).

Contractor shall provide the names of the nominated Site Supervisor for each site, and other site personnel. The Contractor shall also provide evidence of qualifications, including:

- Contractor’s general safety induction and site-specific induction

- Formal first aid training, including CPR - must be at least two qualified First Aid personnel on each site

- Qualification or endorsed training as applicable to work being undertaken, including but not limited to:

o	All electrical works by qualified electrician

o	All works on proprietary components to be conducted by personnel meeting OEM requirements

o	All MV electrical works by personnel with demonstrated experience in installation, termination and jointing of medium voltage systems

o	Earthing works by personnel with demonstrated experience in installation of earthing systems

o	Communications installations, including fibre terminations, by trained and experienced technician

    - Workmanship and Materials

Workmanship shall be of first-class commercial quality and in accordance with the best shop practice. Like parts shall be interchangeable. Machining of fits on renewable parts shall be accurate and shall be to specified dimensions, so that replacement parts may be readily installed.

Unless otherwise specified, materials and components used for the Works specified shall be new and unused. Materials and components shall conform to the standards current at the time of execution of the Agreement.

    - Packing and Shipping

      - Packing

All items of Plant supplied by the Contractor shall be adequately packed and protected for shipment and outdoor storage at Site.

The Contractor shall ensure that the Plant shall be protected against corrosion, weather damage, condensation, distortion, and damage by vermin and the ingress of foreign matter.

Packing of any Plant shall comply with the approved shipping preparation and packing procedures and shall include but not be limited to the following:

    - Plant shall be properly packed.

    - Plant shall be shipped in weather proof and watertight containers unless otherwise agreed with the Employer.

    - Containers, crates or packages shall be checked for defects internally and externally prior to packing.

    - Weights and lifting points shall be clearly visible on each package.

    - Plant shall be not wrapped in plastic unless it is coupled with adequate moisture absorbent material, such as silica gel and the like.

    - Bright metal parts shall be greased coated or similar rust inhibitor applied commensurate with the type of machinery.

    - Machined surfaces shall be protected with wood blocks or similar approved means and reinforced externally with metal bands or plates.

    - Exposed threaded joints shall be encased or plugged as required.

For imported components, packing material shall comply with import and export regulations. All wood packing in each consignment shall be free from bark and all visible signs of insect and fungal attack at the time of shipment. Furthermore, the importation of packing materials such as second- hand sacking, hays, straw, chaff, rice husks and peat shall be prohibited. The Contractor shall be responsible for obtaining approval of the packing timber and materials before delivery. Packing lists shall state the type of packing used and certify that none of the prohibited material has been included.

The Employer may require to inspect and approve the packing before the items are dispatched but the Contractor shall be entirely responsible for ensuring the packing is suitable for transit and such inspection shall not exonerate the Contractor from any loss or damage to faulty packing.

Waste packing material, and in particular non-biodegradable waste material such as plastic packaging, shall be minimized.

      - Unloading and Storage at Site

The Contractor shall at Site place the equipment in the Contractor’s storage area in the following manner:

    - Any containers or any packages placed in power house area shall be in locations as directed by the Employer.

    - Certify that the contents of any container or any package agree with the said packing lists.

    - Remove from Site any unwanted packing debris and any empty containers immediately after completion of unloading at Site.

    - For works in public sites, material handling and transfer of equipment from contractors' temporary site to job site and material management at such sites is responsibility of contractor and shall be executed per E&S requirements prescribed for the project.

    - Existing Works and Underground Services

The Contractor shall note that the drawings of existing services are incomplete and not accurate. During construction planning, the Employer will make available any current, localized information on existing services, however, the accuracy of such information may not be relied upon by the Contractor. The Contractor shall ascertain the location of any buried services in the vicinity of the Works using electromagnetic, radiodetection or ground penetrating radar (or other suitable equipment) before commencing construction. If services are identified, then the Contractor shall give notice of this to the Employer at least three (3) working days prior to the commencement of any construction activity that may affect those services(s).

The Contractor shall take all reasonable actions and provide all things reasonably necessary to protect and maintain existing services to the satisfaction of the Employer.  In the case of damage occurring to existing services, the Contractor shall immediately report the damage to the Employer.  The cost of the necessary repairs or renewals shall be borne entirely by the Contractor.

If it is found to be necessary to alter the location or level of any existing services to conform with the Works, the Contractor shall relocate, redirect or alter any existing services as required to execute the Works and to the satisfaction of the Employer.  This will include altering finished surface levels of existing services.

If uncharted services are encountered during excavation, the Employer shall be notified before proceeding.

Any connections to live equipment will only be permitted with the consent and under the supervision of the Employer. The Contractor shall notify the Employer prior to carrying out any such work, detailing the method to be employed.

Any connection requiring statutory or other approvals shall be the Contractor’s responsibility.

      - Services Shutdown

Where it is a requirement to temporarily shut down or disconnect services (such as electricity or water) for the completion of the works the Contractor shall notify the Employer at least three (3) days prior.

Generally, the Contractor will be required to undertake shutdowns outside of normal business hours unless by prior approval by the Employer and minimize the extent, number and duration of any such shutdowns /planned outages as much as possible. Except in contingency events, shutdowns should be planned not to exceed 6 hours.

      - HV Switching and Isolations

The Employer will provide/organize for all HV switching and isolations for equipment connections. The Contractor shall provide a minimum of five (5) working days’ notice for HV equipment isolation requirements.

    - Structural Integrity

The Contractor shall be responsible for ensuring the structural integrity of any temporary works, and of any existing works where impinged upon by new works.

    - Hazardous Areas

No sections of the installation are within hazardous areas or require hazardous equipment ratings.

    - Site Clearance and Demolition

The Contractor shall be responsible for obtaining all site permits or approvals and equipment isolations before commencing clearance of the Works. All equipment isolations will be completed by Employer’s Power Station staff in conjunction with the Contractor.

The Contractor shall carry out all demolition necessary to complete the Works and shall be responsible for the removal and disposal as directed by the Employer of all demolished and decommissioned equipment.

Further contractor shall carry our any site-specific preparatory works such as vegetation clearing, levelling etc where needed. This is expected to be minimal.

    - Building Permits

The Contractor is required to obtain building permits and local council authorization for the new civil structures designed by the Contractor. Contractor must provide all required design inputs and documentation to facilitate submission.

    - Site Induction Requirements

The Contractor shall be required to comply with all of the site requirements including compliance to all isolation, induction, site safety, first aid, and emergency procedures. The Contractor shall ensure that all site personnel have all of the requisite certification for site.

    - Project information board

During construction, Contractor is required to install a temporary project information board, setting out (at a minimum):

  - Title and brief description of the works being undertaken

  - Expected duration of site works

  - Work hours

  - Where to access Grievance Redress Mechanism and other project information

  - Any notices of interruptions that may affect local community, such as road closures

  - Contact person and phone number(s).

Contractors are to supply and install a permanent project information board at a prominent location (to be agreed with the Employer) at the project site. This shall be of a material and construction suitable to last at least 10 years in site conditions. The information board shall be approximately 2 m wide by 1 m high. Graphics to be prepared by the Contractor and approved by the Employer (must be supplied in a readily exchangeable electronic format). Graphics should depict the installation, show project title, headline system parameters, and key project stakeholder information.

    - Community relations

Contractor will take advice from the Employer, obtaining a full brief of current situations and establish a plan that will complement the local culture and leave zero legacy.

Contractor will be obligated to:

  - abide by the local laws and regulations;

  - recognize and respect the culture, values and traditions of those communities; and

  - behave in a socially responsible manner during both working and after hours.

Reporting, documentation, and meetings

Documentation required for submission under the implementation stage of the project, including all engineering and test documentation, management plans and studies, progressive reporting and other documentation, is described in this section.

  - Management plans

    - Project execution plan (PEP)

The Contractor shall prepare a Project Execution Plan for the project and will comply with the requirements of the Project Execution Plan upon approval by the Employer.

The PEP shall define in detail the implementation methodology and strategy for delivering the design, procurement, construction and commissioning of the Project, successfully in accordance with the requirements of the Employer and the agreed Project objectives.

The PEP shall provide a roadmap for the effective execution of the project and shall be disseminated to all project team members.  The PEP shall outline the objectives, processes and strategies that will be employed by the Contractor to manage and execute the works and establish the framework to ensure the project expectations and key performance indicators are met.

The PEP shall be the primary document of the suite of documents listed below which apply specifically to the project and which outline the Contractor’s management principles for the project.

  - Project Execution Plan

  - Occupational and Health Safety Management Plan (OHSMP) (Refer to E&S section for further details) Revise the ESCP

  - Code of conduct for contractors’ workers (Refer to E&S section for further details) Quality Management Plan

  - Project Controls Plan

      - Project Schedule

The Contractor must provide a baseline project schedule for approval of the Employer, and consistent with the required project schedule.

The schedule must be fully resourced, logic linked and follow best industry practice.

The Contractor must provide progress updates to the approved schedule weekly and monthly.

The Safety Management Plan shall be consistent with the Environmental and Social Requirements. A copy of the Safety Management Plan will be provided to the Employer within 2 weeks of the execution of contract, or otherwise as agreed between the parties.

operations.

    - Regular reporting

Monthly Report

The Contractor shall establish an agreed template in conjunction with the Employer for Monthly Reporting which shall include the following:

- Contract program status (planned activities, actual activities achieved), including a 4 week lookahead;

- Milestone Status (planned v actual);

- Quantity / Labour Hour Report;

- Workforce summary;

- Plant and Equipment Summary;

- Early Warning Register;

- HSE Statistics

- Contract program issued including status (planned activities, actual activities achieved). On request, Contract Program shall be exported from the Contractor’s software to Microsoft Excel or Project format for submission to the Employer.;

- Risk Register;

- Issues List;

- Document Register;

- Change/Variation Register;

- Extension of time (EOT) Register;

- Request for information (RFI) Register;

- Other items as reasonably requested by the Employer.

Key personnel from both the Employer and the Contractor shall meet once a week to discuss all elements of project execution. The location of these meetings may be onsite or remote.

    - Quality management plan (QMP)

The Quality Management Plan (QMP) shall define how the Contractor assures itself that its procurement, manufacturing, supply, construction, and installation complies with the requirements of the Contract and addresses all activities relevant to the Works and shall demonstrate how all Work under the Contract performed by the Contractor will conform to the requirements of the Contract.

The QMP shall be adequate to cover all construction operations, including both onsite and offsite manufacturing, fabrication, assembly and installation works, and shall include the controls to be implemented by the Contractor and its Subcontractors, both directly and indirectly by identifying the Quality System documentation that the Subcontractors are required to produce to meet the Contract requirements.

The QMP shall define the documented quality system to be implemented by the Contractor throughout the Works, in accordance with the requirements of ISO 9001, and shall refer to all of the Contractor's relevant procedures and manuals.

The QMP shall address the interfaces between the Employer and the Contractor and other relevant entities. The QMP shall include an organisation chart showing the Contractor's corporate and project organization responsible for managing, performing and verifying the Works. The organisation chart shall be supported with a reporting and functional description of the Contractor's project organisation and identification of the quality related responsibilities of key positions.

The quality management function within the Contractor’s project organization shall be completely independent from the construction and engineering operations to guarantee the independence of the decisions.

The QMP shall be developed in accordance with the Employer’s requirements and in accordance with ISO 9001.

The QMP will clearly identify all Inspection and testing requirements related to completion of the Work under the Contract.

The Contractor shall conduct inspection and testing as per the agreed QMP. The Contractor will ensure the Employer is invited to attend, prior to commencing any tests for which the Employer has an agreed Witness or Hold Point.

The Contractor bears the full risk and liability of proceeding, inclusive of any rework and/or re-performance of the work instructed by the Employer due to the Contractor’s non-compliance with this provision.

Waiver of Employer attendance at inspections and testing can only be given in writing by the Employer.

The Contractor shall notify the Employer of items requiring inspection and testing. In the event of the Employer’s non-attendance, the Contractor shall ensure a comprehensive inspection report is available for review by the Employer.

      - Quality Management System

The Contractor will maintain a Quality Management System accredited to ISO 9001 requirements (or demonstrate equivalent industry standard and practices) and shall be capable of demonstrating that all the requirements of the Contract and all applicable Laws and applicable codes and standards are being met. Third party certification of assessed capability (i.e. approval to ISO 9001) is not considered a demonstration that the specified Quality Management System (QMS) requirements of the Contract have been met.

  - Document management system

The Contractor is to provide and use a web-based document management system for project document and drawing submissions, and tracking of all information requests and responses, as well as the Employer’s review responses. The selected system must be fit for purpose and is subject to approval of the Employer. A single system is to be implemented project-wide.

The Contractor is to ensure the Employer has free access to the system.

The system shall maintain a document register which lists all documents and drawings submitted by the Contractor along with:

- title, document number and revision;

- planned issue date for Employer’s review;

- actual issue date for Employer’s review;

- review status; and

- actual date of approval.

All drawings are to be submitted in PDF and native format. Diagrams, such as single line drawings and schematics, shall be prepared in accordance with IEC 61082-1. Graphical symbols used in schematic diagrams shall be in accordance with IEC 60617 (for electrotechnical diagrams) and the ISO 14617 series (for other diagrams). Naming of all documents and drawings must be sufficient to facilitate sorting by Section, discipline, and other logical categorisation.

Submissions shall be planned and executed in a coordinated and consolidated manner, meeting the following minimum requirements:

- A planned document and drawing register for design; inspection and test; and manufacturer data shall be provided at commencement of design and updated at least monthly.

- Design submissions at the design submission milestones must include all documents and drawings required for all document categories at the corresponding submission schedule milestone (30% / 80% / IFC), packaged together.

- Inspection and test plans shall be consolidated according to upcoming works

- Inspection and test certificates shall be consolidated by island, section of works, progress milestone or similar logical category.

- Manufacturer data records (MDRs), certificates, and factory acceptance test reports shall be consolidated by island, lot, shipment, type, or similar logical category.

- Minor or occasional individual or small sets of documents and drawings may be submitted separate to the above requirements subject to Employer agreement.

The Contractor is to provide the Employer with access to the project and document management system until completion of the Defects Liability Period.

On completion of Works, the Contractor is to export from the project management system and provide to the Employer a full copy of all correspondence, documents and drawings including as-built drawings for all elements of the Project in native format and in PDF format. The export shall include a logical document and folder structure, and reference key / table of contents to enable easy location of all elements.

  - Documentation deliverables

Where noted, documentation to be provided on a per-island basis. Other documents shall include island specific sections where applicable.

Design documentation shall be provided in three revisions:

- 30%: preliminary designs, suitable to establish equipment conformance with specification and confirm equipment quantities. 30% design shall be sufficient to confirm and progress procurement of all major equipment. 30% design shall be completed within 3 months of contract effectiveness.

- 80%: detailed design providing full details of all schematics, connections, mountings, foundations, etc. sufficient to construct the project with only minor outstanding items or quality control remaining. 80% design shall be completed within 5 months of contract effectiveness.

- Issued for use (IFU) or Issued for construction (IFC): IFU reports or analysis and IFC drawings are the final drawings that shall be sufficient to undertake all construction activities. IFC/IFU design shall be completed within 6 months of contract effectiveness.

Employer or it’s representative may review documentation deliverables and notify the Contractor of any issues of non-compliance with the Technical Specifications, which shall be corrected and resubmitted. However, this does not relieve the Contractor of its responsibility to provide complete and accurate deliverables, managed through an internal quality assurance program.

Where noted, documents are to be provided in Maldives language as well as English.

|  | Deliverable | Typical revisions (IFU=issued for use; IFC=issued for construction) | Per island | Maldives language version |
| --- | --- | --- | --- | --- |
|  | Within 63 days of award |  |  |  |
|  | Updated ESCP |  |  |  |
|  | Occupational Health Safety Management Plan (OHSMP) |  |  |  |
|  | Update Environment and Social Screening reports (ESSR) |  |  |  |
|  | Workers general safety and health awareness training completion reports |  |  |  |
|  | Preliminary (within 3 months of commencement) |  |  |  |
| 1 | HSE safety management plan (SMP), work method statements, job hazard analysis, safety in design review and emergency evacuation plan. | Draft/IFU |  |  |
| 2 | Drawing and design management plan including document naming and revisions / mark-up systems | Draft/IFU |  |  |
| 3 | Project management plan (PMP) | Draft/IFU |  |  |
| 4 | Quality Management Plan (QMP) and draft quality assurance manual (QAM) | Draft/IFU |  |  |
| 5 | Document register | Draft/IFU, update when documents issued |  |  |
| 6 | Notification prior to procurement of long lead time items | Draft/IFU |  |  |
| 7 | Summary / overview of inspection test plan (ITP), inspection test checklists (ITC) and factory acceptance tests (FAT), including matrix of tests | Draft/IFU |  |  |
|  | Design (30% within 3 months, 80% within 5 months, IFC/IFU within 6 months of commencement) |  |  |  |
| 1 | Design drawing package to include, at a minimum: |  |  |  |
| a | Basis of design report | 30%/80%/IFC |  |  |
| b | Site layout | 30%/80%/IFC |  |  |
| c | Sub-surface works layout | 80%/IFC |  |  |
| d | Site drainage plan, erosion and sediment control plan | 80%/IFC |  |  |
| e | Detailed layout drawings of switchboards and panels and building interconnection | 80%/IFC |  |  |
| f | AC and DC electrical single line diagrams of all systems, and equipment (panels, boards, breakers, RMUs, transformers, etc.) | 30%/80%/IFC |  |  |
| g | Electrical schematics of all systems, boards, panels | 80%/IFC |  |  |
| h | Protection details | 80%/IFC |  |  |
| i | Earthing drawings | 30%/80%/IFC |  |  |
| j | Trench and cable tray section drawings | 30%/80%/IFC |  |  |
| k | Details of auxiliary power systems | 30%/80%/IFC |  |  |
| l | Communications network drawing | 30%/80%/IFC |  |  |
| m | Electrical, mechanical and civil Specifications documents, including detailed installation and materials compliance requirements | 80%/IFC |  |  |
| n | Protection single line diagram | 30%/80%/IFC |  |  |
| 2 | Complete bill of quantities | 30%/IFC |  |  |
| 3 | Studies: |  |  |  |
| a | Load flow and fault level study | 30%/IFU |  |  |
| b | Protection study | 80%/IFU |  |  |
| c | Earthing study | 30%/80% |  |  |
| d | Civil and structural engineering reports | 80%/IFU |  |  |
| e | Cable sizing calculations | 30%/80%/IFC |  |  |
| f | Arc flash study | 80%/IFU |  |  |
| g | Short circuit study | 80%/IFU |  |  |
| h | lightning study | 80%/IFU |  |  |
|  | Factory (within 10 months of commencement) |  |  |  |
| 1 | Factory acceptance test report for major equipment | Final |  |  |
| 2 | Vendor verification requirements, factory audit report, equipment certificates / type certificates, standards compatibility statements | Final |  |  |
| 3 | Shipping documents | Final |  |  |
|  | Prior to site works |  |  |  |
| 4 | ITP and ITC containing, as a minimum, the following information for each significant activity identified in the relevant process: | Draft / IFU |  |  |
| a | Description of activity |  |  |  |
| b | Specification requirements/reference |  |  |  |
| c | Person responsible for activity (title) |  |  |  |
| d | Hold Points and Witness Points |  |  |  |
| e | Activity checklists |  |  |  |
| f | Inspection and test type |  |  |  |
| g | Tolerances or other acceptance criteria |  |  |  |
| h | Identification of relevant procedure and quality records |  |  |  |
| i | Test/inspection frequency |  |  |  |
| j | Work item or work lot identification |  |  |  |
| k | The Employer may request the Contractor to include additional Hold Points or Witness Points and the Contractor must make provision for the Contractor and the Employer to sign off at such points. |  |  |  |
| 2 | Transport and logistics management plan | Draft / IFU |  |  |
| 3 | installation method, including construction schedule, site utilisation (laydown areas etc.), logistics, staff facilities (toilets, site office), waste management etc. | Draft / IFU |  |  |
| 4 | Construction environmental management plan (CEMP) | Draft / IFU |  |  |
| 5 | Safety data sheets (SDS) for all substances used on site | Draft / IFU |  |  |
| 6 | Training and capacity building plan | Draft / IFU |  |  |
|  | During site works |  |  |  |
| 1 | Monthly progress report, including safeguards monitoring | Final |  |  |
| 2 | Register of entries and exits on site and pre-start meetings | Final | YES |  |
| 3 | Safety incident reporting | Final |  |  |
| 4 | Environmental incident reporting | Final |  |  |
| 5 | Completed ITCs and quality documentation | Final | YES |  |
|  | Prior to Completion |  |  |  |
| 1 | ‘As Installed’ control system programs, configuration settings, and protection relay settings | Final | YES |  |
| 2 | Technical data sheets of all major components | Final |  |  |
| 3 | Manufacturer’s software packages needed for future operation/maintenance. | Final |  |  |
| 4 | Asset register hierarchy | Draft | YES |  |
| 5 | List of maintenance tools supplied | Final | YES |  |
| 6 | List of other tools Employer should hold | Final | YES |  |
| 7 | List of spare parts and consumables supplied | Final | YES |  |
| 8 | Signage for standard operational procedures | Draft / IFU | YES | YES |
| 9 | Six hard copies and one soft copy (in a freely printable format) of Operations and Maintenance Manuals of the facilities including all OEM documentation and any required log books. O&M procedures to be graphically illustrated. | Draft / IFU | YES | Procedures and log-books only |
| 10 | Ten-year maintenance schedule | Draft / IFU | YES | YES |
| 11 | Preventative maintenance requirements | Draft / IFU | YES |  |
| 12 | Detailed pre-commissioning and test report | Draft / Final | YES |  |
| 13 | Red line drawings suitable for operation (at handover/completion) | IFU |  |  |
| 14 | Electrical safety certificate | Preliminary / Final |  |  |
|  | Within four (4) months of Completion |  |  |  |
| 1 | Commissioning report | Draft / Final | YES |  |
| 2 | ‘As Installed or As-built’ drawings & data sheets (electrical, layout, structural, communications and civil). | Final | YES |  |
| 3 | Completed asset register | Final | YES |  |
| 4 | Warranty novation agreements | Draft |  |  |
| 5 | Completed ITCs and quality documentation (consolidated package) | Final |  |  |

  - Equipment naming convention and hierarchy

Employer may provide naming convention and hierarchy to apply for drawings and physical tagging of all equipment. If not provided by Employer, Contractor must provide an internally consistent / logical, unique, and easy-to-follow naming convention and apply.

  - Asset register

Contractor must provide an asset register that lists all equipment installed, its name, number / tag / designation, reference technical specification, manufacturer, barcode, installed location (GPS referenced). Cable routes shall be surveyed and GPS route included in the register.

  - Meetings

The Contractor must allow for the following meetings, at a minimum:

| Meeting description | Location |
| --- | --- |
| Kick-off meeting | May be video conference or on site |
| HAZOPS | May be video conference or on site |
| Safety in design review at 30% design stage | Video conference |
| 30% design review meeting | Video conference |
| Weekly or fortnightly (as needed) engineering meetings to clarify information or issues arising in the design process | Video conference |
| 80% design review meeting | Video conference |
| Daily / weekly prestart meetings | On site |
| Fortnightly quality meetings during construction to discuss and resolve site issues | Video conference, including site representative |
| Initial training sessions with local staff (minimum 3 days per island) | On site |

Training and capacity building

The Contractor must provide comprehensive training and capacity building sufficient to enable the Employer’s staff to take over the operations and maintenance tasks for the Plant. To this end, the Contractor must supply:

- A training and capacity building plan, including:

  - Plan for initial training sessions with local staff

  - Matrix of skills and qualifications required, and mapping to existing local staffing with gap analysis

  - Identification of any areas that require specialist OEM training, and options for local staff to receive such training

- Comprehensive operations and maintenance manuals, including:

  - A detailed technical description of the system.

  - A complete list of all system components, with associated manufacturers literature, specifications, and warranties.

  - A recommended maintenance schedule, with complete maintenance instructions.

  - Detailed troubleshooting guides referencing all the system components.  This shall include repairs and diagnostic procedures that can be done by the supplier or a qualified third party.

  - All routine procedures, including isolation.

  - Emergency shut down procedures.

- Equipment data sheets

- 10-year schedule of maintenance, setting out required maintenance activities and the intervals at which to carry these out.

Environmental and social risk

Requirements for managing environmental and social risk of the project are included in the Environmental and Social Code of Practice (Appendix D).

Equipment requirements

See Appendix B – Grid Infrastructure Requirements.

Service conditions

  - Environmental conditions

The MV network, including all supporting infrastructure, shall be designed and constructed to operate normally under the environmental conditions summarized in Table ‎8.1.

Table ‎8.1: Environmental conditions

| Criteria | Condition |
| --- | --- |
| Minimum Ambient Temperature (oC) | 17.2 oC |
| Maximum Ambient Temperature (oC) | 40 oC |
| Humidity (%) | 79% |
| Wind Speed (m/s) | Up to 70m/s |
| Altitude (m) | 1.5 m above sea level |
| Corrosion | Compliance with ISO-12944, C5M |

  - Corrosion protection requirements

Equipment shall incorporate all necessary passive corrosion protection sufficient to achieve the design life in the site environmental conditions. Local environmental conditions shall be assumed to be at least as corrosive as Category C5 M of ISO 12944-2.

Corrosion protection shall include all internal systems (taking into account levels of atmospheric moisture, salt, dust, etc). Corrosion protection will not require major maintenance, such as replacement of major components or surface protections (sacrificial materials designed for replacement is acceptable). Electronic equipment should be suitably coated to prevent corrosion.

Use of hermetically sealed compartments to achieve corrosion protection shall demonstrate consideration for operations and maintenance requirements, including the effect of opening compartments for maintenance purposes.

Any fixings and fasteners should give consideration to corrosion requirements. Dissimilar metals should be avoided and otherwise separated by nylon washers.

Civil and structural works requirements

  - Geotechnical

Geotechnical and soil resistivity data for the site are not available and the Contractor is expected to make provision for foreseeable circumstances, and carry out necessary testing as part of its design. Contractor may assume trenching through sand and sandy soil at all sites, but must also make provision for occasional soft rock and minor obstacles. Contractor must have capability to source and utilise suitable machinery for trenching through hard rock if required, however, this will be treated as a change in scope in accordance with the Change Process.

  - Other

There are existing concealed and underground services on-site that may not be fully mapped. The Contractor shall undertake its own investigations in cooperation with local power station operators to confirm.

The worksite is critical infrastructure for supply of electricity in each island. Any access to the site must not interfere with power station operation unless explicitly agreed with the Employer. The Employer will provide all reasonable access for the Contractor to enter the worksite and undertake work. Contractor will be required to meet minimum training levels, complete permit to work (or similar) procedures and demarcate the worksite. If the Contractor breaches any conditions of this access the access may be revoked until remedied without Contractor recourse.

The Contractor must ensure that the equipment configuration is appropriate for the site. This includes due consideration of impacts to other activities at the site, such as access to other equipment and safety.

  - Scope of civil works

Under the project, civil works are expected to include:

- Construction of substation housing for new Substations

- Foundations of the substations and switchgear

- Trenching for cable laying

- Reinstatement of any road construction at crossings

- Site drainage and erosion control and rehabilitation.

  - Civil works requirements

Civil works requirements shall comply with local regulations, including the Maldives National Building Code Handbook.

Concrete shall be specified, and comply with ISO standards, including but not limited to:

- ISO 12439:2010 Mixing water for concrete

- ISO 14824:2012 Grout for prestressing tendons

- ISO 16204:2012 Durability — Service life design of concrete structures

- ISO 19595:2017 Natural aggregates for concrete

- ISO 19596:2017 Admixtures for concrete

- ISO 22904:2020 Additions for concrete

- ISO 22965-1:2007 Concrete — Part 1: Methods of specifying and guidance for the specifier

- ISO 22965-2:2007 Concrete — Part 2: Specification of constituent materials, production of concrete and compliance of concrete

- ISO 22966:2009 Execution of concrete structures

  - Scope of structural works

Under the project, structural works are expected to include:

- Cable management systems (cable ladders, trays, etc.)

- Any required ancillary structures, such as poles for instrumentation, lightning protection, lighting or security.

  - Requirements of structural works

Civil works requirements shall comply with local regulations, including the Maldives National Building Code Handbook.

Wind loadings must consider cyclonic conditions, with wind gusts up to 75 m/s. Earthquake loadings must be considered.

Quality control

The Contractor shall provide a Quality Management Plan (QMP) that describes the quality control methods for manufacture of all major equipment and equipment installation and testing. The scope of the QMP shall include:

- Full production chain of quality assurance

- Subcontracted works and manufactured components of the project

- Comprehensive matrix of testing planned, including FAT, Manufacturer Data Records, and Inspection Test Plans

- Inclusion of checks, witnessing and auditing required for quality control

- Document management for quality assurance documentation.

  - Vendor verification

Prior to placement of orders, vendor qualifications must be verified for specified equipment.

The specified equipment is:

- Transformers

- Switchgear (including RMUs)

- Cables

Vendor will be required to provide the following information:

- Current Business License

- Commitment letter stating the place of manufacture of the equipment to be supplied.

- Current certification for compliance with ISO 9001, ISO 14001 and ISO 18001, or demonstrate equivalent industry accreditation or practices.

- Commitment letter stating the bill of materials and their suppliers for equipment to be supplied for the project. Up to three alternate bill of materials may be used.

- Type test Reports and certificates for the equipment to be supplied, in accordance with ISO/IEC 17025, which are not older than 5 years and from a reputable testing laboratory with at least 15 years international track record. Type test reports and certificates must be for the place of manufacture for the equipment to be supplied.

- Reference list of minimum 3 completed projects in the region/ similar environment

- Written confirmation that:

  - The vendor has a local service centre or representative operating in the Maldives, Sri Lanka, or India (provide contact details), capable of servicing the supplied equipment.

  - The requested delivery schedule can be met.

  - The vendor has sighted the ESCP, equipment specification, quality requirements, documentation and training requirements of these Employer Requirements.

  - That product packaging will comply with the ESCP.

- Commitment letter that the vendor plans to offer product support for the supplied equipment, including maintenance of spare parts and technical support team, a minimum of 10 years.

If the vendor is unable to provide such information, Employer may require bidder to select an alternate vendor that can satisfy these requirements.

  - Independent factory quality assurance

For each of the following equipment, the Contractor shall engage a suitably qualified, independent inspector to conduct an initial factory audit. If an existing audit report is available that has been completed for the particular equipment and factory within the six months prior to placing orders, this may be used in place of conducting a new audit for this project.

Equipment covered by this requirement:

- Transformers

- Switchgear

- Cables

The independent inspector shall include:

- Conduct a factory audit:

  - On site

  - Completed at least 2 weeks prior to commencement of production.

  - Any identified non-conformances to be rectified before commencement of production.

  - Audit shall review

    - Standard operating procedures

      - Administrative Policies and Practices.

      - Quality and Reliability Policies and Practices.

      - Facility Logistics and Environment Policies and Practices.

      - Maintenance of certifications.

    - Equipment used in manufacturing

    - Production environment, including material storage and handling

  - A report shall be provided identifying any non-conformances with respect to the approved quality management plan, the vendor’s own procedures (Standard Operating Procedures), and good industry practice.

  - Vendor shall undertake corrective actions with respect to any non-conformances prior to production. These shall be verified by the independent inspector.

  - Witness and Hold Points

The Contractor shall provide all test plans including recommended Hold and Witness points. The Employer shall have the option to review and nominate additional Hold or Witness Points if reasonably required.

The Employer’s presence is required at Witness Points. The Contractor may proceed past the point provided the agreed notice of test (written / e-mail / documented notification) is given and the Employer elects not to be present at the time of the test.

    - Hold Points

Where Hold Points have been identified by the Employer in the Contract Program, no work is to proceed beyond these points prior to the Employer’s inspection, and/or prior to the Employer providing approval. Waiver of the inspection can only be given in writing by the Employer.

  - Inspection and testing

The Employer shall have the option to witness, or appoint a third party to witness, any testing of the transformers, switchgear or cables. At least 10 days’ notice of planned testing shall be provided.

Inspection and testing shall be planned with due consideration for the limitations on site testing, including resources and disruption of the grid. All efforts shall be made to rigorously confirm product quality and performance prior to shipment to site.

    - Factory acceptance tests (FAT)

The Employer shall have the option to witness, or appoint a third party to witness, any testing Major component FAT. At least 10 days’ notice of planned testing shall be provided.

Major components shall be subject to FAT including:

- Transformer

- Switchgear

- Cables

Contractor shall prepare a FAT plan detailing the required tests, test equipment, and test plan. FAT plan should be in accordance with applicable standards and include tests required by the standards.

The FAT shall include pre-energization (cold test) quality control checks including fabrication, installation, connections, electrical safety tests, and subsystem functionality. These shall ensure installation and equipment is as per specification.

The FAT shall include energized (hot) quality control tests to confirm all operational capabilities and to measure equipment performance in accordance with the functional guarantees.

Energized FAT (for Employer witness) shall not proceed until the Contractor has met the following conditions:

- FAT Plan, including detailed ITP has been provided and reviewed.

- No further work is required to complete the build of the equipment, and, excepting packing or other such requirements to make safe the equipment for transport, the equipment is complete and ready for shipment.

- Evidence is submitted to show that all pre-energization checks are completed satisfactorily, and that the equipment is fully capable of energization.

- Evidence is submitted to show that all control programming and bench tests of control systems are complete.

The scope of the FAT shall be sufficient to:

- Comprehensively ensure that the equipment operates as agreed in the Employer Requirements

- Ensure that the equipment operates as intended

- Allow the Employer to observe operation characteristics that may impact integration to the power station

Other components and materials shall be subject to end-of-line testing and factory quality control, and be issued with the associated manufacturer data records. This includes:

- Cables (electrical and fiber)

- Metalwork

- Cabinets and enclosures

- PLCs, control, networking and associated equipment

    - Inspection and test plans

The Contractor shall prepare an Inspection and Test Plans (ITPs) covering all aspects of the works; these shall be submitted to the Employer for review and approval prior to any Inspection and Testing of the works. The Contractor shall carry out inspection and testing in accordance with the best industry practice and manufacturers recommendations.

    - Commissioning Management Plan

The Contractor must provide the Employer with a Commissioning Management Plan as part of its Inspection and Test Plans. The Commissioning Management plan must detail the schedule of ITPs and checklists to be provided and the dates on which they will be provided to the Employer.

The Employer reserves the right to inspect the Works to the extent necessary to satisfy himself that the work conforms to the drawings and specifications and to verify that all the required testing and inspections have been completed to the satisfaction of the Employer and Client Engineers.

The Employer may appoint an Inspection agent to carry out inspection services and to witness and verify tests. The Contractor shall liaise and co-ordinate fully with the Inspector and take all necessary measures to facilitate testing and verification.

The ITPs shall clearly define the objectives, any pre-requisites and pass / fail criteria. The pass criteria shall be correct operation. Any failed test shall be registered as a defect or non-conformance (as applicable) and rectified by the Contractor. On the identification of a failed test the Employer reserves the right to halt all further testing until satisfactory remedies have been implemented and recorded.

The ITP shall be marked up during testing and each test signed as completed by the Contractor and witnessed by the Employer (at its discretion). A copy of the signed off ITP and related test certificates shall be delivered to the Employer in electronic form at the successful completion of the tests.

No testing shall commence before the ITP has been approved by the Employer.

ITPs and checklists are to be signed off progressively as work progresses. ITPs and checklists are required to be submitted to the Employer progressively throughout construction, with test records, completed ITPs and checklists forming part of the verification records for the work and be compiled into the MDR and As-Built documentation.

    - Materials handling

Quality control must include materials handling procedures. This includes procedures for:

- Inspection prior to shipment and on receipt at site

- Transport of equipment, loading and unloading

- Storage requirements

- Tracking of equipment and storage locations

Procedures shall include completion of relevant quality control documentation.

    - Pre-Commissioning Tests

      - General

The Contractor shall carry out Pre-Commissioning Tests on-site following completion of installation of the Plant and prior to completion, in accordance with the Contract. The purpose of the Pre-Commissioning Tests is to confirm that the installation of the Plant is complete and correct, and in a safe condition for livening and operation.

      - Electrical Pre-Commissioning Tests

The Contractor shall pre-commission all of the electrical works.

The Electrical Pre-Commissioning Tests shall include all requisite cold checks, high potential testing, meggering, phasing, insulation resistance, continuity, point to point termination checks, polarity, phase rotation, protection testing (including secondary current injection) and functional operation of all devices and controls.

The Contractor shall provide all suitably calibrated test equipment to perform all pre- commissioning and post livening tests and suitably qualified and experienced personnel to provide the testing.

The Contractor shall provide detailed test sheets for the commissioning of each protection and metering type. The Employer test sheets shall be limited to an overall check sheet encompassing all checks suitable for sign off before livening.

No item of plant shall be livened until clearance is obtained from the Employer, at which time the necessary warning notice in accordance with safety procedures shall be attached to the relevant circuit switch or isolator, and where appropriate, to the plant item itself.

In addition to any testing required under local regulations, the Electrical Pre-Commissioning Tests shall include but not be limited to the following:

      - Visual Inspections

Visual inspections shall include:

- Checking plant for conformity with specifications, free from damage, corrosion or visual defects

- Removal of packing or protective materials from instruments, equipment and devices

- Systems complete “component count”

- Switches, fuses and ancillary equipment correctly labelled and set to appropriate current ratings

- Checking all fasteners, fittings, supports, alignments and clearances

- Checking of all earthing

- Electrical systems certified for compliance with the relevant standards

      - Transformer

Transformers are liable to get damaged during transit and therefore they shall be visually examined. Before commissioning of any transformer, the following points shall be checked for safe energization of the transformer.

- All the accessories have been fixed properly and transformer body and neural are properly earthed.

- The transformer oil dehydration is over and results are satisfactory and approved. In case transformers are idle for more than one month after dehydration, transformer oil has been given at least two circulations.

- The oil level, in the transformer tank and all the bushings is up to the marked point and the oil have been tested for dielectric strength and acidity.

- The pressure relief device is functional with alarm and trip initiation on operation of the device.

- The operation of off-loads tap changers on all the tap positions is satisfactory.

- All the other protective relays, alarm and annunciation relays have been tested.

- Polarity test of transformer winding is correct.

- Phase sequence and connections have been checked for proper vector group.

- The ratio test and winding resistance on all the tap positions is alright.

- Winding and oil temperature thermometer pockets contain oil. That winding and oil temperature settings on dial gauges are functional.

- The simulation tests for all the alarm, annunciation and trip circuits have been checked and are all right.

- The insulation resistance of all the control circuits and IR value of the transformer windings and all the incoming and outgoing cables have been checked with 1000V Megger.

- The setting of all the protective relays is at the desired value and DC Trip supply is available.

- The silica gel is in reactivated condition. The breather pipe is clear from any blocking and contains oil up to the proper level. (As Applicable)

- Buchholz relay has been tested and checked up for any friction in the movement and floats are free. All the other protective relays, alarm and annunciation relays have been tested. (As Applicable)

- All the valves in the cooling system and valve between the buchholz relay and the conservator tank are in open position. (As Applicable).

      - Switchgear

Tests to be carried out on the switchgear shall include, but not be limited to the following:

- High potential tests on busbars, including metal enclosed bus, and switchgear

- Contact resistance measurements of joints in bus and cable connections

- Circuit breaker contact resistance and timing test

- Mechanical tests

- Insulation resistance test

- Point-to-point wiring continuity checks on all low voltage circuits to confirm that the final connections agree with the panel wiring diagrams

- Meggering at the appropriate voltage of all high voltage circuits

- Energizing of all low voltage circuits

- Functional testing of all equipment including interlocks

- Earthing system continuity test

- Injection testing

- Step and touch verification

- Testing of all protection relays and associated circuits by primary and secondary tests.

- Polarity tests, winding resistance, connected burden test, earthing of CTs and VTs.

- Verification of protection relay settings.

- Measurement of CT magnetisation curves.

      - Remote Terminal Units

The RTU shall pass the manufacturer’s standard routine tests in accordance with relevant standards.

- Rigorous testing of each input and output function of the RTUs

- RTU 24/48V DC Power supply redundancy test.

- Verification of AC input without transducers

- Verification of the IED capability

- Verification of the use of the local user interface for maintenance and testing

- Verification of the ability to download parameters and configuration data from the Central Control Station

- Verification that RTU firmware and software support RTU sizing and expansion requirements

- Verification of successful communications

- Verify that Communication errors are detected

- Select-Check back-Before-Operate procedures are properly performed for control outputs

- Verify no erroneous control operation occurs and no incorrect data is generated when power is turned on or off or when operating on low battery voltage

- Testing for secure operation

      - Medium Voltage Cables

All medium voltage cables shall be tested for:

- Visual check

- Insulation resistance test

- Continuity (conductor/screen/sheath)

- Ductor testing of terminations

- DC HV Test

- Correct phasing

- Labelling

- Cable connection / termination bolt tightness test/cable joints

      - Control and Instrument Cables

Control and instrument cables shall be tested for:

- Continuity

- Labelling

- Terminations against schematics

- Removal against schematics

      - Low Voltage Cables

Low Voltage cables shall be tested for:

- Visual check

- Phase identification

- Continuity

- Insulation resistance

- Labelling

- Terminations against schematics

      - Earthing

Conductivity tests of the system and earthing resistance tests shall be performed at points throughout the system before any electrical equipment is energized from the permanent source of power.

The commissioning testing of the earthing system will include performance testing, continuity testing and visual inspection for design compliance. The objectives of the testing will be to:

- Verify the safety performance installed earthing system in accordance with URA Electrical Installation Requirements, IEEE 80 - Guide for Safety in AC Substation Grounding, and other relevant standards codes, guides and legal requirements;

- Establish benchmarks for the earthing system performance for future audits by simulated earth fault current injection tests to determine earth grid voltage rise, step and touch voltages and earthing system impedances; and

- Report on the condition of the earthing systems in terms of compliance with the design, standards and to provide a statement of compliance or non-compliance. The intent of the report is to provide a comprehensive assessment of the condition and performance of the earthing systems and provide sufficient information such that remedial action can be arranged based on the recommendations provided in the report.

The performance testing shall use the off-frequency current injection test to perform the following testing:

- Earth grid voltage rise (EGVR)

- Fault current distribution

- Earthing system and earth grid impedances

- Earth potential rise (EPR) voltage profiles

- Prospective touch and step potentials at relevant locations inside and outside the substation

- Transfer potentials around the substation

Physical inspection of the earthing system shall include inspection of the earthing system to determine condition and compliance to design (conductor size, material, connections).

The Contractor shall carry out electrical continuity measurements on the earthing system, to a specific reference point(s), to determine whether plant equipment is adequately earthed in compliance with design and relevant standards.

      - Fibre Cables

Fiber cables shall be tested for:

- Optical Time Domain Reflectometer (OTDR) Tests, all cores in both directions;

- Insertion loss tests

- Labelling

- Terminations against schematics

      - Protection Equipment

All protection items shall be checked for the necessary protections associated with the protection of cables/ transformers/ and motor generator sets.

Min Op trip checks via secondary injection testing of protection relays as installed at site required.

      - Instrumentation

All instrument items shall be calibrated prior to being brought to site and a calibration certificate shall be provided for each instrument.

Instrumentation shall be tested where applicable for;

- Full loop test using primary signal injection, i.e., temperature, pressure, flow etc.

- Check of the complete measurement/display from instrument to HMI for correct display including value and unit of measure and alarm points

The Contractor shall liaise with the Employer to carry out the above, and provide comprehensive calibration reports and testing check lists for each instrument.

    - Mechanical, Civil and Structural pre-commissioning tests

The Contractor shall pre-commission all of the Mechanical, Civil and Structural works.

The Mechanical, Civil and Structural Pre-Commissioning Tests shall include all requisite checks to ensure that the condition of works is sound and in accordance with the design.

      - Visual Inspections

Visual inspections shall include:

- Site survey to confirm installation at correct location and elevation in accordance with design

- Checking plant for conformity with standards and specifications, including materials, finishes, dimensions, connections, compaction

- Checking all fasteners, fittings, supports, alignments and clearances

- Checking for any evident damage, scratches, discolouration, corrosion, burrs, holes or other such defects

- Checking for any safety risks

- Checking that Plant is accessible and operable, and tasks as set out in the Operations and Maintenance plan can be carried out

- Required operating documentation is available on site

- All spares and tools provided and stored

- Any operating procedures, labels and other signage are in place

- Checking for proper function of drainage and erosion controls

- Any revegetation and permanent erosion control measures are in place.

      - Materials tests

All materials tests, including Manufacturer Data Records and site testing for locally acquired materials, shall be compiled and available.

      - Third party Inspections

The Contractor is required to engage an appropriately qualified third party to inspect and certify compliance of Mechanical, Civil and Structural works with local regulations.

    - Energization

The Inspections and Tests shall be deemed to have been completed when the Contractor has obtained from the Employer written verification that the said Inspections and Tests have been completed and passed in accordance with the Contract and that the Plant is ready for the commencement of the commissioning and livening.

The Contractor shall provide a detailed plan for energization of equipment. This shall be provided in accordance with the network operator’s standard practices, and the following requirements:

- Provided at least two weeks ahead of planned energization

- Planned date, time of commencement

- Expected date, time and duration for any outage

- List of necessary pre-conditions for energisation, including pre-commissioning test results submitted

- Detailed steps and schedule for the livening process, including allocations of responsibilities, necessary checks and confirmations prior to each operation

- Required actions from the network operator

- Contingency plans

- Risk assessment appropriate to the task

Checks during livening shall include operation of all essential services and system communications.

All checks during livening shall be accompanied by the necessary check sheets. Documentation shall be provided in accordance with the network operator’s standard procedures.

    - Hand Over

Following successful livening, and the Works operating as specified, and subject to completion of required training and operations and maintenance documentation, the Contractor may hand-over the Plant for operation to the Employer.

The Contractor shall provide to the Employer signed and dated reproducible copies of Reports, Red Lined As Built Drawings / Schedules and Inspection Test Sheets / Plans clearly showing the extent to which Inspections and Tests have been completed and the result of such inspection and testing. The Contractor must sign supplied check lists.

Handover documentation to include all operator and maintenance training, and higher-level site engineer training on the equipment supplied.

Warranty requirements

In addition to the Contractors obligations during defect liability period (DLP) and extended defects liability period (EDLP), the Contractor is also required to offer to assign all OEM warranties to the Employer. Novation of the warranty shall retain all warranty features available to the Contractor.

OEM warranties should apply for the maximum period offered by the OEM, and shall be a minimum of the following:

- Transformer: 2 years

- Switchgear: 2 years

- Cables: 2 years

- Other equipment: 2 years

## Appendix B – Grid Infrastructure Requirements

1.	Relationship to other parts of the Employer Requirements	201

2.	Scope of Works	201

3.	Equipment - General Technical Requirements	205

4.	Communications Interface	216

5.	Phase 1(Lot 01 and Lot 02) Island Specific Estimated Requirements	217

6.	Phase 2 (Lot 03) Island Specific Estimated Requirements	267

7.	Backup radio link	288

8.	Standards	288

9.	Spare parts	290

10.	Typical SCADA IO list	290

- Relationship to other parts of the Employer Requirements

This part of the Employer Requirements (Attachment B–Grid Infrastructure Requirements), provides key technical requirements for implementation of the project. It shall be read in conjunction with other parts of the Employer’s Requirements.

In particular, note:

- Employer Requirements:

  - This document provides the necessary overview information on the project scope and general requirements. It also includes summary information on the island specific capacities and requirements.

- Appendix A –General Requirements:

  - This document provides general requirements for implementation of the project.

- Appendix C – Drawings

This contains limited drawings and related information on the sites, including maps and single line diagrams. For detailed drawings, bidders are referred to the online data room.

- Appendix D – Environmental and Social Requirements:

  - This document specifies the Code of Practice that the Contractor must comply with.

- Appendix E – Supplementary information:

  - Supplementary information is provided for information only. The supplementary information has not been validated, may contain inaccuracies, and may change without notice. It is included to assist Bidders in evaluating their interest in the project and their proposed approach. The Bidder may not rely on the supplementary information in making their offer. Where supplementary information relates to particulars that may impact on the Bidders offer, the Bidder should make its own enquiries and satisfy itself as to the actual situation.

- Scope of Works

The contractor is required to verify the design and construct Medium Voltage (MV) 11kV network upgrades (including communications backbone) and Low Voltage (LV) 400V upgrades at multiple sites across the islands to facilitate the connection of Solar Farm installations and use of solar energy. There are four types of network modifications required.

- Installation of radial feeder to Solar Farm

- Installation of radial feeder and communications to solar farm and upgrade of associated distribution substation equipment at loop connection point

- Installation of a complete 11kV network, consisting of a switched main MV distribution loop and associated distribution substations and radial feeders to Solar Farms, and communications backbone.

- General grid upgrades (not associated with a specific interconnection):

  - Specified upgrades to the existing 11kV network, such supply and install, or replacement of conductors, substations, switchgear, transformers, boards or communications to modernise infrastructure and provide for capacity for future load growth.

  - Specified upgrades to the existing 400kV network, such replacing conductors and distribution boxes, installing new feeder routes and reconnecting customers to provide for capacity for future load growth.

  - General scope of works

Broadly, the scope of works includes:

    - Assessing the existing network connection point available to the solar installation

- Refer to section 5 below for further details. The assessment report shall determine:

- That the chosen point is suitable for proposed loads and future expected generation injection

- Highlight any constructability issues associated with location

- Highlight alternative configurations to minimise project costs and or optimise the overall system and installation

    - Design the 11kV network modifications.

- Network design and planning:

- Site inspection to micro-site route, conduct soil testing and concealed services survey.

- Confirm selection of 11kV switchgear, 11kV feeder cables and all associated secondary equipment

- Load flow studies, using solar generation and network loads provided by the Employer to confirm voltage profile is within allowable limits within modified regions of the 11kV network.

- Fault level studies to identify fault levels throughout modified regions of the network. Maximum, minimum and projected ultimate fault levels must be considered for all fault and network switching scenarios.

- Earthing studies, where applicable, to establish the earth philosophy of the medium voltage network and provide adequate earth fault detection for safe operation and management of the network.

- Design of suitable feeder protection systems

- Grading of radial feeder protection and main loop protection

- Design a fibre optic backbone for each MV network to facilitate communication between all controllers, MV circuit breakers and switches, protection relays and further IEDs that participate in the power system.

- Design and configure the connection of all communications devices associated with each radial feeder, protection and control, to the Fibre Optic communication backbone.

- Develop and integrate a signal and IO tag database for each site to facilitate interfacing to each island’s power system SCADA.

- Develop a construction procedure for each location to minimise network interruptions during construction and commissioning

- Develop commissioning and test procedure for each modified region of the network.

- Civil works and installation of the Switchgear enclosures/ demountable buildings.

- Supply and install all equipment required to implement the design, as per the scope of work for each island

- Control and auxiliary supply for the 11 kV protection and metering system.

- Trenching and laying of 11 kV Cables

- Installation of earthing system

- Terminate and connect the 11kV feeder cables at each end

- Supply, install and commission fibre optic backbone for power system network communications on each island

- Provide routine test records verifying the results of Factory Acceptance Tests (FAT) for the MV Cables, MV switchgears and MV transformers.

- Commission the feeder ready for service. Commission tests shall include as a minimum:

- IR test of install cables

- CT ratio checks by primary injection

- Protection trip checks by secondary injection, including confirmation of TCC at least three points

- Step and touch potential test for equipment at each end of the radial feeder

- Communications links – confirmation of operation and data transfer rates

As a general concept it is expected that each 11 kV connection into the Main loop will consist of a ground based outdoor ring main unit (RMU) providing two isolators, a feeder circuit breaker, feeder earth switch, protection and control interfaces.

    - Design the 400V network modifications.

- Network design and planning:

- Confirm selection of feeder cable sizing for specified loading (to be provided by Employer) and prepare procurement specifications for cables, distribution boxes, and all associated equipment.

- Protection design for selection of LV fuses, and coordination with MV protection system where applicable.

- Earthing studies, where applicable, to specify earthing requirements for the safe operation and management of the network.

- Develop a construction procedure for each location to minimise network interruptions during construction and commissioning

- Develop commissioning and test procedure for each modified region of the network.

- Supply and install all equipment required to implement the design, as per the scope of work for each island

- Terminate and connect the LV feeder cables at each end

- Commission the feeder ready for service. Commission tests shall include as a minimum:

- IR test of install cables

- Step and touch potential test for equipment at each end of the radial feeder

  - Final cable routes

The Contractor is to use cable routes as per the Employer’s Drawings & Supplementary Information, however, micrositing may be required based on site investigations. Final design cable routes are to be approved by the Employer.

Final design cable routes shall be presented as a comprehensive and accurate GIS data set, freely accessible to the Employer via online viewer (and archive submitted).

Final design cable routes shall minimise road crossings and disturbance of any existing infrastructure. Final design cable routes shall be wholly within roadways or other easements, which will be provided by the Employer.

  - Medium Voltage network upgrade verification

The current specification provides a base case for the proposed 11kV network upgrades. The contractor will undertake, with the local supply authorities, a review workshop of all proposed network upgrades to establish:

- The proposed feeders and sub distribution substations number and location are appropriate for expected future growth, while minimising the upgrade capital expenditure.

- The proposed and existing distributed generation systems, embedded throughout the networks, cannot form unprotected islands following network interruptions.

- The proposed upgrades do not produce single points of failure that would result in more than 20% loss of supply to the distribution customer base for a single contingency failure.

- Identify expected failure modes for the proposed grid.

  - Design Life

The plant primary equipment such as switchgear, transformer and cables should be designed to operate for over 25 years without major repairs or retrofits and all components shall be design for at least this lifetime.

Electronic equipment shall have a minimum design life of 10 years with spares identified and provided.

The plant shall be design with due consideration given for the eventual decommissioning involving completed removal of all components of the plant.

Equipment shall be suitable for operation over its entire design life for the service conditions outlined in appendix A.

  - Equipment Consistency

- The design intent shall be to minimise the different equipment types, manufacturers, component ratings or models and spares.

- Equipment - General Technical Requirements

  - HV Switchgear

All switchgear must be selected to ensure it is reliable, compatible with subsystems and equivalent products, readily serviced, and that spare parts are readily available. To this end, all components must be selected from suppliers continuously servicing utilities in major international markets for a minimum of 10 years.  Products offered must have demonstrated satisfactory performance in operation for at least 3 years, and manufacturers must offer a commitment to support the product (offer spare parts or service as applicable) for a minimum of 10 years.

    - Nominal system values

|  | Parameter | Value |
| --- | --- | --- |
| 1 | Nominal System Voltage | 11kV |
| 2 | Maximum Continuous System Voltage | 12kV |
| 3 | Circuit Breaker Nominal Current (Ir) | TBD (if used) by Contractor |
| 4 | Lighting Impulse Withstand Voltage (Up) | 75 kV |
| 5 | Power Frequency Voltage Withstand (Ud) | 28 kV |
| 6 | System Frequency | 50 Hz |
| 7 | Rated Short Circuit Current | 21 kA |
| 8 | Duration of Short Circuit | 3s |
| 9 | Peak making current (Ip) | 53 kA |
| 10 | Time constant | > 45ms |
| 11 | Bus bar and Isolators Nominal current (Ir) | TBD |

    - RMU Configuration

RMUs shall have the following minimum general configuration:

- Ring switches: 2

- Circuit breakers: 1 or 2 as specified

Enclosure

- IP Rating: IP65

- Rain shield: N/A

- Lifting rings: minimum 2, OEM to confirm suitability

- Colour: to be specified

- Paint: ISO C5 Marine Grade Paint coated enclosures

- Height above ground: Base must be mounted a minimum of 500 mm above the local ground surface to reduce potential for inundation. Provision shall be made for operator access for normal operations and maintenance, without the operator requiring additional access equipment.

Circuit Breakers (if applicable)

- Type: Vacuum

- Rated current: TBD

- Closing (Motor driven charging): Yes

- Spring recharge after closing: Yes

Ring Switches

- Remote operation capability: Yes
Safe operating procedures for closure to be established between Contractor and Grid Operator. Grid Operator shall have authority for remote disconnect if required for system safety or stability (dispatch control to be used preferentially).

Fuse Switches

- Remote operation capability: Yes

- Remote Fuse statues capability: Yes

Earth Switches

- Type: Fault making

- Making capacity: 40 kA peak

- Circuit earth switch interlock: Yes, with associated circuit breaker

- Remote operation capability: Yes

Feeder CTs & VTs

- Contractor to specify

Feeder Protection Relay (if applicable)

- Required

- Functions – as detailed in section ‎3.4 below.

Communications interfaces: Modbus and DNP3

SCADA interface: Modbus and DNP3

Capacitive Voltage Indication

- Required: Yes

- Electrical interlock: Contractor to specify

Surge Arrestor

- Required: Contractor to specify

Auxiliary Power

- Required: Yes

- Auxiliary equipment AC voltage: 400/230 V AC

- Tripping and closing supply voltage: 110 V DC

- Indication supply voltage: 110 V DC

- Spring charge motor voltage: 110 V DC

- Alarm supply voltage: 110 V DC

- Redundant trip coils: Yes

- Redundant trip supplies: Yes

- Load: To be calculated by Contractor

- UPS power: Yes, to comprise of rectifier and battery bank

- Backup duration: Minimum 12 hours without AC supply

- Redundant DC supplies: required

- Small power and lighting to be included.

Metering

- Optional – refer to section 3.2 for general requirements

  - New switchboards

Details for new switchboard are detailed in the relevant sections for individual islands of this appendix.

  - Metering

The contract shall undertake a network metering review to determine if and where check metering should be installed throughout the network.

Check metering maybe via dedicated Power Quality Meters or through secondary IED’s such as protection relays

Check metering may share CT supplies and VT secondary supplies.

    - Power Quality Meters

As a minimum where used, Power Quality Metres shall provide:

- Power Quantities:

- All 3-phase configurations.

- Active power [kW], Reactive power [kVAr], Apparent power [kVA]

- Line – Line Voltage

- Line currents

- Frequency nominal 50Hz system

- Communication and remote read:

- Modbus and DNP3 compatible

- Modbus TCP/IP preferred

- Data logging: Minimum 1 year storage at 30 minute intervals

- Battery backup: Yes

- Display: Configurable

- Complies with:

- EMC: EN 50081-1,2, EN 50082-1,2 Voltage characteristics: EN 50160, EN 61000-2-2, EN 61000-2-12

- Power quality measurement methods: IEC 61000-4-30, Class A

- IEC 62052-11, IEC 62053-21, IEC 62052-22, IEC 62053-23 compliant

  - Transformers

Power Transformers must be selected to ensure they are reliable, compatible with subsystems and equivalent products, readily serviced, and that spare parts are readily available. To this end, transformers must be selected from suppliers continuously servicing utilities in major international markets for a minimum of 10 years. Products offered must have demonstrated satisfactory performance in operation for at least 3 years, and manufacturers must offer a commitment to support the product (offer spare parts or service as applicable) for a minimum of 10 years.

Transformers shall be rated for the environment in which each will operate and shall be provided with protection and monitoring devices such as, but not limited to, pressure relay, oil and winding temperature and oil level.

Transformers will be sized by the tenderer to accommodate the expected full load capacity over the full design output, active and reactive power range. An allowance of a 5% capacity shall be added to the final transformer calculation.

Transformers will be provided with off load tap changers. The number and range of taps shall as a minimum cover +5% to -5% in steps of 2.5%. A wider tap range must be supplied in case determined by the Contractor detail design of the site. Tap position indications will be incorporated with site control system for remote monitoring.

Note: Throughout the specification, two winding transformers have been referred to as indicative of the requirements for the sites. This specification does not prohibit the use of thee winding transformers. Three winding transformers will be considered where load size and or harmonic constraints would suggest a three winding transformer is the cost-effective solution.

Construction Characteristics

- Type: Oil immersed transformer of sealed type construction

- Oil type: Mineral oil

- Primary insulation level: 12 kV

- Primary voltage: 11 kV

- Secondary voltage (no load): 400V

- Impedance: Contractor to specify

- Winding configuration for

- Distribution Transformers: Dyn11 grounded

- Step up Transformer (within Power House): YNd1

- Impulse withstand: 75 kVpeak

- Harmonic K factor: TBD

- Power frequency withstand: 28 kVrms

- Frequency: 50 Hz

- Rating: Contractor to specify

- Cooling: ONAN

- HV connection: Bottom (conduit)

- LV connection: Bottom (conduit)

- IP Rating (Enclosure): 56

- Operating temperature: -4°… + 45 °C without de-ratings

- Altitude: < 1000 m

- Environmental class: E2

- Climate class: C1

- Fire class: F1

- Accessories

- Oil and winding temperature monitoring;

- Pressure relief (monitored);

- Bucholz relays (where a conservator tank is employed);

- Oil level indicator;

- Oil drain valve and filler cap;

- Ratings plate in English

- 4 flat bi-directional rollers

- 2 earthing points

- Anti-vibration pads

  - Environmental Protection

RMU’s, Transformers and associated auxiliary equipment shall be ground mounted and enclosed in a substation shed for protection against the elements. For all new substations contractor will be required to construct Substation shed. Included in Appendix: E, Supplementary Information, includes typical drawings of substation enclosures that the Employer is currently using.

Transformers shall be self bunded, or bunding may be incorporated within the substation shed floor / foundation design. The transformers and switch gears are to be installed minimum 1m raised foundations.

Substation sheds shall provide adequate ventilation and lighting, walkways and access areas will conform to the requirements of AS2067-2016 or IEC 61936-1:2010.  Protective barriers are to be installed where approach distances cannot be maintained.

RMU arc flash exhaust gases to be ducted to external atmosphere through controlled ducting, overhead, rear of floor exits will be permitted. RMU arc flash exhaust points must be kept clear of all personnel, equipment, and other obstructions for a minimum of 3m.

Transformer explosion vents to be ducted to external atmosphere.

  - Protection

RMU’s shall be provided with multifunction protection relays. The back-up protection functions will be provided by the next upstream protection device to the RMU.

Inter-tripping if required may be via dedicated fibre optic link using Modbus TCP/IP and DNP3 protocols or hardwired pilot wires.

Each RMU shall have the following minimum protection functions installed on each circuit breaker:

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

  - Control / Communications interface and Infra structure

All new Medium Voltage network switching equipment shall interface with the Power System SCADA for remote monitoring and control. As a minimum, the following information will be made available to the power system SCADA from each new MW switchgear installation:

- Monitoring

- RMU bus voltages

- Feeder line currents for each feeder

- Feeder kW and kVar

- Open and Close statuses of switching devices, Circuit Breakers, Re-closers, isolator and Earth switches

- Alarms - Cause of trip information and time stamp with a GPS for precise time reference

- Protection relay statuses

- Site communications heartbeat

- Control

- Open / Close commands

- Tap changer raise lower commands, were applicable

- AVR set point commands, were applicable

Refer to Section ‎11 for system communication details.

A locally mounted HMI shall be provided to allow full local control of the RMU and its auxiliaries. The HMI shall be mounted in a suitably weather proof enclosure, remote from the RMU such that the Operator does not need to stand in front of the RMU during local operation of the RMU and its CB’s, isolators and earth switches.

  - Earthing

General earthing shall be according to the section: Standards ‎8 and shall include the following at minimum:

- Transformers and Neutral points;

- Fencing;

- Platforms and handrails and

- Buildings/enclosures.

Particular attention shall be given to:

- Achieving low-resistance connections that are resistant to degradation at all locations where grounding conductors or rods are bonded together

- Achieving the best possible contact with earth

- Verifications through tests that all electrical bonding within the grounding system has been properly affected

The design calculations shall include any area of the PV array exposed to step, touch and transfer potentials induced by earth potential rise, low frequency induction as well as electromagnetic and electric fields for the installation.

The LV/HV transformer earthing design is to use a common LV/HV grid. The design is to take into account:

- The touch voltages limits for any local pipes as specified in the Standards.

- The EPR transferred to the solar power station on an 11 kV earth fault.

  - Electrical cables

All cabling to be procured, as well as the design methodology and considerations, must strictly comply with Sections 3 to 5 of the Utility Regulatory Authority (URA) Installation Standards.

MV cables must be 3C x Cu/XLPE/SCT/PVC/SWA/PVC, 6.35/11kV to British Standard or IEC 60502.

LV cables must be 4C x CU/XLPE/SWA/PVC, 0.6/1kV to British Standard or IEC 60502.

Additionally:

- Cables shall be labelled at both ends, with permanent labels.

- Above ground cabling shall be placed and protected such that DC clamp meters can be used to confirm no current flow for safety isolation purposes. No tools shall be required to allow such cable access. Service loops shall be placed in all cables external to the combiner box to allow re-termination if required.

- All outdoor enclosure cable entries are to be done from the bottom of the enclosure, to prevent water ingress.

- For underground cables, cable markers shall be installed at each change of direction, road crossing, and every 200 m of straight line length. Cable markers should designate the underground service details, depth, and relevant contact details. Cable markers should be selected to last the design life. Cable markers should be sensitive to the location (for example, flush mounted where they would obstruct other activities) and agreed with the Employer.

- Underground cables shall be protected from damage by vermin. A termite-protection layer shall be included in all underground cables. Water blocking shall be included in all 11 kV cables.

  - Fibre optic cables

Fibre optic cables shall be:

- Single mode

- Minimum 12 cores or 50% spare capacity (whichever is greater)

- Certified as suitable for underground direct buried application, including termite protection

Where fibre optic cables pass existing substations (that are not upgraded under this contract), cable loops shall be added to provide sufficient length for future termination. Fibre and fibre loops must be marked for easy location and protected to enable future replacement of the substation.

Fibre optic cables must be separate to MV electrical cables (not part of the MV cable construction).

  - Low voltage distribution panel

Substations with transformers for customer supply shall be fitted with a 400V distribution board, including a main isolation switch, check metering and a minimum of six (6) sub distribution feeder circuits (or as determined during detailed design). Each sub distribution feeder circuit shall be fitted with a circuit breaker with 300 A rating, unless otherwise specified or determined during design.

  - Low voltage distribution box

The electrical distribution boxes will be installed at the locations marked on the relevant LV distribution plans or as determined during detailed design. The distribution boxes shall be designed, manufactured and installed in accordance with the Installation Standards, and the IEC 60364 Electrical Installations for Buildings. The distribution boards will meet the following requirements:

- The distribution board shall be lockable, using the local utility FENEKA’s standard key.

- The distribution board shall be certified to at least IP56.

- The base of the distribution board shall be mounted at least 1 m from finished surface to avoid water damage from flooding.

- The distribution board shall be earthed in accordance with the earthing and fault loop requirements as specified in the Installation Standards and IEC 60364 Electrical Installations for Buildings.

- The feeder cables shall be fitted with permanent mechanical protection.

- The distribution boards shall be clearly and permanently labelled with the board number and circuit number.

- Each distribution board shall be fitted with the following components as shown in Figure ‎3:1.

Figure 3:1: The distribution box wiring diagram

- The distribution boards shall have 12, 18 or 24 circuits as required depending on the location and determined through detailed design.

  - Engineering studies

The MV network design process will produce the following, minimum set, of detail design reports to support the design. Studies shall be undertaken on modified regions of the network only, and as applicable to the modifications.

Employer will provide existing Power Factory steady state models for the islands in Lot01 and Lot02. As part of the required studies, Contractor is to produce or update steady-state power system models for the Works, including all parameters of equipment provided under the Contract.

- Power system studies including but not limited to the following:

  - Short-circuit analysis, minimum and maximum fault levels and locations;

  - Load flow;

  - Insulation co-ordination and lightning mitigation

  - Arc fault levels;

- Protection study that documents:

- All protection devices and schemes;

- Anti-islanding schemes and backups;

- Protection coordination with upstream devices;

- CT and VT sizing calculations.

- Earthing study documenting:

- Reporting site resistivity levels

- Expected EPR contours at each site

- Earthing system design methodology

- Recommend mitigation / grid design

- Cable sizing report documenting:

- Soil thermal and electrical resistivity reports

- HV AC cable Sizing calculations (capacity, volt drop, fault capacity, design assumptions, losses etc.)

- HV Cable trench design parameters

The LV network design process will produce the following, minimum set, of detail design reports to support the design:

- Protection sizing report documenting:

- Selection of fuses at each distribution board (Employer to specify)

- Protection compatibility with upstream devices

- Protection requirements for connection of solar PV into the LV distribution grid.

- Cable sizing report documenting:

- Soil thermal and electrical resistivity reports

- LV AC cable Sizing calculations (capacity, volt drop, fault capacity, design assumptions, losses etc.)

- LV Cable trench design parameters

- Earthing design parameters

The communications infrastructure design process will produce the following, minimum set, of detail design reports (note that LV networks require only installation of communication equipment at the power station, allowing wireless / 4G communications to solar PV plant):

- Communications design report, including:

- Any site investigations or surveys (MV networks only)

- Design of fibre optic cable, terminations, and installation route  (MV networks only)

- Design of communications equipment including FOBOT or other as required to connect the substations and solar PV plant

- Cable trench design parameters (including fibre cable buried with MV) (MV networks only)

- Installation and test specifications.

- Communications Interface

To support centralised grid operation and dispatch control, data from the PV Plants and Distribution Substations, must be available via a router / switch / patch-panel. The communications connection point must include gateway options for fibre optic connection and redundant 3G / 4G connection (PV Plants connected to the LV network do not require optic fibre connection and will use 3G/4G connection only). Communication infrastructure must be installed in a readily accessible panel.

All communications must be capable of Modbus and DNP3 compliance.

All IO modules shall include 25% spare capacity.

Section ‎10 presents a typical medium scale HV IO list. Numbers of IO will vary with chosen site configurations and equipment specifications. The list is provided as indicative of the expected level of data to be transmitted to the SCADA system.

Indicative communications architecture diagram, including remainder of the grid, is shown in Figure ‎4.1: . Scope limits under this contract are as follows:

- Contractor is required to install all fibre optic cable for network communications (per bill of quantities)

- Contractor is required to install all communications required to interconnect the RMUs it installs to the fibre optic network

- Communications infrastructure at solar PV plant is to be provided by others

- Contractor is required to provide termination for fibre optic cable at solar PV plant communications interface, where provided

- Communications infrastructure at the power station, BESS, and centralised SCADA will be provided by others

- Contractor is required to provide termination for fibre optic cable at the power station on each island (communications rack and point of termination to be defined by Employer).

Figure ‎4:1: Intended Communications Architecture (Contractor’s scope in red)

- Phase 1(Lot 01 and Lot 02) Island Specific Estimated Requirements

  - Estimate accuracy

Contractor shall verify or determine all quantities, lengths, sizes, loadings, ratings contained in this section during its design phase.

In the event that the Contractor’s reasonable design identifies a requirement to change from the estimates in this section, then the price adjustment shall be based on the table of unit prices for equipment included in the Contract.

  - Addu city

Administratively, Addu Atoll is the location of Addu City, one of the four cities of the Maldives. Addu City consists of the inhabited areas of Addu Atoll, namely the natural islands of Hulhudhoo, Meedhoo, Maradhoo, Feydhoo, and Hithadhoo. In addition to the areas that are included as a part of Addu City, Addu Atoll has a number of other inhabited and uninhabited islands, including the island of Gan, where Gan International Airport is located.

Addu Atoll comprises and are of 130km2 for the lagoon and 15km2 of land and a population of over 34,000 people.

The interconnected islands of Hithadhoo, Maradhoo, Maradhoo Feydhoo, Feydhoo collectively “Addu-mainland” is connected by one electricity grid while Hulhudhoo and Meedhoo operates on a separate grid.

Figure ‎5:1: Addu Atoll

    - Addu-mainland

      - One (1) MW Floating PV -Maradhoo Harbour Area Lagoon– (#1)

The new Solar PV installation is proposed to be connected to Substation 23, (Figure ‎5:2) which currently comprises a 200kVA transformer, high voltage disconnectors and the low voltage distribution to the consumer loads.

Figure ‎5:2: Grid connection cable route Maradhoo Feydhoo FPV

Power

House

SS 24

SS23

TX

Solar

Farm

The Contractor is responsible for removal of the existing Substation 23 11kV switchgear and the design, supply, install and commission a new 11kV ground mounted RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers. As well as the associated remote monitoring and control equipment, protection system and communication interfaces. Refer Figure ‎5:10: Feeder 3 and 4 Upgrades – contractor’s scope shown in red.

Figure ‎5:3: Maradhoo – substation 23 RMU

Table ‎5.1: 1 MW Floating PV -Maradhoo Harbour Area Lagoon Estimated Cable Requirements

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 160 | 70 |

Table ‎5.2: Maradhoo – substation 23 Feeder details

| Feeder | RMU connection | Nominal Load Amps @11kV | Nominal Load kVA |
| --- | --- | --- | --- |
| Solar PV | Circuit Breaker | 52A | 1000 |
| Existing distribution transformer | Circuit breaker | 10A | 200 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

- Removal and disposal of redundant equipment

- Installation of 11kV RMU and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 11kV underground feeder cable from substation 23 to the new solar field point of connection RMU

- Termination of 11kV underground feeder cable from substation 23 to the new solar field at both ends

- Commissioning of RMU and ancillary equipment

- Commissioning of new solar field 11kV feeder and associated ancillary equipment

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways, landscaping and security fencing

      - Eight (8) MW (indicative) Floating PV - Port Area Lagoon (RAF Area) – (#2)

A new circuit will be run from the existing Power House 11kV switchboard to the Port Area Lagoon (RAF Area) (Figure 5:4). The 11 kV switchboard is to be provided by the Contractor under Section ‎5.2.2.

Figure 5:4 Grid connection cable route RAF area FPV

The Contractor is responsible for the design, installation and commissioning of the new underground feeder from the Power House to the lagoon area. The Contractor will install a new ground mounted 11kV RMU adjacent to the Solar Field point of connection 11kV RMU, with two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers. The Contractor will install underground cables linking the new 11kV RMU to the 8MW Solar Farm POC RMU. Refer Figure ‎5:10: Feeder 3 and 4 Upgrades – contractor’s scope shown in red.

Power

House

Spare

Spare

Solar

Farm

Figure ‎5:5: Port Area Lagoon (RAF Area) RMU

Table ‎5.3: Estimated cable requirements for 8MW Floating PV in the Port Lagoon Area (RAF)

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 600 | 2 x 150 |

Table ‎5.4: RMU for 8MW Floating PV in the Port Lagoon Area (RAF)

| Feeder | RMU connection | Nominal Load Amps @11kV | Nominal Load kVA |
| --- | --- | --- | --- |
| Solar PV | Circuit Breaker | 234A | 9000 |
| Spare | Circuit Breaker | 42A | 800 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design and supply of all required 11kV cable, termination kits, conduits etc. require to complete the works.

- Installation of 600m of underground 11kV cable from Power House to Port Lagoon Area

- Termination of new  11kV cable in Power House 11kV switchboard

- Setting and configuration of new 11kV feeder protection relay in the Power House, settings must co-ordinate upstream and downstream

- Installation of 11kV RMU and ancillary equipment in Port Lagoon Area (RAF) adjacent to Solar Filed point of connection RMU.

- Termination of new  11kV cable to new RMU

- Installation and termination of 11kV cable to link new RMU and Solar Field RMU

- Installation of communication cables and FOBOT boxes

- Commissioning of new 11kV feeder, CB, protection, RMU and ancillary equipment

- Commissioning of new solar field 11kV feeder and associated ancillary equipment

- Make good pathways, landscaping and security fencing

      - 800 kW  Solar PV - Feydhoo Harbour Area– (#3)

The new 800 kW  Solar PV installation, in two parts, is proposed to be connected to the 11kV grid at Substation 41. Currently substation 41 consists of two disconnect switches and a stub bus only. Contractor is responsible for the design, installation and commissioning of the new underground feeder from the SS41 to each solar PV area.

Figure ‎5:6 Grid connection cable route Feydhoo Harbour PV

The Contractor is also responsible for removal of the existing Substation 41 11kV switchgear and the design, supply, install and commission a new 11kV ground mounted RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers. As well as the associated remote monitoring and control equipment, protection system and communication interfaces. Refer Figure ‎5:10: Feeder 3 and 4 Upgrades – Contractor’s scope shown in red.

SS41

Isol Sw

317

Solar Farm1

Solar

Farm2

Figure 5:7: Substation 41 RMU

Table ‎5.5: Estimated cable requirements for 800 kW Solar PV - Feydhoo Harbour Area

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 947 | 70 |
| 141 | 70 |

Table ‎5.6: RMU for 800 kW Solar PV - Feydhoo Harbour Area

| Feeder | RMU connection | Nominal Load Amps @11kV | Nominal Load kVA |
| --- | --- | --- | --- |
| Solar PV1 | Circuit Breaker | 26A | 500 |
| Solar PV1 | Circuit Breaker | 21A | 400 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

- Removal and disposal of redundant equipment

- Installation of 11kV RMU and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 11kV underground feeder cable from substation 41 to the new solar field point of connection RMU

- Termination of 11kV underground feeder cable from substation 41 to the new solar field at both ends

- Commissioning of RMU and ancillary equipment

- Commissioning of new solar field 11kV feeder and associated ancillary equipment

- Make good pathways, landscaping and security fencing

      - 400 kW Solar PV - Feydhoo Harbour Area– (#4)

Figure 5:8 Grid connection cable route Maradhoo Feydhoo PV

The new 400 kW  Solar PV installation is proposed to be connected to the 11kV grid at Substation 26, which currently comprises a 500kVA transformer, high voltage disconnectors and the low voltage distribution to the consumer loads. Contractor is responsible for the design, installation and commissioning of the new underground feeder from the SS26 to the solar PV area. The Contractor is also responsible for removal of the existing Substation 26 11kV switchgear and the design, supply, install and commission a new 11kV ground mounted RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers. As well as the associated remote monitoring and control equipment, protection system and communication interfaces. Refer Figure ‎5:10: Feeder 3 and 4 Upgrades – Contractor’s scope shown in red.

SS25

SS27

SS26 TX

Solar

Farm

Figure ‎5:9: Substation 26 RMU

Table ‎5.7: Estimated cable requirements for 400 kW Solar PV - Feydhoo Harbour Area

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 180 | 70 |

Table ‎5.8: RMU for 400 kW Solar PV - Feydhoo Harbour Area

| Feeder | RMU connection | Nominal Load Amps @11kV | Nominal Load kVA |
| --- | --- | --- | --- |
| Solar PV | Circuit Breaker | 21A | 400 |
| Existing distribution transformer | Circuit Breaker | 26A | 500 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

- Removal and disposal of redundant equipment

- Installation of 11kV RMU and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 11kV underground feeder cable from substation 41 to the new solar field point of connection RMU

- Termination of 11kV underground feeder cable from substation 41 to the new solar field at both ends

- Commissioning of RMU and ancillary equipment

- Commissioning of new solar field 11kV feeder and associated ancillary equipment

- Make good pathways, landscaping and security fencing

Figure ‎5:10: Feeder 3 and 4 Upgrades

      - 0.5 MW Solar PV - Hithadhoo Stadium

The new Solar PV installation is proposed to be connected to Substation 18, which currently comprises a 200kVA transformer, high voltage disconnectors and the low voltage distribution to the consumer loads.

Figure ‎5:11 PV connection cable from solar farm site to SS-18

The Contractor is responsible for removal of the existing Substation 18 11kV switchgear and the design, supply, install and commission a new 11kV ground mounted RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers. As well as the associated remote monitoring and control equipment, protection system and communication interfaces. Refer Figure ‎5:15: Feeder 1 and 2 Upgrades – contractor’s scope shown in red.

SS17

SS 19

SS18

TX

Solar

Farm

Figure ‎5:12: Hithadhoo Stadium – substation 18 RMU

Table ‎5.9: Estimated cable requirements for 0.5 MW Solar PV - Hithadhoo Stadium

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 250 | 70 |

Table ‎5.10: Hithadhoo Stadium – substation 18 Feeder details

| Feeder | RMU connection | Nominal Load Amps @11kV | Nominal Load kVA |
| --- | --- | --- | --- |
| Solar PV | Circuit Breaker | 42A | 800 |
| Existing distribution transformer | Circuit Breaker | 10A | 200 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

- Removal and disposal of redundant equipment

- Installation of 11kV RMU and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 11kV underground feeder cable from substation 18 to the new solar field point of connection RMU

- Termination of 11kV underground feeder cable from substation 18 to the new solar field at both ends

- Commissioning of RMU and ancillary equipment

- Commissioning of new solar field 11kV feeder and associated ancillary equipment

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways, landscaping and security fencing

#### 0.5 MW PV -Hithadoo Harbour Area

The new Solar PV installation is proposed to be connected to Substation 45, which is currently comprises a 300kVA transformer, high voltage disconnectors and the low voltage distribution to the consumer loads. The location of Substation 45 will change from its current location, as shown in Figure ‎5:13.

Figure ‎5:13: Hithadoo Harbour Area – substation 45 relocation

The Contractor is responsible for removal of the existing Substation 45, relocation of the distribution transformer to the new Substation 45 which is to be constructed by the contractor in addition to the design, supply, install and commission a new 11kV ground mounted RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers . As well as the associated remote monitoring and control equipment, protection system and communication interfaces. Contractor is also responsible for all reconnections of 400V feeders and 11kV feeders to the new Substation 45, including additional cable as needed. 11kV feeders shall not be jointed for this purpose. Refer Figure ‎5:15: Feeder 1 and 2 Upgrades – contractor’s scope shown in red.

SS20

Spare

SS45

TX

Solar

Farm

Figure ‎5:14: Hithadoo Harbour Area – substation 45 RMU

Table ‎5.11: Estimated cable requirements for Hithadoo Harbour Area

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 360 | 70 |

Table ‎5.12: Hithadoo Harbour Area – substation 45 Feeder details

| Feeder | RMU connection | Nominal Load Amps @11kV | Nominal Load kVA |
| --- | --- | --- | --- |
| Solar PV | Circuit Breaker | 26A | 500 |
| Existing distribution transformer | Circuit Breaker | 16A | 300 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

- Removal and disposal of redundant equipment

- Installation of 11kV RMU and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 11kV underground feeder cable from substation 45 to the new solar field point of connection RMU

- Termination of 11kV underground feeder cable from substation 45 to the new solar field at both ends

- Commissioning of RMU and ancillary equipment

- Commissioning of new solar field 11kV feeder and associated ancillary equipment

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways, landscaping and security fencing

Figure ‎5:15: Feeder 1 and 2 Upgrades

    - MV grid upgrades

The Contractor is required to undertake upgrades to the existing MV network as listed below.

- Install 5 new substations:

  - Substation numbers: Kohinoor; Stage Area; Hikkinbin; China flat (SS18-2); Fish factory

  - Substation equipment:

    - 800 kVA ONAN Transformer

    - RMU with 2 isolation switches and 2 circuit breakers

    - All associated protection relays, CTs, VTs and metering as required

    - Low voltage distribution board

- Replace existing 11 kV feeder cable (31km) and reconfiguration to add two feeders (9km):

  - Total length: 40,000 m

  - Size:185 mm2

  - Re-terminate 30 substations (including those installed by the Contractor)

- Communications backbone:

  - Install fibre optic communications backbone to all new 11 kV feeder cable routes and substations installed by the Contractor, and the solar PV sites.

Contractor may refer to Supplementary Information on the network layout at Addu-mainland.

      - Contractor responsibilities:

Contractor is responsible for:

- Design verification and optimisation of the proposed network upgrades – refer to section ‎2.3 above.

- Site investigations, surveys and studies required to verify the design and installation plan

- Supply of all required materials and equipment

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

  - Removal and disposal of redundant equipment

  - Installation of 11kV RMU and ancillary equipment

  - Installation of communication cables and FOBOT boxes

  - Design, supply and installation of 11kV underground feeder cable

  - Design, supply and installation of 11kV feeder and transformer protection schemes

  - Termination of 11kV underground feeder cable at existing and new substations

- Commissioning of RMU and ancillary equipment

- Commissioning of 11kV feeder cables and associated ancillary equipment

- Commissioning of fibre optic communications

- Confirmation of full 11kV network operation and protection systems

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

    - Network Outages

The contractor shall program the MV network upgrade works, dismantling, installation and commission to ensure that power interruption to consumers lasts no more than 6 hours per day.

The contractor shall assign a community liaison officer to interface to all impacted customer and ensure minimum disruption during the network upgrade works.

The contractor shall make all arrangements required to provide alternative power to customers during construction and commissioning activities.

    - MV board upgrade Addu Power House

      - Overview

The contractor will design supply and install a new MV distribution switchboard at Addu power station. The 11kV Distribution Switchboard shall consist of:

- 1 unit of 3000A, 12kV Bus Coupler

- 10 units of 630A, 12kV Incoming switchgears

- 5 units of 630A (G1,2,3,5,6) and 5 units of 1,250A (G4,7,B1,2,FS1), 12kV Outgoing switchgears

Figure ‎5:16: Addu MV board

      - Scope of Supply

- This specification covers design, manufacture, shop testing, inspection, packing, delivery to site, erection, testing and commissioning of 11 kV Distribution Panel, fully type tested according to IEC 60298 standards.

- This switchboard shall be complete with all components necessary for its effective and trouble free operation along with associated equipment etc. such components should be deemed to be within the scope of supplier’s supply.

- The design of the switchgear shall be exclusive and specific responsibility of supplier and should be comply with current good engineering practice, the relevant codes and recommendation, the project specific requirements.

- Each breaker shall be withdraw able type VCB, with over current, earth fault and CB fail protection.

- The design of the switchgear shall be based on safety to personnel and equipment during operation and maintenance, reliability of service, ease of maintenance, mechanical protection of equipment, interchangeability of equipment and ready addition of future loads.

      - Switchboard General Requirement:

- Rated Operating voltage: 11 kV

- Maximum operating Voltage : 12kV

- Rated power frequency stand voltage: 28kV

- Rated Frequency : 50Hz

- Rated Busbar current: 3000 A

- Rated Short-time thermal current : 50 kA

- Duration of short-time current: 3 s

- Rated peak withstand current: 130 kA

- Conductor type: Copper

- The panel shall have following features:

  - Factory-assembled, type-tested switchgear according to IEC 62271-200 or VDE 0671-200

  - Shall use standard components available worldwide which meets the relevant international standards.

  - Each section shall be separated with Pressure-resistant partitions. Partition class PM (metal-clad in pressure-resistant design)

  - Quality assurance in accordance with DIN EN ISO 9001.

  - All operations shall be possible only with closed high-voltage door

  - Shall be a Metallic enclosure with earthed shutters and partitions

  - Internal arc classified switchgear according to IAC A FLR; front, lateral and rear accessibility; for all short-circuit currents up to the expected ultimate fault current and an arc duration of 1 s, optionally 0.1 s

  - Unambiguous position indicators and control elements on the high-voltage door

  - Positively driven shutters (separately lockable)

  - Incoming and outgoing feeders shall be evenly arranged on either side of Bus coupler.

  - Cable entry gland plates shall be fixed at the bottom of each feeder panel.

- The individual components and the installation as a whole shall be resistant to corrosion and light industrial pollution, water, ultraviolet radiation, and general wear. No visible signs of corrosion shall be evident for a period of five (5) years.

- All equipment is to be protected from damage by any other agent relevant to the location.

      - Switchboard Main Components

Circuit Breaker

- Motorized 630A Vacuum circuit breaker and earthing Switch with making capacity

- Mechanical tripped on fault indicator

- Auxiliary contacts 1NO and 1NC

- Anti-reflex operating handle

- Shunt Trip circuit for external trip signal

- Mechanical ON/OFF/EARTH Indication

- The Vacuum Circuit breakers should be Maintenance-free and type tested.

Busbars

- Three phase copper busbar of capacity 3000A, 12kV shall be provided. The bus bar shall be integrated in the cubicle, busbars shall be rated to withstand all dynamic and thermal stresses for the full length of the switchgear.

- The busbar shall be air insulated.

- Earthing Switch

- Earthing switches shall be rated equal to the switchgear rating. Earthing switches shall be make-proof and quick make type capable of making Rated Fault Current. Earthing switch shall be operated from the front of the cubicle by means of a removable handle.

Protection and Metering

- The front panel shall display the mimic diagram of the main circuit with the position indicators for the switching devices.

- Multifunction Power Meter shall be fixed on the front door for each feeder cubicle (incoming and outgoing), displaying at least Voltage, Current and Power.

- Incoming Feeders shall have Sync Check, and shall be protected with Self Powered Over Current and Earth Fault Relays.

- Outgoing Feeders shall be protected with Self Powered Over Current Relays, Earth Fault Relays and under frequency protection.

- The position indicators of VCB shall be visible through the front cover and indicating lights shall be wired to auxiliary contact of the VCB to indicate the status of VCB.

- The voltage indicators shall be situated on the front door, one for each module, and indicate the voltage condition of each incoming/outgoing cable. Identification of the phases is achieved with labels L1, L2 and L3 on the front of the voltage indicators. The voltage indicator shall satisfy the requirements of IEC61243.

Cable compartment

- Cable Compartment shall have room to terminate up to a maximum of two single core HV cables per phase. Removable steel covers bolted to the mainframe shall close the cable compartment and access to the compartment shall be by removing these cable covers.

- Each module has a separate cable compartment that is segregated from each other by means of a partition wall. In case of an arc inside the tank.

- A pressure relief valve shall be fitted, such that in case of an arc inside the tank, by opening of the pressure relief the partition wall prevents the hot gases flowing out from the pressure relief to enter the cable compartments.

- The cable terminals shall be suitable for 3C x 70 sq mm XLPE Cable with straight Cable Termination Protectors.

Interlocking

- The interlocking mechanism for the cable switch shall have a built in logical mechanical interlocking system to prevent operation of the switch when the earthing switch is closed, and to prevent operation of the earthing switch when the switch is in the closed position. The mechanism for the T-off switch shall have a built in interlocking system to prevent operation of the switch when the earthing switch is closed, and to prevent operation of the earthing switch when the switch is in the closed position. In addition an interlocking device shall allow access to the fuses only when the earthing switch is in the earthed position and opening of the earthing switch is only possible when the fuse cover is closed and secured.

- The mechanism for the VCB and the disconnector-earthing switch shall be have a built in mechanical interlocking system to prevent operation of the disconnector-earthing switch when the VCB is in the closed position.

Current Transformers

- All current transformers should be comply with IEC 60185. Current transformers should be of dry type, with ratings and ratios as required.

- Shall use standardized block-type current transformers

Auxiliaries.

- The switchgear should be prepared for options like motor operation, auxiliary contacts and short-circuit indicators. Necessary terminal blocks and wiring etc. should be placed behind the front cover of each module.

Testing and Certification

- Units should be type tested in accordance with the Standards ‎8. Type tests certificates for the following tests must be provided

  - Short time and peak withstand current test

  - Temperature rise tests.

  - Dielectric tests.

  - Test of apparatus i.e. circuit breaker and earthing switch

  - Arc fault test

  - Measurement of resistance of main circuit.

  - Mechanical endurance test.

  - Duty cycle test.

  - Internal arc test for HT chamber.

  - Degree of protection for IP2X.

Routine Tests

- Routine tests shall be carried out in accordance with the Standards ‎8. These tests shall be done to ensure the reliability of the unit.

- The following tests shall be performed as routine tests before the delivery of units;

  - Dielectric tests on the main circuits

  - Test of auxiliary and control circuits

  - Measurement of the resistance of the main circuit

  - Withstand voltage at power frequency

  - Withstand voltage on the auxiliary circuits

  - Mechanical tightness tests

  - Operation of functional locks, interlocks, signalling devices and auxiliary devices

  - Suitability and correct operation of protections, control instruments and electrical connections of the circuit breaker operating mechanism

  - Verification of wiring

  - Visual inspection

      - FENAKA role

The Distribution Switchboard will be installed inside the Addu power house at a location nominated by FENAKA.

FENAKA will be responsible for removal of any existing equipment within the power station and its confines.

In addition to Services specified in the DoR matrix in the Employer’s Requirement, FENKA will support the Contractor during installation and connect / reconnect of the Switchboard by providing:

- Inductions, HV and LV switching and access permit as required

- Secondary systems commissioning

  - Addu - Hulhumeedhoo

Hulhumeedhoo is an island located on the north-eastern point of Addu City and it is the 5th largest island in the Maldives. It counts on a resident population of around 4,000 people.

    - 1 MW FPV – Harbour

The Employer is currently reviewing options to connect a 1 MW floating solar PV plant at SS6 or SS9 on Hulhumeedhoo. However, no requirement is made here for the Contractor to undertake this connection at the time of bidding.

    - 1 MW PV - Waste yard

The new Solar PV installation (by others) will include an RMU a new 11kV ground mounted RMU consisting of two (2) 11 kV circuit breakers. The proposed 11 kV network will directly pass this solar PV site. Supply and installation of the new 11 kV network is required of the Contractor under MV Upgrades in 5.3.3. Contractor will be required to connect the solar PV RMU into the 11kV feeder loop as part of this work.

    - MV grid upgrades

The Contractor is responsible for undertaking specified upgrades to the existing network on Hulhumeedhoo:

- Replace transformers at six (6) existing substations:

  - Substation numbers:  (SS1, SS2, SS3, SS4, SS5, SS8)

  - Substation equipment:

Two (2) x 800 kVA ONAN Transformers (SS2, SS1)

Four (4) x 500 kVA ONAN Transformers (SS3, SS4, SS5, SS8)

RMU requirements ( One (1) x 4 way RMU , Five(5) x 3 way RMU)

- Install new substations at three (3) locations:

  - Substation numbers:  (SS9, SS10, SS13)

  - Substation equipment:

Three (3) x 500 kVA ONAN Transformers

Two (2) x RMU with 2 isolation switches and 1 circuit breaker

One (1) x RMU with 2 isolation switches and 2 circuit breaker

Low voltage distribution board

  - SS9 (only) is to be installed at a third party premises (outdoor) and is exempt from the requirements for environmental protection using a shed enclosure. It may be installed in an outdoor installation in a fenced compound (Contractor to supply fencing), with alternate environmental protection meeting the design life requirements.

- Replace existing 11 kV feeder cable (Refer to Appendix C: Drawings for network map and SLDs):

  - Total length: 21,000 m

  - Size:185 mm2

  - Re-terminate substations

- Communications backbone:

  - Install an optic fibre communications backbone to all new 11 kV feeder cable routes and substations, and the solar PV site.

Contractor may refer to Drawings & Supplementary Information for further details on the network layout at Hulhumeedhoo.

Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Supply of all required materials and equipment

- Civil works for the new substations

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

  - Removal and disposal of redundant equipment

  - Installation of 11kV RMU and ancillary equipment

  - Installation of communication cables and FOBOT boxes

  - Design, supply and installation of 11kV underground feeder cable

  - Termination of 11kV underground feeder cable at existing and new substations

- Commissioning of RMU and ancillary equipment

- Commissioning of 11kV feeder cables and associated ancillary equipment

- Commissioning of fibre optic communications

- Confirmation of full 11kV network operation and protections

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

    - Network Outages

The contractor shall program the MV network upgrade works, dismantling, installation and commission to ensure that power interruption to consumers lasts no more than 6 hours per day.

The contractor shall assign a community liaison officer to interface to all impacted customer and ensure minimum disruption during the network upgrade works.

The contractor shall make all arrangements required to provide alternative power to customers during construction and commissioning activities.

    - Existing power station upgrades

The Contractor is required to undertake upgrades to the existing power station switchyard as listed below:

- Disconnect and dispose of the existing two step-up transformers.

- Supply and install two (2) step-up ONAN transformers:

  - Rating: 3,500 kVA

- Assess suitability and identify additional upgrade scope which may be required to accommodate the new transformers. Including but not limited to:

  - HV and LV connection cables

  - Transformer foundation slabs and footings

  - Transformer bund and drain systems

  - Transformer control and monitoring systems

- Secondary equipment, including the Secondary protection systems, CT’s / VTs, HV and LV switchgear and surge arresters, will be supplied and installed by FENAKA and is not part of the Contractor’s scope. However, Contractor is required to complete all connections.

- Design, supply and install all LV and HV equipment required to achieve transformer size upgrade.

- Commission transformers and associated LV and HV equipment

  - Fuvahmulah

The Fuvahmulah city is about 4.5 km by 1.2 km with a submerged reef (Rashikedefaro) extending for about 3 km in a south-easterly direction. The island is the third largest in the Maldives and has a population of over 13,000 people.

Figure ‎5:17 Fuvahmulah Island – Proposed Powerhouse location

FENAKA will be building a Powerhouse on a new site. The new powerhouse scope includes the provision of step-up transformers and 11kV switchgear. A circuit breaker, protection relay and CTs will be made available at the new Powerhouse, by others, for the new Solar Farm feeder.

The Contractor is responsible for the interconnection and commissioning of the Solar Farm feeder.

Table ‎5.13: Fuvahmulah Estimated Cable Requirements

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 850 | 70 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design and supply of all required 11kV cable, termination kits, conduits etc. require to complete the works.

- Installation of 850m of underground 11kV cable from the new Power House to the Solar Farm point of connection RMU

- Termination of new 11kV cable in Power House 11kV switchboard

- Setting and configuration of new 11kV feeder protection relay in the Power House, settings must co-ordinate upstream and downstream

- Installation and termination of 11kV feeder at the Solar Field RMU point of connection

- Installation of communication cables and FOBOT boxes

- Commissioning of new solar field 11kV feeder, CB, protection and associated ancillary equipment

- Make good pathways, landscaping and security fencing

    - Communications

The Contractor is responsible for the design, installation and commissioning of a new underground multimode fibre optic communications link between the new Power House and the Solar Field

The communications works involves:

- Site preparation and traffic control

- Site investigations, surveys and signal strength studies required for the communication path design

- Design of fibre optic cable and installation route

- Supply, installation and commissioning of fibre optic cable, and all associated conduits, cable joints, repeater stations etc. required to complete the fibre optic backbone link.

- Removal and disposal of redundant equipment

- Installation of communication cables and FOBOT boxes

- Termination of fibre optic cables at the new Power House and the Solar Field

- Commissioning of Fibre Optic system

- Make good pathways, landscaping and security fencing

    - MV grid upgrades

There are no general grid upgrades within the scope of works for Fuvahmulah.

  - Thinadhoo

Thinadhoo is about 1.56 km by 0.92 km and has a population of around 8000 people. FENAKA will be carrying out power house upgrade works . An 11kV circuit breaker, protection relay and CTs will be made available at the Powerhouse, by others, for the new Solar Farm feeder.

    - Thinadhoo Solar Fields

The Contractor is responsible for the interconnection and commissioning of the Solar Farm feeder. Refer Figure ‎5:19 Thinadhoo – Solar Field 11kV feeder  – contractor’s scope shown in red.

Figure ‎5:18 Thinadhoo island

Table ‎5.18: Thinadhoo Estimated Cable Requirements

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 620 | 70 |
| 620 | 70 |

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design and supply of all required 11kV cable, termination kits, conduits etc. require to complete the works.

- Installation of 850m of underground 11kV cable from the new Power House to the Solar Farm point of connection RMU

- Termination of new  11kV cable in Power House 11kV switchboard

- Setting and configuration of new 11kV feeder protection relay in the Power House, settings must co-ordinate upstream and downstream

- Installation and termination of 11kV feeder at the Solar Field RMU point of connection

- Installation of communication cables and FOBOT boxes

- Commissioning of new solar field 11kV feeder, CB, protection and associated ancillary equipment

- Make good pathways, landscaping

Figure ‎5:19 Thinadhoo – Solar Field 11kV feeder

    - MV grid upgrades

The Contractor is required to undertake upgrades to the existing MV network as listed below:

- Replace transformers and switch gear in four (4) of the existing substations and construction of 4 new substations with supply and installation of new transformers and switchgears. For details on the locations of respective Substations refer to Appendix C: Drawings.

  - Substation numbers:

Existing: SS10-A, SS10-B, SS-13, SS-14

New: SS-15, SS-16, SS-17, SS-18

  - Substation equipment (for each substation):

800 kVA ONAN Transformer

RMU with 2 isolation switches and 1 circuit breaker

Low voltage distribution board

- Replace existing 11 kV feeder cable (Refer   Appendix C: Drawings for cable route):

  - Total length: 6,500 m (includes approximately 2,750 m new ring main cable, 2,750 m replacement of existing cable and 1,000 m connection to solar farm)

  - Size:185 mm2

  - Terminate / re-terminate substations

- Communications backbone:

  - Install an optic fibre communications backbone to all new 11 kV feeder cable routes and substations, and the solar PV site.

Contractor may refer to Drawings & Supplementary Information on further details of the network layout at Thinadhoo.

      - Contractor responsibilities:

Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Supply of all required materials and equipment

- Civil works for the new substations

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

  - Removal and disposal of redundant equipment

  - Installation of 11kV RMU and ancillary equipment

  - Installation of communication cables and FOBOT boxes

  - Design, supply and installation of 11kV underground feeder cable

  - Termination of 11kV underground feeder cable at existing and new substations

- Commissioning of RMU and ancillary equipment

- Commissioning of 11kV feeder cables and associated ancillary equipment

- Commissioning of fibre optic communications

- Confirmation of full 11kV network operation and protections

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

    - Network Outages

The contractor shall program the MV network upgrade works, dismantling, installation and commission to ensure that power interruption to consumers lasts no more than 6 hours per day.

The contractor shall assign a community liaison officer to interface to all impacted customer and ensure minimum disruption during the network upgrade works.

The contractor shall make all arrangements required to provide alternative power to customers during construction and commissioning activities.

Contractor may refer to Supplementary Information on the network layout at Thinadhoo.

    - Existing power station upgrades

The Contractor is required to undertake upgrades to the existing power station switchyard as listed below:

- Disconnect and dispose of the existing two step-up transformers.

- Supply and install two (2) step-up ONAN transformers:

  - Rating: 3,500 kVA

- Assess suitability and identify additional upgrade scope which may be required to accommodate the new transformers. Including but not limited to:

  - HV and LV connection cables

  - Transformer foundation slabs and footings

  - Transformer bund and drain systems

  - Transformer control and monitoring systems

- Secondary equipment, including the Secondary protection systems, CT’s / VTs, HV and LV switchgear and surge arresters, will be supplied and installed by FENAKA and is not part of the Contractor’s scope. However, Contractor is required to complete all connections.

- Design, supply and install all LV and HV equipment required to achieve transformer size upgrade.

- Commission transformers and associated LV and HV equipment

  - Kulhudhuffushi

Kulhudhuffushi is one of the biggest and most populous islands in the Northern part of the Maldives. The island itself is the administrative capital of the South Thiladhunmathi Atoll and covers an area of 5.2km2 by 2.9km and has a population of over 10,000 people.

Figure ‎5:20: Kulhudhuffushi Island

The existing 11kV network consists of two feeders from the Power House forming a ring main loop around the island.

    - MV grid upgrades

The Contractor is responsible for the following:

- Procurement, trenching, installation of 3 core 185mm2, 11kV cable (estimated length: 16.5km)

- Design, supply, installation and commissioning of two (2) new 11kV substations (to replace existing ones) :

  - SS4: 1 x ground-mounted RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers

  - SS6: 1 x ground-mounted RMU consisting of two (2) 11kV isolation switches and one (1) circuit breaker

  - Additionally, each substation must be equipped with one (1) ONAN 800kVA transformer as well as the associated remote monitoring and control equipment, protection system and communication interfaces.

Figure ‎5:21 Kulhudhuffushi – Proposed System

Contractor may refer to Drawings & Supplementary Information for more details on the network layout at Kulhudhuffushi.

      - Contractor responsibilities:

Additionally, the Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Supply of all required materials and equipment

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

  - Removal and disposal of redundant equipment

  - Installation of 11kV RMU and ancillary equipment

  - Installation of communication cables and FOBOT boxes

  - Design, supply and installation of 11kV underground feeder cable

  - Termination of 11kV underground feeder cable at existing and new substations

- Commissioning of RMU and ancillary equipment

- Commissioning of 11kV feeder cables and associated ancillary equipment

- Commissioning of fibre optic communications

- Confirmation of full 11kV network operation and protections

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

    - Network Outages

The contractor shall program the MV network upgrade works, dismantling, installation and commission to ensure that power interruption to consumers lasts no more than 6 hours per day.

The contractor shall assign a community liaison officer to interface to all impacted customer and ensure minimum disruption during the network upgrade works.

The contractor shall make all arrangements required to provide alternative power to customers during construction and commissioning activities.

Contractor may refer to Supplementary Information on the network layout at Kulhudhufushi.

  - Hinnavaru

Hinnavaru is one of the inhabited islands of Lhaviyani Atoll. The island has a population of around 5000 people and covers an area of 0.53km2 with 1.16km length and 0.58km wide.

The present distribution system is based on an LV network, the Contractor will build an 11kV network and communications infrastructure to support the new solar installation and future load growth on the island.

The MV network will consist of two feeders originating from the existing Power House and forming a loop around the island, refer Figure ‎5:22 Hinnavaru Island

Figure ‎5:22 Hinnavaru Island

The MV network scope of works maybe subdivided as:

- Existing Power House 11kV switchyard

- Island 11kV network

- 11kV sub distribution substations

- Solar PV sites POC to 11kV

    - Existing Power House

The scope of works for the new Power House involves the design, supply, installation and commission of a new 11kV switchyard, 11kV switchboard and control and protection interfaces between the new 11kV switchyard and the existing Power House LV systems.

The new switchyard configuration is shown in Figure ‎5:23 Hinnavaru – new 11kV Switchyard and comprises two 3500 kVA transformers, and 11kV switchboard of 4 feeders, 2 transformer feeders and one bus tie circuit breakers, surge diverters and associated protection, control and ancillary systems. Environmental protection shall be provided by the Contractor.

Each 11kV feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Each 11kV Transformer feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- Bucholtz / Over Pressures

- Oil over temperature

- 46 – Negative sequence over current

- 49 – Thermal overload

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Figure ‎5:23 Hinnavaru – new 11kV Switchyard

- The Existing Power House works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the upgrade design works

- All associated civil works for the switchyard area, including but not limited to:

  - Earth grid construction

  - Transformer foundations and bunding

  - Switchboard foundations

  - Site drainage.

- Design supply and commissioning of the switchyard earth grid

- Design supply and commissioning of the switchyard 11kV systems, switchgear, cables, transformers, ancillary protection and control systems to match proposed future loads and fault levels.

- Installation of 11kV Switchboard with suitable outdoor kiosk and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 400V underground feeder cable from new substation to existing Power house distribution boards.

- Commissioning of 11kV systems and ancillary equipment

- Make good pathways, landscaping and security fencing

    - Island 11kV network

The scope of works for the Island 11kV network includes the design, supply, installation and commission of two 11kV underground feeders originating at the new 11kV switchyard and forming an 11kV loop around the island.

Each RMU will be configured as shown in and Figure ‎5:24 Hinnavaru – substation RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers. As well as the associated remote monitoring and control equipment, protection system and communication interfaces.

Loop

FDR1

Loop

FDR2

SS-xx

TX

Solar

Farm

As applicable

Figure ‎5:24 Hinnavaru – substation RMU

Loop

FDR1

Loop

FDR2

SS-xx

TX

Solar

Farm

As applicable

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design, supply, installation and commissioning of 11kV underground feeder cables for the main loop circuits and associated radial feeders.

- All associated civil works required to install the 11kV network, including but not limited to:

  - Cable trenching

  - Road crossing design supply and construction

  - Drainage system modifications

  - RMU foundations

- Installation of 11kV RMUs and substation ancillary equipment

- Installation of communication cables and FOBOT boxes

- Commissioning of 11kV network, RMUs, substations and ancillary equipment

- Make good pathways, landscaping and security fencing

Estimated distances and cross section cables for the 11kV network are presented in Table ‎5.15: Total Estimated 11kV Cable Requirements for Hinnavaru below:

Table ‎5.15: Total Estimated 11kV Cable Requirements for Hinnavaru

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 2600 | 120 |
| 300 | 70 |

Table ‎5.16: Substations and Required Transformers

| Substation | Rated Power (kVA) |
| --- | --- |
| SS-1 | 500 |
| SS-2 | 500 |
| SS-3 | 800 |
| SS-4 | 800 |
| SS-5 | 800 |

Table ‎5.17: Low voltage distribution panels

| Substation | Main Circuit Breaker @400V | Additional LV Breakers |
| --- | --- | --- |
| SS-1 | 750A | 6 x 250A |
| SS-2 | 750A | 6 x 250A |
| SS-3 | 1200A | 6 x 300A |
| SS-4 | 1200A | 6 x 300A |
| SS-5 | 1200A | 6 x 300A |

details on the network layout at Hinnavaru.

    - 11kV sub distribution substations

The Contractor will design supply and install five new substations to support the LV distribution network. Each substation will consist of an 11/0.4 kV transformer and 400V distribution board fed from the new RMU’s installed as part of the 11kV network works.

Substation transformer sizes are given in Table ‎5.16, the 400V distribution boards shall be fitted with a main isolation switch, check metering and a minimum sub distribution feeder circuits as shown in Table ‎5.17.

The works involves:

- Site preparation and traffic control

- Design, supply, installation and commissioning of 11kV underground feeder cables for the main loop circuits and associated radial feeders.

- All associated civil works required to install the substations (for new substations) including but not limited to:

  - Foundations (To climate proof the infrastructure transformers and switchgear to be installed on 1m level raised foundations)

  - Substation housing (Detailed design provided in Appendix C: Drawings)

  - Fencing

  - Drainage

  - Earthing systems

- Installation of substation transformers, LV distribution boards and substation ancillary equipment

- Installation of communication cables and FOBOT boxes

- Commissioning of 11kV substations and ancillary equipment

- Confirmation of distribution transformer LV voltages and phase rotation

- Make good pathways, landscaping and security fencing

    - Solar PV sites POC to 11kV

There is one  proposed new Solar PV site for Hinnavaru Island, refer to Figure ‎5:22 Hinnavaru Island. The Contractor is responsible for the design, supply and commissioning of interconnecting underground feeders between the Solar Farm POC RMU and the nearest 11kV network substation / connection point. The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design and supply of all required 11kV cable, termination kits, conduits etc. require to complete the works.

- Installation of underground 11kV cable from the nearest connection point / RMU on the new 11kV network to the Solar Farm point of connection RMU

- Termination of the  11kV cables at both ends

- Installation of communication cables and FOBOT boxes

- Commissioning of new solar field 11kV feeders and associated ancillary equipment

- Make good pathways, landscaping and security fencing

    - Communications

The Contractor is responsible for the design, installation and commissioning of a new underground multimode fibre optic communications link between all RMU’s in the network, the existing Power House, the BESS and the new Solar Fields. The fibre network connecting the substations will follow the same route as the MV cable.

The communications works involves:

- Site preparation and traffic control

- Site investigations, surveys and signal strength studies required for the communication path design

- Design of fibre optic cable and installation route

- Supply, installation and commissioning of fibre optic cable, and all associated conduits, cable joints, repeater stations etc. required to complete the fibre optic backbone link.

- Removal and disposal of redundant equipment

- Installation of communication cables and FOBOT boxes

- Termination of fibre optic cables at the new Power House and the Solar Field

- Commissioning of Fibre Optic system

- Make good pathways, landscaping and security fencing

    - 400V LV feeder reconnection

The Contractor will design, supply and install new LV feeder cable sections from the new substations to the first distribution box on selected feeders, and remove the existing LV connection to the powerhouse (or previous distribution box as applicable).

Table ‎5.18: Required reconnection of LV feeders

| Feeder – DB | Connect to | Cable size (mm2) | Cable length (m) |
| --- | --- | --- | --- |
| A2 | SS1 | 95 | 102 |
| B2 | SS1 | 95 | 163 |
| C7 | SS2 | 50 | 57 |
| D6 | SS2 | 120 | 152 |
| F4 | SS2 | 50 | 185 |
| B5 | SS2 | 50 | 60 |
| B8 | SS3 | 50 | 87 |
| A8 | SS3 | 50 | 68 |
| A11 | SS4 | 95 | 116 |
| E6 | SS5 | 70 | 133 |
| F9 | SS5 | 95 | 148 |
| G10 | SS5 | 70 | 159 |
| C1 | PH | N/A | N/A |
| D1 | PH | N/A | N/A |
| E1 | PH | N/A | N/A |
| G1 | PH | N/A | N/A |

The works involves:

- Site preparation and traffic control

- Design, supply, installation and commissioning of 400V feeder cables from the specified substation to the specified distribution box.

- Commissioning of new cables and connected LV feeder

- Make good pathways, landscaping and security fencing

  - Eydhafushi

Eydhafushi is the capital of Baa Atoll. The island is geographically located at the southern edge of Baa Atoll (Southern Maalhosmadulu Atoll or Maalhosmadulu Dhekunuburi). The island has a population of around 3000 people and covers an area of 0.55km2 with 1.22km length and 0.60km wide.

The present distribution system is based on an LV network, the Contractor will build an 11kV network and communications infrastructure to support the new solar installation and future load growth on the island.

The MV network will consist of two feeders originating from the existing Power House and forming a loop around the island, refer Figure ‎5:25 Eydhafushi Island.

The present power system is composed of low voltage circuits only and the Contractor is expected to build the entire 11kV network and communications infrastructure.

Figure ‎5:25 Eydhafushi Island

The MV network scope of works maybe subdivided as:

    - Existing Power House 11kV switchyard

    - Island 11kV network

    - 11kV sub distribution substations

    - Solar PV sites POC to 11kV

    - Existing Power House

The scope of works for the new Power House involves the design, supply, installation and commission of a new 11kV switchyard, 11kV switchboard and control and protection interfaces between the new 11kV switchyard and the existing Power House LV systems.

The new switchyard configuration is shown in  Figure ‎5:26 Eydhafushi – new 11kV Switchyard and comprises two 3500 kVA  transformers, and 11kV switchboard of 4 feeders, 2 transformer feeders and one bus tie circuit breakers, surge diverters and associated protection, control and ancillary systems. Environmental protection shall be provided by the Contractor.

Each 11kV feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Each 11kV Transformer feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- Bucholtz / Over Pressures

- Oil over temperature

- 46 – Negative sequence over current

- 49 – Thermal overload

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Figure ‎5:26 Eydhafushi – new 11kV Switchyard

The Existing Power House works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the upgrade design works

- All associated civil works for the switchyard area, including but not limited to:

  - Earth grid construction

  - Transformer foundations and bunding

  - Switchboard foundations

  - Site drainage.

- Design supply and commissioning of the switchyard earth grid

- Design supply and commissioning of the switchyard 11kV systems, switchgear, cables, transformers, ancillary protection and control systems to match proposed future loads and fault levels.

- Installation of 11kV Switchboard with suitable outdoor kiosk and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 400V underground feeder cable from new substation to existing Power house distribution boards.

- Commissioning of 11kV systems and ancillary equipment

- Make good pathways, landscaping and security fencing

    - Island 11kV network

The scope of works for the Island 11kV network includes the design, supply, installation and commission of two 11kV underground feeders originating at the new 11kV switchyard and forming an 11kV loop around the island.

Each RMU will be configured as shown in and Figure ‎5:27 Eydhafushi – substation RMU consisting of two (2) 11 kV isolation switches and two (2) 11 kV circuit breakers . As well as the associated remote monitoring and control equipment, protection system and communication interfaces.

Figure ‎5:27 Eydhafushi – substation RMU

Loop

FDR1

Loop

FDR2

SS-xx

TX

Solar

Farm

As applicable

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design, supply, installation and commissioning of 11kV underground feeder cables for the main loop circuits and associated radial feeders.

- All associated civil works required to install the 11kV network, including but not limited to:

  - Cable trenching

  - Road crossing design supply and construction

  - Drainage system modifications

  - RMU foundations

- Installation of 11kV RMUs and substation ancillary equipment

- Installation of communication cables and FOBOT boxes

- Commissioning of 11kV network, RMUs, substations and ancillary equipment

- Make good pathways, landscaping and security fencing

Estimated distances and cross section cables for the 11kV network are presented in Table ‎5.19: Total Estimated 11kV Cable Requirements for Eydhafushi below:

Table ‎5.19: Total Estimated 11kV Cable Requirements for Eydhafushi

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 2800 | 120 |
| 600 | 70 |

Table ‎5.20: Distances and Cables Cross Sections

| Section | Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- | --- |
| PV1-SS1 | 250 | 70 |
| PV2-SS2 | 250 | 70 |
| PV3-SS4 | 100 | 70 |
| Powerhouse-SS1 | 500 | 120 |
| SS1-SS2 | 400 | 120 |
| SS2-SS3 | 410 | 120 |
| SS3-SS4 | 340 | 120 |
| SS4-SS5 | 550 | 120 |
| SS5-Powehouse | 600 | 120 |

    - 11kV sub distribution substations

The Contractor will design supply and install five new substations to support the LV distribution network. Each substation will consist of an 11/0.4 kV transformer and 400V distribution board fed from the new RMU’s installed as part of the 11kV network works.

Substation transformer sizes are given in Table ‎5.21: Substations and Required Transformers, the 400V distribution boards shall be fitted with a main isolation switch, check metering and a minimum sub distribution feeder circuits as shown in Table ‎5.22: Low voltage distribution panels.

The works involves:

- Site preparation and traffic control

- Design, supply, installation and commissioning of 11kV underground feeder cables for the main loop circuits and associated radial feeders.

- All associated civil works required to install the substations (for new substations) including but not limited to:

  - Foundations (To climate proof the infrastructure transformers and switchgear to be installed on 1m level raised foundations)

  - Substation housing (Detailed design provided in Appendix: Drawings)

  - Drainage

  - Earthing systems

- Installation of substation transformers, LV distribution boards and substation ancillary equipment

- Installation of communication cables and FOBOT boxes

- Commissioning of 11kV substations and ancillary equipment

- Confirmation of distribution transformer LV voltages and phase rotation

- Make good pathways, landscaping and security fencing

Table ‎5.21: Substations and Required Transformers

| Substation | Rated Power (kVA) |
| --- | --- |
| SS-1 | 800 |
| SS-2 | 800 |
| SS-3 | 800 |
| SS-4 | 800 |
| SS-5 | 800 |

Table ‎5.22: Low voltage distribution panels

| Substation | Main Circuit Breaker @400V | Additional LV Breakers |
| --- | --- | --- |
| SS-1 | 1200A | 6 x 300A |
| SS-2 | 1200A | 6 x 300A |
| SS-3 | 1200A | 6 x 300A |
| SS-4 | 1200A | 6 x 300A |
| SS-5 | 1200A | 6 x 300A |

Contractor may refer to Drawings & Supplementary Information for further details on the network layout at Eydhafushi.

    - Solar PV sites POC to 11kV

There are three proposed new Solar PV sites for Eydhafushi Island, refer to Figure ‎5:25 Eydhafushi Island. The Contractor is responsible for the design, supply and commissioning of interconnecting underground feeders between each Solar Farm POC RMU and the nearest 11kV network substation / connection point.

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design and supply of all required 11kV cable, termination kits, conduits etc. require to complete the works.

- Installation of underground 11kV cable from the nearest connection point / RMU on the new 11kV network to the Solar Farm point of connection RMU

- Termination of the 11kV cables at both ends

- Installation of communication cables and FOBOT boxes

- Commissioning of new solar field 11kV feeders and associated ancillary equipment

- Make good pathways, landscaping and security fencing

    - Communications

The Contractor is responsible for the design, installation and commissioning of a new underground multimode fibre optic communications link between all RMU’s in the network, the existing Power House and the new Solar Fields. The fibre network connecting the substations will follow the same route as the MV cable.

The communications works involves:

- Site preparation and traffic control

- Site investigations, surveys and signal strength studies required for the communication path design

- Design of fibre optic cable and installation route

- Supply, installation and commissioning of fibre optic cable, and all associated conduits, cable joints, repeater stations etc. required to complete the fibre optic backbone link.

- Removal and disposal of redundant equipment

- Installation of communication cables and FOBOT boxes

- Termination of fibre optic cables at the new Power House and the Solar Field

- Commissioning of Fibre Optic system

- Make good pathways, landscaping and security fencing

    - 400V LV feeder reconnection

The Contractor will design, supply and install new LV feeder cable sections from the new substations to the first distribution box on selected feeders, and remove the existing LV connection to the powerhouse (or previous distribution box as applicable).

Table ‎5.23: Required reconnection of LV feeders for Eydafushi

| Feeder – DB | Connect to | Cable size (mm2) | Cable length (m) |
| --- | --- | --- | --- |
| 2-7 | SS1 | 95 | 55 |
| 4-6 | SS1 | 95 | 160 |
| 5-3 | SS2 | 150 | 265 |
| 6-1 | SS2 | 150 | 320 |
| 7-3 | SS2 | 95 | 38 |
| 5-3 | SS3 | 95 | 110 |
| 9-2 | SS3 | 95 | 125 |
| 3-5 | SS5 | 95 | 122 |

The works involves:

- Site preparation and traffic control

- Design, supply, installation and commissioning of 400V feeder cables from the specified substation to the specified distribution box.

- Commissioning of new cables and connected LV feeder

- Make good pathways, landscaping and security fencing

- Phase 2 (Lot 03) Island Specific Estimated Requirements

  - Estimate accuracy

Contractor shall verify or determine all quantities, lengths, sizes, loadings, ratings contained in this section during its design phase.

In the event that the Contractor’s reasonable design identifies a requirement to change from the estimates in this section, then the price adjustment shall be based on the table of unit prices for equipment included in the Contract.

  - Interconnection requirements for solar PV plant

There are no specific interconnection requirements specified for solar PV plant on Phase 2 (Lot 03) islands. Interconnection will be the responsibility of the Solar PV provider, who will connect either to the existing network, or to the general grid upgrades to be provided by the Contractor as described below.

  - Ga. Villigili

No works required.

  - Lh. Naifaru

No works required.

  - L. Fonadhoo

Fonadhoo is the main island in Laamu atoll of the Maldives. It is geographically located towards the south-east of the Laamu Atoll, and has a population of 2,266 and an area of approximately 1.7 km2.

The present distribution system includes two 11 kV radial feeders, one to the north-east of the central power station has two substations and the second, to the south-west of the central power station, has three substations. An LV distribution network with 26 400 V feeders supplies the mainly residential and small business customer loads.

The Contractor is required to modernise the MV network, installing two (2) new transformers and a new main MV board at the power station, installing two new substations, and installation of 11 kV cable to form a ring network, including replacement of existing 11 kV cable.

Specifically, the Contractor is responsible for:

- Supply and install two (2) step-up ONAN transformers at the power station:

  - Rating: 3,500 kVA

- Supply and install a medium voltage panel at the power station:

  - Incoming connections: two (2) from step-up transformers

  - Outgoing connections: four (4), two (2) for the north-east MV ring and two (2) for the south-west MV ring

  - See Section ‎6.5.2 for further information.

- Installation of 2 new substations:

  - Substation numbers: SS4, SS5

  - Substation equipment:

    - Two (2) x 500 kVA ONAN Transformer

    - Two (2) x RMU with 2 isolation switches and 1 circuit breaker

    - Low voltage distribution board

- Replace and duplicate existing 11 kV feeder cable to from ring network:

  - Total length: 4,100 m

  - Size:70 mm2

  - Re-terminate substations

- Route: See Figure ‎6:2

- Communications backbone:

  - Install an optic fibre communications backbone to all new 11 kV feeder cable routes and substations.

- Civil works for the construction of new substation housings

    - Contractor responsibilities:

Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Supply of all required materials and equipment

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 11kV cables, main loop and feeder cables as appropriate

  - Removal and disposal of redundant equipment

  - Installation of 11kV RMU and ancillary equipment

  - Installation of communication cables and FOBOT boxes

  - Design, supply and installation of 11kV underground feeder cable

  - Termination of 11kV underground feeder cable at existing and new substations

- Commissioning of RMU and ancillary equipment

- Commissioning of 11kV feeder cables and associated ancillary equipment

- Commissioning of fibre optic communications

- Confirmation of full 11kV network operation and protections

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

4

2

Figure 6:1: L. Fonadhoo –11kV General upgrades - SLD

Figure ‎6:2 L. Fonadhoo –11kV General upgrades - Map

    - MV Switchyard requirements

Switchboard must include control and protection interfaces between the new 11kV switchyard and the existing Power House LV systems. Each 11kV feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Each 11kV Transformer feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- Bucholtz / Over Pressures

- Oil over temperature

- 46 – Negative sequence over current

- 49 – Thermal overload

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Environmental protection shall be provided by the Contractor.

  - L. Gan

No works required.

  - L. Isdhoo, L. Kalaidhoo and L. Dhabidhoo

L. Isdhoo, L. Kalaidhoo and L. Dhabidhoo are located in the Haddhunmathi Atoll, administrative code Laamu part of Maldives.

Figure 6:3: L. Laamu Atoll

Currently each village operates a low voltage distribution network. Under the project, a medium voltage interconnected network is planned. A New Powerhouse is being procured by FENAKA which will include low voltage distribution panels for the diesel generators and auxiliary systems. The new powerhouse will be built in Kalaidhoo and will service all three islands via an 11kV medium voltage network as shown in Figure ‎6:4. The Contractor is responsible for design, supply and installation of the MV network, except for the 11kV cable from the powerhouse to and including Dhanbidhoo, which will be the responsibility of FENAKA.

Figure 6:4: Isdhoo, Kalaidhoo and Dhabidhoo interconnected 11kV network

Specifically, the Contractor is responsible for:

- Supply and install two (2) step-up ONAN transformers at the power station:

  - Rating: 3,500 kVA

- Supply and install a medium voltage switchgear at the power station with a minimum of:

  - Incoming connections: two (2) from step-up transformers

  - Outgoing connections: eight (8), six for the new RMU’s (and two spare feeders of similar ratings)

  - See also Section ‎6.7.2

- Add six (6) new substations:

  - Distribution Substations SS1, SS2, SS3, SS6:

    - 500 kVA ONAN Transformer

    - RMU with 2 isolation switches and 1 circuit breakers

  - Distribution Substations SS4, SS5,

    - 500 kVA ONAN Transformer

    - RMU with 2 isolation switches and 2 circuit breakers

- install 11 kV feeder cables ring network:

  - Total length: 10.6 km

  - Size:70 mm2

  - Re-terminate substations

  - Route: See Figure ‎6:4

- Communications backbone:

  - Install an optic fibre communications backbone to all new 11 kV feeder cable routes and substations.

      - Contractor responsibilities:

Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Connection of MV feeders at the Powerhouse

- Supply of all required materials and equipment

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Connection of 11kV cables, main loop and feeder cables as appropriate

  - Removal and disposal of redundant equipment

  - Installation of 11kV RMU and ancillary equipment

  - Installation of communication cables and FOBOT boxes

  - Design, supply and installation of 11kV underground feeder cable

  - Termination of 11kV underground feeder cable at existing and new substations

  - Termination of 11kV underground feeder at 2 x solar farm RMUs (on Kalaidhoo and Dhabidhoo) as part of the ring network

- Commissioning of RMU and ancillary equipment

- Commissioning of 11kV feeder cables and associated ancillary equipment

- Commissioning of fibre optic communications

- Confirmation of full 11kV network operation and protections

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

      - FENAKA role

The 11kV cable section from the Powerhouse to SS6 is installed undersea, this section of cable and associated termination points will be designed, supplied, installed and commissioned by FENAKA

MV cable for Dhabidhoo excluded from Contractor’s scope

Figure ‎6:5 - Schematic of the Proposed System and Scope of Supply within the Dashed Line (except MV cable for Dhabidhoo, including undersea link)

    - MV Switchyard requirements

Switchboard must include control and protection interfaces between the new 11kV switchyard and the existing Power House LV systems. Each 11kV feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Each 11kV Transformer feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- Bucholtz / Over Pressures

- Oil over temperature

- 46 – Negative sequence over current

- 49 – Thermal overload

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Environmental protection shall be provided by the Contractor.

  - L. Maabaidhoo

Maabaidhoo is one of the inhabited islands of Laamu Atoll, Medhu-dekunu Province in the Maldives. L. Maabaidhoo is located approximately 300km north of Addu Mainland and has a population of approximately 650 people and an area of approximately 3.86 km2. Kadhdhoo Airport is situated on a nearby island.

The current distribution system includes three Cummins generators supplying a common 400 V busbar. There are at present five (5) low voltage feeders supplying 27 local distribution boxes spaced throughout the residential community.

The three generators and low voltage busbar are to remain, as are the customer connections between customers and the distribution boxes. The contractor is required to modernise the LV network by:

- Removing the existing low voltage buried cables currently supplying the distribution boxes (in cases where no new cable is installed, existing cables may be made safe and left in-ground).

- Supply and install 22 new distribution boxes

- Supply and install new low  voltage buried radial feeders between the existing powerhouse low voltage bus and the 49 distribution boxes (27 existing and 22 new)

- Contractor may refer to Drawings & Supplementary Information for further detailson the network layout for Maabaidhoo.

- Cable lengths are as per Bill of Quantities

Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Connection of LV feeders at the Powerhouse

- Supply of all required materials and equipment

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 400V cables as appropriate

  - Removal and disposal of redundant equipment

  - Design, supply and installation of 400V underground feeder cable

  - Termination of 400V underground feeder cable at existing and new distribution boxes

- Commissioning of 400V feeder cables and associated ancillary equipment

- Testing to ensure earth fault loop impedance comply with relevant standards as per the local Installation Standards, or the earthing requirements as specified in IEC 60364 Electrical Installations for Buildings

- Confirmation of full 400 V network operation and protections

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required

  - L. Maamendhoo

No works required.

  - L. Maavah

No works required.

  - L. Kunahandhoo

L. Kunahandhoo is a small island (0.9 km2) with an average population of around 816 people. The existing powerhouse is located in a populated area and on a side of the island away from most distribution boxes.

Power is distributed through the island by radial low voltage (400V, 3 phase) feeders originating from the existing powerhouse

The current distribution system includes three Cummins generators supplying a common 400 V busbar. There are at present five (5) low voltage feeders supplying 28 local distribution boxes spaced throughout the residential community.

The three generators and low voltage busbar are to remain, as are the customer connections between customers and the distribution boxes. The contractor is required to modernise the LV network by:

- Removing the existing low voltage buried cable supplying existing distribution boxes

- Supply and install 25 new distribution boxes as per the attached plans

- Supply and install new low voltage buried radial feeders between the existing powerhouse low voltage bus and the 53 distribution boxes (28 existing and 25 new)

- Contractor may refer to Drawings & Supplementary Information for further details on the network layout for Maabaidhoo.

- Cable lengths are as per Bill of Quantities

      - Contractor responsibilities:

Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Connection of LV feeders at the Powerhouse

- Supply of all required materials and equipment

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 400V cables as appropriate

  - Removal and disposal of redundant equipment

  - Design, supply and installation of 400V underground feeder cable

  - Termination of 400V underground feeder cable at existing and new distribution boxes

- Commissioning of 400V feeder cables and associated ancillary equipment

- Testing to ensure earth fault loop impedance comply with relevant standards as per the local Installation Standards, or the earthing requirements as specified in IEC 60364 Electrical Installations for Buildings

- Confirmation of full 400 V network operation and protections

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

  - L. Hithadhoo

L.Hithadhoo is a small island of 1.1 km2 with an average population of around 1011 people. The existing powerhouse is on the northern most side of the island near the harbor area.

Presently, power is distributed through the island by radial low voltage (400V, 3 phase) feeders originating from the existing powerhouse

The current distribution system includes four (4) Cummins generators supplying a common 400 V busbar. There are at present five (5) low voltage feeders supplying 46 local distribution boxes spaced throughout the residential community.

The four generators and low voltage busbar are to remain, as are the customer connections between customers and the distribution boxes. The contractor is required to modernise the LV network by:

- Removing the existing low voltage buried cable supplying existing distribution boxes

- Supply and install new low voltage buried cable feeders connected back to the low voltage busbar to existing 46 distribution boards.

- Cable lengths are as per Bill of Quantities

Preliminary map and single line diagram in included in Appendix C, Supplementary data. These are to be finalised during the design stage. Note that additional quantities of cable are included above relative to the information in the Supplementary data to support connection of distributed solar PV to the distribution network.

      - Contractor responsibilities:

Contractor is responsible for:

- Site investigations, surveys and studies required to verify the design and installation plan

- Connection of LV feeders at the Powerhouse

- Supply of all required materials and equipment

- Undertake site preparation and traffic control.

- Full installation and testing including

  - Disconnection and reconnection of the existing 400V cables as appropriate

  - Removal and disposal of redundant equipment

  - Design, supply and installation of 400V underground feeder cable

  - Termination of 400V underground feeder cable at existing and new distribution boxes

- Commissioning of 400V feeder cables and associated ancillary equipment

- Testing to ensure earth fault loop impedance comply with relevant standards as per the local Installation Standards, or the earthing requirements as specified in IEC 60364 Electrical Installations for Buildings

- Confirmation of full 400 V network operation and protections

- Confirm earthing and fault currents

- Confirmation of restoration of distribution transformer LV voltages and phase rotation

- Make good pathways/ roads / routes, landscaping and security fencing as required.

  - Sh. Fundahoo

Funadhoo Island is located on the eastern rim of Miladhummadulhu Atoll and is amongst the largest inhabited islands in Northern Maldives. The nearest island is Farukolhu Island located within the same lagoon about 1,100m to the north. Funadhoo is approximately 3000m long and 585 m at its widest point. The island has a population of around 2000 people.

The present distribution system is based on an LV network, the Contractor will build an 11kV network and communications infrastructure to support the new solar installation and future load growth on the island.

The MV network will consist of two feeders originating from the existing Power House and forming a loop around the island, refer Figure ‎6:6: Funadhoo Island.

Figure ‎6:6: Funadhoo Island

The MV network scope of works maybe subdivided as:

- Existing Power House new 11kV switchyard

- Island 11kV network

- 11kV sub distribution substations

- Solar PV sites POC to 11kV

    - Existing Power House

The scope of works for the Power House involves the design, supply, installation and commission of a new 11kV switchyard, 11kV switchboard and LV and control and protection interfaces between the new 11kV switchyard and the existing Power House LV systems.

The new switchyard configuration is shown in Figure ‎6:7: Funadhoo Power House 11kV Switchyard SLD and comprises two 2500 kVA transformers, and 11kV switchboard of 4 feeders, 2 transformer feeders and one bus tie circuit breakers, surge diverters and associated protection, control and ancillary systems.

Each 11kV feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Each 11kV Transformer feeder Circuit breaker will be provided with an IED communicating to the Fibre Optic network, providing the following functions as a minimum:

- Bucholtz / Over Pressures

- Oil over temperature

- 46 – Negative sequence over current

- 49 – Thermal overload

- 50 – Instantaneous overcurrent;

- 50N – Instantaneous earth fault overcurrent;

- 51 – Time delay overcurrent;

- 51N – Time delay earth fault overcurrent; and

- 50CBF – Circuit breaker fail.

Figure ‎6:7: Funadhoo Power House 11kV Switchyard SLD

- The new 11kV switchyard works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the upgrade design works

- All associated civil works for the switchyard area, including but not limited to:

  - Earth grid construction

  - Transformer foundations and bunding

  - Switchboard foundations

  - Site drainage.

- Design supply and commissioning of the switchyard earth grid

- Design supply and commissioning of the switchyard 11kV systems, switchgear, cables, transformers, ancillary protection and control systems to match proposed future loads and fault levels.

- Design supply installation of 11kV switchgear building to house new switchgear and associated auxiliary systems.

- Installation of 11kV Switchboard and ancillary equipment

- Installation of communication cables and FOBOT boxes

- Design, supply and installation of 400V underground feeder cable from new substation to existing Power house distribution boards.

- Decommissioning of existing 415V feeders and reconfiguration of 415V distribution board.

- Commissioning of modified 415V feeders and 415V distribution board.

- Commissioning of 11kV systems and ancillary equipment

- Make good pathways, landscaping and security fencing

    - Island 11kV network

The scope of works for the Island 11kV network includes the design, supply, installation and commission of two 11kV underground feeders originating at the new 11kV switchyard and forming an 11kV loop around the island. The 11kV loop will provide connection access for the existing load, the proposed solar fields and future growth areas associated with land reclamation projects.

Each RMU will be configured as shown in and Figure ‎6:8: Funadhoo – substation RMU consisting of 2-11kV circuit breakers and 2 – fuse switches. As well as the associated remote monitoring and control equipment, protection system and communication interfaces.

Loop

FDR1

Loop

FDR2

SS-xx

TX

Solar

Farm

As applicable

Figure ‎6:8: Funadhoo – substation RMU

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design, supply, installation and commissioning of 11kV underground feeder cables for the main loop circuits and associated radial feeders.

- All associated civil works required to install the 11kV network, including but not limited to:

  - Cable trenching

  - Road crossing design supply and construction

  - Drainage system modifications

  - RMU foundations

- Installation of 11kV RMUs and substation ancillary equipment

- Installation of communication cables and FOBOT boxes

- Commissioning of 11kV network, RMUs, substations and ancillary equipment

- Make good pathways, landscaping and security fencing

Estimated distances and cross section cables for the 11kV network are presented in Table ‎6.1: Estimated 11kV cable requirements for .

Table ‎6.1: Estimated 11kV cable requirements for Funadhoo

| Distance (m) | Cable Cross Section (mm2)@11kV |
| --- | --- |
| 4000 | 120 |
| 100 | 70 |

Table ‎6.2: Substation Transformer requirements

| Substation | Rated Power (kVA) |
| --- | --- |
| RMU&TX1 | 500 |
| RMU&TX2 | 500 |
| RMU&TX3 | 500 |

Table ‎6.3: Substation 400V distribution panel requirements

| Substation | Main Circuit Breaker @400V | Additional LV Breakers |
| --- | --- | --- |
| RMU&TX1 | 750A | 8 x 100A |
| RMU&TX2 | 750A | 8 x 100A |
| RMU&TX3 | 750A | 8 x 100A |

    - 11kV sub distribution substations

The Contractor will design supply and install five new substations to support the LV distribution network. Each substation will consist of an 11/0.4 kV transformer and 400V distribution board fed from the new RMU’s installed as part of the 11kV network works.

Substation transformer sizes are given in Table ‎6.2: Substation Transformer requirements, the 400V distribution boards shall be fitted with a main isolation switch, check metering and a minimum sub distribution feeder circuits as shown in Table ‎6.3: Substation 400V distribution panel requirements.

The works involves:

- Site preparation and traffic control

- Design, supply, installation and commissioning of 11kV underground feeder cables for the main loop circuits and associated radial feeders.

- All associated civil works required to install the substations including but not limited to:

  - Foundations

  - Fencing

  - Drainage

  - Earthing systems

- Installation of substation transformers, LV distribution boards and substation ancillary equipment

- Installation of communication cables and FOBOT boxes

- Commissioning of 11kV substations and ancillary equipment

- Confirmation of distribution transformer LV voltages and phase rotation

- Disconnection and reconnection of the existing 400V distribution feeders, including design supply and installation of required 415V cables to facilitate re configuration of distribution network. Refer to section

- Make good pathways, landscaping and security fencing

    - Proposed Distribution network re-configuration

The existing 415V distribution system is fed from the Power House via 10 feeders split across two 400V busses. The following redistribution of load, based on physical distance, is proposed.

The contractor is required to review and confirm that the proposed reconfiguration, including impacts on loading, allowance for future island growth areas and voltage control of the proposal are acceptable to the Island Distribution Authority before proceeding with the detailed design.

      - Feeder 1

No changes are proposed for Feeder 1.

      - Feeder 2 & 3

Feeders 2 and 3 are to be shortened. Feeder 2 will be terminated at DB-50, and Feeder 3 will be terminated at DB-73. The remainders of Feeders 2 and 3 will be transferred to RMU & TX3. See Figure ‎6:9: Funadhoo – LV feeders 2 and 3 re-configuration.

Figure ‎6:9: Funadhoo – LV feeders 2 and 3 re-configuration

      - Feeder 4

No changes are proposed for Feeder 4.

      - Feeder 5

No changes are proposed for Feeder 5.

      - Feeder 6

Feeder 6 will be decommissioned from the Power House and its DB load transferred to RMU & TX1, see Figure ‎6:10: Funadhoo – LV feeder 6 re-configuration.

Figure ‎6:10: Funadhoo – LV feeder 6 re-configuration

      - Feeder 7

Feeder 7 will be shortened with loads previously fed from DB3 transferred to the new RMU & TX2, see Figure ‎6:11: Funadhoo – LV feeder 7 re-configuration.

Figure ‎6:11: Funadhoo – LV feeder 7 re-configuration

      - Feeder 8

No changes are proposed for Feeder 8.

      - Feeder 9

No changes are proposed for Feeder 9.

      - Feeder 10

No changes are proposed for Feeder 10.

    - Solar PV sites POC to 11kV

There are two proposed new Solar PV sites for Funadhoo Island. The Contractor is responsible for the design, supply and commissioning of interconnecting underground feeders between each Solar Farm POC RMU and the nearest 11kV network substation / connection point.

The works involves:

- Site preparation and traffic control

- Site investigations and surveys required for the network upgrade design works

- Design and supply of all required 11kV cable, termination kits, conduits etc. require to complete the works.

- Installation of underground 11kV cable from the nearest connection point / RMU on the new 11kV network to the Solar Farm point of connection RMU

- Termination of the  11kV cables at both ends

- Installation of communication cables and FOBOT boxes

- Commissioning of new solar field 11kV feeders and associated ancillary equipment

- Make good pathways, landscaping and security fencing

    - Communications

The Contractor is responsible for the design, installation and commissioning of a new underground multimode fibre optic communications link between all RMU’s in the network, the existing Power House, the BESS and the new Solar Fields. The fibre network connecting the substations will follow the same route as the MV cable.

The communications works involves:

- Site preparation and traffic control

- Site investigations, surveys and signal strength studies required for the communication path design

- Design of fibre optic cable and installation route

- Supply, installation and commissioning of fibre optic cable, and all associated conduits, cable joints, repeater stations etc. required to complete the fibre optic backbone link.

- Removal and disposal of redundant equipment

- Installation of communication cables and FOBOT boxes

- Termination of fibre optic cables at the new Power House and the Solar Field

- Commissioning of Fibre Optic system

- Make good pathways, landscaping and security fencing

- Backup radio link

On each island, Contractor shall provide an alternative communications path from each solar PV plant (where they are connected directly to the MV network) to the power station, that will be utilized in the event of a fault in the fiber optic link. The alternative communications path is expected to utilize an unlicensed frequency radio link or 3G / 4G / 5G public network (subject to confirmation of signal strength and reliability).

At each site, Contractor is expected to design supply, install, and test a radio modem and antenna, along with required mounting, enclosures, etc.

- Standards

All equipment shall be installed and all work shall be carried out in accordance with statutory requirements of the relevant jurisdiction (including amendments). The primary regulatory requirement for electrical installations in the Maldives is the Electrical Installation Standards of the Utilities Regulatory Authority (URA).

The Maldives typically adopts the use of International Electrotechnical Commission (IEC) standards, and International Standards Organisation (ISO) standards. Where there is no requirement under the Electrical Installation Standards, all equipment and works supplied under these specifications shall conform to the latest editions of the IEC or ISO standards, or where no IEC or ISO standards, to British Standard (BS), or equivalent national standards as may be approved by the Employer. Such standards include, but are not limited to:

- IEC 60529: Degree of protection

- IEC 60617: Graphical Symbols for Diagrams

- IEC 61082-1: Preparation of documents used in electrotechnology - Part 1: Rules

- IEC 60076: Power transformers – All parts as applicable

- IEC 62052-11, IEC 62053-21, IEC 62052-22, IEC 62053-23 Electricity metering equipment (AC)

- IEEE80-2000 Guide for Safety in AC Substation Grounding Sponsor Substations Committee of the IEEE Power Engineering Society

- IEEE 81:  IEEE guide for measuring earth resistivity, ground impedance and earth surface potentials of a grounding system

- 1815.1-2015 - IEEE Standard for Exchanging Information Between Networks Implementing IEC 61850 and IEEE Std 1815(TM) [Distributed Network Protocol (DNP3)]

- IEC/TR 60479-5: Effects of current on human beings and livestock – Part 5 touch voltage threshold values for physiological effects

- IEC/BS EN 62305 – Protection against lightning – all parts as applicable

- EN50160 on voltage characteristics of electricity supplied by public distribution systems

- IEEE519 IEEE Recommended Practice and Requirements for Harmonic Control in Electric Power Systems

- IEC 61000: Electromagnetic compatibility (EMC) all parts as applicable

- IEC 61936-1: Power installations exceeding 1 kV a.c. - Part 1: Common rules

- ENA TS 41-26:  UK Energy Network Association Technical Specification for Distribution Switchgear*

- IEC 61869 – Instrument Transformer Series

- IEC 60071-1:2019 - Insulation co-ordination - Part 1: Definitions, principles and rules

- IEC 60071-2:2018 – Part 2 Insulation co-ordination - Part 2: Application guidelines

- IEC 60085: Electrical Insulation – Thermal evaluation and designation

- IEC 60099-4: 3.0 – Surge Arrestors – Part 4: Metal-oxide surge arrestors without gaps for A.C Systems.

- IEC 60099-5: 3.0 Surge Arrestors – Part 5: Selection and application recommendations

- IEC 60137:2017 (ED.7.0): Insulated bushings for alternating voltages above 1000 V

- IEC 60287 series: Electric cables

- IEC 60228: Conductors of insulated cables

- IEC 60502 series: Power cables with extruded insulation and their accessories for rated voltages from 1 kV (Um= 1,2 kV) up to 30 kV (Um= 36 kV) - ALL PARTS

- IEC 62271 series: High-voltage switchgear and control gear

- IEEE 32 Requirements, Terminology, and Test Procedure for Neutral Grounding Devices

- ISO 2178:2016 - Measurement of coating thickness

- ISO 2409:2020 – Paints and varnishes — Cross-cut test

In case the equipment or materials offered from a country where the relevant standards to which the equipment or materials offer better performance or safeguards for the Employer than IEC or BS Specifications, these are acceptable. The Contractor must substantiate any such claims by submitting an independent assessment, by an appropriately qualified person, that identifies differences in the standards and demonstrates the benefit for the Employer.

All listed standards must be complied with unless exception is granted, or noted in these Employer Requirements. If a requirement included in the Employer Requirements exceeds a standard listed, then the requirement within the Employer Requirements shall be adhered to.

Standard(s) referred to shall mean the current Edition / Revision together with Amendments issued.

All installations and materials and cabling shall be in accordance with the IEC 60364 Electrical Installations for Buildings. All works shall conform to the requirements of the URA.

- Spare parts

The Contractor shall supply the following spare parts as minimum:

- 1 termination kit and 1 jointing kit for each cable type on each island

- 1 spare fobot per island

- 1 spare 4-way RMU (2 CBs, 2 isolating switch) per Lot

- 1 reel of fiber optic cable (minimum length 200m) per island

- 3 fiber optic splicing kit per island

- 1 complete set of tools for O&M per island

- 1 complete set of basic consumables required for maintenance per island

In addition, Contractor shall provide a list of recommended spares with list prices that the Employer may elect to purchase.

- Typical SCADA IO list

Type Legend

ANA	Analogue Status Input

STA	Digital Status Input

ALM	Digital Alarm Status

ACO	Analogue Control

DCO	Digital Control

| SOURCE | TYPE | DESCRIPTION | Units | COMMENTS |
| --- | --- | --- | --- | --- |
| CUBICLE/S | ALM | CUBICLE DOOR OPEN ALARM |  | Required for all control cubicle types Including communications and power supply cubicles |
| ETHERNET SWITCH/S | STA | ETHERNET SWITCH ETHERNET SWITCH HEALTHY |  |  |
|  | ALM | ETHERNET SWITCH ETHERNET SWITCH COMMUNICATIONS ERROR |  |  |
| OLM (Optical Link Module) | ALM | OLM OPTICAL LINK MODULE 1 FAULT |  |  |
|  | ALM | OLM OPTICAL LINK MODULE 2 FAULT |  |  |
| HV CB IF APPLICABE | STA | HV CB CIRCUIT BREAKER OPENED STATUS |  |  |
|  | STA | HV CB CIRCUIT BREAKER CLOSED STATUS |  |  |
|  | STA | HV CB EARTH SWITCH OPENED STATUS |  |  |
|  | STA | HV CB EARTH SWITCH CLOSED STATUS |  |  |
|  | DCO | HV CB CIRCUIT BREAKER OPEN COMMAND |  |  |
|  | DCO | HV CB CIRCUIT BREAKER CLOSE COMMAND |  |  |
|  | DCO | HV CB EARTH SWITCH OPEN COMMAND |  | Remote earthing command |
|  | DCO | HV CB EARTH SWITCH CLOSE COMMAND |  | Remote earthing command |
|  | STA | HV CB LOCAL CONTROL SELECTED |  |  |
|  | STA | HV CB REMOTE CONTROL SELECTED |  |  |
| PROTECTION RELAY IF APPLICABE | ANA | PROTECTION RELAY ACTIVE POWER (P) | kW |  |
|  | ANA | PROTECTION RELAY REACTIVE POWER (Q) | kVAR |  |
|  | ANA | PROTECTION RELAY MAX. ACTIVE POWER (MP) | kW |  |
|  | ANA | PROTECTION RELAY MAX. REACTIVE POWER (MQ) | kVAR |  |
|  | ANA | PROTECTION RELAY ACTIVE ENERGY (KWH) | kWh |  |
|  | ANA | PROTECTION RELAY REACTIVE ENERGY (kVARH) | kVARh |  |
|  | ANA | PROTECTION RELAY POWER FACTOR (PF) | - |  |
|  | ANA | PROTECTION RELAY FREQUENCY (HZ) | Hz |  |
|  | ANA | PROTECTION RELAY CURRENT I1 | A |  |
|  | ANA | PROTECTION RELAY CURRENT I2 | A |  |
|  | ANA | PROTECTION RELAY CURRENT I3 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT I1 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT I2 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT I3 | A |  |
|  | ANA | PROTECTION RELAY MAX. CURRENT N | A |  |
|  | ANA | PROTECTION RELAY PHASE-PHASE V1 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-PHASE V2 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-PHASE V3 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-GROUND V1 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-GROUND V2 | kV |  |
|  | ANA | PROTECTION RELAY PHASE-GROUND V3 | kV |  |
|  | STA | PROTECTION RELAY PROTECTION RELAY HEALTHY |  |  |
|  | ALM | PROTECTION RELAY PROTECTION RELAY FAIL |  |  |
|  | ALM | PROTECTION RELAY VT OR MOTOR MCB TRIP |  |  |
|  | ALM | PROTECTION RELAY PROTECTION RELAY TRIP |  |  |
|  | ALM | PROTECTION RELAY PROTECTION RELAY WATCHDOG |  |  |
|  | ALM | PROTECTION RELAY COMMUNICATION FAILURE |  | Derived internally |
|  | ANA | PROTECTION RELAY PANEL BACK SURFACE TEMPERATURE | degC | One required for each switchgear |
|  | ALM | PROTECTION RELAY ANSI CODE 'XX' TRIP ALARM |  | One alarm to be provided for each ANSI protection function |
| HV SW / FUSED SWITCH | STA | HV SW SWITCH OPENED STATUS |  | Required for each item of switchgear |
|  | STA | HV SW SWITCH CLOSED STATUS |  |  |
|  | STA | HV FUSE SW SWITCH RED Φ FUSE STATUS |  |  |
|  | STA | HV FUSE SW SWITCH WHITE Φ FUSE STATUS |  |  |
|  | STA | HV FUSE SW SWITCH BLUE Φ FUSE STATUS |  |  |
|  | STA | HV SW EARTH SWITCH OPENED STATUS |  |  |
|  | STA | HV SW EARTH SWITCH CLOSED STATUS |  |  |
|  | DCO | HV SW SWITCH OPEN COMMAND |  |  |
|  | DCO | HV SW SWITCH CLOSE COMMAND |  |  |
|  | DCO | HV SW EARTH SWITCH OPEN COMMAND |  |  |
|  | DCO | HV SW EARTH SWITCH CLOSE COMMAND |  |  |
|  | STA | HV SW LOCAL CONTROL SELECTED |  |  |
|  | STA | HV SW REMOTE CONTROL SELECTED |  |  |
| BATTERY CHARGER | ALM | BATTERY CHARGER AC SUPPLY FAILED |  |  |
|  | STA | BATTERY CHARGER BATTERY HEALTHY |  |  |
|  | ALM | BATTERY CHARGER CHARGER FAILED |  |  |
|  | STA | BATTERY CHARGER BATTERY VOLTAGE HIGH |  |  |
|  | STA | BATTERY CHARGER BATTERY VOLTAGE LOW |  |  |
|  | ALM | BATTERY CHARGER BATTERY EARTH FAULT |  |  |
|  | STA | BATTERY CHARGER BOOST STATUS |  |  |

## Appendix C - Drawings

## Appendix D - Environmental and Social (ES) requirements

The Employer had undertaken EIA screening for grid upgrading from EPA and Environmental and Social Screening from the World Bank.  The screening decision and environmental and Social Screening Reports (ESSR) are provided in data room developed for the project (link: 20220112-pub-essr-grid-upgrading-works-phase-1-and-2-islands-arise-project.pdf (environment.gov.mv) also provided in bidder data room). As per the screening decision, the Contractor is required to comply with the Environmental and Social Code of Practice (ESCP) for Grid Upgrading Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) Project, included as Appendix D of these Employer Requirements. The ESCP lists several key requirements from the contractor, these are listed below:

- Develop a Code of Conduct for Construction workforce as per the Labour Management Procedure (LMP) (Labour Management Procedures: Accelerating Renewable Energy Integration and Sustainable Energy (ARISE) Project (P172788) (environment.gov.mv) also provided in bidder data room) of the project and submit to review by Employer.

- The Contractor shall follow all the good practices highlighted in Chapter 3 of ESCP.

- The Contractor shall prepare an Occupational Health Safety Management Plan (OHSMP) and submit to approval of Employer as per Chapter 3 of ESCP.

- The Contractor shall undertake environmental and social monitoring and report to the Ministry as per the monitoring plan outlined in Chapter 4 of ESCP.

- The Contractor shall implement requirements of the contractor under the project Grievance Redress Mechanism provided in Annex 7 of ESCP.

- The Contractor shall implement Workers Grievance Redress Mechanism as highlighted in Annex 7 of ESCP.

- The Contractor shall undertake all works as per local environmental and social laws and regulations of Maldives. Summary of applicable laws are provided in Annex 6 of ESCP.

In addition, as per Environmental Social Management Framework (ESMF) (www.environment.gov.mv/v2/wp-content/files/2020/downloads/20200311-pub-environmental-and-social-management-framework-arise-project.pdf also provided in bidder data room) of the project the following are required from the Contractor:

- The Contractor shall update the ESCP, ESSR and prepare OHSMP based on detailed site assessments of the contractor and submit to approval of Employer within 63 days of award.

- The Contractor shall be responsible to ensure all construction material are sourced from approved sites or licensed commercial vendors. All key environmental parameters such as vibration and noise shall not exceed the limitation imposed by the Environmental Protection Agency.

- If the Contractor fails to adhere to the mitigation and monitoring plan to a level acceptable to the Project Engineer, Environmental Social Safeguards Specialist or other monitoring Agencies, the Employer will temporarily suspend the work until such time proper mitigation measures and monitoring are implemented.

- The contractor shall allocate 2.5 percent of the total contract value as Environmental Social Health Safety (ESHS) Performance Security.

- If any of the defects identified by the Project Engineer or Environmental and Social Safeguards Specialist are not remedied by the Contractor within the time given by the Employer, the Employer will consider the Contractor’s work as non-compliance towards environmental and social safeguards and necessary remedial action will be undertaken by the Employer through a third party. Further the cost of the third party and 12% (twelve percent) for supervision charges will be deducted from the Contractors Payment or from the ESHS Performance Security. Any additional cost or time incurred due to above will be at contractor’s expense and will not be subjected to extension of time or claim.

- The Contractor will be responsible for cleaning up and disposing of all waste materials and rehabilitating (landscaping) all construction sites and work areas so that these can be returned as close as possible to their previous use. This includes the stabilization and landscaping of all of the construction sites. Any borrow pits that were operated by the contractor are to be reshaped and closed. Any contaminated soil must be removed from fuel and oil storage areas. All construction debris is to be removed. Payment will be withheld from the contractor until all of the sites are satisfactorily cleaned, all spoils removed and the sites satisfactorily rehabilitated. The final payment will be released only after confirmation by the Project Engineer or Environmental and Social Safeguards Specialist that the above-mentioned tasks have been completed satisfactorily by the Contractor.

- Any legal penalties in relation to environmental and social non-compliance, imposed by any government agency, related to works undertaken by the contractor due to non-compliance of provisions included in the contract should be borne by the contractor.

In addition, the following should be used as guidance by the contractor:

- “Generic Environmental and Social Management Plan (ESMP) for Management of Environmental and Social Impacts During the Construction/Installation of Solar PV and BESS Systems and Grid Infrastructure” provided in Annex 10 of ESMF (link: https://www.environment.gov.mv/v2/en/download/10026).

## Appendix E: Supplementary Information

Refer ARISE Grid-Upgrading Bid Data Room

PART 3 – Conditions of Contract and Contract Forms

Section VIII - General Conditions (GC)

Red Book:

© FIDIC 2017. All rights reserved.

The Conditions of Contract are the “General Conditions” which form part of the “Conditions of Contract for Construction for Building and Engineering Works Designed by the Employer (“Red book”) Second edition 2017” published by the Federation Internationale Des Ingenieurs – Conseils (FIDIC) and the following “Particular Conditions” which comprise of the Bank’s COPA and the amendments and additions to such General Conditions.

An original copy of the above FIDIC publication i.e. “Conditions of Contract for Building and Engineering Works Designed by the Employer” must be obtained from FIDIC.

International Federation of Consulting Engineers (FIDIC)

FIDIC Bookshop – Box- 311 – CH – 1215 Geneva 15 Switzerland

Fax:  +41 22 799 49 054

Telephone:  +41 22 799 49 01

E-mail:  fidic@fidic.org

www.fidic.org

FIDIC code: ISBN13: 978-2-88432-084-9

Section IX - Particular Conditions

The following Particular Conditions shall supplement the General Conditions. Whenever there is a conflict, the provisions herein shall prevail over those in the General Conditions.

Particular Conditions

Part A – Contract Data

| Conditions | Sub-Clause | Data |
| --- | --- | --- |
| Where the Contract allows for Cost Plus Profit, percentage profit to be added to the Cost | 1.1.20 | N/A |
| Employer’s name and address | 1.1.31 | Ministry of Environment, Climate Change and Technology Green Building, Handhuvaree Hingun, Maafannu, Male', Maldives |
| Engineer’s name and address | 1.1.35 | Employer to Assign |
| Bank’s name | 1.1.89 | World Bank & AIIB |
| Borrower’s name | 1.1.90 | Government of the Republic of Maldives |
| Time for Completion | 1.1.84 | Three Hundred & Sixty-Five (365) Days |
| Defects Notification Period | 1.1.27 | Three Hundred & Sixty-Five (365) Days |
| Sections | 1.1.73 | N/A |
| Electronic transmission system | 1.3 (a) (ii) | Electronic Mail |
| Address of Employer for communications: | 1.3(d) | Ministry of Environment, Climate Change and Technology Green Building, Handhuvaree Hingun, Maafannu, Male', 20392, Republic of Maldives arise@environment.gov.mv |
| Address of Engineer for communications: | 1.3(d) | Employer to Assign |
| Address of Contractor for communications: | 1.3(d) | Tenderer to Complete |
| Governing Law | 1.4 | Laws of Republic of Maldives |
| Ruling language | 1.4 | English Language |
| Language for communications | 1.4 | English Language |
| Time for the Parties to sign a Contract Agreement | 1.6 | Within Twenty-Eight (28) Days after receipt of the Letter of Acceptance |
| Number of additional paper copies of Contractor’s Documents | 1.8 | One (01) |
| Total liability of the Contractor to the Employer under or in connection with the Contract | 1.15 | One (1) Time Accepted Contract Amount |
| Site | 1.1.74 | None |
| Time for access to the Site | 2.1 | Twenty-Eight (28) Days from the Notification of Award |
| Engineer’s Duties and Authority | 3.2 | Variations resulting in an increase of the Accepted Contract Amount in excess of 0.05% shall require written consent of the Employer. |
| Performance Security | 4.2 | The Performance Security will be in the form of a Demand Guarantee in the amount(s) of 10% of the Accepted Contract Amount and in the same currency (ies) of the Accepted Contract Amount. |
| Environmental and Social (ES) Performance Security | 4.2 | The ES Performance Security will be in the form of Demand Guarantee in the amount(s) of 2.5% of the Accepted Contract Amount and in the same currency (ies) of the Accepted Contract Amount. |
| Period for notification of errors in the items of reference | 4.7.2 (a) | Twenty-Eight (28) Days |
| Period of payment for temporary utilities | 4.19 | N/A |
| Number of additional paper copies of progress reports | 4.20 | None |
| Maximum allowable accumulated value of work subcontracted | 5.1(a) | Thirty (30) Percent Accepted Contract Amount |
| Parts of the Works for which subcontracting is not permitted | 5.1(b) | None |
| Normal working hours | 6.5 | 8 Hours a Day; 6 Days a Week |
| Number of additional paper copies of program | 8.3 | One (1) |
| Delay damages payable for each day of delay | 8.8 | 0.11% of the Accepted Contract Amount, less provisional sum, for DAAB. |
| Maximum amount of delay damages | 8.8 | 10% of the Accepted Contract Amount less provisional sum for DAAB. |
| Method of measurement | 12.2 | N/A |
| Percentage profit | 12.3 | N/A |
| Percentage rate to be applied to Provisional Sums for overhead charges and profit | 13.4 (b)(ii) | N/A |
| Total advance payment | 14.2 | 10% Percentage of the Accepted Contract Amount payable in the currencies and proportions in which the Accepted Contract Amount is payable |
| Repayment of Advance payment | 14.2.3 | N/A |
| Period of payment | 14.3 | N/A |
| Number of additional paper copies of Statements | 14.3(b) | One (1) |
| Percentage of retention | 14.3(iii) | Five (5) Percent |
| Limit of Retention Money | 14.3(iii) | N/A |
| Plant and Materials | 14.5(b)(i) | Refer Appendix 1 |
|  | 14.5(c)(i) | Refer Appendix 1 |
| Minimum Amount of Interim Payment Certificates | 14.6.2 | N/A |
| Period of payment of Advance Payment to the Contractor | 14.7(a) | Twenty-Eight (28) Days |
| Period for the Employer to make interim payments to the Contractor under Sub-Clause 14.6 (interim Payment) | 14.7b(i) | N/A |
| Period for the Employer to make interim payments to the Contractor under Sub-Clause 14.13 (Final Payment) | 14.7b(ii) | N/A |
| Period for the Employer to make final payment to the Contractor | 14.7(c) | Fifty-Six (56) Days |
| financing charges for delayed payment (percentage points above the average bank short-term lending rate as referred to under sub-paragraph (a)) | 14.8 | 2% above SOFR |
| Number of additional paper copies of draft Final Statement | 14.11.1(b) | One (1) |
| Forces of nature, the risks of which are allocated to the Contractor | 17.2(d) | N/A |
| Permitted deductible limits | 19.1 | insurance required for the Works: 110% of Accepted Contract Amount. insurance required for Goods: 110% of Accepted Contract Amount. insurance required for liability for breach of professional duty: USD 100,000. insurance required against liability for fitness for purpose: USD 100,000. insurance required for injury to persons and damage to property: 10% of Accepted Contract Amount. insurance required for injury to employees: Maldivian Rufiyaa 200,000. per person other insurances required by Laws and by local practice. |
| Additional amount to be insured (as a percentage of the replacement value, if less or more than 15%) | 19.2.1(b) | Twenty (20) percent |
| List of Exceptional Risks which shall not be excluded from the insurance cover for the Works | 19.2.1(iv) | N/A |
| Extent of insurance required for Goods | 19.2.2 | Full replacement value including delivery to Site |
| Amount of insurance required for Goods |  |  |
| amount of insurance required for liability for breach of professional duty | 19.2.3(a) | The amount agreed with the Employer |
| Insurance required against liability for fitness for purpose | 19.2.3(b) | Yes |
| Period of insurance required for liability for breach of professional duty | 19.2.3 | The period agreed with the Employer |
| Amount of insurance required for injury to persons and damage to property | 19.2.4 | The amount agreed with the Employer |
| Time for appointment of DAAB member (s) | 21.1 | Forty-Two (42) Days after signature by both parties of the Contract Agreement |
| The DAAB shall be comprised of | 21.1 | One (1) Member |
| List of proposed members of DAAB | 21.1 | Proposed by Employer: To be Determined Proposed by Contractor: Tenderer to Complete |
| Appointment (if not agreed) to be made by | 21.2 | Federation Internationale des Ingenieurs-Conseil (FIDIC) of Lausanne, Switzerland |
| Rules of arbitration | 21.6(a) | Sub-Clause 21.6(a) of PART B – Special Provisions shall apply. |
|  | 21.6 (b) | Sub-Clause 21.6(b) of PART B – Special Provisions shall not apply. |
| Place of arbitration | 21.6(a) | Singapore |

Part B - Special Provisions

| ### Sub-Clause 1.1.10 Contract |  | “the Contractor’s Proposal” is deleted. |
| --- | --- | --- |
| ### Sub-Clause 1.1.49 Laws |  | The Sub-Clause is replaced with: “Laws” means all national (or state) legislation, statutes, ordinances and other laws, and regulations and by-laws of any legally constituted public authority.” |
| ### Sub-Clause 1.1.74 ### Site |  | The Sub-Clause is replaced with: “Site” means the places where the Permanent Works are to be executed, including storage and working area, and to which Plant and Materials are to be delivered, and any other places specified in the Contract as forming part of the Site.” |
| ### Sub-Clause 1.1.77 ### Statement |  | On the second line after “Payment Certificate under…”, add “Sub-Clause 14.2.1 [Advance Payment Guarantee] (if applicable),”. |
| ### Sub-Clause 1.1.81 ### Tender |  | “the Contractor’s Proposal” is deleted. |
| Sub-Clause 1.1.89 to 1.1.92 are added after Sub-Clause 1.1.88 |  |  |
| Sub-Clause 1.1 89 Bank |  | “Bank” means the financing institution (if any) named in the Contract Data. |
| ### Sub-Clause 1.1.90 ### Borrower |  | “Borrower” means the person (if any) named as the borrower in the Contract Data. |
| ### Sub-Clause 1.1.91 ### ES |  | “ES” means Environmental and Social (including Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH)). |
| ### Sub-Clause 1.1.92 ### Sexual Exploitation and Abuse (SEA), and Sexual Harassment (SH) |  | “Sexual Exploitation and Abuse” “(SEA)” means the following: Sexual Exploitation is defined as any actual or attempted abuse of position of vulnerability, differential power or trust, for sexual purposes, including, but not limited to, profiting monetarily, socially or politically from the sexual exploitation of another. Sexual Abuse is defined as the actual or threatened physical intrusion of a sexual nature, whether by force or under unequal or coercive conditions; and “Sexual Harassment” “(SH)” is defined as unwelcome sexual advances, requests for sexual favors, and other verbal or physical conduct of a sexual nature by the Contractor’s Personnel with other Contractor’s or Employer’s Personnel. |
| ### Sub-Clause 1.2 ### Interpretation |  | Sub-paragraph (a) is replaced with the following: - “Words indicating one gender include all genders; “he/she” is replaced with:” it”; “him/her” is replaced with “it”; “his” and “his/her” are replaced with: “its”; “himself/herself” are replaced with: “itself”.” Further, “and” is deleted from the end of sub-paragraph (i) and added at the end of sub-paragraph (j). sub-paragraph (k) is added: (k) “The word “tender” is synonymous with “bid” or “proposal”, the word tenderer with “bidder” or “proposer” and the words “tender documents” with “request for bids documents” or “request for proposal documents”, as applicable.” |
| ### Sub-Clause 1.5 Priority of Documents |  | The following documents are added in the list of Priority Documents after (e): “(f) the Particular Conditions Part C- Fraud and Corruption; - the Particular Conditions Part D- Environmental and Social (ES) Metrics for Progress Reports; - Particular Conditions- Part E- Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment Performance Declaration for Subcontractors;” and the list renumbered accordingly. |
| ### Sub-Clause 1.6 ### Contract Agreement |  | The last paragraph is replaced with: “If the Contractor comprises a JV, the authorised representative of the JV shall sign the Contract Agreement in accordance with sub –clauses 1.14 (Joint and Several Liability).” |
| ### Sub-Clause 1.12 Confidentiality |  | The following is added at the end of the second paragraph: “The Contractor shall be permitted to disclose information required to establish its qualifications to compete for other projects.” “or” at the end of (b) is deleted. “or” at the end of (c) is added. The following is then added as (d): “is being provided to the Bank .” |
| ### Sub-Clause 1.17 Inspections & Audit by the Bank |  | The following Sub-Clause is added after Sub-Clause 1.16: “Pursuant to paragraph 2.2 e. of Particular Conditions - Part C- Fraud and Corruption, the Contractor shall permit and shall cause its agents (where declared or not), subcontractors, subconsultants, service providers, suppliers, and personnel, to permit, the Bank and/or persons appointed by the Bank to inspect the site and/or the accounts, records and other documents relating to the procurement process, selection and/or contract execution, and to have such accounts, records and other documents audited by auditors appointed by the Bank. The Contractor’s and its Subcontractors’ and subconsultants’ attention is drawn to Sub-Clause 15.8 (Fraud and Corruption) which provides, inter alia, that acts intended to materially impede the exercise of the Bank’s inspection and audit rights constitute a prohibited practice subject to contract termination (as well as to a determination of ineligibility pursuant to the Bank’s prevailing sanctions procedures).” |
| ### Sub-Clause 2.4 Employer’s Financial Arrangements |  | The first paragraph is replaced with: “The Employer shall submit, before the Commencement Date, reasonable evidence that financial arrangements have been made for financing the Employer’s obligations under the Contract.” The following sub-paragraph is added at the end of Sub-Clause 2.4: “In addition, if the Bank has notified to the Borrower that the Bank has suspended disbursements under its loan, which finances in whole or in part the execution of the Works, the Employer shall give notice of such suspension to the Contractor with detailed particulars, including the date of such notification, with a copy to the Engineer, within 7 days of the Borrower having received the suspension notification from the Bank. If alternative funds will be available in appropriate currencies to the Employer to continue making payments to the Contractor beyond a date 60 days after the date of Bank notification of the suspension, the Employer shall provide reasonable evidence in its notice of the extent to which such funds will be available.” |
| ### Sub-Clause 2.6 ### Employer-Supplied Materials and Employer’s Equipment |  | [If Employer- Supplied Materials are listed in the Works’ Requirements for the Contractor’s use in the execution of Works, the following provisions may be added]: The following is added after the last paragraph of Sub-Clause 2.6: “The Employer shall supply to the Contractor the Employer-Supplied Materials listed in the Specification, at the time(s) stated in the Specification (if not stated, within the times that shall be required to enable the Contractor to proceed with execution of the Works in accordance with the Programme). When made available by the Employer, the Contractor shall visually inspect the Employer-Supplied Materials and shall promptly give a Notice to the Engineer of any shortage, defect or default in them. Thereafter, the Contractor shall rectify such shortage, defect or default to the extent instructed by the Engineer. Such instruction shall be deemed to have been given under Sub-Clause 13.3.1 [Variation by Instruction]. After this visual inspection, the Employer-Supplied Materials shall come under the care, custody and control of the Contractor. The Contractor’s obligations of inspection, care, custody, and control shall not relieve the Employer of liability of any shortage, defect or default not apparent from a visual inspection.” [If Employer’s Equipment are listed in the Specification for the Contractor’s use in the execution of Works, the following provisions may be added]: The following is added after the last paragraph of Sub-Clause 2.6: “The Employer shall make the Employer’s Equipment listed in the Specification available to the Contractor at the time(s) stated in the Specification (if not stated, within the times that shall be required to enable the Contractor to proceed with execution of the Works in accordance with the Programme). Unless expressly stated otherwise in the Specification, the Employer’s Equipment shall be provided for the exclusive use of the Contractor. When made available by the Employer, the Contractor shall visually inspect the Employer’s Equipment and shall promptly give a Notice to the Engineer of any shortage, defect or default in them. Thereafter, the Contractor shall rectify such shortage, defect or default to the extent instructed by the Engineer. Such instruction shall be deemed to have been given under Sub-Clause 13.3.1 [Variation by Instruction]. The Contractor shall be responsible for the Employer’s Equipment while it is under the Contractor’s control and/or any of the Contractor’s Personnel is operating it, driving it, directing it, using it, or in control of it. The Contractor shall not remove from the Site any items of the Employer’s Equipment without the consent of the Employer. However, consent shall not be required for vehicles transporting Goods or Contractor’s personnel to or from the Site.” |
| ### Sub-Clause 3.1 ### The Engineer |  | The following is added at the end of the first sub-paragraph: “The Engineer’s staff shall include suitably qualified engineers and other professionals who are competent to carry out these duties.” |
| ### Sub-Clause 3.2 Engineer’s Duties and Authority |  | The Engineer shall obtain the consent in writing of the Employer before taking action under the following Sub-Clauses of these Conditions: - Sub-Clause 13.1: Right to vary - instructing a variation, except; - in an emergency situation as determined by the Engineer; or - (if such a Variation would increase the Accepted Contract Amount by less than the percentage specified in the Contract Data. - Sub-Clause 13.2 (Value Engineering): stating consent or otherwise to a value engineering proposal submitted by the Contractor in accordance with Sub-Clause 13.2. Notwithstanding the obligation, as set out above, to obtain consent in writing, if, in the opinion of the Engineer, an emergency occurs affecting the safety of life or of the Works or of adjoining property, it may, without relieving the Contractor of any of his duties and responsibility under the Contract, instruct the Contractor to execute all such work or to do all such things as may, in the opinion of the Engineer, be necessary to abate or reduce the risk. The Contractor shall forthwith comply, despite the absence of consent of the Employer, with any such instruction of the Engineer. The Engineer shall determine an addition to the Contract Price, in respect of such instruction, and EOT if any, in accordance with Clause 13 and shall notify the Contractor accordingly, with a copy to the Employer. |
| ### Sub-Clause 3.3 Engineer’s Representative |  | The following is added at the end of Sub-Clause 3.3: “The Engineer shall obtain the consent of the Employer before appointing or replacing an Engineer’s Representative.” |
| ### Sub-Clause 3.4 Delegation by the Engineer |  | The following is added at the end of the second paragraph: “If any assistants are not fluent in this language, the Engineer shall make competent interpreters available during all working hours, in a number sufficient for those assistants to properly perform their assigned duties and/or exercise their delegated authority.” |
| ### Sub-Clause 3.6 Replacement of the Engineer |  | In the first paragraph, “42 days” is replaced with: “21 days”; In the third para, “shall” is replaced with: “should”. |
| ### Sub-Clause 4.1 Contractor’s General Obligations |  | The following is inserted after the paragraph “The Contractor shall provide the Plant (and spare parts, if any) …”: “All equipment, material, and services to be incorporated in or required for the Works shall have their origin in any eligible source country as defined by the Bank.” The following is inserted after the paragraph “The Contractor shall, whenever required by the Engineer...”: “The Contractor shall not carry out mobilization to Site (e.g. limited clearance for haul roads, site accesses and work site establishment, geotechnical investigations or investigations to select ancillary features such as quarries and borrow pits) unless the Engineer gives a Notice of No-objection to the Contractor, a Notice that shall not be unreasonably delayed, to the measures the Contractor proposes to manage the environmental and social risks and impacts, which at a minimum shall include applying the Environmental Social Code of Practice (ESCP (APPENDIX ... )) and Code of Conduct for Contractor’s Personnel submitted as part of the Bid and agreed as part of the Contract. The Contractor shall submit, to the Employer for Review any additional ES requirements as are necessary to manage the ES risks and impacts of ongoing Works (e.g. excavation, earth works, bridge and structure works, stream and road diversions, quarrying or extraction of materials, concrete batching and asphalt manufacture). The Contractor shall update the ESCP within 63 days of notification, and submit for review and approval of Employer the ESCP periodically thereafter (but not less than every six (6) months), and update it as required to ensure that it contains measures appropriate to the Works. The ESCP (APPENDIX D) shall be part of the Contractor’s Documents. The procedures for Review of the ESCP (APPENDIX D) and its updates shall be as described in Sub-Clause 4.4.1 [Preparation and Review].” The following is added as (g); (g) and (h) of the Sub-Clause are then renumbered as (h) and (i) respectively.(g) “if so stated in the Specification, the Contractor shall: - design structural elements of the Works taking into account climate change considerations; - apply the concept of universal access (the concept of universal access means unimpeded access for people of all ages and abilities in different situations and under various circumstances; - consider the incremental risks of the public’s potential exposure to operational accidents or natural hazards, including extreme weather events; and - any other requirement stated in the Specification.” The following is added at the end of the Sub-Clause: “The Contractor shall provide relevant contract- related information, as the Employer and/or Engineer may reasonably request to conduct Stakeholder engagements. “Stakeholder” refers to individuals or groups who: - are affected or likely to be affected by the Contract; and - may have an interest in the Contract. The Contractor shall also directly participate in Stakeholder engagements, as the Employer and/or Engineer may reasonably request.” |
| ### Sub-Clause 4.2 Performance Security and ES Performance Security |  | The first paragraph is replaced with: “The Contractor shall obtain (at its cost) a Performance Security for proper performance and, if applicable, an Environmental and Social (ES) Performance Security for compliance with the Contractor’s ES obligations, in the amounts stated in the Contract Data and denominated in the currency(ies) of the Contract or in a freely convertible currency acceptable to the Employer. If amounts are not stated in the Contract Data, this Sub-Clause shall not apply.” In the following Sub-Clauses of the General Conditions, the term “Performance Security” is replaced with: “Performance Security and, if applicable, an Environmental and Social (ES) Performance Security”: 2.1- Right of Access to the Site; 14.2- Advance Payment; 14.6- Issue of IPC; 14.12- Discharge; 14.13- Issue of FPC; 14.14 Cessation of Employer’s Liability; 15.2- Termination for Contractor’s Default; 15.5- Termination for Employer’s Convenience. |
| ### Sub-Clause 4.2.1 ### Contractor’s ### obligations |  | The first paragraph is replaced with: “The Contractor shall deliver the Performance Security and, if applicable, an ES Performance Security to the Employer within 28 days after receiving the Letter of Acceptance and shall send a copy to the Engineer. The Performance Security shall be issued by a reputable bank or financial institution selected by the Contractor and shall be in the form annexed to the Particular Conditions, as stipulated by the Employer in the Contract Data, or in another form approved by the Employer. The ES Performance Security shall be issued by a reputable bank selected by the Contractor and shall be in the form annexed to the Particular Conditions, as stipulated by the Employer in the Contract Data, or in another form approved by the Employer.” Thereafter, throughout Sub-Clause 4.2 “Performance Security” is replaced with: “Performance Security and, if applicable, ES Performance Security.” |
| ### Sub-Clause 4.2.2 Claims under the Performance Security |  | The first paragraph is replaced in its entirety with: “The Employer shall not make a claim under the Performance Security, except for amounts for which the Employer is entitled under the Contract.” |
| ### Sub-Clause 4.2.3 Return of Performance Security |  | In sub-paragraph (a) “21 days” is replaced with: “28 days”. |
| ### Sub-Clause 4.3 Contractor’s Representative |  | The following is added at the end of the last paragraph: “If any of these persons is not fluent in this language, the Contractor shall make competent interpreters available during all working hours in a number deemed sufficient by the Engineer.” |
| ### Sub-Clause 4.6 ### Co-operation |  | On the second-last line of the first paragraph before “Contractor’s”, “of the” is added. The following is added after the first paragraph: “The Contractor shall also, as stated in the Specification or as instructed by the Engineer, cooperate with and allow appropriate opportunities for the Employer’s Personnel to conduct any environmental and social assessment.” |
| ### Sub-Clause 4.7 Setting out |  | In the second bullet-point of sub-paragraph (b) of Sub-Clause 4.7.3: before “if the items of reference”, the following is add: “when examining the items of reference within the period stated in sub-paragraph (a) of Sub-Clause 4.7.2,”. On the second and third lines, the following is deleted “and the contractor’s Notice is given after the period stated in sub-paragraph (a) of Sub-Clause 4.7.2”. |
| ### Sub-Clause 4.8 Health and Safety Obligations |  | The following are included after deleting “and” at the end of (f) and replacing “.” with “;” at the end of (g): “ - provide health and safety toolbox training of Contractor’s Personnel as per the ESCP (Appendix D) and maintain training records; - actively engage the Contractor’s Personnel in promoting understanding, and methods for, implementation of health and safety requirements, as well as in providing information to Contractor’s Personnel, and provision of personal protective equipment without expense to the Contractor’s Personnel; - put in place workplace processes for Contractor’s Personnel to report work situations that they believe are not safe or healthy, and to remove themselves from a work situation which they have reasonable justification to believe presents an imminent and serious danger to their life or health; - Contractor’s Personnel who remove themselves from such work situations shall not be required to return to work until necessary remedial action to correct the situation has been taken. Contractor’s Personnel shall not be retaliated against or otherwise subject to reprisal or negative action for such reporting or removal; - subject to Sub-Clause 4.6, collaborate with the entities and Personnel under paragraph (a) , (b) and (c) of Sub-Clause 4.6, in applying the health and safety requirements. This is without prejudice to the responsibility of the relevant entities for the health and safety of their own personnel; and - establish and implement a system for regular (not less than six-monthly) review of health and safety performance and the working environment.” The second and third paragraphs are replaced with the following: “Subject to Sub-Clause 4.1, within 63 days of award the Contractor shall submit to the Employer for Review an Occupational Health and Safety Management Plan (OHSMP) which has been specifically prepared for the Works, the Site and other places (if any) where the Contractor intends to execute the Works. The procedures for Review of the OHSMP and its updates shall be as described in Sub-Clause 4.4.1 [Preparation and Review]. The OHSMP shall be in addition to any other similar document required under applicable health and safety regulations and Laws. The OHSMP shall set out all the health and safety requirements under the Contract, - which shall include at a minimum: - the procedures to establish and maintain a safe working environment without risk to health at all workplaces, machinery, equipment and processes under the control of the Contractor, including control measures for chemical, physical and biological substances and agents; - details of the training to be provided, records to be kept; - the procedures for prevention, preparedness and response activities to be implemented in the case of an emergency event (i.e. an unanticipated incident, arising from both natural and man-made hazards, typically in the form of fire, explosions, leaks or spills, which may occur for a variety of different reasons including failure to implement operating procedures that are designed to prevent their occurrence, extreme weather or lack of early warning); - the measures to be taken to avoid or minimize the potential for community exposure to water-borne, water-based, water-related, and vector-borne diseases, - the measures to be implemented to avoid or minimize the spread of communicable diseases (including transfer of Sexually Transmitted Diseases or Infections (STDs), such as HIV virus) and non-communicable diseases associated with the execution of the Works, taking into consideration differentiated exposure to and higher sensitivity of vulnerable groups. This includes taking measures to avoid or minimize the transmission of communicable diseases that may be associated with the influx of temporary or permanent Contract-related labour; - the policies and procedures on the management and quality of accommodation and welfare facilities if such accommodation and welfare facilities are provided by the Contractor in accordance with Sub-Clause 6.6; and - any other requirements stated in the Specification. The paragraph starting with: “In addition to the reporting requirement of…” is deleted and replaced with the addition to GC Sub-Clause 4.20 in Sub-Clause 4.20 of the Special Provisions. |
| ### Sub-Clause 4.15 ### Access Route |  | The following is added at the end of Sub-Clause 4.15: “The Contractor shall take all necessary safety measures to avoid the occurrence of incidents and injuries to any third party, associated with the use of, if any, Contractor’s Equipment on public roads or other public infrastructure. The Contractor shall monitor road safety incidents and accidents to identify negative safety issues, and establish and implement necessary measures to resolve them.” |
| ### Sub-Clause 4.18 Protection of the Environment |  | ### Sub-Clause 4.18 Protection of the Environment is replaced with: “The Contractor shall take all necessary measures to: - protect the environment (both on and off the Site); and - limit damage and nuisance to people and property resulting from pollution, noise and other results of the Contractor’s operations and/ or activities. The Contractor shall ensure that emissions, surface discharges, effluent and any other pollutants from the Contractor’s activities shall exceed neither the values indicated in the Specification, nor those prescribed by applicable Laws. In the event of damage to the environment, property and/or nuisance to people, on or off Site as a result of the Contractor’s operations, the Contractor shall agree with the Employer the appropriate actions and time scale to remedy, as practicable, the damaged environment to its former condition. The Contractor shall implement such remedies at its cost to the satisfaction of the Engineer.” |
| ### Sub-Clause 4.20 Progress Reports |  | Replace “4.20 (g) with: “the Environmental and Social (ES) metrics set out in Particular Conditions - Part D” The following is added at the end of the Sub-Clause: “In addition to the reporting requirement of this sub-paragraph (g) of Sub-Clause 4.20 [Progress Reports] the Contractor shall inform the Employer immediately of any allegation, incident or accident, which has or is likely to have a significant adverse effect on the environment, the affected communities, the public, Employer’s Personnel or Contractor’s Personnel. This includes, but is not limited to, any incident or accident causing fatality or serious injury; significant adverse effects or damage to private property; or any allegation of SEA and/or SH. In case of SEA and/or SH, while maintaining confidentiality as appropriate, the type of allegation (sexual exploitation, sexual abuse or sexual harassment), gender and age of the person who experienced the alleged incident should be included in the information. The Contractor, upon becoming aware of the allegation, incident or accident, shall also immediately inform the Employer of any such incident or accident on the Subcontractors’ or suppliers’ premises relating to the Works which has or is likely to have a significant adverse effect on the environment, the affected communities, the public, Employer’s Personnel or Contractor’s, its Subcontractors’ and suppliers’ personnel. The notification shall provide sufficient detail regarding such incidents or accidents. The Contractor shall provide full details of such incidents or accidents to the Employer within the timeframe agreed with the Employer. The Contractor shall require its Subcontractors and suppliers (other than Subcontractors) to immediately notify the Contractor of any incidents or accidents referred to in this Subclause.” |
| ### Sub-Clause 4.21 Security of the Site |  | ### Sub-Clause 4.21 Security of the Site is replaced with: ### “Sub-Clause 4.21 Security of the Site The Contractor shall be responsible for the security of the Site, and: - for keeping unauthorised persons off the Site; - authorised persons shall be limited to the Contractor’s Personnel, the Employer’s Personnel, and to any other personnel identified as authorised personnel (including the Employer’s other contractors on the Site), by a Notice from the Employer or the Engineer to the Contractor. Subject to Sub-Clause 4.1, the Contractor shall submit for the Engineer’s No-objection a security management plan that sets out the security arrangements for the Site. - The Contractor shall (i) conduct appropriate background checks on any personnel retained to provide security; (ii) train the security personnel adequately (or determine that they are properly trained) in the use of force (and where applicable, firearms), and appropriate conduct towards Contractor’s Personnel, Employer’s Personnel and affected communities; and (iii) require the security personnel to act within the applicable Laws and any requirements set out in the Specification. The Contractor shall not permit any use of force by security personnel in providing security except when used for preventive and defensive purposes in proportion to the nature and extent of the threat. In making security arrangements, the Contractor shall also comply with any additional requirements stated in the Specification.” |
| ### Sub-Clause 4.22 ### Contractor’s Operations on Site |  | ### On the third line of the second paragraph before “4.17”, “Sub- Clause” is added. |
| ### Sub-Clause 4.23 Archaeological and Geological Findings |  | ### The first paragraph is replaced with the following: “All fossils, coins, articles of value or antiquity, structures, groups of structures, and other remains or items of geological, archaeological, paleontological, historical, architectural or religious interest found on the Site shall be placed under the care and custody of the Employer. The Contractor shall: - take all reasonable precautions, including fencing-off the area or site of the finding, to avoid further disturbance and prevent Contractor’s Personnel or other persons from removing or damaging any of these findings; - train relevant Contractor’s Personnel on appropriate actions to be taken in the event of such findings; and - implement any other action consistent with the requirements of the Specification and relevant Laws.” |
| ### Sub-Clause 4.24 Suppliers (other than Subcontractors) |  | 4.24.1 Forced Labour The Contractor shall take measures to require its suppliers (other than Subcontractors) not to employ or engage forced labour including trafficked persons as described in Sub-Clause 6.21. If forced labour/trafficking cases are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 4.24.2 Child labour The Contractor shall take measures to require its suppliers (other than Subcontractors) not to employ or engage child labour as described in Sub-Clause 6.22. If child labour cases are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 4.24.3 Serious Safety Issues The Contractor, including its Subcontractors, shall comply with all applicable safety obligations, including as stated in Sub-Clauses 4.8, 5.1 and 6.7. The Contractor shall also take measures to require its suppliers (other than Subcontractors) to adopt procedures and mitigation measures adequate to address safety issues related to their personnel. If serious safety issues are identified, the Contractor shall take measures to require the suppliers to take appropriate steps to remedy them. Where the supplier does not remedy the situation, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to manage such risks. 4.24.4 Obtaining natural resource materials in relation to supplier The Contractor shall obtain natural resource materials from suppliers that can demonstrate, through compliance with the applicable verification and/ or certification requirements, that obtaining such materials is not contributing to the risk of significant conversion or significant degradation of natural or critical habitats such as unsustainably harvested wood products, gravel or sand extraction from river beds or beaches. If a supplier cannot continue to demonstrate that obtaining such materials is not contributing to the risk of significant conversion or significant degradation of natural or critical habitats, the Contractor shall within a reasonable period substitute the supplier with a supplier that is able to demonstrate that they are not significantly adversely impacting the habitats. |
| ### Sub-Clause 4.25 ### Code of Conduct |  | The Contractor shall have a Code of Conduct for the Contractor’s Personnel. The Contractor shall take all necessary measures to ensure that each Contractor’s Personnel is made aware of the Code of Conduct including specific behaviors that are prohibited, and understands the consequences of engaging in such prohibited behaviors. These measures include providing instructions and documentation that can be understood by the Contractor’s Personnel and seeking to obtain that person’s signature acknowledging receipt of such instructions and/or documentation, as appropriate. The Contractor shall also ensure that the Code of Conduct is visibly displayed in multiple locations on the Site and any other place where the Works will be carried out, as well as in areas outside the Site accessible to the local community and project affected people. The posted Code of Conduct shall be provided in languages comprehensible to Contractor’s Personnel, Employer’s Personnel and the local community. The Contractor’s Management Strategy and Implementation Plans shall include appropriate processes for the Contractor to verify compliance with these obligations. |
| ### Sub-Clause 5.1 Subcontractors |  | The following is added at the beginning of the second paragraph. “The Contractor shall require that its Subcontractors execute the Works in accordance with the Contract, including complying with the relevant ES requirements and the obligations set out in Sub-Clause 4.25 above.” The following is added after the first sentence of the fourth paragraph: “The Contractor’s submission to the Engineer shall also include the Subcontractor’s declaration in accordance with the Particular Conditions- Part E- Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment Performance Declaration for Subcontractors.” The following is added at the end of the last paragraph of Sub-Clause 5.1: “All subcontracts relating to the Works shall include provisions which entitle the Employer to require the subcontract to be assigned to the Employer under sub-paragraph (a) of Sub-Clause 15.2.3 [After Termination]. Where practicable, the Contractor shall give fair and reasonable opportunity for contractors from the Country to be appointed as Subcontractors.” |
| ### Sub-Clause 5.2.2 Objection to Nomination |  | In sub-paragraph (a), on the first line before “Subcontractor”, “nominated” is added. In sub-paragraph (c): “and” is deleted from the end of (i); “.” at the end of (ii) is replaced with: “, and”. The following is then added as (iii): “(iii) be paid only if and when the Contractor has received from the Employer payments for sums due under the Subcontract referred to under Sub-Clause 5.2.3 [ Payment to nominated Subcontractors].” |
| ### Sub-Clause 6.1 Engagement of Staff and Labour |  | The following paragraphs are added at the end of the Sub-Clause: - “The Contractor shall provide the Contractor’s Personnel information and documentation that are clear and understandable regarding their terms and conditions of employment. The information and documentation shall set out their rights under relevant labour Laws applicable to the Contractor’s Personnel (which will include any applicable collective agreements), including their rights related to hours of work, wages, overtime, compensation and benefits, as well as those arising from any requirements in the Specification. The Contractor’s Personnel shall be informed when any material changes to their terms or conditions of employment occur. The Contractor is encouraged, to the extent practicable and reasonable, to employ staff and labour with appropriate qualifications and experience from sources within the Country.” |
| ### Sub-Clause 6.2 Rates of Wages and Conditions of Labour |  | The following paragraphs are added at the end of the Sub-Clause: “The Contractor shall inform the Contractor’s Personnel about: - any deduction to their payment and the conditions of such deductions in accordance with the applicable Laws or as stated in the Specification; and - their liability to pay personal income taxes in the Country in respect of such of their salaries, wages, allowances and any benefits as are subject to tax under the Laws of the Country for the time being in force. The Contractor shall perform such duties in regard to such deductions thereof as may be imposed on him by such Laws. Where required by applicable Laws or as stated in the Specification, the Contractor shall provide the Contractor’s Personnel written notice of termination of employment and details of severance payments in a timely manner. The Contractor shall have paid the Contractor’s Personnel (either directly or where appropriate for their benefit) all due wages and entitlements including, as applicable, social security benefits and pension contributions, on or before the end of their engagement/ employment.” |
| ### Sub-Clause 6.5 Working Hours |  | The following is inserted at the end of the Sub-Clause: “The Contractor shall provide the Contractor’s Personnel annual holiday and sick, maternity and family leave, as required by applicable Laws or as stated in the Specification.” |
| ### Sub-Clause 6.6 ### Facilities for Staff and Labour |  | The following is added as the last paragraph: “If stated in the Specification, the Contractor shall give access to or provide services that accommodate the physical, social and cultural needs of the Contractor’s Personnel. The Contractor shall also provide similar facilities for the Employer’s Personnel as stated in the Specification.” |
| ### Sub-Clause 6.7 Health and Safety of Personnel |  | In the second paragraph, “The Contractor” is replaced with: “Except as otherwise stated in the Specification, the Contractor…” |
| ### Sub-Clause 6.9 Contractor’s Personnel |  | The Sub-Clause is replaced with: “The Contractor’s Personnel (including Key Personnel, if any) shall be appropriately qualified, skilled, experienced and competent in their respective trades or occupations. The Engineer may require the Contractor to remove (or cause to be removed) any person employed on the Site or Works, including the Contractor’s Representative and Key Personnel (if any), who: - persists in any misconduct or lack of care; - carries out duties incompetently or negligently; - fails to comply with any provision of the Contract; - persists in any conduct which is prejudicial to safety, health, or the protection of the environment; - based on reasonable evidence, is determined to have engaged in Fraud and Corruption during the execution of the Works; - has been recruited from the Employer’s Personnel in breach of Sub-Clause 6.3 [Recruitment of Persons]; - undertakes behaviour which breaches the Code of Conduct for Contractor’s Personnel (ES). If appropriate, the Contractor shall then promptly appoint (or cause to be appointed) a suitable replacement with equivalent skills and experience. In the case of replacement of the Contractor’s Representative, Sub-Clause 4.3 [Contractor’s Representative] shall apply. In the case of replacement of Key Personnel (if any), Sub-Clause 6.12 [Key Personnel] shall apply. Subject to the requirements in Sub-Clause 4.3 [Contractor’s Representative] and 6.12 [Key Personnel], and notwithstanding any requirement from the Engineer to remove or cause to remove any person, the Contractor shall take immediate action as appropriate in response to any violation of (a) through (g) above. Such immediate action shall include removing (or causing to be removed) from the Site or other places where the Works are being carried out, any Contractor’s Personnel who engages in (a), (b), (c), (d), (e) or (g) above or has been recruited as stated in (f) above.” |
| ### Sub-Clause 6.12 Key Personnel |  | The following is inserted at the end of the last paragraph: “If any of the Key Personnel are not fluent in this language, the Contractor shall make competent interpreters available during all working hours in a number deemed sufficient by the Engineer.” |
| The following Sub-Clauses 6.13 to 6.27 are added after sub-clause 6.12 |  |  |
| ### Sub-Clause 6.13 ### Foreign Personnel |  | The Contractor may bring into the Country any foreign personnel who are necessary for the execution of the Works to the extent allowed by the applicable Laws. The Contractor shall ensure that these personnel are provided with the required residence visas and work permits. The Employer will, if requested by the Contractor, use its best endeavours in a timely and expeditious manner to assist the Contractor in obtaining any local, state, national, or government permission required for bringing in the Contractor’s personnel. The Contractor shall be responsible for the return of these personnel to the place where they were recruited or to their domicile. In the event of the death in the Country of any of these personnel or members of their families, the Contractor shall similarly be responsible for making the appropriate arrangements for their return or burial. |
| ### Sub-Clause 6.14 Supply of Foodstuffs |  | The Contractor shall arrange for the provision of a sufficient supply of suitable food as may be stated in the Specification at reasonable prices for the Contractor’s Personnel for the purposes of or in connection with the Contract. |
| ### Sub-Clause 6.15 Supply of Water |  | The Contractor shall, having regard to local conditions, provide on the Site an adequate supply of drinking and other water for the use of the Contractor’s Personnel. |
| ### Sub-Clause 6.16 Measures against Insect and Pest Nuisance |  | The Contractor shall at all times take the necessary precautions to protect the Contractor’s Personnel employed on the Site from insect and pest nuisance, and to reduce the danger to their health. The Contractor shall comply with all the regulations of the local health authorities, including use of appropriate insecticide. |
| ### Sub-Clause 6.17 Alcoholic Liquor or Drugs |  | The Contractor shall not, otherwise than in accordance with the Laws of the Country, import, sell, give, barter or otherwise dispose of any alcoholic liquor or drugs, or permit or allow importation, sale, gift, barter or disposal thereto by Contractor’s Personnel. |
| ### Sub-Clause 6.18 Arms and Ammunition |  | The Contractor shall not give, barter, or otherwise dispose of, to any person, any arms or ammunition of any kind, or allow Contractor’s Personnel to do so. |
| ### Sub-Clause 6.19 Festivals and Religious Customs |  | The Contractor shall respect the Country’s recognized festivals, days of rest and religious or other customs. |
| ### Sub-Clause 6.20 Funeral Arrangements |  | The Contractor shall be responsible, to the extent required by local regulations, for making any funeral arrangements for any of its local employees who may die while engaged upon the Works. |
| ### Sub-Clause 6.21 Forced Labour |  | The Contractor, including its Subcontractors, shall not employ or engage forced labour. Forced labour consists of any work or service, not voluntarily performed, that is exacted from an individual under threat of force or penalty, and includes any kind of involuntary or compulsory labour, such as indentured labour, bonded labour or similar labour-contracting arrangements. No persons shall be employed or engaged who have been subject to trafficking. Trafficking in persons is defined as the recruitment, transportation, transfer, harbouring or receipt of persons by means of the threat or use of force or other forms of coercion, abduction, fraud, deception, abuse of power, or of a position of vulnerability, or of the giving or receiving of payments or benefits to achieve the consent of a person having control over another person, for the purposes of exploitation. |
| ### Sub-Clause 6.22 Child Labour |  | The Contractor, including its Subcontractors, shall not employ or engage a child under the age of 14 unless the national law specifies a higher age (the minimum age). The Contractor, including its Subcontractors, shall not employ or engage a child between the minimum age and the age of 18 in a manner that is likely to be hazardous, or to interfere with, the child’s education, or to be harmful to the child’s health or physical, mental, spiritual, moral, or social development. The Contractor including its Subcontractors, shall only employ or engage children between the minimum age and the age of 18 after an appropriate risk assessment has been conducted by the Contractor with the Engineer’s consent. The Contractor shall be subject to regular monitoring by the Engineer that includes monitoring of health, working conditions and hours of work. Work considered hazardous for children is work that, by its nature or the circumstances in which it is carried out, is likely to jeopardize the health, safety, or morals of children. Such work activities prohibited for children include work: - with exposure to physical, psychological or sexual abuse; - underground, underwater, working at heights or in confined spaces; - with dangerous machinery, equipment or tools, or involving handling or transport of heavy loads; - in unhealthy environments exposing children to hazardous substances, agents, or processes, or to temperatures, noise or vibration damaging to health; or - under difficult conditions such as work for long hours, during the night or in confinement on the premises of the employer. |
| ### Sub-Clause 6.23 Employment Records of Workers |  | The Contractor shall keep complete and accurate records of the employment of labour at the Site. The records shall include the names, ages, genders, hours worked, and wages paid to all workers. These records shall be summarised on a monthly basis and submitted to the Engineer. These records shall be included in the details to be submitted by the Contractor under Sub-Clause 6.10 [Records of Contractor’s Personnel and Equipment]. |
| ### Sub-Clause 6.24 Workers’ Organisations |  | In countries where the relevant labour laws recognise workers’ rights to form and to join workers’ organisations of their choosing and to bargain collectively without interference, the Contractor shall comply with such laws. In such circumstances, the role of legally established workers’ organizations and legitimate workers’ representatives will be respected, and they will be provided with information needed for meaningful negotiation in a timely manner. Where the relevant labour laws substantially restrict workers’ organisations, the Contractor shall enable alternative means for the Contractor’s Personnel to express their grievances and protect their rights regarding working conditions and terms of employment. The Contractor shall not seek to influence or control these alternative means. The Contractor shall not discriminate or retaliate against the Contractor’s Personnel who participate, or seek to participate, in such organisations and collective bargaining or alternative mechanisms. Workers’ organisations are expected to fairly represent the workers in the workforce. |
| ### Sub-Clause 6.25 Non-Discrimination and Equal Opportunity |  | The Contractor shall not make decisions relating to the employment or treatment of Contractor’s Personnel on the basis of personal characteristics unrelated to inherent job requirements. The Contractor shall base the employment of Contractor’s Personnel on the principle of equal opportunity and fair treatment, and shall not discriminate with respect to any aspects of the employment relationship, including recruitment and hiring, compensation (including wages and benefits), working conditions and terms of employment, access to training, job assignment, promotion, termination of employment or retirement, and disciplinary practices. Special measures of protection or assistance to remedy past discrimination or selection for a particular job based on the inherent requirements of the job shall not be deemed discrimination. The Contractor shall provide protection and assistance as necessary to ensure non-discrimination and equal opportunity, including for specific groups such as women, people with disabilities, migrant workers and children (of working age in accordance with Sub-Clause 6.22). |
| ### Sub-Clause 6.26 Contractor’s Personnel Grievance Mechanism |  | The Contractor shall have a grievance mechanism for Contractor’s Personnel, and where relevant the workers’ organizations stated in Sub-Clause 6.24, to raise workplace concerns. The grievance mechanism shall be proportionate to the nature, scale, risks and impacts of the Contract. The mechanism shall address concerns promptly, using an understandable and transparent process that provides timely feedback to those concerned in a language they understand, without any retribution, and shall operate in an independent and objective manner. The Contractor’s Personnel shall be informed of the grievance mechanism at the time of engagement for the Contract, and the measures put in place to protect them against any reprisal for its use. Measures will be put in place to make the grievance mechanism easily accessible to all Contractor’s Personnel. The grievance mechanism shall not impede access to other judicial or administrative remedies that might be available, or substitute for grievance mechanisms provided through collective agreements. The grievance mechanism may utilize existing grievance mechanisms, providing that they are properly designed and implemented, address concerns promptly, and are readily accessible to Contractor’s Personnel. Existing grievance mechanisms may be supplemented as needed with Contract-specific arrangements. |
| ### Sub-Clause 6.27 ### Training of Contractor’s Personnel |  | The Contractor shall provide appropriate training to relevant Contractor’s Personnel on ES aspects of the Contract, including appropriate sensitization on prohibition of SEA and SH, and health and safety training referred to in Sub-Clause 4.8 As stated in the Specification or as instructed by the Engineer, the Contractor shall also allow appropriate opportunities for the relevant Contractor’s Personnel to be trained on ES aspects of the Contract by the Employer’s Personnel. The Contractor shall provide training on SEA and SH, including its prevention, to any of its personnel who has a role to supervise other Contractor’s Personnel. |
| ### Sub-Clause 7.3 Inspection |  | The following is added in the first paragraph after “Employer’s Personnel” “(including the Bank staff or consultants acting on the Bank’s behalf, stakeholders and third parties, such as independent experts, local communities, or non-governmental organizations)” The following is added as (b) (iv): “(iv) carryout environmental and social audit, and” |
| ### Sub-Clause 7.7 ### Ownership of Plant and Materials |  | The following is added before the first paragraph: “Except as otherwise provided in the Contract,” |
| ### Sub-Clause 8.1 Commencement of Work |  | The Sub- Clause is replaced in its entirety with the following: “The Engineer shall give a Notice to the Contractor stating the Commencement Date, not less than 14 days before the Commencement Date. The Notice shall be issued promptly after the Engineer determines the fulfilment of the following conditions: - signature of the Contract Agreement by both Parties, and if required, approval of the Contract by relevant authorities of the Country; - delivery to the Contractor of reasonable evidence of the Employer’s financial arrangements (under Sub-Clause 2.4 [Employer’s Financial Arrangements]); - except if otherwise specified in the Contract Data, effective access to and possession of the Site given to the Contractor together with such permission(s) under (a) of Sub-Clause 1.13 [Compliance with Laws] as required for the commencement of the Works; - receipt by the Contractor of the Advance Payment under Sub-Clause 14.2 [Advance Payment] provided that the corresponding bank guarantee has been delivered by the Contractor; - constitution of the DAAB in accordance with Sub-Clause 21.1 and Sub-Clause 21.2 as applicable. Subject to Sub-Clause 4.1 on the ESCP (APPENDIX D ) and Sub-Clause 4.8 on the OHSMP, the Contractor shall commence the execution of the Works as soon as is reasonably practicable after the Commencement Date, and shall then proceed with the Works with due expedition and without delay.” |
| ### Sub-Clause 11.7 Right of Access after Taking Over |  | In the second paragraph, “Whenever the Contractor intends to access any part of the Works during the relevant DNP:” is replaced with: “Whenever, until the date 28 days after issue of the Performance Certificate, the Contractor intends to access any part of the Works:” |
| ### Sub-Clause 13.3.1 Variation by Instruction |  | Subparagraph 13.3.1 (a) is replaced with: “a description of the varied work performed or to be performed, including details of the resources and methods adopted or to be adopted by the Contractor, and sufficient ES information to enable an evaluation of ES risks and impacts;” |
| ### Sub-Clause 13.4 Provisional Sums |  | The following is inserted as the penultimate paragraph: “The Provisional Sum shall be used to cover the Employer's share of the DAAB members’ fees and expenses, in accordance with Clause 21. No prior instruction of the Engineer shall be required with respect to the work of the DAAB. The Contractor shall submit the DAAB members’ invoices and satisfactory evidence of having paid 100% of such invoices as part of the substantiation of those Statements submitted under Sub-Clause 14.3.” |
| ### Sub-Clause 13.6 Adjustments for Changes in Laws |  | The following paragraph is added at the end of the Sub-Clause: “Notwithstanding the foregoing, the Contractor shall not be entitled to an extension of time if the relevant delay has already been taken into account in the determination of a previous extension of time and such Cost shall not be separately paid if the same shall already have been taken into account in the indexing of any inputs to the Table of Adjustment Data in accordance with the provisions of Sub-Clause 13.7 [Adjustments for Changes in Cost].” |
| ### Sub-Clause 14.1 The Contract Price |  | The following is added at the end of the Sub-Clause: “Notwithstanding the provisions of subparagraph (b), Contractor's Equipment, including essential spare parts therefore, imported by the Contractor for the sole purpose of executing the Contract shall be temporarily exempt from the payment of import duties and taxes upon initial importation, provided the Contractor shall post with the customs authorities at the port of entry an approved export bond or bank guarantee, valid until the Time for Completion plus six months, in an amount equal to the full import duties and taxes which would be payable on the assessed imported value of such Contractor's Equipment and spare parts, and callable in the event the Contractor's Equipment is not exported from the Country on completion of the Contract. A copy of the bond or bank guarantee endorsed by the customs authorities shall be provided by the Contractor to the Employer upon the importation of individual items of Contractor's Equipment and spare parts. Upon export of individual items of Contractor's Equipment or spare parts, or upon the completion of the Contract, the Contractor shall prepare, for approval by the customs authorities, an assessment of the residual value of the Contractor's Equipment and spare part to be exported, based on the depreciation scale (s and other criteria used by the customs authorities for such purposes under the provisions of the applicable Laws. Import duties and taxes shall be due and payable to the customs authorities by the Contractor on (a) the difference between the initial imported value and the residual value of the Contractor's Equipment and spare parts to exported; and (b) on the initial imported value of the Contractor's Equipment and spare parts remaining in the Country after completion of the Contract. Upon payment of such dues within 28 days of being invoiced, the bond or bank guarantee shall be reduced or released accordingly; otherwise the security shall be called in the full amount remaining.” |
| ### Sub-Clause 14.2.1 Advance Payment Guarantee |  | The first paragraph is replaced with: “The Contractor shall obtain (at the Contractor’s cost) an Advance Payment Guarantee in amounts and currencies equal to the advance payment, and shall submit it to the Employer with a copy to the Engineer. This guarantee shall be issued by reputable bank or financial institution selected by the Contractor and shall be based on the sample form annexed to the Particular Conditions or in another form agreed by the Employer (but such agreement shall not relieve the Contractor from any obligation under this Sub-Clause).” |
| ### Sub-Clause 14.3 Application for Interim Payment |  | The following is inserted at the end of (vi) after: [Agreement or Determination]: “any reimbursement due to the Contractor under the Dispute Avoidance/ Adjudication Agreement. (Appendix General Conditions of Dispute Avoidance/ Adjudication Agreement).” |
| ### Sub-Clause 14.6.2 Withholding (amounts in) an IPC |  | “and/or” from subparagraph (b) is deleted. The following is then added as subparagraph (c) and sub-paragraph (c) of the Sub-Clause is renumbered as (d): “(c) if the Contractor was, or is, failing to perform any ES obligations or work under the Contract, the value of this work or obligation, as determined by the Engineer, may be withheld until the work or obligation has been performed, and/or the cost of rectification or replacement, as determined by the Engineer, may be withheld until rectification or replacement has been completed. Failure to perform includes, but is not limited to the following: - failure to comply with any ES obligations or work described in the Works’ Requirements which may include: working outside site boundaries, excessive dust, damage to offsite vegetation, pollution of water courses from oils or sedimentation, contamination of land e.g. from oils, human waste, damage to archaeology or cultural heritage features, air pollution as a result of unauthorized and/or inefficient combustion; - failure to regularly review ESCP (APPENDIX ... ) and/or update it in a timely manner to address emerging ES issues, or anticipated risks or impacts; - failure to implement the ESCP (APPENDIX ... ) e.g. failure to provide required training or sensitization; - failing to have appropriate consents/permits prior to undertaking Works or related activities; - failure to submit ES report/s (as described in Particular Conditions - Part D), or failure to submit such reports in a timely manner; - failure to implement remediation as instructed by the Engineer within the specified timeframe (e.g. remediation addressing non-compliance/s).” |
| ### Sub-Clause 14.7 Payment |  | At the end of sub-paragraph (b): “and” is replaced with “or” and the following inserted as (iii): “(iii) at a time when the Bank’s loan or credit (from which part of the payments to the Contractor is being made) is suspended, the amount shown on any statement submitted by the Contractor within 14 days after such statement is submitted, any discrepancy being rectified in the next payment to the Contractor; and” At the end of sub-paragraph (c): “.” is replaced with “;” and the following inserted: “or, at a time when the Bank’s loan or credit (from which part of the payments to the Contractor is being made) is suspended the undisputed amount shown in the Final Statement within 56 days after the date of notification of the suspension in accordance with Sub-Clause 16.2 [Termination by Contractor].” |
| ### Sub-Clause 14.9 Release of Retention Money |  | The following is added at the end of Sub-Clause 14.9: “Unless otherwise stated in the Contract, when the Taking-Over Certificate has been issued for the Works and the first half of the Retention Money has been certified for payment by the Engineer, the Contractor shall be entitled to substitute a guarantee, in the form annexed to the Particular Conditions or in another form approved by the Employer and issued by a reputable bank or financial institution selected by the Contractor, for the second half of the Retention Money. The Contractor shall ensure that the guarantee is in the amounts and currencies of the second half of the Retention Money and is valid and enforceable until the Contractor has executed and completed the Works and remedied any defects, as specified for the Performance Security and, if applicable, an ES Performance Security in Sub-Clause 4.2. On receipt by the Employer of the required guarantee, the Engineer shall certify and the Employer shall pay the second half of the Retention Money. The release of the second half of the Retention Money against a guarantee shall then be in lieu of the release after the latest of the expiry dates of the Defects Notification Periods. The Employer shall return the guarantee to the Contractor within 21 days after receiving a copy of the Performance Certificate. If the Performance Security and, if applicable, an ES Performance Security required under Sub-Clause 4.2 is in the form of a demand guarantee, and the amount guaranteed under them when the Taking-Over Certificate is issued is more than half of the Retention Money, then the Retention Money guarantee will not be required. If the amount guaranteed under the Performance Security and, if applicable, an ES Performance Security, when the Taking-Over Certificate is issued is less than half of the Retention Money, the Retention Money guarantee will only be required for the difference between half of the Retention Money and the amount guaranteed under the Performance Security and, if applicable, an ES Performance Security.” |
| ### Sub-Clause 14.12 Discharge |  | On the seventh line of the first paragraph, “Sub-Clause 21.6 [Arbitration]” is replaced with: “Clause 21 [Disputes and Arbitration]’. |
| ### Sub-Clause 14.15 Currencies of Payment |  | Throughout Sub-Clause 14.15, “Contract Data” is replaced with: “Schedule of Payment Currencies”. |
| ### Sub-Clause 15.1 Notice to Correct |  | “and” is deleted from (b) and “.” is replaced by: “; and” in (c). The following is then added as (d) “(d) specify the time within which the Contractor shall respond to the Notice to Correct.” In the third para., “shall immediately respond” is replaced with: “shall respond within the time specified in (d)”. Further, in the third para., “to comply with the time specified in the Notice to Correct.” is replaced with: “to comply with the time specified in (c).” |
| ### Sub-Clause 15.2.1 Notice |  | Sub-paragraph (h) is replaced with: “based on reasonable evidence, has engaged in Fraud and Corruption as defined in paragraph 2.2 of the Particular Conditions - Part C- Fraud and Corruption, in competing for or in executing the Contract.” |
| ### Sub-Clause 15.8 Fraud and Corruption |  | The following new Sub-Clause is added: “ 15.8.1 The Bank requires compliance with the Bank’s Anti-Corruption Guidelines and its prevailing sanctions policies and procedures as set forth in the Bank’s Sanctions Framework, as set forth in Particular Conditions - Part C- Fraud and Corruption. 15.8.2 The Employer requires the Contractor to disclose any commissions or fees that may have been paid or are to be paid to agents or any other party with respect to the bidding process or execution of the Contract. The information disclosed must include at least the name and address of the agent or other party, the amount and currency, and the purpose of the commission, gratuity or fee.” |
| ### Sub-Clause 16.1 Suspension by Contractor |  | The following paragraph is inserted after the first paragraph: “Notwithstanding the above, if the Bank has suspended disbursements under the loan or credit from which payments to the Contractor are being made, in whole or in part, for the execution of the Works, and no alternative funds are available as provided for in Sub-Clause 2.4 [Employer’s Financial Arrangements], the Contractor may by notice suspend work or reduce the rate of work at any time, but not less than 7 days after the Borrower having received the suspension notification from the Bank.” |
| ### Sub-Clause 16.2.1 Notice |  | Sub-paragraph (j) is deleted in its entirety. At the end of sub-paragraph (i): “; or” is replaced with: “.” sub-paragraph (f) is replaced with: “(f) the Contractor does not receive a Notice of the Commencement Date under Sub-Clause 8.1 [Commencement of Works] within 180 days after receiving the Letter of Acceptance, for reasons not attributable to the Contractor.” |
| ### Sub-Clause 16.2.2 ### Termination |  | The following is added at the end of Sub-Clause 16.2.2: “In the event the Bank suspends the loan or credit from which part or whole of the payments to the Contractor are being made, if the Contractor has not received the sums due to him upon expiration of the 14 days referred to in Sub-Clause 14.7 [Payment] for payments under Interim Payment Certificates, the Contractor may, without prejudice to the Contractor's entitlement to financing charges under Sub-Clause 14.8 [Delayed Payment], take one of the following actions, namely (i) suspend work or reduce the rate of work under Sub-Clause 16.1 above, or (ii) terminate the Contract by giving notice to the Employer, with a copy to the Engineer, such termination to take effect 14 days after the giving of the notice.” |
| ### Sub-Clause 16.3 ### Contractor’s Obligations After Termination |  | [If the Employer has made available any Employer- Supplied Materials and/or Employer’s Equipment in accordance with Sub-Clause 2.6, include the following:] “and” is deleted from the end of sub-paragraph (b), sub-paragraph (c) deleted and the following added: “ - deliver to the Engineer all Employer- Supplied Materials and/or Employer’s Equipment made available to the Contractor in accordance with Sub-Clause 2.6 [Employer-Supplied materials and Employer’s Equipment]; and - remove all other Goods from the Site, except as necessary for safety, and leave the Site.” |
| ### Sub-Clause 17.1 Responsibility for Care of the Works |  | On the fourth and fifth lines of the first paragraph, replace “Date of Completion of the Works” with “issue of the Taking-Over Certificate for the Works”. [If Employer- Supplied Materials are listed in the Specification for the Contractor’s use in the execution of Works, include the following provision. See also Sub-Clause 2.6 [Employer-Supplied Materials and Employer’s Equipment]] After the two instances of “Goods” in the last paragraph, the following is added: “Employer- Supplied Materials”. [If Employer’s Equipment are listed in the Works’ Requirements for the Contractor’s use in the execution of Works, include the following provision. See also Sub-Clause 2.6 [Employer-Supplied Materials and Employer’s Equipment]] After the two instances of “Goods” in the last paragraph, the following is added: “, Employer’s Equipment,”. |
| ### Sub-Clause 17.3 Intellectual and Industrial Property Rights |  | On the first line of the second paragraph, replace “notice” is replaced with “a Notice”. |
| ### Sub-Clause 17.7 Use of Employer’s Accommodation/Facilities |  | The following Sub-Clause is added as 17.7: “The Contractor shall take full responsibility for the care of the Employer-provided accommodation and facilities, if any, as detailed in the Specification, from the respective dates of hand-over to the Contractor until cessation of occupation (where hand-over or cessation of occupation may take place after the date stated in the Taking-Over Certificate for the Works) If any loss or damage happens to any of the above items while the Contractor is responsible for their care arising from any cause whatsoever other than those for which the Employer is liable, the Contractor shall, at its own cost, rectify the loss or damage to the satisfaction of the Engineer.” |
| ### Sub-Clause 18.1 ### Exceptional Events |  | Sub-paragraph (c) is substituted with: “(c) riot, commotion, disorder or sabotage by persons other than the Contractor’s Personnel and other employees of the Contractor and Subcontractors;” |
| ### Sub-Clause 18.4 Consequences of an Exceptional Event |  | The following is added at the end of sub-paragraph (b) after deleting the “.”: “, including the costs of rectifying or replacing the Works and/or Goods damaged or destroyed by Exceptional Events, to the extent they are not indemnified through the insurance policy referred to in Sub-Clause 19.2 [ Insurance to be provided by the Contractor].” |
| ### Sub-Clause 18.5 ### Optional Termination |  | In sub-paragraph (c), “and necessarily” is inserted after ““was reasonably”. |
| ### Sub-Clause 19.1 ### General Requirements |  | The following paragraphs are added after the first: “Wherever the Employer is the insuring Party, each insurance shall be effected with insurers and in terms acceptable to the Contractor. These terms shall be consistent with terms (if any) agreed by both Parties before the date of the Letter of Acceptance. This agreement of terms shall take precedence over the provisions of this Clause." |
| ### Sub-Clause 19.2 insurance to be provided by the Contractor |  | The following is inserted as the first sentence in Sub-Clause 19.2: “The Contractor shall be entitled to place all insurances relating to the Contract (including, but not limited to the insurance referred to Clause 19) with insurers from any eligible source country.” |
| ### Sub-Clause 19.2.1 The Works |  | On the last line of the second paragraph, “Clause 12 [Tests after completion]” is deleted. |
| ### Sub-Clause 19.2.5 ### Injury to employees |  | The second paragraph is replaced with: “The Employer and the Engineer shall also be indemnified under the policy of insurance, against liability for claims, damages, losses and expenses (including legal fees and expenses) arising from injury, sickness, disease or death of any person employed by the Contractor or any other of the Contractor’s Personnel, except that this insurance may exclude losses and claims to the extent that they arise from any act or neglect of the Employer or of the Employer's Personnel.” |
| ### Sub-Clause 20.1 ### Claims |  | In a): “any additional payment” is replaced with “payment”. |
| ### Sub-Clause 20.2 Claims for Payment and/or EOT |  | The first paragraph is replaced with: “If either Party considers that it is entitled to claim under 20.1 (a) or (b), the following claim procedure shall apply:” |
| ### Sub-Clause 21.1 ### Constitution of the DAAB |  | In the second paragraph, at the end of the first sentence after deleting: “.”, the following is added: “, each of whom shall meet the criteria set forth in Sub-Clause 3.3 of Appendix- General Conditions of Dispute Avoidance/ Adjudication Agreement.” After the second paragraph insert the following paragraph: “If the Contract is with a foreign Contractor, the DAAB members shall not have the same nationality as the Employer or the Contractor.” |
| ### Sub-Clause 21.2 ### Failure to Appoint DAAB Member (s) |  | For both (a) and (b): “by the date stated in the first paragraph of Sub-Clause 21.1 [Constitution of the DAAB]” is replaced with: “within 42 days from the date the Contract is signed by both Parties” |
| ### Sub-Clause 21.6 ### Arbitration |  | In the first paragraph, delete starting from: “international arbitration” up to the end of (c), and replace with the following: “arbitration. Arbitration shall be conducted as follows: - if the contract is with foreign contractors, unless otherwise specified in the Contract Data; the dispute shall be finally settled under the Rules of Arbitration of the International Chamber of Commerce; by one or three arbitrators appointed in accordance with these Rules. The place of arbitration shall be the neutral location specified in the Contract Data; and the arbitration shall be conducted in the ruling language defined in Sub-Clause 1.4 [Law and Language]. (b) If the Contract is with domestic contractors, arbitration with proceedings conducted in accordance with the laws of the Employer’s country.” |
| Appendix- General Conditions of Dispute Avoidance/Adjudication Agreement |  |  |
| Title |  | “General Conditions of Dispute Avoidance/Adjudication Agreement” is replaced with “General Conditions of DAAB Agreement”. |
| - Definitions |  | Sub-Clause 1.2: In both the first and third lines, “DAA Agreement” is replaced with “DAAB Agreement”. Sub-Clause 1.3: -In the first line, “Dispute Avoidance/Adjudication Agreement” or “DAA Agreement” means” is replaced with: “DAAB Agreement” is as defined under the Contract and is”. - In the first line of sub-paragraph (c), “DAA Agreement” is replaced with “DAAB Agreement”. - In sub-paragraph (c)(ii), “chairman” is replaced with “chairperson”. Sub-Clause 1.3 “DAAB Activities” is replaced with Sub-Clause 1.4 “DAAB Activities” and the subsequent Sub- Clauses under Clause 1 “Definitions” renumbered: Sub-Clause 1.7 to 12: Replace all instances of “DAA Agreement” with “DAAB Agreement”. In Sub-Clause 1.8 a(i):” authorised representative of the contractor or of the Employer” is replaced with: “Contractor’s Representative or authorised representative of the Employer”. |
| - General Provisions |  | Sub-Clause 2.2 is deleted in its entirety. |
| - Warranties |  | Sub-Clause 3.3 is deleted and replaced with the following: “When appointing the DAAB Member, each Party relies on the DAAB Member’s representations, that he/she: - has at least a bachelor’s degree in relevant disciplines such as law, engineering, construction management or contract management; - has at least ten years of experience in contract administration/management and dispute resolution, out of which at least five years of experience as an arbitrator or adjudicator in construction-related disputes; - has received formal training as an adjudicator from an internationally recognized organization; - has experience and/or is knowledgeable in the type of work which the Contractor is to carry out under the Contract; - has experience in the interpretation of construction and/or engineering contract documents; - has familiarity with the forms of contract published by FIDIC since 1999, and an understanding of the dispute resolution procedures contained therein; and - is fluent in the language for communications stated in the Contract Data (or the language as agreed between the Parties and the DAAB).” |
| 7. Confidentiality |  | In Sub-Clause 7.3: “or” is deleted after sub-paragraph (b), and the following added: “or (d) is being provided to the Bank.” |
| 9. Fees and Expenses |  | In Sub-Clause 9.1 (c): “business class or equivalent” is replaced with: “in less than first class”. |
|  |  | In Sub-Clause 9.4: “and air fares” and “other” are deleted from the first and second sentences respectively. |
| - Resignation and Termination |  | In Sub-Clause 10.3: “the DAA Agreement” is replaced with: “a DAAB member’s DAAB Agreement”. |
| Annex- DAAB Procedural Rules |  |  |
| Rule 4.2 | On the fourth line, “chairman” is replaced with “chairperson”. |  |
| Rule 8.3 | On the sixth line, “chairman” is replaced with “chairperson”. |  |
| Form of Dispute Avoidance/Adjudication Agreement |  |  |
| All instances of “DAA Agreement” are replaced with: “DAAB Agreement”. In C (b): “chairman” is replaced with “chairperson”. |  |  |

Particular Conditions

Part C- Fraud and Corruption

1.	Purpose

1.1	The Bank’s Anti-Corruption Guidelines and this annex apply with respect to procurement under Bank Investment Project Financing operations.

2.	Requirements

2.1	The Bank requires that Borrowers (including beneficiaries of Bank financing); bidders, consultants, contractors and suppliers; any sub-contractors, sub-consultants, service providers or suppliers; any agents (whether declared or not); and any of their personnel, observe the highest standard of ethics during the procurement process, selection and contract execution of Bank-financed contracts, and refrain from Fraud and Corruption.

2.2	To this end, the Bank:

a.	Defines, for the purposes of this provision, the terms set forth below as follows:

i.	“corrupt practice” is the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party;

ii.	“fraudulent practice” is any act or omission, including misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain financial or other benefit or to avoid an obligation;

iii.	“collusive practice” is an arrangement between two or more parties designed to achieve an improper purpose, including to influence improperly the actions of another party;

iv.	“coercive practice” is impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party;

v.	“obstructive practice” is:

(a)	deliberately destroying, falsifying, altering, or concealing of evidence material to the investigation or making false statements to investigators in order to materially impede a Bank investigation into allegations of a corrupt, fraudulent, coercive, or collusive practice; and/or threatening, harass or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or

(b)	acts intended to materially impede the exercise of the Bank’s inspection and audit rights provided for under paragraph 2.2 e. below.

b.	Rejects a proposal for award if the Bank determines that the firm or individual recommended for award, any of its personnel, or its agents, or its sub-consultants, sub-contractors, service providers, suppliers and/ or their employees, has, directly or indirectly, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices in competing for the contract in question;

c.	In addition to the legal remedies set out in the relevant Legal Agreement, may take other appropriate actions, including declaring misprocurement, if the Bank determines at any time that representatives of the Borrower or of a recipient of any part of the proceeds of the loan engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices during the procurement process, selection and/or execution of the contract in question,  without the Borrower having taken timely and appropriate action satisfactory to the Bank to address such practices when they occur, including by failing to inform the Bank in a timely manner at the time  they knew of the practices;

d.	Pursuant to the Bank’s Anti- Corruption Guidelines and in accordance with the Bank’s prevailing sanctions policies and procedures, may sanction a firm or individual, either indefinitely or for a stated period of time, including by publicly declaring such firm or individual ineligible (i) to be awarded or otherwise benefit from a Bank-financed contract, financially or in any other manner;  (ii) to be a nominated  sub-contractor, consultant, manufacturer or supplier, or service provider of an otherwise eligible firm being awarded a Bank-financed contract; and (iii) to receive the proceeds of any loan made by the Bank or otherwise to participate further in the preparation or implementation of any Bank-financed project;

e.        Requires that a clause be included in bidding/request for proposals documents and in contracts financed by a Bank loan, requiring (i) bidders, consultants, contractors, and suppliers, and their sub-contractors, sub-consultants, service providers, suppliers, agents personnel, permit the Bank to inspect  all accounts, records and other documents relating to the submission of bids and contract performance, and to have them audited by auditors appointed by the Bank.

Particular Conditions

Part D- Environmental and Social (ES)

Metrics for Progress Reports

[Note to Employer: the following metrics may be amended to reflect the specifics of the Contract. The Employer shall ensure that the metrics provided are appropriate for the Works and impacts/key issues identified in the environmental and social assessment.]

Metrics for regular reporting:

        - environmental incidents or non-compliances with contract requirements, including contamination, pollution or damage to ground or water supplies;

        - health and safety incidents, accidents, injuries that require treatment and all fatalities;

        - interactions with regulators:  identify agency, dates, subjects, outcomes (report the negative if none);

        - status of all permits and agreements:

- work permits: number required, number received, actions taken for those not received;

- status of permits and consents:

- list areas/facilities with permits required (quarries, asphalt & batch plants), dates of application, dates issued (actions to follow up if not issued), dates submitted to resident engineer (or equivalent), status of area (waiting for permits, working, abandoned without reclamation, decommissioning plan being implemented, etc.);

- list areas with landowner agreements required (borrow and spoil areas, camp sites), dates of agreements, dates submitted to resident engineer (or equivalent);

- identify major activities undertaken in each area in the reporting period and highlights of environmental and social protection (land clearing, boundary marking, topsoil salvage, traffic management, decommissioning planning, decommissioning implementation);

- for quarries: status of relocation and compensation (completed, or details of activities and current status in the reporting period).

        - health and safety supervision:

- safety officer: number days worked, number of full inspections & partial inspections, reports to construction/project management;

- number of workers, work hours, metric of PPE use (percentage of workers with full personal protection equipment (PPE), partial, etc.), worker violations observed (by type of violation, PPE or otherwise), warnings given, repeat warnings given, follow-up actions taken (if any);

        - worker accommodations:

- number of expats housed in accommodations, number of locals;

- date of last inspection, and highlights of inspection including status of accommodations’ compliance with national and local law and good practice, including sanitation, space, etc.;

- actions taken to recommend/require improved conditions, or to improve conditions.

        - Health services: provider of health services, information and/or training, location of clinic, number of non-safety disease or illness treatments and diagnoses (no names to be provided);

        - gender (for expats and locals separately): number of female workers, percentage of workforce, gender issues raised and dealt with (cross-reference grievances or other sections as needed);

        - training:

- number of new workers, number receiving induction training, dates of induction training;

- number and dates of toolbox talks, number of workers receiving Occupational Health and Safety (OHS), environmental and social training;

- number and dates of communicable diseases (including STDs) sensitization and/or training, no. workers receiving training (in the reporting period and in the past); same questions for gender sensitization, flag person training.

- number and date of SEA and SH prevention sensitization and/or training events, including number of workers receiving training on Code of Conduct for Contractor’s Personnel (in the reporting period and in the past), etc.

        - environmental and social supervision:

- environmentalist: days worked, areas inspected and numbers of inspections of each (road section, work camp, accommodations, quarries, borrow areas, spoil areas, swamps, forest crossings, etc.), highlights of activities/findings (including violations of environmental and/or social best practices, actions taken), reports to environmental and/or social specialist/construction/site management;

- sociologist: days worked, number of partial and full site inspections (by area: road section, work camp, accommodations, quarries, borrow areas, spoil areas, clinic, HIV/AIDS center, community centers, etc.), highlights of activities (including violations of environmental and/or social requirements observed, actions taken), reports to environmental and/or social specialist/construction/site management; and

- community liaison person(s): days worked (hours community center open), number of people met, highlights of activities (issues raised, etc.), reports to environmental and/or social specialist /construction/site management.

        - Grievances: list new grievances (e.g. number of allegations of SEA and SH) received in the reporting period and number of unresolved past grievances by date received, complainant’s age and sex, how received, to whom referred to for action, resolution and date (if completed), data resolution reported to complainant, any required follow-up (Cross-reference other sections as needed):

- Worker grievances;

- Community grievances

        - Traffic, road safety and vehicles/equipment:

- traffic and road safety incidents and accidents involving project vehicles & equipment: provide date, location, damage, cause, follow-up;

- traffic and road safety incidents and accidents involving non-project vehicles or property (also reported under immediate metrics): provide date, location, damage, cause, follow-up;

- overall condition of vehicles/equipment (subjective judgment by environmentalist); non-routine repairs and maintenance needed to improve safety and/or environmental performance (to control smoke, etc.).

        - Environmental mitigations and issues (what has been done):

- dust: number of working bowsers, number of waterings/day, number of complaints, warnings given by environmentalist, actions taken to resolve; highlights of quarry dust control (covers, sprays, operational status); % of rock/ spoil lorries with covers, actions taken for uncovered vehicles;

- erosion control: controls implemented by location, status of water crossings, environmentalist inspections and results, actions taken to resolve issues, emergency repairs needed to control erosion/sedimentation;

- quarries, borrow areas, spoil areas, asphalt plants, batch plants: identify major activities undertaken in the reporting period at each, and highlights of environmental and social protection: land clearing, boundary marking, topsoil salvage, traffic management, decommissioning planning, decommissioning implementation;

- blasting: number of blasts (and locations), status of implementation of blasting plan (including notices, evacuations, etc.), incidents of off-site damage or complaints (cross-reference other sections as needed);

- spill clean-ups, if any:  material spilled, location, amount, actions taken, material disposal (report all spills that result in water or soil contamination;

- waste management: types and quantities generated and managed, including amount taken offsite (and by whom) or reused/recycled/disposed on-site;

- details of tree plantings and other mitigations required undertaken in the reporting period;

- details of water and swamp protection mitigations required undertaken in the reporting period.

        - compliance:

- compliance status for conditions of all relevant consents/permits, for the Work, including quarries, etc.): statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance;

- compliance status of ESCP (APPENDIX ... )/ESIP requirements: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- compliance status of SEA and SH prevention and response action plan: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- compliance status of Health and Safety Management Plan re: statement of compliance or listing of issues and actions taken (or to be taken) to reach compliance

- other unresolved issues from previous reporting periods related to environmental and social: continued violations, continued failure of equipment, continued lack of vehicle covers, spills not dealt with, continued compensation or blasting issues, etc.  Cross-reference other sections as needed.

Particular Conditions

Part E- Sexual Exploitation and Abuse (SEA) and/or Sexual Harassment Performance Declaration for Subcontractors

[The following table shall be filled in by each subcontractor proposed by the Contractor, that was not named in the Contract]

Subcontractor’s Name: [insert full name]
Date: [insert day, month, year]

Contract reference [insert contract reference]
Page [insert page number] of [insert total number] pages

SEA and/or SH Declaration

We:  (a) have not been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.  (b) are subject to disqualification by the Bank for non-compliance with SEA/ SH obligations.  (c) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations. An arbitral award on the disqualification case has been made in our favor.  (d) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations for a period of two years. We have subsequently demonstrated that we have adequate capacity and commitment to comply with SEA /SH obligations.  (e) had been subject to disqualification by the Bank for non-compliance with SEA/ SH obligations for a period of two years. We have attached specific evidence demonstrating that we have adequate capacity and commitment to comply with SEA and SH obligations.

[If (c) above is applicable, attach evidence of an arbitral award reversing the findings on the issues underlying the disqualification.]

[If (d) or (e) above are applicable, provide the following information:]

Period of disqualification: From: _______________ To: ________________

If previously provided on another Bank financed works contract, details of evidence that demonstrated adequate capacity and commitment to comply with SEA/SH obligations (as per (d) above) Name of Employer: ___________________________________________ Name of Project: _____________________________________ Contract description: _____________________________________________________ Brief summary of evidence provided: ________________________________________ ______________________________________________________________________ Contact Information: (Tel, email, name of contact person): _______________________ ______________________________________________________________________

As an alternative to the evidence under (d), other evidence demonstrating adequate capacity and commitment to comply with SEA/SH obligations (as per (e) above) ) [attach details as appropriate]. ___________________________________________________________________________ ____________________________________________________________________________

Name of the Subcontractor

Name of the person duly authorized to sign on behalf of the Subcontractor	_______

Title of the person signing on behalf of the Subcontractor	______________________

Signature of the person named above	______________________

Date signed ________________________________ day of ___________________, _____

Countersignature of authorized representative of the Contractor:

Signature: ________________________________________________________

Date signed ________________________________ day of ___________________, _____

Appendix 1.  Terms and Procedures of Payment

In accordance with the provisions of GC Clause 14 (Contract Price and Payment), the Employer shall pay the Contractor in the following manner and at the following times, on the basis of the Price Breakdown given in the section on Price Schedules.  Payments will be made in the currencies quoted by the Bidder unless otherwise agreed between the Parties.  Applications for payment in respect of part deliveries may be made by the Contractor as work proceeds.

TERMS OF PAYMENT

In respect of plant and equipment supplied from abroad, the following payments shall be made:

Ten percent (10%) of the total Accepted Contract Amount as an Advance Payment against receipt of invoice, and an irrevocable advance payment security acceptable to the employer for the equivalent amount made out in favor of the Employer.

Thirty percent (30%) of the total Accepted Contract Amount or pro rata CIP amount upon Incoterm “Carriage & Insurance Paid To (CIP)”, upon delivery of the material to the carrier and within forty-five (45) days after receipt of invoice and documents.

Fifteen percent (15%) of the total Accepted Contract Amount or pro rata DPU amount upon Incoterm “Delivered at Place Unloaded (DPU)” upon delivery on Site and within forty-five (45) days after receipt of invoice and documents.

Forty percent (40%) of the total Accepted Contract Amount or pro rata upon issue of the Operational Acceptance Certificate and within forty-five (45) days after receipt of invoice and documents.

Five percent (5%) of the total Accepted Contract Amount upon completion of the retention period and within forty-five (45) days after receipt of invoice.

In the event that the Employer fails to make any payment on its respective due date, the Employer shall pay to the Contractor interest on the amount of such delayed payment at the rate specified in the Contract Data Sheet.

Section X - Contract Forms

Table of Forms

Notification of Intention to Award	352

Contract Agreement	357

Performance Security	359

Environmental and Social (ES) Performance Security	361

Advance Payment Security	363

Demand Guarantee	363

Retention Money Security	365

Notification of Intention to Award

[This Notification of Intention to Award shall be sent to each Bidder that submitted a Bid.]

[Send this Notification to the Bidder’s Authorized Representative named in the Bidder Information Form]

For the attention of Bidder’s Authorized Representative

Name: [insert Authorized Representative’s name]

Address: [insert Authorized Representative’s Address]

Telephone/Fax numbers: [insert Authorized Representative’s telephone/fax numbers]

Email Address: [insert Authorized Representative’s email address]

[IMPORTANT: insert the date that this Notification is transmitted to Bidders. The Notification must be sent to all Bidders simultaneously. This means on the same date and as close to the same time as possible.]

DATE OF TRANSMISSION: This Notification is sent by: [email/fax] on [date] (local time)

Notification of Intention to Award

Employer: [insert the name of the Employer]

Project: [insert name of project]

Contract title: [insert the name of the contract]

Country: [insert country where RFB is issued]

Loan No. /Credit No. / Grant No.: [insert reference number for loan/credit/grant]

RFB No: [insert RFB reference number from Procurement Plan]

This Notification of Intention to Award (Notification) notifies you of our decision to award the above contract. The transmission of this Notification begins the Standstill Period. During the Standstill Period you may:

- request a debriefing in relation to the evaluation of your Bid, and/or

- submit a Procurement-related Complaint in relation to the decision to award the contract.

- The successful Bidder

| Name: | [insert name of successful Bidder] |
| --- | --- |
| Address: | [insert address of the successful Bidder] |
| Contract price: | [insert contract price of the successful Bid] |

- Other Bidders [INSTRUCTIONS: insert names of all Bidders that submitted a Bid. If the Bid’s price was evaluated include the evaluated price as well as the Bid price as read out.]

| Name of Bidder | Bid price | Evaluated Bid price (if applicable) |
| --- | --- | --- |
| [insert name] | [insert Bid price] | [insert evaluated price] |
| [insert name] | [insert Bid price] | [insert evaluated price] |
| [insert name] | [insert Bid price] | [insert evaluated price] |
| [insert name] | [insert Bid price] | [insert evaluated price] |
| [insert name] | [insert Bid price] | [insert evaluated price] |

- Reason/s why your Bid was unsuccessful

[INSTRUCTIONS: State the reason/s why this Bidder’s Bid was unsuccessful. Do NOT include: (a) a point by point comparison with another Bidder’s Bid or (b) information that is marked confidential by the Bidder in its Bid.]

- How to request a debriefing

DEADLINE: The deadline to request a debriefing expires at midnight on [insert date] (local time). You may request a debriefing in relation to the results of the evaluation of your Bid. If you decide to request a debriefing your written request must be made within three (3) Business Days of receipt of this Notification of Intention to Award. Provide the contract name, reference number, name of the Bidder, contact details; and address the request for debriefing as follows: Attention: [insert full name of person, if applicable] Title/position: [insert title/position] Agency: [insert name of Employer] Email address: [insert email address] Fax number: [insert fax number] delete if not used If your request for a debriefing is received within the 3 Business Days deadline, we will provide the debriefing within five (5) Business Days of receipt of your request. If we are unable to provide the debriefing within this period, the Standstill Period shall be extended by five (5) Business Days after the date that the debriefing is provided. If this happens, we will notify you and confirm the date that the extended Standstill Period will end. The debriefing may be in writing, by phone, video conference call or in person. We shall promptly advise you in writing how the debriefing will take place and confirm the date and time. If the deadline to request a debriefing has expired, you may still request a debriefing. In this case, we will provide the debriefing as soon as practicable, and normally no later than fifteen (15) Business Days from the date of publication of the Contract Award Notice.

- How to make a complaint

Period: Procurement-related Complaint challenging the decision to award shall be submitted by midnight, [insert date] (local time). Provide the contract name, reference number, name of the Bidder, contact details; and address the Procurement-related Complaint as follows: Attention: [insert full name of person, if applicable] Title/position: [insert title/position] Agency: [insert name of Employer] Email address: [insert email address] Fax number: [insert fax number] delete if not used At this point in the procurement process, you may submit a Procurement-related Complaint challenging the decision to award the contract. You do not need to have requested, or received, a debriefing before making this complaint. Your complaint must be submitted within the Standstill Period and received by us before the Standstill Period ends. Further information: For more information see the Procurement Regulations for IPF Borrowers (Procurement Regulations)[https://policies.worldbank.org/sites/ppf3/PPFDocuments/Forms/DispPage.aspx?docid=4005] (Annex III). You should read these provisions before preparing and submitting your complaint. In addition, the World Bank’s Guidance “How to make a Procurement-related Complaint” [http://www.worldbank.org/en/projects-operations/products-and-services/brief/procurement-new-framework#framework] provides a useful explanation of the process, as well as a sample letter of complaint. In summary, there are four essential requirements: - You must be an ‘interested party’. In this case, that means a Bidder who submitted a Bid in this bidding process, and is the recipient of a Notification of Intention to Award. - The complaint can only challenge the decision to award the contract. - You must submit the complaint within the period stated above. - You must include, in your complaint, all of the information required by the Procurement Regulations (as described in Annex III).

- Standstill Period

DEADLINE: The Standstill Period is due to end at midnight on [insert date] (local time). The Standstill Period lasts ten (10) Business Days after the date of transmission of this Notification of Intention to Award. The Standstill Period may be extended as stated in Section 4 above.

If you have any questions regarding this Notification, please do not hesitate to contact us.

On behalf of the Employer:

Signature: 	______________________________________________

Name:	______________________________________________

Title/position:	______________________________________________

Telephone:	______________________________________________

Email:	______________________________________________

# Letter of Acceptance

[letterhead paper of the Employer]

[date]

To:  [name and address of the Contractor]

This is to notify you that your Bid dated [date] for execution of the [name of the Contract and identification number, as given in the Contract Data] for the Accepted Contract Amount [amount in numbers and words] [name of currency], as corrected and modified in accordance with the Instructions to Bidders, is hereby accepted by our Agency.

You are requested to furnish (i) the Performance Security and an Environmental and Social Performance Security [Delete ES Performance Security if it is not required under the contract] within 28 days in accordance with the Conditions of Contract, using, for that purpose, one of the Performance Security Forms and the ES Performance Security Form, [Delete reference to the ES Performance Security Form if it is not required under the contract] and (ii) the additional information on beneficial ownership in accordance with BDS ITB 47.1, within eight (8) Business days using the Beneficial Ownership Disclosure Form, included in Section X, Contract Forms, of the bidding document.

Authorized Signature:

Name and Title of Signatory:

Name of Agency:

Attachment:  Contract Agreement

Contract Agreement

THIS AGREEMENT made the ________ day of ________________________, _____, between ______________________________________of __________________________ (hereinafter “the Employer”), of the one part, and ______________________ of _____________________ (hereinafter “the Contractor”), of the other part:

WHEREAS the Employer desires that the Works known as _______________________________ should be executed by the Contractor, and has accepted a Bid by the Contractor for the execution and completion of these Works and the remedying of any defects therein,

The Employer and the Contractor agree as follows:

1.	In this Agreement words and expressions shall have the same meanings as are respectively assigned to them in the Contract documents referred to.

2.	The following documents shall be deemed to form and be read and construed as part of this Agreement. This Agreement shall prevail over all other Contract documents.

- the Letter of Acceptance;

- the Letter of Bid;

- the addenda Nos ________ (if any);

- the Particular Conditions;

- the General Conditions;

- the Specification;

- the Drawings; and

- the completed Schedules and any other documents forming part of the contract, including, but not limited to:

    - the ES Management Strategies and Implementation Plans; and

    - Code of Conduct for Contractor’s Personnel (ES).

3.	In consideration of the payments to be made by the Employer to the Contractor as specified in this Agreement, the Contractor hereby covenants with the Employer to execute the Works and to remedy defects therein in conformity in all respects with the provisions of the Contract.

4.	The Employer hereby covenants to pay the Contractor in consideration of the execution and completion of the Works and the remedying of defects therein, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

IN WITNESS whereof the parties hereto have caused this Agreement to be executed in accordance with the laws of _____________________________ on the day, month and year specified above.

Signed by ________________________________________________ (for the Employer)

Signed by __________________________________________________ (for the Contractor)

Performance Security

Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	Ministry of Environment, Climate Change and Technology

Date:	________________[Insert date of issue]

PERFORMANCE GUARANTEE No.:	_________________

Guarantor:  [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ (hereinafter called "the Applicant") has entered into Contract No. _____________ dated ____________ with the Beneficiary, for the execution of _____________________ (hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, a performance guarantee is required.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ (                    ),1 such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating that the Applicant is in breach of its obligation(s) under the Contract, without the Beneficiary needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire, no later than the …. Day of ……, 2…2, and any demand for payment under it must be received by us at this office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

_____________________ 
[signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

Environmental and Social (ES) Performance Security

ES Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	[insert name and Address of Employer]

Date:	_ [Insert date of issue]

ES PERFORMANCE GUARANTEE No.:	[Insert guarantee reference number]

Guarantor: [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ (hereinafter called "the Applicant") has entered into Contract No. _____________ dated ____________ with the Beneficiary, for the execution of _____________________ (hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, a performance guarantee is required.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ (                    ),1 such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating that the Applicant is in breach of its Environmental and/or Social (ES) obligation(s) under the Contract, without the Beneficiary needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire, no later than the …. Day of ……, 2… 2, and any demand for payment under it must be received by us at this office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

_____________________ 
[signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

Advance Payment Security

Demand Guarantee

[Guarantor letterhead or SWIFT identifier code]

[Guarantor letterhead or SWIFT identifier code]

Beneficiary:	___________________ [Insert name and Address of Employer]

Date:	________________ [Insert date of issue]

ADVANCE PAYMENT GUARANTEE No.:	[Insert guarantee reference number]

Guarantor:  [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ (hereinafter called “the Applicant”) has entered into Contract No. _____________ dated ____________ with the Beneficiary, for the execution of _____________________ (hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, an advance payment in the sum ___________ (                    ) is to be made against an advance payment guarantee.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ (                    ) 1 upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating either that the Applicant:

    - has used the advance payment for purposes other than the costs of mobilization in respect of the Works; or

    - has failed to repay the advance payment in accordance with the Contract conditions, specifying the amount which the Applicant has failed to repay.

A demand under this guarantee may be presented as from the presentation to the Guarantor of a certificate from the Beneficiary’s bank stating that the advance payment referred to above has been credited to the Applicant on its account number ___________ at _________________..

The maximum amount of this guarantee shall be progressively reduced by the amount of the advance payment repaid by the Applicant as specified in copies of interim statements or payment certificates which shall be presented to us.  This guarantee shall expire, at the latest, upon our receipt of a copy of the interim payment certificate indicating that ninety (90) percent of the Accepted Contract Amount, less provisional sums, has been certified for payment, or on the ___ day of _____, 2___,2 whichever is earlier.  Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

____________________ 
[signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

Retention Money Security

Demand Guarantee

________________________________ [Guarantor letterhead or SWIFT identifier code]

Beneficiary:	___________________ [Insert name and Address of Employer]

Date:	________________ [Insert date of issue]

RETENTION MONEY GUARANTEE No.:	[Insert guarantee reference number]

Guarantor:  [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that ________________ [insert name of Contractor, which in the case of a joint venture shall be the name of the joint venture] (hereinafter called "the Applicant") has entered into Contract No. _____________ [insert reference number of the contract] dated ____________ with the Beneficiary, for the execution of _____________________ [insert name of contract and brief description of Works] (hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, the Beneficiary retains moneys up to the limit set forth in the Contract (“the Retention Money”), and that when the Taking-Over Certificate has been issued under the Contract and the first half of the Retention Money has been certified for payment, payment of [insert the second half of the Retention Money or if the amount guaranteed under the Performance Guarantee when the Taking-Over Certificate is issued is less than half of the Retention Money, the difference between half of the Retention Money and the amount guaranteed under the Performance Security and, if required, the ES Performance Security] is to be made against a Retention Money guarantee.

At the request of the Applicant, we, as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of ___________ [insert amount in figures] (                    ) [amount in words]1 upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand,  stating that the Applicant is in breach of its obligation(s) under the Contract, without your needing to prove or show grounds for your demand or the sum specified therein.

A demand under this guarantee may be presented as from the presentation to the Guarantor of a certificate from the Beneficiary’s bank stating that the second half of the Retention Money as referred to above has been credited to the Applicant on its account number ___________ at _________________ [insert name and address of Applicant’s bank].

This guarantee shall expire no later than the …. Day of ……, 2…2, and any demand for payment under it must be received by us at the office indicated above on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees (URDG) 2010 Revision, ICC Publication No. 758, except that the supporting statement under Article 15(a) is hereby excluded.

____________________ 
[signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.

An individual firm is considered a domestic Bidder for purposes of the margin of preference if it is registered in the country of the Employer, has more than 50 percent ownership by nationals of the country of the Employer, and if it does not subcontract more than 10 percent of the contract price, excluding provisional sums, to foreign contractors. JVs are considered as domestic Bidders and eligible for domestic preference only if the individual member firms are registered in the country of the Employer or have more than 50 percent ownership by nationals of the country of the Employer, and the JV shall be registered in the country of the Borrower. The JV shall not subcontract more than 10 percent of the contract price, excluding provisional sums, to foreign firms. JVs between foreign and national firms will not be eligible for domestic preference.

Nonperformance, as decided by the Employer, shall include all contracts where (a) nonperformance was not challenged by the contractor, including through referral to the dispute resolution mechanism under the respective contract, and (b) contracts that were so challenged but fully settled against the contractor. Nonperformance shall not include contracts where Employers decision was overruled by the dispute resolution mechanism. Nonperformance must be based on all information on fully settled disputes or litigation, i.e. dispute or litigation that has been resolved in accordance with the dispute resolution mechanism under the respective contract and where all appeal instances available to the Bidder have been exhausted.

This requirement also applies to contracts executed by the Bidder as JV member.

The Bidder shall provide accurate information on the related Bid Form about any litigation or arbitration resulting from contracts completed or ongoing under its execution over the last five years. A consistent history of awards against the Bidder or any member of a joint venture may result in failure of the Bid.

The Employer may use this information to seek further information or clarifications in carrying out its due diligence.

The similarity shall be based on the physical size, complexity, methods/technology and/or other characteristics described in Section VII, Works’ Requirement. Summation of number of small value contracts (less than the value specified under requirement) to meet the overall requirement will not be accepted.

The bid evaluation process applies a stringent process to deviations from the Employer Requirements. It is in the interest of bidders to minimise any deviations.

If the most recent set of financial statements is for a period earlier than 12 months from the date of Bid, the reason for this should be justified.

For the avoidance of doubt, a sanctioned party’s ineligibility to be awarded a contract shall include, without limitation, (i) applying for pre-qualification, expressing interest in a consultancy, and bidding, either directly or as a nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider, in respect of such contract, and (ii) entering into an addendum or amendment introducing a material modification to any existing contract.

A nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider (different names are used depending on the particular bidding document) is one which has been: (i) included by the bidder in its pre-qualification application or bid because it brings specific and critical experience and know-how that allow the bidder to meet the qualification requirements for the particular bid; or (ii) appointed by the Borrower.

Inspections in this context usually are investigative (i.e., forensic) in nature.  They involve fact-finding activities undertaken by the Bank or persons appointed by the Bank to address specific matters related to investigations/audits, such as evaluating the veracity of an allegation of possible Fraud and Corruption, through the appropriate mechanisms.  Such activity includes but is not limited to: accessing and examining a firm's or individual's financial records and information, and making copies thereof as relevant; accessing and examining any other documents, data and information (whether in hard copy or electronic format) deemed relevant for the investigation/audit, and making copies thereof as relevant; interviewing staff and other relevant individuals; performing physical inspections and site visits; and obtaining third party verification of information.

Witness may include in-person, or remote via video conference. Contractor must be able to provide for either option. Employer witness may include Employer nominated representative.

The bus bar and isolators must withstand the system power flow since they may be installed in series with the new lines

Chosen to match load and provide N-1 redundancy to existing Power House generation

The Substations must be connected in series with the RMU – circuit breakers to be sized considering maximum transformer ratings

Chosen to match load and provide N-1 redundancy

For the avoidance of doubt, a sanctioned party’s ineligibility to be awarded a contract shall include, without limitation, (i) applying for pre-qualification, expressing interest in a consultancy, and bidding, either directly or as a nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider, in respect of such contract, and (ii) entering into an addendum or amendment introducing a material modification to any existing contract.

A nominated sub-contractor, nominated consultant, nominated manufacturer or supplier, or nominated service provider (different names are used depending on the particular bidding document) is one which has been: (i) included by the bidder in its pre-qualification application or bid because it brings specific and critical experience and know-how that allow the bidder to meet the qualification requirements for the particular bid; or (ii) appointed by the Borrower.

Inspections in this context usually are investigative (i.e., forensic) in nature.  They involve fact-finding activities undertaken by the Bank or persons appointed by the Bank to address specific matters related to investigations/audits, such as evaluating the veracity of an allegation of possible Fraud and Corruption, through the appropriate mechanisms.  Such activity includes but is not limited to: accessing and examining a firm's or individual's financial records and information, and making copies thereof as relevant; accessing and examining any other documents, data and information (whether in hard copy or electronic format) deemed relevant for the investigation/audit, and making copies thereof as relevant; interviewing staff and other relevant individuals; performing physical inspections and site visits; and obtaining third party verification of information.

1	The Guarantor shall insert an amount representing the percentage of the Accepted Contract Amount specified in the Letter of Acceptance, less provisional sums, if any, and denominated either in the currency(cies) of the Contract or a freely convertible currency acceptable to the Beneficiary.

2	Insert the date twenty-eight days after the expected completion date as described in GC Clause 11.9. The Employer should note that in the event of an extension of this date for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor.  Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph:  “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months][one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”

1	The Guarantor shall insert an amount representing the percentage of the Accepted Contract Amount specified in the Letter of Acceptance, less provisional sums, if any, and denominated either in the currency (cies) of the Contract or a freely convertible currency acceptable to the Beneficiary.

2	Insert the date twenty-eight days after the expected completion date as described in GC Clause 11.9. The Employer should note that in the event of an extension of this date for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor.  Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph: “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months] [one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”

1	The Guarantor shall insert an amount representing the amount of the advance payment and denominated either in the currency(ies) of the advance payment as specified in the Contract, or in a freely convertible currency acceptable to the Employer.

2 	Insert the expected expiration date of the Time for Completion.  The Employer should note that in the event of an extension of the time for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor.  Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph:  “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months][one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”

1	The Guarantor shall insert an amount representing the amount of the second half of the Retention Money or if the amount guaranteed under the Performance Guarantee when the Taking-Over Certificate is issued is less than half of the Retention Money, the difference between half of the Retention Money and the amount guaranteed under the Performance Security and denominated either in the currency(ies) of the second half of the Retention Money as specified in the Contract, or in a freely convertible currency acceptable to the Beneficiary.

2	Insert the same expiry date as set forth in the performance security, representing the date twenty-eight days after the completion date described in GC Clause 11.9.  The Employer should note that in the event of an extension of this date for completion of the Contract, the Employer would need to request an extension of this guarantee from the Guarantor.  Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the Employer might consider adding the following text to the form, at the end of the penultimate paragraph:  “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [six months][one year], in response to the Beneficiary’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”