Republic of Maldives

Ministry of Energy and Environment

Procurement of Plant

Design, Supply, and Installation

of a Waste incineration plant with energy recovery

Single-Stage: One-Envelope

Bidding Procedure

ICB No: (IUL)13-K/13/2018/2

Project: Small Scale Waste to Energy Project at S. Hithadhoo

Employer: Ministry of Energy and Environment

Abu Dhabi Fund for Development (ADFD)

November 2017

Procurement of Plant

Design, Supply, and Installation

of a Waste incineration plant

Single-Stage: One-Envelope

Bidding Procedure

BIDDING DOCUMENT

for

Procurement

of a Waste incineration plant with energy recovery in Addu City

Invitation for Bids No.: (IUL)13-K/13/2018/2

Employer: Ministry of Environment and Energy

Country: Republic of the Maldives

Preface

“We the Ministry of Energy of Maldives of the Republic of the Maldives have received to Abu Dhabi Fund for Development (ADFD) for a loans financing towards the cost of a Small Scale Waste to Energy Project at S. Hithadhoo. It is intended that the proceeds of this financing be applied to cover payments due under the contract for which this invitation to bid is issued.

This document was developed under the guidelines for the procurement of goods and contracting for the execution of works by the members of the coordination group for the Arab fund for economic and social development and related to all members and institutions of this group, in its version of 2001

Single-Stage Bidding Procedure Documents Structure Flowchart

| 1 | Bidding Document | issued by Employer |
| --- | --- | --- |
|  | Section 1 - Instructions to Bidders (ITB); Section 2 - Bid Data Sheet (BDS); Section 3 - Evaluation and Qualification Criteria (EQC); Section 4 - Bidding Forms (BDF); Section 5 - Eligible Countries (ELC); Section 6 - Employer’s Requirements (ERQ); Section 7 - General Conditions of Contract (GCC); Section 8 - Special Conditions of Contract (SCC); Section 9 - Contract Forms (COF). |  |

| 2 | The Bid | submitted by Bidder |
| --- | --- | --- |
|  | (a) Letter of Bid; (b) Completed schedules as required, including Price Schedules, in accordance with ITB 12 and ITB 18; (c) Bid Security or Bid-Securing Declaration, in accordance with ITB 21; (d) Alternative Bids, if permissible, in accordance with ITB 13; (e) Written confirmation authorizing the signatory of the Bid to commit the Bidder, in accordance with ITB 22.2; (f) Documentary evidence in accordance with ITB 14.1, that the plant and services offered by the Bidder in its bid or in any alternative bid, if permitted, are eligible; (g) Documentary evidence in accordance with ITB 15, the Bidder’s eligibility and qualifications to perform the contract if its Bid is accepted; (h) Technical Proposal in accordance with ITB 17; (i) Documentary evidence in accordance with ITB 16, that the plant and services offered by the Bidder conform to the Bidding Document; (j) Joint Venture agreement, or letter of intent to enter into a Joint Venture including a draft agreement, indicating at least the parts of the Plant to be executed by the respective partners in the case of a bid submitted by a Joint Venture; (k) List of subcontractors, in accordance with ITB 17.2; and (l) Any other document required in the BDS. |  |

| 3 | The Contract | issued by Employer and submitted by Bidder |
| --- | --- | --- |
|  | (a) Letter of Acceptance; (b) Contract Agreement and the Appendices hereto; (c) Letter of Bid and Price Schedules submitted by the Contractor; (d) Special Conditions of Contract; (e) List of Eligible Countries that was specified in Section 5 of the Bidding Document; (f) General Conditions of Contract; (g) Specifications; (h) Drawings; (i) Other completed Bidding Forms submitted with the Letter of Bid; (j) Any other documents forming part of the Employer’s Requirements; (k) Any other documents as needed and specified.(Withdrawal Procedures) |  |

Table of Contents - Summary Description

PART I	BIDDING PROCEDURES

Section 1 -	Instructions to Bidders (ITB)	  1-1

This Section specifies the procedures to be followed by Bidders in the preparation and submission of their Bids. Information is also provided on the submission, opening, and evaluation of bids and on the award of contract.

Section 2 -	Bid Data Sheet (BDS) 	  2-1

This Section consists of provisions that are specific to each procurement and supplement the information or requirements included in Section 1 - Instructions to Bidders.

Section 3 -	Evaluation and Qualification Criteria (EQC) 	  3-1

This Section contains the bid evaluation criteria to determine the lowest evaluated bid and lists the necessary qualifications of Bidders.

Section 4 -	Bidding Forms (BDF) 	  4-1

This Section contains the forms which are to be completed by the Bidder and submitted as part of its Bid.

Section 5 -	Eligibility (ELC) 	  5-1

This Section contains the Eligibility criteria by projects funded under ADFD.

PART II  	REQUIREMENTS

Section 6 -	Employer’s Requirements (ERQ) 	  6-1

This Section contains the Scope of Supply of Plant and Services, Specifications, the Drawings, and Supplementary Information that describe the Facilities to be procured, Personnel Requirements, Equipment Requirements, Certificates, and Change Orders.

PART III	CONDITIONS OF CONTRACT AND CONTRACT FORMS

Section 7 -	General Conditions of Contract (GCC) 	  7-1

This Section contains the general clauses to be applied in all contracts. These Conditions are subject to the variations and additions set out in Section 8 (Special Conditions of Contract).

Section 8 -	Special Conditions of Contract (SCC) 	  8-1

This Section contains provisions that are specific to each contract and that modify or supplement the GCC.  Whenever there is a conflict, the provisions herein shall prevail over those in the GCC.  The clause number of the SCC is the corresponding clause number of the GCC.

Section 9 -	Contract Forms (COF)	  9-1

This Section contains forms, which, once completed, will form part of the Contract. The forms for Performance Security and Advance Payment Security, when required, shall only be completed by the successful Bidder after contract award.

ANNEX	WITHDRAWAL PROCEDURES

Section 1 - Instructions to Bidders

## Table of Clauses

A.   General	1-3

1.	Scope of Bid	1-3

2.	Source of Funds	1-3

3.	Fraud and Corruption	1-3

4.	Eligible Bidders	1-4

5.	Eligible  Plant and Services	1-6

B.	Contents of Bidding Document	1-6

6.	Sections of  Bidding Document	1-6

7.	Clarification of Bidding Document, Site Visit, Pre-Bid Meeting	1-7

8.	Amendment of Bidding Document	1-8

C.	Preparation of Bids	1-8

9.	Cost of Bidding	1-8

10.	Language of Bid	1-8

11.	Documents Comprising the Bid	1-8

12.	Letter of Bid and Schedules	1-9

13.	Alternative Bids	1-9

14.	Documents Establishing the Eligibility of  Plant and Services	1-9

15.	Documents Establishing the Eligibility and Qualifications of the Bidder	1-9

16.	Documents Establishing Conformity of the Plant and Services	1-9

17.	Technical Proposal, Subcontractors	1-10

18.	Bid Prices and Discounts	1-10

19.	Currencies of Bid and Payment	1-12

20.	Period of Validity of Bids	1-12

21.	Bid Security/Bid-Securing Declaration	1-13

22.	Format and Signing of Bid	1-14

D.	Submission and Opening of Bids	1-14

23.	Submission, Sealing and Marking of Bids	1-14

24.	Deadline for Submission of Bids	1-15

25.	Late Bids	1-15

26.	Withdrawal,  Substitution, and Modification of Bids	1-15

27.	Bid Opening	1-15

E.	Evaluation and Comparison of Bids	1-16

28.	Confidentiality	1-16

29.	Clarification of Bids	1-17

30.	Deviations, Reservations, and Omissions	1-17

31.	Determination of  Responsiveness	1-17

32.	Nonmaterial Nonconformities	1-17

33.	Correction of Arithmetical Errors	1-18

34.	Conversion to Single Currency	1-18

35.	Margin of Preference	1-18

36.	Evaluation of Bids	1-18

37.	Comparison of Bids	1-20

38.	Eligibility and Qualification of the Bidder	1-20

39.	Employer’s Right to Accept Any Bid, and to Reject Any or All Bids	1-21

F.	Award of Contract	1-21

40.	Award Criteria	1-21

41.	Notification of Award	1-21

42.	Signing of Contract	1-21

43.	Performance Security	1-22

Section 1 - Instructions to Bidders

| - General |  |
| --- | --- |
| - Scope of Bid | - In connection with the Invitation for Bids (IFB) indicated in the Bid Data Sheet (BDS), the Employer, as indicated in the BDS, issues this Bidding Document for the procurement of plant and services as specified in Section 6 (Employer’s Requirements). The name, identification, and number of lot/s (contract/s) of the international competitive bidding (ICB) are provided in the BDS. |
|  | - Unless otherwise stated, throughout this Bidding Document definitions and interpretations shall be as prescribed in Section 7 (General Conditions of Contract) (GCC)). |
| - Source of Funds | - The Borrower or Recipient (hereinafter called “Borrower”) indicated in the BDS has applied for or received financing (hereinafter called “funds”) from the Abu Dhabi Fund for Development (hereinafter called “ADFD”) toward the cost of the project named in the BDS. The Borrower intends to apply a portion of the funds to eligible payments under the contract(s) for which this Bidding Document is issued. |
|  | - Payments shall be made directly to the contractor/supplier in line with ADFD procedures. A copy of the ADFD withdrawal procedures is part of the contract documents. |
| - Fraud and Corruption | - ADFD’s Anticorruption Policy requires Borrowers (including beneficiaries of ADFD-financed activity), as well as Bidders, Suppliers, and Contractors under ADFD-financed contracts, observe the highest standard of ethics during the procurement and execution of such contracts. In pursuance of this policy, ADFD - defines, for the purposes of this provision, the terms set forth below as follows: - “corrupt practice” means the offering, giving, receiving, or soliciting, directly or indirectly, anything of value to influence improperly the actions of another party; - “fraudulent practice” means any act or omission, including a misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain a financial or other benefit or to avoid an obligation; - “coercive practice” means impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party; - “collusive practice” means an arrangement between two or more parties designed to achieve an improper purpose, including influencing improperly the actions of another party; - “obstructive practice” means (a) deliberately destroying, falsifying, altering, or concealing of evidence material to an ADFD investigation; (b) making false statements to investigators in order to materially impede an ADFD investigation; (c) failing to comply with requests to provide information, documents, or records in connection with an Office of Anticorruption and Integrity (OAI) investigation; (d) threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation; or (e) materially impeding ADFDʼs contractual rights of audit or access to information; and - “integrity violation" is any act which violates ADFD’s Anticorruption Policy, including (i) to (v) above and the following: abuse, conflict of interest, violations of ADFD sanctions, retaliation against whistleblowers or witnesses, and other violations of ADFD's Anticorruption Policy, including failure to adhere to the highest ethical standard. - will reject a proposal for award if it determines that the Bidder recommended for award has, directly or through an agent, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices or other integrity violations in competing for the Contract; - will cancel the portion of the financing allocated to a contract if it determines at any time that representatives of the Borrower or of a beneficiary of ADFD-financing engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices or other integrity violations during the procurement or the execution of that contract, without the Borrower having taken timely and appropriate action satisfactory to ADFD to remedy the situation; - will impose remedial actions on a firm or an individual, at any time, in accordance with ADFD’s Anticorruption Policy and Integrity Principles and Guidelines (both as amended from time to time), including declaring ineligible, either indefinitely or for a stated period of time, to participate in ADFD-financed, -administered, or -supported activities or to benefit from an ADFD-financed, -administered, or -supported contract, financially or otherwise, if it at any time determines that the firm or individual has, directly or through an agent, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices, or other integrity violations; and - will have the right to require that a provision be included in the Bidding Documents and in contracts financed by ADFD, requiring Bidders, suppliers and contractors to permit ADFD or its representative to inspect their accounts and records and other documents relating to the bid submission and contract performance and to have them audited by auditors appointed by ADFD. |
|  | - Furthermore, Bidders shall be aware of the provision stated in GCC 9.6 and GCC 42.2.1 (c). |
| - Eligible Bidders | - A Bidder may be a natural person, private entity, or government-owned enterprise subject to ITB 4.5 - or any combination of them with a formal intent to enter into an agreement or under an existing agreement in the form of a Joint Venture. In the case of a Joint Venture, - all partners shall be jointly and severally liable; and - the Joint Venture shall nominate a Representative who shall have the authority to conduct all business for and on behalf of any and all the partners of the Joint Venture during the bidding process and, in the event the Joint Venture is awarded the Contract, during contract execution. |
|  | - A Bidder, and all partners constituting the Bidder, shall have the nationality of an eligible country, in accordance with Section 5 (Eligible Countries). A Bidder shall be deemed to have the nationality of a country if the Bidder is a citizen or is constituted, incorporated, or registered, and operates in conformity with the provisions of the laws of that country. This criterion shall also apply to the determination of the nationality of proposed subcontractors or suppliers for any part of the Contract, including related services. |
|  | - A Bidder shall not have a conflict of interest. All Bidders found to have a conflict of interest shall be disqualified. A Bidder may be considered to be in a conflict of interest with one or more parties in this bidding process if any of, including but not limited to, the following apply: - they have controlling shareholders in common; or - they receive or have received any direct or indirect subsidy from any of them; or - they have the same legal representative for purposes of this bid; or - they have a relationship with each other, directly or through common third parties, that puts them in a position to have access to material information about or improperly influence the bid of another Bidder, or influence the decisions of the Employer regarding this bidding process; or - a Bidder participates in more than one bid in this bidding process, either individually or as a partner in a joint venture, except for alternative offers permitted under ITB 13. This will result in the disqualification of all Bids in which it is involved. However, subject to any finding of a conflict of interest in terms of ITB 4.3 (a) - (d) above, this does not limit the participation of a Bidder as a subcontractor in another Bid or of a firm as a subcontractor in more than one Bid; or - a Bidder or any affiliated entity, participated as a consultant in the preparation of the design or technical specifications of the plant and services that are the subject of the Bid; or - a Bidder was affiliated with a firm or entity that has been hired (or is proposed to be hired) by the Employer or Borrower as Project Manager for the Contract. |
|  | - A firm shall not be eligible to participate in any procurement activities under an ADFD-financed, -administered, or -supported project while under temporary suspension or debarment by ADFD pursuant to its Anticorruption Policy (see ITB 3), whether such debarment was directly imposed by ADFD, or enforced by ADFD pursuant to the Agreement for Mutual Enforcement of Debarment Decisions. A bid from a temporary suspended or debarred firm will be rejected. |
|  | - Government-owned enterprises in the Borrower’s country shall be eligible only if they can establish that they (i) are legally and financially autonomous, (ii) operate under commercial law, and (iii) are not dependent agencies of the Employer. |
|  | - Bidders shall provide such evidence of their continued eligibility satisfactory to the Employer, as the Employer shall reasonably request. |
|  | - Firms shall be excluded if by an act of compliance with a decision of the United Nations Security Council taken under Chapter VII of the Charter of the United Nations, the Borrower’s country prohibits any import of goods or contracting of works or services from that country or any payments to persons or entities in that country. |
|  | - In case a prequalification process has been conducted prior to the bidding process, this bidding is open only to prequalified Bidders. |
| - Eligible Plant and Services | - The plant and services to be supplied under the Contract shall have their origin in eligible source countries as defined in ITB 4.2 and all expenditures under the Contract will be limited to such plant and services. |
|  | - For purposes of ITB 5.1 above, “origin” means the place where the plant, or component parts thereof are mined, grown, produced, or manufactured, and from which the services are provided. Plant components are produced when, through manufacturing, processing, or substantial or major assembling of components, a commercially recognized product results that is substantially in its basic characteristics or in purpose or utility from its components. |
| - Contents of Bidding Document |  |
| - Sections of Bidding Document | - The Bidding Document consists of Parts I, II, and III, which include all the sections indicated below, and should be read in conjunction with any addenda issued in accordance with ITB 8. PART I Bidding Procedures Section 1 - Instructions to Bidders (ITB) Section 2 - Bid Data Sheet (BDS) Section 3 - Evaluation and Qualification Criteria (EQC) Section 4 - Bidding Forms (BDF) Section 5 – Eligibility criteria PART II Requirements Section 6 - Employer’s Requirements (ERQ) PART III Conditions of Contract and Contract Forms Section 7 - General Conditions of Contract (GCC) Section 8 - Special Conditions of Contract (SCC) Section 9 - Contract Forms (COF) |
|  | - The IFB issued by the Employer is not part of the Bidding Document. |
|  | - The Employer is not responsible for the completeness of the Bidding Document and its addenda, if they were not obtained directly from the source stated by the Employer in the IFB. |
|  | - The Bidder is expected to examine all instructions, forms, terms, and specifications in the Bidding Document. Failure to furnish all information or documentation required by the Bidding Document may result in the rejection of the Bid. |
| - Clarification of Bidding Document, Site Visit, Pre-Bid Meeting | - A prospective Bidder requiring any clarification on the Bidding Document shall contact the Employer in writing at the Employer’s address indicated in the BDS, or raise his enquiries during the pre-bid meeting if provided for in accordance with ITB 7.4. The Employer will respond to any request for clarification, provided that such request is received no later than 21 days prior to the deadline for submission of bids. The Employer’s response shall be in writing with copies to all Bidders who have acquired the Bidding Document in accordance with ITB 6.3, including a description of the inquiry but without identifying its source. Should the Employer deem it necessary to amend the Bidding Document as a result of a request for clarification, it shall do so following the procedure under ITB 8 and ITB 24.2. |
|  | - The Bidder is advised to visit and examine the site where the plant is to be installed and its surroundings and obtain for itself on its own responsibility all information that may be necessary for preparing the Bid and entering into a contract for the provision of plant and services. The costs of visiting the site shall be at the Bidder’s own expense. |
|  | - The Bidder and any of its personnel or agents will be granted permission by the Employer to enter its premises and lands for the purpose of such visit, but only upon the express condition that the Bidder, its personnel, and agents, will release and indemnify the Employer and its personnel and agents from and against all liability in respect thereof, and will be responsible for death or personal injury, loss of or damage to property, and any other loss, damage, costs, and expenses incurred as a result of the inspection. |
|  | - The Bidder’s designated representative is invited to attend a pre-bid meeting, if provided for in the BDS. The purpose of the meeting will be to clarify issues and to answer questions on any matter that may be raised at that stage. |
|  | - The Bidder is requested to submit any questions in writing, to reach the Employer not later than 1 week before the pre-bid meeting. |
|  | - Minutes of the pre-bid meeting, including the text of the questions raised, without identifying the source, and the responses given, together with any responses prepared after the meeting, will be transmitted promptly to all Bidders who have acquired the Bidding Document in accordance with ITB 6.3. Any modification to the Bidding Document that may become necessary as a result of the pre-bid meeting shall be made by the Employer exclusively through the issue of an addendum pursuant to ITB 8 and not through the minutes of the pre-bid meeting. |
|  | - Nonattendance at the pre-bid meeting will not be a cause for disqualification of a Bidder. |
| - Amendment of Bidding Document | - At any time prior to the deadline for submission of Bids, the Employer may amend the Bidding Document by issuing addenda. |
|  | - Any addendum issued shall be part of the Bidding Document and shall be communicated in writing to all who have obtained the Bidding Document from the Employer in accordance with ITB 6.3. |
|  | - To give prospective Bidders reasonable time in which to take an addendum into account in preparing their Bids, the Employer may, at its discretion, extend the deadline for the submission of Bids, pursuant to ITB 24.2 |
| - Preparation of Bids |  |
| - Cost of Bidding | - The Bidder shall bear all costs associated with the preparation and submission of its Bid, and the Employer shall in no case be responsible or liable for those costs, regardless of the conduct or outcome of the bidding process. |
| - Language of Bid | - The Bid, as well as all correspondence and documents relating to the bid exchanged by the Bidder and the Employer, shall be written in the English language. Supporting documents and printed literature that are part of the Bid may be in another language provided they are accompanied by an accurate translation of the relevant passages into the English language, in which case, for purposes of interpretation of the Bid, such translation shall govern. |
| - Documents Comprising the Bid | - The Bid submitted by the Bidder shall comprise the following: - Letter of Bid; - completed schedules as required, including Price Schedules, in accordance with ITB 12 and ITB 18; - Bid Security or Bid-Securing Declaration, in accordance with ITB 21; - alternative Bids, if permissible, in accordance with ITB 13; - written confirmation authorizing the signatory of the Bid to commit the Bidder, in accordance with ITB 22.2; - documentary evidence in accordance with ITB 14.1, that the plant and services offered by the Bidder in its Bid or in any alternative bid, if permitted, are eligible; - documentary evidence in accordance with ITB 15, the Bidder’s eligibility and qualifications to perform the contract if its Bid is accepted; - Technical Proposal in accordance with ITB 17. - documentary evidence in accordance with ITB 16, that the plant and services offered by the Bidder conform to the Bidding Document; - list of subcontractors, in accordance with ITB 17.2; and - any other document required in the BDS. - In addition to the requirements under ITB 11.1, Bids submitted by a Joint Venture shall include a copy of the Joint Venture Agreement entered into by all partners. Alternatively, a Letter of Intent to execute a Joint Venture Agreement in the event of a successful Bid shall be signed by all partners and submitted with the Bid, together with a copy of the proposed agreement. |
| - Letter of Bid and Schedules | - The Bidder shall complete the Letter of Bid, including the appropriate Price Schedules, using the relevant forms furnished in Section 4 (Bidding Forms). The forms must be completed as instructed in each form and as required in the BDS. |
| - Alternative Bids | - The BDS indicates whether alternative Bids are allowed. If they are allowed, the BDS will also indicate whether they are permitted in accordance with ITB 13.3, or invited in accordance with ITB13.2 and/or ITB 13.4. |
|  | - When alternatives to the Time Schedule are explicitly invited, a statement to that effect will be included in the BDS, and the method of evaluating different time schedules will be described in Section 3 (Evaluation and Qualification Criteria). |
|  | - Except as provided under ITB 13.4 below, Bidders wishing to offer technical alternatives to the Employer’s requirements as described in the Bidding Document must also provide (i) a price at which they are prepared to offer a plant meeting the Employer’s requirements; and (ii) all information necessary for a complete evaluation of the alternatives by the Employer, including drawings, design calculations, technical specifications, breakdown of prices, and proposed installation methodology and other relevant details. Only the technical alternatives, if any, of the lowest evaluated Bidder conforming to the basic technical requirements shall be considered by the Employer. |
|  | - When Bidders are invited in the BDS to submit alternative technical solutions for specified parts of the facilities, such parts shall be described in Section 6 (Employer’s Requirements). Technical alternatives for the specific parts of the facilities that comply with the performance and technical criteria specified for the plant and services shall be considered by the Employer on their own merits, pursuant to ITB 36. |
| - Documents Establishing the Eligibility of Plant and Services | - To establish the eligibility of the plant and services in accordance with ITB 5, Bidders shall complete the country of origin declarations in the Price Schedule Forms, included in Section 4 (Bidding Forms). |
| - Documents Establishing the Eligibility and Qualifications of the Bidder | - To establish its eligibility and qualifications to perform the Contract in accordance with Section 3 (Evaluation and Qualification Criteria), the Bidder shall provide the information requested in the corresponding information sheets included in Section 4 (Bidding Forms). |
|  | - Domestic Bidders, individually or in joint ventures, applying for eligibility for domestic preference shall supply all information required to satisfy the criteria for eligibility as described in ITB 35. |
| - Documents Establishing Conformity of the Plant and Services | - The documentary evidence of the conformity of the plant and services to the Bidding Document may be in the form of literature, drawings, and data, and shall furnish: - a detailed description of the essential technical and performance characteristics of the plant and services, including the functional guarantees of the proposed plant and services, in response to the specification; - a list giving full particulars, including available sources, of all spare parts and special tools necessary for the proper and continuing functioning of the plant for the period named in the BDS, following completion of plant and services in accordance with provisions of the contract; and - a commentary on the Employer’s Specifications and adequate evidence demonstrating the substantial responsiveness of the plant and services to those specifications. Bidders shall note that standards for workmanship, materials, and equipment designated by the Employer in the Bidding Document are intended to be descriptive (establishing standards of quality and performance) only and not restrictive. The Bidder may substitute alternative standards, brand names, and/or catalog numbers in its Bid, provided that it demonstrates to the Employer’s satisfaction that the substitutions are substantially equivalent or superior to the standards designated in the Specifications. |
| - Technical Proposal, Subcontractors | - The Bidder shall furnish a Technical Proposal including a statement of work methods, equipment, personnel, schedule, and any other information as stipulated in Section 4 (Bidding Forms), in sufficient detail to demonstrate the adequacy of the Bidders’ proposal to meet the work requirements and the completion time. |
|  | - For major items of plant and services as listed by the Employer in Criterion 2.5 of Section 3 (Evaluation and Qualification Criteria), which the Bidder intends to purchase or subcontract, the Bidder shall give details of the name and nationality of the proposed Subcontractors, including Manufacturers, for each of those items. In addition, the Bidder shall include in its Bid information establishing compliance with the requirements specified by the Employer for these items. Bidders are free to list more than one Subcontractor against each item of the plant and services. Quoted rates and prices will be deemed to apply to whichever Subcontractor is appointed, and no adjustment of the rates and prices will be permitted. |
|  | - The Bidder shall be responsible for ensuring that any Subcontractor proposed complies with the requirements of ITB 4, and that any plant, or services to be provided by the Subcontractor comply with the requirements of ITB 5 and ITB 15.1 |
| - Bid Prices and Discounts | - Unless otherwise specified in the BDS and/or Section 6 (Employer’s Requirements), Bidders shall quote for the entire plant and services on a “single responsibility” basis such that the total Bid price covers all the Contractor’s obligations mentioned in or to be reasonably inferred from the Bidding Document in respect of the design, manufacture, including procurement and subcontracting (if any), delivery, construction, installation, and completion of the plant. This includes all requirements under the Contractor’s responsibilities for testing, pre-commissioning and commissioning of the plant and, where so required by the Bidding Document, the acquisition of all permits, approvals, and licenses, etc.; the operation, maintenance, and training services and such other items and services as may be specified in the Bidding Document, all in accordance with the requirements of the General Conditions. Items against which no price is entered by the Bidder will not be paid for by the Employer when executed and shall be deemed to be covered by the prices for other items. |
|  | - Bidders are required to quote the price for the commercial, contractual, and technical obligations outlined in the Bidding Document. |
|  | - Bidders shall give a breakdown of the prices in the manner and detail called for in the Price Schedules included in Section 4 (Bidding Forms). Where no different Price Schedules are included in the Bidding Document, Bidders shall present their prices in the following manner: Separate numbered Schedules included in Section 4 (Bidding Forms) shall be used for each of the following elements. The total amount from each Schedule (Nos. 1 to 4) shall be summarized in a Grand Summary (Schedule No. 5) giving the total bid price(s) to be entered in the Letter of Bid. Absence of the total bid price in the Letter of Bid may result in the rejection of the Bid. Schedule No. 1: Plant and Mandatory Spare Parts Supplied from Abroad Schedule No. 2: Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country Schedule No. 3: Design Services Schedule No. 4: Installation and Other Services Schedule No. 5 Grand Summary (Schedule Nos. 1 to 4) Schedule No. 6: Recommended Spare Parts Bidders shall note that the plant and mandatory spare parts included in Schedule Nos. 1 and 2 above exclude materials used for civil, building, and other construction works. All such materials shall be included and priced under Schedule No. 4, Installation and Other Services. |
|  | - In the Schedules, Bidders shall give the required details and a breakdown of their prices as follows: - Plant to be Supplied from Abroad (Schedule No. 1): #### the price of the plant shall be quoted carriage and insurance paid (CIP)-named place of destination basis specified in the BDS; #### all customs duties and other taxes paid or payable in the Employer’s country on the plant if the contract is awarded to the Bidder; and #### the total price for the plant - Plant Supplied from Within the Employer’s Country (Schedule No. 2): #### the price of the plant shall be quoted on an EXW Incoterm basis (ex works, ex factory, ex warehouse, ex showroom, as applicable), including all customs duties and sales and other taxes already paid or payable on the components and raw material used in the manufacture or assembly of plant quoted ex works or ex factory, or on the previously imported plant of foreign origin quoted ex warehouse, ex showroom; #### sales tax and other taxes payable in the Employer’s country on the plant if the contract is awarded to the Bidder; and #### the total price for the plant. - Design Services. (Schedule No. 3). Rates or prices shall include all taxes, duties, levies, and charges payable in the Employerʼs country as of 28 days prior to the deadline for submission of Bids. - Installation and Other Services (Schedule No. 4) shall be quoted separately and shall include rates or prices for local transportation, insurance, and other services incidental to delivery of the plant, all labor, contractor’s equipment, temporary works, materials, consumables, and all matters and things of whatsoever nature, including operations and maintenance services, the provision of operations and maintenance manuals, training, etc., where identified in the Bidding Document, as necessary for the proper execution of the installation and other services, including all taxes, duties, levies and charges payable in the Employer’s country as of 28 days prior to the deadline for submission of bids. - Recommended spare parts (Schedule No. 6) shall be quoted separately as specified in either subparagraph (a) or (b) above in accordance with the origin of the spare parts. |
|  | - The current edition of Incoterms, published by the International Chamber of Commerce shall govern. |
|  | - The prices shall be either fixed or adjustable as specified in the BDS. - In the case of Fixed Price, prices quoted by the Bidder shall be fixed during the Bidder’s performance of the contract and not subject to variation on any account. A Bid submitted with an adjustable price quotation will be treated as nonresponsive and rejected. - In the case of Adjustable Price, prices quoted by the Bidder shall be subject to adjustment during performance of the contract to reflect changes in the cost elements such as labor, material, transport and contractor’s equipment in accordance with the procedures specified in the corresponding appendix to the Contract Agreement. A Bid submitted with a fixed price quotation will not be rejected, but the price adjustment will be treated as zero. Bidders are required to indicate the source of labor and material indexes in the corresponding Form in Section 4 (Bidding Forms). |
|  | - If so indicated in BDS 1.1, Bids are being invited for individual lots (contracts) or for any combination of lots (packages). Bidders wishing to offer any price reduction (discount) for the award of more than one contract shall specify in their Letter of Bid the price reductions applicable to each package, or alternatively, to individual contracts within the package, and the manner in which the price reductions will apply. |
| - Currencies of Bid and Payment | - The currency(ies) of the bid shall be, as specified in the BDS. - Bidders may be required by the Employer to justify, to the Employerʼs satisfaction, their local and foreign currency requirements. |
| - Period of Validity of Bids | - Bids shall remain valid for the period specified in the BDS after the bid submission deadline date prescribed by the Employer. A bid valid for a shorter period shall be rejected by the Employer as non-responsive. |
|  | - In exceptional circumstances, prior to the expiration of the bid validity period, the Employer may request Bidders to extend the period of validity of their Bids. The request and the responses shall be made in writing. If a bid security is requested in accordance with ITB 21, it shall also be extended 28 days beyond the deadline of the extended bid validity period. A Bidder may refuse the request without forfeiting its bid security. A Bidder granting the request shall not be required or permitted to modify its Bid. |
| - Bid Security/Bid Securing Declaration | - Unless otherwise specified in the BDS, the Bidder shall furnish as part of its Bid, in original form, either a Bid-Securing Declaration or a bid security as specified in the BDS. In the case of a bid security, the amount and currency shall be as specified in the BDS. - If a Bid-Securing Declaration is required pursuant to ITB 21.1, it shall use the form included in Section 4 (Bidding Forms). The Employer will declare a Bidder ineligible to be awarded a Contract for a specified period of time, as indicated in the BDS, if a Bid-Securing Declaration is executed. |
|  | - If a bid security is specified pursuant to ITB 21.1, bid security shall be, at the Bidder’s option, in any of the following forms: - an unconditional bank guarantee, - an irrevocable letter of credit, or - a cashier’s or certified check. all from a reputable source from an eligible country as described in Section 5 (Eligible Countries). In the case of a bank guarantee, the bid security shall be submitted using either the Bid Security Form included in Section 4 (Bidding Forms) or another form acceptable to the Employer. The form must include the complete name of the Bidder. The bid security shall be valid for 28 days beyond the original validity period of the Bid, or beyond any period of extension if requested under ITB 20.2. |
|  | - Unless otherwise specified in the BDS, any Bid not accompanied by a substantially compliant bid security or Bid-Securing Declaration, if one is required in accordance with ITB 21.1, shall be rejected by the Employer as non-responsive. |
|  | - If a bid security is specified pursuant to ITB 21.1, the bid security of unsuccessful Bidders shall be returned as promptly as possible upon the successful Bidder’s furnishing of the performance security pursuant to ITB 43. |
|  | - If a bid security is specified pursuant to ITB 21.1, the bid security of the successful Bidder shall be returned as promptly as possible once the successful Bidder has signed the Contract and furnished the required performance security. |
|  | - The bid security may be forfeited or the Bid-Securing Declaration executed: - if a Bidder withdraws its Bid during the period of bid validity specified by the Bidder on the Letter of Bid, except as provided in ITB 20.2, or - if the successful Bidder fails to #### sign the Contract in accordance with ITB 42, or #### furnish a performance security in accordance with ITB 43, or #### accept the arithmetical corrections of its Bid in accordance with ITB 33. |
|  | - The bid security or the Bid-Securing Declaration of a Joint Venture shall be in the name of the Joint Venture that submits the bid. If the Joint Venture has not been legally constituted at the time of bidding, the bid security or the Bid-Securing Declaration shall be in the names of all future partners as named in the letter of intent referred to in ITB 4.1. |
| - Format and Signing of Bid | - The Bidder shall prepare one original set of the documents comprising the Bid as described in ITB 11 and clearly mark it “ORIGINAL.” Alternative Bids, if permitted in accordance with ITB 13, shall be clearly marked “ALTERNATIVE”. In addition, the Bidder shall submit copies of the Bid, in the number specified in the BDS and clearly mark them “COPY.” In the event of any discrepancy between the original and the copies, the original shall prevail. |
|  | - The original and all copies of the Bid shall be typed or written in indelible ink and shall be signed by a person duly authorized to sign on behalf of the Bidder. This authorization shall consist of a written confirmation as specified in the BDS and shall be attached to the Bid. The name and position held by each person signing the authorization must be typed or printed below the signature. All pages of the bid, except for unamended printed literature, shall be signed or initialed by the person signing the Bid. If a Bidder submits a deficient authorization, the Bid shall not be rejected in the first instance. The Employer shall request the Bidder to submit an acceptable authorization within the number of days as specified in the BDS. Failure to provide an acceptable authorization within the prescribed period of receiving such a request shall cause the rejection of the Bid. |
|  | - A Bid submitted by a Joint Venture shall be signed so as to be legally binding on all partners. |
|  | - Any amendments such as interlineations, erasures, or overwriting shall be valid only if they are signed or initialed by the person signing the Bid. |
| - Submission and Opening of Bids |  |
| - Submission, Sealing and Marking of Bids | - Bidders may always submit their Bids by mail or by hand. When so specified in the BDS, Bidders shall have the option of submitting their Bids electronically. Procedures for submission, sealing and marking are as follows: - Bidders submitting Bids by mail or by hand shall enclose the original and each copy of the Bid, including alternative Bids, if permitted in accordance with ITB 13, in separate sealed envelopes, duly marking the envelopes as “ORIGINAL”, “ALTERNATIVE,” and “COPY.” These envelopes containing the original and the copies shall then be enclosed in one single envelope. The rest of the procedure shall be in accordance with ITB 23.2 and ITB 23.3. - Bidders submitting Bids electronically shall follow the electronic bid submission procedures specified in the BDS. |
|  | - The inner and outer envelopes shall - bear the name and address of the Bidder, - be addressed to the Employer in accordance with ITB 24.1, - bear the specific identification of this bidding process indicated in the BDS 1.1, and - bear a warning not to open before the time and date for bid opening. |
|  | - If all envelopes are not sealed and marked as required, the Employer will assume no responsibility for the misplacement or premature opening of the Bid. |
| - Deadline for Submission of Bids | - Bids must be received by the Employer at the address and no later than the date and time indicated in the BDS. |
|  | - The Employer may, at its discretion, extend the deadline for the submission of bids by amending the Bidding Document in accordance with ITB 8, in which case all rights and obligations of the Employer and Bidders previously subject to the deadline shall thereafter be subject to the deadline as extended. |
| - Late Bids | - The Employer shall not consider any Bid that arrives after the deadline for submission of Bids, in accordance with ITB 24. Any Bid received by the Employer after the deadline for submission of Bids shall be declared late, rejected, and returned unopened to the Bidder. |
| - Withdrawal, Substitution, and Modification of Bids | - A Bidder may withdraw, substitute, or modify its Bid after it has been submitted by sending a written notice, duly signed by an authorized representative, and shall include a copy of the authorization in accordance with ITB 22.2, (except that withdrawal notices do not require copies). The corresponding substitution or modification of the Bid must accompany the respective written notice. All notices must be: - prepared and submitted in accordance with ITB 22 and ITB 23 (except that withdrawal notices do not require copies), and in addition, the respective envelopes shall be clearly marked “WITHDRAWAL,” “SUBSTITUTION,” “MODIFICATION;” and - received by the Employer prior to the deadline prescribed for submission of Bids, in accordance with ITB 24. |
|  | - Bids requested to be withdrawn in accordance with ITB 26.1 shall be returned unopened to the Bidders. |
|  | - No Bid may be withdrawn, substituted, or modified in the interval between the deadline for submission of Bids and the expiration of the period of bid validity specified by the Bidder on the Letter of Bid or any extension thereof. |
| - Bid Opening | - The Employer shall open the Bids in public at the address, on the date, and time specified in the BDS in the presence of Bidders` designated representatives and anyone who choose to attend. Any specific electronic bid opening procedures required if electronic bidding is permitted in accordance with ITB 23.1, shall be as specified in the BDS. |
|  | - First, envelopes marked “WITHDRAWAL” shall be opened and read out and the envelope with the corresponding Bid shall not be opened, but returned to the Bidder. No bid withdrawal shall be permitted unless the corresponding withdrawal notice contains a valid authorization to request the withdrawal and is read out at bid opening. Next, envelopes marked “SUBSTITUTION” shall be opened and read out and exchanged with the corresponding Bid being substituted, and the substituted Bid shall not be opened, but returned to the Bidder. No bid substitution shall be permitted unless the corresponding substitution notice contains a valid authorization to request the substitution and is read out at bid opening. Envelopes marked “MODIFICATION” shall be opened and read out with the corresponding Bid. No bid modification shall be permitted unless the corresponding modification notice contains a valid authorization to request the modification and is read out at bid opening. Only envelopes that are opened and read out at bid opening shall be considered further. |
|  | - All other envelopes shall be opened one at a time, reading out the name of the Bidder and whether there is a modification; the Bid Price(s), including any discounts and alternative Bids; the presence of a bid security, or a Bid-Securing Declaration, if required; and any other details as the Employer may consider appropriate. Only discounts and alternative Bids read out at bid opening shall be considered for evaluation. Unless otherwise specified in the BDS, all pages of the Letter of Bid and Price Schedules are to be initialed by at least three representatives of the Employer attending the bid opening. No Bid shall be rejected at bid opening except for late Bids, in accordance with ITB 25.1. |
|  | - The Employer shall prepare a record of the bid opening that shall include, as a minimum: the name of the Bidder and whether there is a withdrawal, substitution, or modification; the Bid Price, per lot if applicable, including any discounts and alternative Bids; and the presence or absence of a bid security or a Bid-Securing Declaration, if one was required. The Bidders’ representatives who are present shall be requested to sign the record. The omission of a Bidder’s signature on the record shall not invalidate the contents and effect of the record. A copy of the record shall be distributed to all Bidders who submitted Bids on time, and posted online when electronic bidding is permitted. |
| - Evaluation and Comparison of Bids |  |
| - Confidentiality | - Information relating to the evaluation of Bids and recommendation of contract award shall not be disclosed to Bidders or any other persons not officially concerned with such process until information on the Contract award is communicated to all Bidders. |
|  | - Any attempt by a Bidder to influence the Employer in the evaluation of the Bids or Contract award decisions may result in the rejection of its Bid. |
|  | - Notwithstanding ITB 28.2, from the time of bid opening to the time of Contract award, if any Bidder wishes to contact the Employer on any matter related to the bidding process, it should do so in writing. |
| - Clarification of Bids | - To assist in the examination, evaluation, and comparison of the Bids, and qualification of the Bidders, the Employer may, at its discretion, ask any Bidder for a clarification of its Bid. Any clarification submitted by a Bidder that is not in response to a request by the Employer shall not be considered. The Employer’s request for clarification and the response shall be in writing. No change in the prices or substance of the Bid shall be sought, offered, or permitted, except to confirm the correction of arithmetic errors discovered by the Employer in the evaluation of the Bids, in accordance with ITB 33. |
|  | - If a Bidder does not provide clarifications of its Bid by the date and time set in the Employer’s request for clarification, its Bid may be rejected. |
| - Deviations, Reservations, and Omissions | - During the evaluation of Bids, the following definitions apply: - “Deviation” is a departure from the requirements specified in the Bidding Document; - “Reservation” is the setting of limiting conditions or withholding from complete acceptance of the requirements specified in the Bidding Document; and - “Omission” is the failure to submit part or all of the information or documentation required in the Bidding Document. |
| - Determination of Responsiveness | - The Employer’s determination of a bid’s responsiveness is to be based on the contents of the Bid itself, as defined in ITB11. |
|  | - A substantially responsive Bid is one that meets the requirements of the Bidding Document without material deviation, reservation, or omission. A material deviation, reservation, or omission is one that, - if accepted, would: #### affect in any substantial way the scope, quality, or performance of the plant and services specified in the Contract; or #### limit in any substantial way, inconsistent with the Bidding Document, the Employer’s rights or the Bidder’s obligations under the proposed Contract; or - if rectified, would unfairly affect the competitive position of other Bidders presenting substantially responsive Bids. |
|  | - The Employer shall examine the technical aspects of the Bid submitted in accordance with ITB 17, Technical Proposal, in particular, to confirm that all requirements of Section 6 (Employer’s Requirements) have been met without any material deviation, reservation, or omission. |
|  | - If a Bid is not substantially responsive to the requirements of the Bidding Document, it shall be rejected by the Employer and may not subsequently be made responsive by correction of the material deviation, reservation, or omission. |
| - Nonmaterial Nonconformities | - Provided that a Bid is substantially responsive, the Employer may waive any nonconformities in the Bid that do not constitute a material deviation, reservation, or omission. |
|  | - Provided that a Bid is substantially responsive, the Employer may request that the Bidder submit the necessary information or documentation, within a reasonable period of time, to rectify nonmaterial nonconformities in the Bid related to documentation requirements. Requesting information or documentation on such nonconformities shall not be related to any aspect of the price of the Bid. Failure of the Bidder to comply with the request may result in the rejection of its Bid. |
|  | - Provided that a bid is substantially responsive, the Employer shall rectify quantifiable nonmaterial nonconformities related to the Bid Price. To this effect, the Bid Price shall be adjusted, for comparison purposes only, to reflect the price of a missing or nonconforming item or component. The adjustment shall be made using the method indicated in Section 3 (Evaluation and Qualification Criteria). |
| - Correction of Arithmetical Errors | - Provided that the Bid is substantially responsive, the Employer shall correct arithmetical errors on the following basis: - where there are errors between the total of the amounts given under the column for the price breakdown and the amount given under the Total Price, the amounts given under the column for the price breakdown shall prevail and the Total Price will be corrected accordingly; - where there are errors between the total of the amounts of Schedule Nos. 1 to 4 and the amount given in Schedule No. 5 (Grand Summary), the total of the amounts of Schedule Nos. 1 to 4 shall prevail and the Schedule No. 5 (Grand Summary) will be corrected accordingly; - if there is a discrepancy between the grand total price given in Schedule No. 5 (Grand Summary) and the bid amount in item (c) of the Letter of Bid, the grand total price given in Schedule No. 5 (Grand Summary) will prevail and the bid amount in item (c) of the Letter of Bid will be corrected; and - if there is a discrepancy between words and figures, the amount in words shall prevail, unless the amount expressed in words is related to an arithmetical error, in which case the amount in figures shall prevail subject to (a), (b), and (c) above. |
|  | - If the Bidder that submitted the lowest evaluated Bid does not accept the correction of errors, its Bid shall be disqualified and its bid security may be forfeited, or its Bid-Securing Declaration executed. |
| - Conversion to Single Currency | - For evaluation and comparison purposes, the currency(ies) of the Bid shall be converted into a single currency as specified in the BDS . |
| - Evaluation of Bids | - The Employer shall use the criteria and methodologies indicated in this clause. No other evaluation criteria or methodologies shall be permitted. |
|  | - Technical Evaluation The Employer will carry out a detailed technical evaluation of the Bids not previously rejected as being substantially nonresponsive, to determine whether the technical aspects are in compliance with the Bidding Document. The Bid that does not meet required minimum acceptable standards of completeness, consistency and detail, and the specified minimum and/or maximum requirements for specified functional guarantees will be treated as nonresponsive and hence rejected. To reach such a determination, the Employer will examine and compare the technical aspects of the bids on the basis of the information supplied by the Bidders, taking into account the following: - overall completeness and compliance with the Employer’s Requirements; deviations from the Employer’s Requirements; conformity of the plant and services offered with specified performance criteria; suitability of the plant and services offered in relation to the environmental and climatic conditions prevailing at the site; and quality, function and operation of any process control concept included in the Bid. The Bid that does not meet minimum and/or maximum acceptable standards of completeness, consistency and detail will be rejected for nonresponsiveness; - type, quantity, and long-term availability of mandatory and recommended spare parts and maintenance services; and - other relevant factors, if any, listed in Section 3 (Evaluation and Qualification Criteria). |
|  | - Where alternative technical solutions have been allowed in accordance with ITB 13, and offered by the Bidder, the Employer will make a similar evaluation of the alternatives. Where alternatives have not been allowed but have been offered, they shall be ignored. |
|  | - Economic Evaluation I. To evaluate a Bid, the Employer shall consider the following: - the bid price, excluding provisional sums and the provision, if any, for contingencies in the Price Schedules; - price adjustment for correction of arithmetical errors in accordance with ITB 33.1; - price adjustment due to discounts offered in accordance with ITB 18.7; - price adjustment due to quantifiable nonmaterial nonconformities in accordance with ITB 32.3; - converting the amount resulting from applying (a) to (c) above, if relevant, to a single currency in accordance with ITB 34; and - the evaluation factors indicated in Section 3 (Evaluation and Qualification Criteria). II. The Employer’s evaluation of a Bid will exclude and not take into account: - in the case of Plant and Mandatory Spare Parts (Schedule No. 1) supplied from abroad, all taxes and duties, applicable in the Employer’s country and payable on the Plant and Mandatory Spare Parts if the Contract is awarded to the Bidder; and - in the case of Plant and Mandatory Spare Parts (Schedule No. 2) supplied from within the Employer’s country, sales and other taxes, applicable in the Employer’s country and payable on the Plant and Mandatory Spare Parts if the Contract is awarded to the Bidder. |
|  | - If price adjustment is allowed in accordance with ITB 18.6, the estimated effect of the price adjustment provisions of the Conditions of Contract, applied over the period of execution of the Contract, shall not be taken into account in bid evaluation. |
|  | - If this Bidding Document allows Bidders to quote separate prices for different lots (contracts), and the award to a single Bidder of multiple lots (contracts), the methodology to determine the lowest evaluated price of the lot (contract) combinations, including any discounts offered in the Letter of Bid, is specified in Section 3 (Evaluation and Qualification Criteria). |
|  | - If the Bid, which results in the lowest Evaluated Bid Price, is seriously unbalanced or front loaded in the opinion of the Employer, the Employer may require the Bidder to produce detailed price analyses for any or all items of the Price Schedules, to demonstrate the internal consistency of those prices with the methods and time schedule proposed. After evaluation of the price analyses, taking into consideration the terms of payments, the Employer may require that the amount of the performance security be increased at the expense of the Bidder to a level sufficient to protect the Employer against financial loss in the event of default of the successful Bidder under the Contract. |
| - Comparison of Bids | - The Employer shall compare all substantially responsive Bids to determine the lowest evaluated Bid, in accordance with ITB 36.4. |
| - Eligibility and Qualification of the Bidder | - The Employer shall determine to its satisfaction whether the Bidder that is selected as having submitted the lowest evaluated and substantially responsive Bid is eligible and meets the qualifying criteria specified in Section 3 (Evaluation and Qualification Criteria). |
|  | - The determination shall be based upon an examination of the documentary evidence of the Bidder’s qualifications submitted by the Bidder, pursuant to ITB 15. |
|  | - An affirmative determination shall be a prerequisite for award of the Contract to the Bidder. A negative determination shall result in disqualification of the Bid, in which event the Employer shall proceed to the next lowest evaluated Bid to make a similar determination of that Bidder’s qualifications to perform satisfactorily. |
|  | - The capabilities of the manufacturers and subcontractors proposed in its Bid for the major items of plant and services to be used by the lowest evaluated Bidder will also be evaluated for acceptability in accordance with Section 3 (Evaluation and Qualification Criteria). Their participation should be confirmed with a letter of intent between the parties, as needed. Should a manufacturer or subcontractor be determined to be unacceptable, the Bid will not be rejected, but the Bidder will be required to propose, without changing its bid price, an acceptable substitute manufacturer or subcontractor meeting the minimum technical specifications stated in Section 6 (Employer’s Requirements). If a Bidder does not provide an acceptable substitute manufacturer or subcontractor by the date and time set in the Employerʼs request for substitution of manufacturer or subcontractor, its Bid may be rejected. - Prior to signing the Contract, the corresponding Appendix to the Contract Agreement shall be completed, listing the approved manufacturers or subcontractors for each item concerned. |
| - Employer’s Right to Accept Any Bid, and to Reject Any or All Bids | - The Employer reserves the right to accept or reject any Bid, and to annul the bidding process and reject all Bids at any time prior to contract award, without thereby incurring any liability to Bidders. In case of annulment, all Bids submitted and specifically, bid securities, shall be promptly returned to the Bidders. |
| - Award of Contract |  |
| - Award Criteria | - The Employer shall award the Contract to the Bidder whose offer has been determined to be the lowest evaluated Bid and is substantially responsive to the Bidding Document, provided further that the Bidder is determined to be eligible and qualified to perform the Contract satisfactorily. |
| - Notification of Award | - Prior to the expiration of the period of bid validity, the Employer shall notify the successful Bidder, in writing, that its Bid has been accepted. |
|  | - At the same time, the Employer shall also notify all other Bidders of the results of the bidding. The Employer will publish in an English language newspaper or well-known freely accessible website the results identifying the Bid and lot numbers, and the following information: (i) name of each Bidder who submitted a Bid; (ii) bid prices as read out at bid opening; (iii) name and evaluated prices of each bid that was evaluated; (iv) name of Bidders whose Bids were rejected and the reasons for their rejection; and (v) name of the winning Bidder, and the price it offered, as well as the duration and summary scope of the contract awarded. After publication of award, unsuccessful Bidders may request in writing to the Employer for a debriefing seeking explanations on the grounds on which their Bids were not selected. The Employer shall promptly respond in writing to any unsuccessful Bidder who, after publication of contract award, request for a debriefing. |
|  | - Until a formal contract is prepared and executed, the notification of award shall constitute a binding Contract. |
| - Signing of Contract | - Promptly after notification, the Employer shall send the successful Bidder the Contract Agreement. |
|  | - Within 28 days of receipt of the Contract Agreement, the successful Bidder shall sign, date, and return it to the Employer. |
| - Performance Security | - Within 28 days of the receipt of notification of award from the Employer, the successful Bidder shall furnish the performance security in accordance with the Conditions of Contract, subject to ITB 36.7, using for that purpose the Performance Security Form included in Section 9 (Contract Forms), or another form acceptable to the Employer. |
|  | - Failure of the successful Bidder to submit the above-mentioned Performance Security or sign the Contract shall constitute sufficient grounds for the annulment of the award and forfeiture of the bid security or execution of the Bid-Securing Declaration. In that event, the Employer may award the Contract to the next lowest evaluated Bidder whose offer is substantially responsive and is determined by the Employer to be qualified to perform the Contract satisfactorily. |

Section 2 - Bid Data Sheet

This section consists of provisions that are specific to each procurement and supplement the information or requirements included in Section 1 - Instructions to Bidders.

| A. General |  |
| --- | --- |
| ITB 1.1 | The number of the Invitation for Bids (IFB) is: [to be insert] |
|  | The Employer is: Ministry of Environment and Energy of the Republic of Maldives |
|  | The name of the international competitive bidding (ICB) is: Procurement of Plant : Design, Supply, and Installation of a Waste incineration plant with energy recovery The identification number of the ICB is: [to be insert] The number and identification of lots (contracts) comprising this ICB is: 01 lot |
| ITB 2.1 | The Borrower is: Government of Maldives |
|  | The name of the Project is: Small Scale Waste to Energy Project at S. Hithadhoo |
| B. Contents of Bidding Document |  |
| ITB 7.1 | For clarification purposes only, the Employer’s address is: Aishath Nadheema Project Officer National Tender Ministry of Finance and Treasury Ameenee Magu, Male’, 20379 Republic of Maldives Tel: (960) 334 9296, (960) 334 9106, (960) 334 9115 E-mail: aishath.nadheema@finance.gov.mv CC: tender@finance.gov.mv Requests for clarification should be received by the Employer no later than (insert date) |
| ITB 7.4 | A Pre-Bid meeting shall not take place. A site visit conducted by the Employer shall not be organized. |
| C. Preparation of Bids |  |
| ITB 11.1 (l) | The Bidder shall submit with its bid the following additional documents: - Bidders company presentation - Documentary proof for technical and financial capacities - Preliminary layout of the facility (ground view and cross section) - Technical description of the different components - List and amount of consumables - Performance diagram |
| ITB 12.1 | The units and rates in figures entered into the Price Schedules should be typewritten or if written by hand, must be in print form. Price Schedules not presented accordingly may be considered non-responsive. |
| ITB 13.1 | Alternative bids are not permitted |
| ITB 13.2 | Alternatives to the Time Schedule . . . . . . . . . be permitted. If alternatives to the Time Schedule are permitted, the evaluation method will be as specified in Section 3 (Evaluation and Qualification Criteria). |
| ITB 13.4 | Alternative technical solutions shall be permitted for the following parts of the plant and services: - The incinerator plant should be solely a grate incineration solution (other solutions: rotary kiln, pyrolysis etc. are not permitted |
| ITB 16.1 (b) | The period following completion of plant and services in accordance with provisions of the contract shall be 2 years |
| ITB 18.1 | Bidders shall quote for the entire plant and services on a “single responsibility” basis such that the total Bid price covers all the Bidder’s obligations mentioned in or to be reasonably inferred from the Bidding Document in respect of the design, manufacture, including procurement and subcontracting (if any), delivery, construction, installation, and completion of the plant. This includes all requirements under the Contractor’s responsibilities for testing, pre-commissioning, and commissioning of the plant and, where so required by the Bidding Document, the acquisition of all permits, approvals, and licenses, the operation, maintenance, and training services and such other items and services as may be specified in the Bidding Document, all in accordance with the requirements of the General Conditions. The following components or services will be provided under the responsibility of the Employer: The organization and support of all custom clearances and legal matters in the Republic of Maldives |
| ITB 18.4(a)(i) | The Incoterm for quoting plant to be supplied from abroad is: DAP Hithadhoo/Addu City |
| ITB 18.6 | The prices quoted by the Bidder shall be fixed |
| ITB 19.1 | The currencies of the Bid shall be as follows: (a) The prices shall be quoted in USD (US Dollars) or equivalent Maldivian rufiyaa (b) A Bidder expecting to incur a portion of its expenditures in the performance of the Contract in more than one currency, and wishing to be paid accordingly, shall so indicate in the Schedule of Prices and the Letter of Bid. (c) If some of the contract expenditures related to Design, Installation and Other Services are to be incurred in the Employerʼs country, such expenditures shall be quoted in either foreign and/or local currency, depending upon the currency in which the costs are to be incurred. (d) Bidders may be required by the Employer to clarify their local and foreign currency requirements, and to substantiate that the amounts included in the Price Schedules are reasonable and responsive to ITB 18.1 in which case a detailed breakdown of its foreign currency requirements shall be provided by the Bidder. (e) During the performance of the contract, the foreign currency portions of the outstanding balance of the Contract Price may be adjusted by agreement between the Employer and the Contractor to reflect any changes in foreign currency requirements for the contract. Any such adjustment shall be effected by comparing the amounts quoted in the bid with the amounts already used in the Facilities and the Contractor’s future needs for imported items. |
| ITB 20.1 | The bid validity period shall be 90 days. |
| ITB 21.1 | The Bidder shall furnish a bid security in the amount of USD 10,000.00 |
| ITB 21.2 | The ineligibility period will be 2 years |
| ITB 21.4 | Subject to the succeeding sentences, any bid not accompanied by an irrevocable and callable bid security shall be rejected by the Employer as nonresponsive. If a Bidder submits a bid security that (i) deviates in form, amount, and/or period of validity, or (ii) does not provide sufficient identification of the Bidder (including, without limitation, failure to indicate the name of the Joint Venture or, where the Joint Venture has not yet been constituted, the names of all future Joint Venture Partners), |
| ITB 22.1 | In addition to the Original of the Tender, the number of copies required is: 1 authentic hard copy (stamped) , 1 authentic soft copy (stamped & scanned) |
| ITB 22.2 | The written confirmation of authorization to sign on behalf of the Bidder shall consist of a legalized Power of Attorney |
| ITB 22.2 | The Bidder shall submit an acceptable authorization within 14 days. |
| D. Submission and Opening of Bids |  |
| ITB 23.1 | Bidders don’t have the option of submitting their bids electronically. |
| ITB 23.1 (b) | If Bidders shall have the option of submitting their bids electronically, the electronic bidding submission procedures shall be:- |
| ITB 24.1 | For Tender submission purposes only, the Employer’s address is: Mr. Ahmed Mujuthaba, Director General, National Tender Ministry of Finance and Treasury Ameenee Magu, Male’, 20379 Republic of Maldives Tel: (960) 334 9220, (960) 334 9106, (960) 334 9115 Fax: (960) 3320706, (960) 3324432 E-mail: aishath.nadheema@finance.gov.mv tender@finance.gov.mv The deadline for Tender submission is: Date: 28th February 2018 Time: 1100 hrs, Maldivian Time on |
| ITB 27.1 | The Tender opening shall take place at: Street Address: National Tender Ministry of Finance and Treasury Ameenee Magu, Male’, 20379 Republic of Maldives Date: 28th February 2018 Time: 1100 hrs, Maldivian Time on |
| ITB 27.1 | Electronic bid opening procedure shall be as follows:-: |
| ITB 27.3 | The Letter of Bid and Price Schedules shall be initialed by 2 representatives of the Employer attending the Bid opening. |
| E. Evaluation and Comparison of Bids |  |
| ITB 34.1 | The currency that shall be used for bid evaluation and comparison purposes to convert all bid prices expressed in various currencies into a single currency is: USD (US Dollar) The source of the selling exchange rate shall be: The United Nations Operational Rates of Exchanges The date for the selling exchange rate shall be: The last date of submission of the proposals |

Section 3 - Evaluation and Qualification Criteria

## Table of Criteria

1.	Evaluation	3-2

1.1	Technical Evaluation	3-2

1.2	Alternative Technical Solutions	3-2

1.3	Economic Evaluation	3-2

1.4	Multiple Contracts	3-4

2.	Qualification	3-5

2.1	Eligibility	3-5

2.1.1	Nationality	3-5

2.1.2	Conflict of Interest	3-5

2.1.3	ADFD Eligibility	3-5

2.1.4	Government-Owned Enterprise	3-5

2.1.5	United Nations Eligibility	3-5

2.2	Pending Litigation and Arbitration	3-6

2.2.1	Pending Litigation and Arbitration	3-6

2.3 	Financial Situation	3-7

2.3.1	Historical Financial Performance	3-7

2.3.2	Average Annual Turnover	3-7

2.3.3	Financial Resources	3-8

2.4	Bidder's Experience	3-9

2.4.1	Contracts of Similar Size and Nature	3-9

2.4.2	Experience in Key Activities	3-10

2.5	Subcontractors	3-11

# 1.	Evaluation

# 1.1	Technical Evaluation

In addition to the criteria listed in ITB 36.2 (a)–(b), other relevant factors are as follows:

Evaluation of the Bidder’s Technical Proposal will include an assessment of the Bidder’s technical capacity to mobilize key equipment and personnel for the contract, consistent with its proposal regarding work methods, scheduling, and material sourcing in sufficient detail and fully in accordance with the requirements stipulated in Section 6 (Employer’s Requirements).

Noncompliance with equipment and personnel requirements described in Section 6 (Employer’s Requirements) shall not normally be a ground for bid rejection and such noncompliance will be subject to clarification during bid evaluation and rectification prior to contract award

Past performance of the lowest evaluated bidder will be assessed prior to contract award.

Tax clearance of the lowest evaluated bidder shall be checked prior to contract award

# 1.2	Alternative Technical Solutions

Technical alternatives, if permitted under ITB 13.4, will be evaluated as follows:-

# 1.3	Economic Evaluation

In addition to the criteria listed in ITB 36.4 (a)–(e), other relevant factors are as follows:

# 1.3.1	Quantifiable Deviations and Omissions

Quantifiable Deviations and Omissions from the contractual obligations: the evaluation shall be based on the evaluated cost of fulfilling the contract in compliance with all contractual obligations under this Bidding Document.

Pursuant to ITB 32.3, the cost of all quantifiable nonmaterial nonconformities or omissions from the contractual and commercial conditions shall be evaluated. The Employer will make its own assessment of the cost of any nonmaterial nonconformities and omissions for the purpose of ensuring fair comparison of Bids.

# 1.3.2	Time Schedule

Time to complete the plant and services from the effective date specified in Article 3 of the Contract Agreement for determining the time for completion of pre-commissioning activities is: 365 days. No credit will be given for earlier completion.

# 1.3.3	Operating and Maintenance (O&M) Costs

The O&M cost factors for calculating the life cycle cost are as follows:

(a)	Number of years for life cycle 1 year

(b)	Operating costs : 1% of contract amount

(c)	Maintenance costs, including the cost of spare parts for the initial period of operation,

(d)	A rate of 1% in percentage to be used to discount to present value all annual future costs calculated under (b) and (c) for the period specified in (a).

# 1.3.4	Functional Guarantees of the Facilities

The minimum and/or maximum requirements stated in the Specification for functional guarantees required in the Specification are the following:

| Functional Guarantee as required in the Specification | Minimum and/or Maximum, as required in the Specification |
| --- | --- |

For the purposes of evaluation, for each percentage point in performance or efficiency below the norm specified in the Specification but above the minimum acceptable levels also specified there, an adjustment of - will be added to the bid price.

# 1.3.5	Work, Services, Facilities, etc., to Be Provided by the Employer

Where bids include the undertaking of work or the provision of services or facilities by the Employer in excess of the provisions allowed for in the Bidding Document, the Employer shall assess the costs of such additional work, services and/or facilities during the duration of the contract. Such costs shall be added to the bid price for evaluation.

# 1.3.6	Specific Additional Criteria

The following additional criteria will be used in the evaluation: N/A

# 1.3.7	Domestic Preference

No margin of preference shall be applied to any of the services or works included in the contract.

Bidders shall not be permitted or required to modify the mix of local and foreign Plant and Equipment after bid opening.

# 1.4	Multiple Contracts

Works are grouped in multiple contracts and pursuant to ITB 36.6, the Employer will evaluate and compare Bids on the basis of a contract, or a combination of contracts, or as a total of contracts to arrive at the least cost combination for the Employer by taking into account discounts offered by Bidders in case of award of multiple contracts.

If a Bidder submits several successful (lowest evaluated substantially responsive) bids, the evaluation will also include an assessment of the Bidder’s capacity to meet the following aggregated requirements as presented in the bid:

- Average annual turnover,

- Financial resources,

- Equipment to be allocated, and

- Personnel to be fielded.

# 2.	Qualification

It is the legal entity or entities comprising the Bidder, and not the Bidder’s parent companies, subsidiaries, or affiliates, that must satisfy the qualification criteria described below.

# 2.1	Eligibility

| Criteria | Compliance Requirements |  |  |  | Documents |
| --- | --- | --- | --- | --- | --- |
| Requirement | Single Entity | Joint Venture |  |  | Submission Requirements |
|  |  | All Partners Combined | Each Partner | One Partner |  |

# 2.1.1   Nationality

| Nationality in accordance with ITB Subclause 4.2. | must meet requirement | must meet requirement | must meet requirement | not applicable | Forms ELI - 1; ELI - 2 with attachments |
| --- | --- | --- | --- | --- | --- |

# 2.1.2	Conflict of Interest

| No conflicts of interest in accordance with ITB Subclause 4.3. | must meet requirement | must meet requirement | must meet requirement | not applicable | Letter of Bid |
| --- | --- | --- | --- | --- | --- |

# 2.1.3	ADFD Eligibility

| Not having been declared ineligible by ADFD, as described in ITB Subclause 4.4. | must meet requirement | must meet requirement | must meet requirement | not applicable | Letter of Bid |
| --- | --- | --- | --- | --- | --- |

# 2.1.4	Government-Owned Enterprise

| Bidder required to meet conditions of ITB Subclause 4.5. | must meet requirement | must meet requirement | must meet requirement | not applicable | Forms ELI - 1; ELI - 2 with attachments |
| --- | --- | --- | --- | --- | --- |

# 2.1.5	United Nations Eligibility

| Not having been excluded by an act of compliance with a United Nations Security Council resolution in accordance with ITB Subclause 4.7. | must meet requirement | must meet requirement | must meet requirement | not applicable | Letter of Bid |
| --- | --- | --- | --- | --- | --- |

# 2.2	Pending Litigation and Arbitration

Pending litigation and arbitration criterion shall not apply.

2.2.1 Pending Litigation and Arbitration

| Criteria | Compliance Requirements |  |  |  | Documents |
| --- | --- | --- | --- | --- | --- |
| Requirement | Single Entity | Joint Venture |  |  | Submission Requirements |
|  |  | All Partners Combined | Each Partner | One Partner |  |
| All pending litigation and arbitration, if any, shall be treated as resolved against the Bidder and so shall in total not represent more than .50 percent of the Bidder’s net worth calculated as the difference between total assets and total liabilities. | must meet requirement by itself or as partner to past or existing Joint Venture | not applicable | must meet requirement by itself or as partner to past or existing Joint Venture | not applicable | Form LIT - 1 |

# 2.3 	Financial Situation

# 2.3.1	Historical Financial Performance

| Criteria | Compliance Requirements |  |  |  | Documents |
| --- | --- | --- | --- | --- | --- |
| Requirement | Single Entity | Joint Venture |  |  | Submission Requirements |
|  |  | All Partners Combined | Each Partner | One Partner |  |
| Submission of audited financial statements or, if not required by the law of the Bidder’s country, other financial statements acceptable to the Employer, for the last .3 years to demonstrate the current soundness of the Bidder’s financial position. As a minimum, the Bidder’s net worth for the last year calculated as the difference between total assets and total liabilities should be positive. | must meet requirement | not applicable | must meet requirement | not applicable | Form FIN - 1 with attachments |

# 2.3.2	Average Annual Turnover

| Criteria | Compliance Requirements |  |  |  | Documents |
| --- | --- | --- | --- | --- | --- |
| Requirement | Single Entity | Joint Venture |  |  | Submission Requirements |
|  |  | All Partners Combined | Each Partner | One Partner |  |
| Minimum average annual turnover of $ 1,500,000.00calculated as total certified payments received for contracts in progress or completed, within the last 3 years. | must meet requirement | must meet requirement | must meet 25 % of the requirement | must meet 50% of the requirement | Form FIN - 2 |

# 2.3.3	Financial Resources

| Criteria | Compliance Requirements |  |  |  | Documents |
| --- | --- | --- | --- | --- | --- |
| Requirement | Single Entity | Joint Venture |  |  | Submission Requirements |
|  |  | All Partners Combined | Each Partner | One Partner |  |
| For Single Entities: The Bidder must demonstrate that its financial resources defined in FIN - 3, less its financial obligations for its current contract commitments defined in FIN - 4, meet or exceed the total requirement for the Subject Contract of $ 450,000 | must meet requirement | not applicable | not applicable | not applicable | Form FIN – 3 and Form FIN - 4 |
| For Joint Ventures: - One partner must demonstrate that its financial resources defined in FIN - 3, less its financial obligations for its own current contract commitments defined in FIN - 4, meet or exceed its required share of 40%. from the total requirement for the Subject Contract. AND | not applicable | not applicable | not applicable | must meet requirement | Form FIN – 3 and Form FIN - 4 |
| - Each partner must demonstrate that its financial resources defined in FIN - 3, less its financial obligations for its own current contract commitments defined in FIN - 4, meet or exceed its required share of 25%. from the total requirement for the Subject Contract. AND | not applicable | not applicable | must meet requirement | not applicable | Form FIN – 3 and Form FIN - 4 |
| - The joint venture must demonstrate that the combined financial resources of all partners defined in FIN - 3, less all the partners’ total financial obligations for the current contract commitments defined in FIN - 4, meet or exceed the total requirement for the Subject Contract of 1,2 Mio USD | not applicable | must meet requirement | not applicable | not applicable | Form FIN – 3 and Form FIN - 4 |

# 2.4	Bidder’s Experience

# 2.4.1	Contracts of Similar Size and Nature

| Criteria | Compliance Requirements |  |  |  | Documents |
| --- | --- | --- | --- | --- | --- |
| Requirement | Single Entity | Joint Venture |  |  | Submission Requirements |
|  |  | All Partners Combined | Each Partner | One Partner |  |
| Participation in at least one contract that has been successfully or substantially completed within the last 5 years and that is similar to the proposed contract, where the value of the Bidder’s participation exceeds $ 1 million The similarity of the Bidder’s participation shall be based on the physical size, nature of works, complexity, methods, technology or other characteristics as described in Section 6 (Employer’s Requirements). | must meet requirement | not applicable | not applicable | must meet requirement | Form EXP - 1 |

# 2.4.2	Experience in Key Activities

# (Must be complied with by the Bidder. In case of a Joint Venture Bidder, at least one of the partners must have experience in the key activity. If the activity can be subcontracted, the requirement must be specified in criterion 2.5 of Section 3.)

| Criteria | Compliance Requirements |  |  |  | Documents |
| --- | --- | --- | --- | --- | --- |
| Requirement | Single Entity | Joint Venture |  |  | Submission Requirements |
|  |  | All Partners Combined | Each Partner | One Partner |  |
| For the above or other contracts executed during the period stipulated in 2.4.1 above, a minimum experience in the following key activities: | must meet requirements | not applicable | not applicable | must meet requirements | Form EXP - 2 |
| Supply, Installation of Waste incinerator plants |  |  |  |  |  |
| Supply Installation of Heat recovery and Energy production plants |  |  |  |  |  |
| Civil works :concrete works and steel work (halls) |  |  |  |  |  |

# 2.5	Subcontractors

Subcontractors or Manufacturers for the following major items of plant and services must meet the following minimum criteria, herein listed for that item. Failure to comply with this requirement will result in rejection of the subcontractor but not the Bidder.

| Item No. | Description of Item | Minimum Criteria to be met | Documents Submission Requirements |
| --- | --- | --- | --- |
| 1 | Electricity and cable works | At least 10 projects in the past 5 years | Form EXP-3 |
| 2 | Water supply, fire fighting supply works | At least 10 projects in the past 5 years |  |
| 3 | Sewage connection works, earthworks | At least 10 projects in the past 5 years |  |
| 4 | Civil works: Concrete works and steel works | At least 5 projects in the past 5 years, minimum 1 Building work (hall or similar) |  |

In the case of a Bidder who offers to supply and install major items of plant under the contract, which the Bidder did not manufacture or otherwise produce, the Bidder shall provide the Manufacturerʼs authorization, using the form provided in Section 4 (Bidding Forms), showing that the Bidder has been duly authorized by the Manufacturer or producer of the related plant and equipment or component to supply and install that item in the Employerʼs country. Failure to submit the Manufacturer’s authorization at the first instance is considered a minor, nonmaterial omission and shall be subject to clarification. However, failure of the Bidder to submit the omitted authorization shall lead to rejection of the Subcontractor or Manufacturer of the item under evaluation in accordance with ITB 38.4.

Section 4 - Bidding Forms

This section contains the forms to be completed by the Bidder and submitted as part of its Bid.

Table of Forms

Letter of Bid	4-2

Price Schedules	4-4

Schedule No. 1.  Plant and Mandatory Spare Parts Supplied from Abroad	4-5

Schedule No. 2.  Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country	4-6

Schedule No. 3.  Design Services	4-7

Schedule No. 4.  Installation and Other Services	4-8

Schedule No. 5.  Grand Summary	4-9

Schedule No. 6.  Recommended Spare Parts	4-10

Tables of Adjustment Data	4-11

Bid Security	4-12

Bid-Securing Declaration	4-13

Technical Proposal	4-14

Site Organization	4-15

Method Statement	4-16

Mobilization Schedule	4-17

Construction Schedule	4-18

Plant	4-19

Personnel	4-20

Form PER – 1: Proposed Personnel	4-20

Form PER – 2:  Resume of Proposed Personnel	4-21

Equipment	4-22

Proposed Subcontractors/Manufactureres for Major Items of Plant and Services	4-23

Manufacturer's Authorization	4-24

Time Schedule	4-25

Functional Guarantee of the Proposed Facilities	4-26

Bidders Qualification	4-27

Form ELI - 1: Bidder’s Information Sheet	4-28

Form ELI - 2: Joint Venture Information Sheet	4-29

Form LIT - 1: Pending Litigation and Arbitration	4-30

Form FIN - 1: Historical Financial Performance	4-31

Form FIN - 2: Average Annual Turnover	4-32

Form FIN - 3:  Availability of Financial Resources	4-33

Form FIN- 4:  Financial Requirements for Current Contract Commitments	4-34

Form FIN- 5:  Self-Assessment Tool for Bidder's Compliance to Financial Resources	4-35

Form EXP - 1:  Contracts of Similar Size and Nature	4-36

Form EXP - 2:  Experience in Key Activities	4-37

Form EXP - 3:  Subcontractors	4-38

Letter of Bid

-Note-

The bidder must accomplish the Letter of Bid on its letterhead clearly showing the bidder’s complete name and address.

Date:

ICB No.:

Invitation for Bid No.:

To: [. . . insert complete name of the employer . . .]

We, the undersigned, declare that:

- We have examined and have no reservations to the Bidding Documents, including Addenda issued in accordance with Instructions to Bidders (ITB) 8.

- We offer to design, manufacture, test, deliver, install, pre-commission, and commission in conformity with the Bidding Document the following Plant and Services: [. . . insert narrative . . .]

The total price of our Bid, excluding any discounts offered in item (d) below is the sum of

[amount of foreign currency in words], [amount in figures], and [amount of local currency in words], [amount in figures]

The total bid price from the Grand Summary (Schedule No. 5) should be entered by the Bidder inside this box. Absence of the total bid price in the Letter of Bid may result in the rejection of the bid.

- The discounts offered and the methodology for their application are as follows: [. . . insert discounts and methodology for their application if any . . .]

- Our Bid shall be valid for a period of  [. . . insert bid validity period as specified in ITB 20.1 of the BDS . . .] days from the date fixed for the bid submission deadline in accordance with the Bidding Documents, and it shall remain binding upon us and may be accepted at any time before the expiration of that period.

- If our Bid is accepted, we commit to obtain a performance security in accordance with the Bidding Documents.

- We, including any Subcontractors or Manufacturers for any part of the Contract, have or will have nationalities from eligible countries, in accordance with ITB 4.2.

- We, including any Subcontractors or Suppliers for any part of the Contract, do not have any conflict of interest in accordance with ITB 4.3.

- We are not participating, as a Bidder in more than one Bid in this bidding process in accordance with ITB 4.3(e), other than alternative offers submitted in accordance with ITB 13.

- Our firm, its affiliates or subsidiaries, including any Subcontractors or Suppliers for any part of the contract, has not been declared ineligible by ADFD, under the Employer’s country laws or official regulations or by an act of compliance with a decision of the United Nations Security Council.

- [We are not a government-owned enterprise] / [We are a government-owned enterprise but meet the requirements of ITB4.5].

- We have paid, or will pay the following commissions, gratuities, or fees with respect to the bidding process or execution of the Contract:

| Name of Recipient | Address | Reason | Amount |
| --- | --- | --- | --- |
|  |  |  | . |

- We understand that this Bid, together with your written acceptance thereof included in your notification of award, shall constitute a binding contract between us, until a formal contract is prepared and executed.

- We understand that you are not bound to accept the lowest evaluated Bid or any other Bid that you may receive.

- We agree to permit ADFD or its representative to inspect our accounts and records and other documents relating to the bid submission and to have them audited by auditors appointed by ADFD.

- If our Bid is accepted, we commit to mobilizing key equipment and personnel in accordance with the requirements set forth in Section 6 (Employer’s Requirements) and our technical proposal, or as otherwise agreed with the Employer.

Name

In the capacity of

Signed

Duly authorized to sign the Bid for and on behalf of

Date

Price Schedules

PREAMBLE

General

1.	The Price Schedules are divided into separate Schedules as follows:

Schedule No. 1:	Plant and Mandatory Spare Parts Supplied from Abroad

Schedule No. 2:	Plant and Mandatory Spare Parts Supplied from within the Employer’s Country

Schedule No. 3:	Design Services

Schedule No. 4:	Installation and Other Services

Schedule No. 5:	Grand Summary

Schedule No. 6:	Recommended Spare Parts

2.	The Schedules do not generally give a full description of the plant to be supplied and the services to be performed under each item. Bidders shall be deemed to have read the Employer’s Requirements and other sections of the Bidding Document and reviewed the Drawings to ascertain the full scope of the requirements included in each item prior to filling in the rates and prices. The entered rates and prices shall be deemed to cover the full scope as aforesaid, including overheads and profit.

3.	If Bidders are unclear or uncertain as to the scope of any item, they shall seek clarification in accordance with ITB 7 prior to submitting their bid.

Pricing

4.	The units and rates in figures entered into the Price Schedules should be typewritten or if written by hand, must be in print form. Price Schedules not presented accordingly may be considered nonresponsive. Any alterations necessary due to errors, etc., shall be initialed by the Bidder.

As specified in the Bid Data Sheet and Special Conditions of Contract, prices shall be fixed and firm for the duration of the Contract, or prices shall be subject to adjustment in accordance with the corresponding Appendix (Price Adjustment) to the Contract Agreement.

5.	Bid prices shall be quoted in the manner indicated and in the currencies specified in the Instructions to Bidders in the Bidding Document.

For each item, Bidders shall complete each appropriate column in the respective Schedules, giving the price breakdown as indicated in the Schedules.

Prices given in the Schedules against each item shall be for the scope covered by that item as detailed in Section 6 (Employer’s Requirements) or elsewhere in the Bidding Document.

6.	Payments will be made to the Contractor in the currency or currencies indicated under each respective item.

7.	When requested by the Employer for the purposes of making payments or partial payments, valuing variations or evaluating claims, or for such other purposes as the Employer may reasonably require, the Contractor shall provide the Employer with a breakdown of any composite or lump sum items included in the Schedules.

Schedules of Rates and Prices

Bidders shall have the choice to offer material equipment from abroad or locally sources as long as it meets the technical specification.

Schedule No. 1: Plant and Mandatory Spare Parts Supplied from Abroad

| Item | Description | Country of Origin | Quantity | Unit Pricea |  | Total Pricea | Taxes and Duties |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Foreign Currency | CIP | Foreign Currency | Local Currency |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 = 4 x 6 | 8 |
|  | Waste incinerator |  | L.S |  |  |  |  |
|  | Energy recovery facility |  | L.S |  |  |  |  |
|  | Spare parts for waste incinerator |  | L.S |  |  |  |  |
|  | Spare part for energy recovery |  | L.S |  |  |  |  |
| TOTAL Column 7 to be carried forward to Schedule No. 5: Grand Summary |  |  |  |  |  |  |  |
| Name of Bidder |  |  |  |  |  |  |  |
| Signature of Bidder |  |  |  |  |  |  |  |

a 	Specify currencies in accordance with ITB 19.1 of the BDS. Create additional columns for up to a maximum of three foreign currencies if so required.

Country of Origin Declaration Form

| Item | Description | Country |
| --- | --- | --- |

Schedule No. 2:  Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country

| Item | Description | Quantity | Unit Pricea |  | Total EXW Pricea | Sales and other taxes |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Local Currency | EXW Price |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 = 3 x 5 | 7 |
|  | Waste incinerator | L.S |  |  |  |  |
|  | Energy recovery facility | L.S |  |  |  |  |
|  | Spare parts for waste incinerator | L.S |  |  |  |  |
|  | Spare part for energy recovery | L.S |  |  |  |  |
| TOTAL Column 5 to be carried forward to Schedule No. 5: Grand Summary |  |  |  |  |  |  |
| Name of Bidder |  |  |  |  |  |  |
| Signature of Bidder |  |  |  |  |  |  |

a    Specify currency in accordance with ITB 19.1 of the BDS.

b     Column 5  EXW Price shall include all customs duties and sales and other taxes already paid or payable on the components and raw materials used in the manufacture or assembly of the item or the customs duties and sales and other taxes already paid on previously imported items.

Schedule No. 3:  Design Services

| Item | Description | Quantity | Unit Pricea |  | Total Pricea |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Foreign Currency Portion |
| 1 | 2 | 3 | 4 | 5 | 6 = 3 x 4 | 7 = 3 x 5 |
|  | Design services for the complete Installation according to the employers requirements (including structural calculations, shop drawings and as build drawings) | L.S |  |  |  |  |
| TOTAL Columns 6 and 7 to be carried forward to Schedule No. 5: Grand Summary |  |  |  |  |  |  |
| Name of Bidder |  |  |  |  |  |  |
| Signature of Bidder |  |  |  |  |  |  |

a 	Specify currency in accordance with ITB 19.1 of the BDS.

Schedule No. 4:  Installation and Other Services

| Item | Description | Quantity | Unit Pricea |  | Total Pricea |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Foreign Currency Portion |
| 1 | 2 | 3 | 4 | 5 | 6 = 3 x 4 | 7 = 3 x 5 |
| 1 | Civil works according suppliers requirements (Concrete works and steel works (Hall, lining) | L.S |  |  |  |  |
| 2 | Supply works till interface according employer’s requirement (electricity, water, sewerage, etc.) | L.S |  |  |  |  |
| 3 | Testing commissioning, one year maintenance | L.S |  |  |  |  |
| 4 | Connection to the electricity grid in cooperation with power supply operator FENAKA | L.S |  |  |  |  |
| TOTAL Columns 6 and 7 to be carried forward to Schedule No. 5: Grand Summary |  |  |  |  |  |  |
| Name of Bidder |  |  |  |  |  |  |
| Signature of Bidder |  |  |  |  |  |  |

a 	Specify currency in accordance with ITB 19.1 of the BDS.

Schedule No. 5:  Grand Summary

| Schedule No. | Title | Total Pricea |  |
| --- | --- | --- | --- |
|  |  | Foreign | Local |
| 1 | Plant and Mandatory Spare Parts Supplied from Abroad b |  |  |
| 2 | Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country b |  |  |
| 3 | Design Services |  |  |
| 4 | Installation and Other Services |  |  |
| Grand Total to be carried forward to Letter of Bid |  |  |  |
| Name of Bidder |  |  |  |
| Signature of Bidder |  |  |  |

a 		Specify currency in accordance with ITB 19.1 of the BDS. Create additional columns for up to a maximum of three foreign currencies if so required.

b   	Taxes and/or duties from Schedules 1 and 2 may be added to the contract price in accordance with GCC 14 (Taxes and Duties) but excluded from bid evaluation in accordance with ITB 36.4.

Schedule No. 6:  Recommended Spare Parts

| Item | Description | Quantity | Unit Pricea |  | Total Pricea |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | EXW Local Parts Local Currency | CIP Imported Parts Foreign Currency | Local Currency Portion | Foreign Currency Portion |
| 1 | 2 | 3 | 4 | 5 | 6 = 3 x 4 | 7 = 3 x 5 |
|  | To be inserted by bidders |  |  |  |  |  |
| TOTAL |  |  |  |  |  |  |
| Name of Bidder |  |  |  |  |  |  |
| Signature of Bidder |  |  |  |  |  |  |

a 	Specify currency in accordance with ITB 19.1 of the BDS.

Tables of Adjustment Data

To be entered by the bidder

Table A - Local Currency

| Index Code |  |  | Index Description |  |  | Source of Index |  |  | Base Value and Date |  |  | Bidder’s Local Currency Amount |  |  | Bidder’s Proposed Weighting |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Nonadjustable |  |  |  | --- |  |  | --- |  |  | --- |  |  | a: 0.15 b: c: d: e: _________ |  |
|  |  |  |  |  |  |  | Total |  |  |  |  |  | 1.00 |  |  |

Table B - Foreign Currency

Name of Currency: USD (US Dollars)

| Index Code |  | Index Description |  | Source of Index |  | Base Value and Date |  | Bidder’s Currency in Type/Amount |  | Equivalent in FC1 |  | Bidder’s Proposed Weighting |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Nonadjustable |  | --- |  | --- |  | --- |  |  |  | a: 0.15 b: c: d: e: _________ |  |
|  |  |  |  |  |  |  |  | Total |  |  |  | 1.00 |

Bid Security

##### Bank Guarantee

Bank’s name, and address of issuing branch or office

Beneficiary: 	Name and address of the employer

Date:

Bid Security No.:

We have been informed that . . . . . name of the bidder. . . . .  (hereinafter called "the Bidder") has submitted to you its bid dated . . . . . . . . . (hereinafter called "the Bid") for the execution of . . . . . . . . name of contract . . . . . . . under Invitation for Bids No. . . . . . . . . . (“the IFB”).

Furthermore, we understand that, according to your conditions, bids must be supported by a bid guarantee.

At the request of the Bidder, we  . . . . . name of Bank. . . . .  hereby irrevocably undertake to pay you any sum or sums not exceeding in total an amount of . . . . . . . . . .amount in words . . . .  . . . . .  (. . . . . . .amount in figures . . . . . . .  ) upon receipt by us of your first demand in writing accompanied by a written statement stating that the Bidder is in breach of its obligation(s) under the bid conditions, because the Bidder

- has withdrawn its Bid during the period of bid validity specified by the Bidder in the Letter of Bid; or

- does not accept the correction of errors in accordance with the Instructions to Bidders (hereinafter “the ITB”); or

- having been notified of the acceptance of its Bid by the Employer during the period of bid validity, (i) fails or refuses to execute the Contract Agreement, or (ii) fails or refuses to furnish the Performance Security, in accordance with the ITB.

This guarantee will expire (a) if the Bidder is the successful Bidder, upon our receipt of copies of the Contract Agreement signed by the Bidder and the Performance Security issued to you upon the instruction of the Bidder; or (b) if the Bidder is not the successful Bidder, upon the earlier of (i) our receipt of a copy of your notification to the Bidder of the name of the successful Bidder, or (ii) 28 days after the expiration of the Bidder’s bid.

Consequently, any demand for payment under this guarantee must be received by us at the office on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees, ICC Publication No. 458.

. . . . . . . . . . . .Authorized signature(s) and bank’s seal (where appropriate) . . . . . . . . . .

-- Note –

In case of a joint venture, the bid security must be in the name of all partners to the joint venture that submits the bid.

Bid-Securing Declaration

Date: [insert date (as day, month and year)]

Bid No.: [insert number of bidding process]

Alternative No.: [insert identification No if this is a bid for an alternative]

To: [insert complete name of the employer]

We, the undersigned, declare that:

We understand that, according to your conditions, Bids must be supported by a Bid-Securing Declaration.

We accept that we will automatically be suspended from being eligible for bidding in any contract with the Borrower for the period of time of [. . .insert number of years as indicated in ITB 21.2 of the BDS. . .] starting on the date that we receive a notification from the Employer, if we are in breach of our obligation(s) under the bid conditions, because we

- have withdrawn our Bid during the period of bid validity specified in the Letter of Bid; or

- do not accept the correction of errors in accordance with the Instructions to Bidders (hereinafter “the ITB”); or

- having been notified of the acceptance of our Bid by the Employer during the period of bid validity, (i) fail or refuse to execute the Contract; if required, or (ii) fail or refuse to furnish the Performance Security, in accordance with the ITB.

We understand that this Bid-Securing Declaration shall expire if we are not the successful Bidder, upon the earlier of (i) our receipt of your notification to us of the name of the successful Bidder; or (ii) 28 days after the expiration of our Bid.

Signed: [insert signature of person whose name and capacity are shown]

In the capacity of [insert legal capacity of person signing the Bid-Securing Declaration]

Name: [insert complete name of person signing the Bid-Securing Declaration]

Duly authorized to sign the bid for and on behalf of [insert complete name of the bidder]

Dated on ____________ day of __________________, _______ [insert date of signing]

Corporate Seal (where appropriate)

-- Note --In case of a joint venture, the Bid-Securing Declaration must be in the name of all partners to the joint venture that submits the bid.

Technical Proposal

Site Organization

Method Statement

Mobilization Schedule

Construction Schedule

Plant

Personnel

Equipment

Proposed Subcontractors for Major Items of Plant and Services

Manufacturer’s Authorization

Time Schedule

Functional Guarantee of the Proposed Facilities

Site Organization

Method Statement

Mobilization Schedule

Construction Schedule

Plant

Personnel

Form PER – 1: Proposed Personnel

Bidders should provide the details of proposed personnel and their experience record in the relevant Information Forms below for each of the candidate.

Form PER – 1: Proposed Personnel

| 1. | Title of position* |
| --- | --- |
|  | Name |
| 2. | Title of position* |
|  | Name |
| 3. | Title of position* |
|  | Name |
| 4. | Title of position* |
|  | Name |
| etc. | Title of position* |
|  | Name |

-- Note --

* As listed in Section 6 (Employer’s Requirements).

Form PER – 2:  Resume of Proposed Personnel

The Bidder shall provide all the information requested below. Use one form for each position.

| Position |  |  |
| --- | --- | --- |
| Personnel information | Name | Date of birth |
|  | Professional qualifications |  |
| Present employment | Name of employer |  |
|  | Address of employer |  |
|  | Telephone | Contact (manager/personnel officer) |
|  | Fax | E-mail |
|  | Job title | Years with present employer |

Summarize professional experience in reverse chronological order. Indicate particular technical and managerial experience relevant to the project.

| ### From | ### To | ### Company/Project/Position/Relevant Technical and Management Experience |
| --- | --- | --- |

Equipment

Form EQU:  Equipment

The Bidder shall provide adequate information and details to demonstrate clearly that it has the capability to meet the equipment requirements indicated in Section 6 (Employer’s Requirements), using the Forms below. A separate Form shall be prepared for each item of equipment listed, or for alternative equipment proposed by the Bidder.

| Item of Equipment |  |  |
| --- | --- | --- |
| Equipment Information | Name of manufacturer | Model and power rating |
|  | Capacity | Year of manufacture |
| Current Status | Current location |  |
|  | Details of current commitments |  |
| Source | Indicate source of the equipment o Owned o Rented o Leased o Specially manufactured |  |

Omit the following information for equipment owned by the Bidder.

| Owner | Name of owner |  |
| --- | --- | --- |
|  | Address of owner |  |
|  | Telephone | Contact name and title |
|  | Fax | Telex |
| Agreements | Details of rental/lease/manufacture agreements specific to the project |  |

Proposed Subcontractors and/or Manufactures for Major Items of Plant and Services

The following Subcontractors and/or Manufacturers are proposed for carrying out the item of the facilities indicated.  Bidders are free to propose more than one for each item.

| Major Items of Plant and Services | Proposed Subcontractors or Manufacturers | Nationality |
| --- | --- | --- |

Manufacturer's Authorization

Date: [insert date (as day, month and year) of bid submission]

ICB No.: [insert number of bidding process]

To:  [insert complete name of the employer]

WHEREAS

We [insert complete name of the manufacturer or manufacturer’s authorized agent], who are official manufacturers or agent authorized by the Manufacturer of [insert type of goods manufactured], having factories at [insert full address of manufacturer’s factories], do hereby authorize [insert complete name of the bidder] to submit a bid the purpose of which is to provide the following goods, manufactured by us [insert name and/or brief description of the goods], and to subsequently negotiate and sign the Contract.

We hereby extend our full guarantee and warranty in accordance with Clause 27 of the General Conditions of Contract, with respect to the goods offered by the above firm.

Signed: [insert signature(s) of authorized representative(s) of the manufacturer]

Name: [insert complete name(s) of authorized representative(s) of the manufacturer]

Title: [insert title]

Duly authorized to sign this Authorization on behalf of: [insert complete name of the manufacturer]

Dated on ____________ day of __________________, _______ [insert date of signing]

-- Note --

The bidder shall require the manufacturer to fill out this form in accordance with the instructions indicated. This letter of authorization should be signed by a person with the proper authority to sign documents that are binding on the manufacturer. The bidder shall include it in its bid, if so indicated in the BDS.

Time Schedule

To be used by Bidder when alternative Time for Completion is invited in ITB 13.2.

Functional Guarantee of the Proposed Facilities

Form FUNC

The Bidder shall copy on the left column of the table below, the identification of each functional guarantee required in the Specification and stated by the Employer in EQC 1.3.4 of Section 3, Evaluation and Qualification Criteria, and on the right column, provide the corresponding value for each functional guarantee of the proposed plant and equipment.

| Functional Guarantee [as required by the Employer in Section 3] | Functional Guarantee Value Offered by the Bidder |
| --- | --- |
| 1. The following parameters are guaranteed values |  |
| Throughput = 1.5 t/h |  |
| field storage 40 m³/h |  |
| transport capacity 1.5 t/h |  |
| operation time 330 days/year |  |
| 2. emission values |  |
| total dust ≤ 10 mg/Nm³ |  |
| total hydrocarbons (THC) 10 mg/Nm³ |  |
| carbon monoxide CO ≤ 50 mg/Nm³ |  |
| HCl ≤10 mg/Nm³ |  |
| SO2 ≤ 50 mg/Nm³ |  |
| Cd ≤ 0.05 mg/Nm³ |  |
| TL ≤ 0.05 mg/Nm³ |  |
| Pb, Cr (Sb, Cu) ≤ 0.5 mg/Nm³ |  |
| As, Co, Ni (Mn, V, Sn) ≤ 0.5 mg/Nm³ |  |
| Hg ≤ 0.05 mg/Nm³ (Basis = 11 Vol.-% O2, dry flue gas) |  |

Bidders Qualification

To establish its qualifications to perform the contract in accordance with Section 3 (Evaluation and Qualification Criteria) the Bidder shall provide the information requested in the corresponding Information Sheets included hereunder.

Form ELI - 1: Bidder’s Information Sheet

| Bidder’s Information |  |
| --- | --- |
| Bidder’s legal name |  |
| In case of a Joint Venture, legal name of each partner |  |
| Bidder’s country of constitution |  |
| Bidder’s year of constitution |  |
| Bidder’s legal address in country of constitution |  |
| Bidder’s authorized representative (name, address, telephone number(s), fax number(s), e-mail address) |  |
| Attached are copies of the following documents: - 1. In case of a single entity, articles of incorporation or constitution of the legal entity named above, in accordance with ITB 4.1 and ITB 4.2 - 2. Authorization to represent the firm or Joint Venture named above, in accordance with ITB 22.2 - 3. In case of a Joint Venture, a letter of intent to form a Joint Venture or Joint Venture agreement, in accordance with ITB 4.1 - 4. In case of a government-owned enterprise, any additional documents not covered under 1 above required to comply with ITB 4.5 |  |

Form ELI - 2: Joint Venture Information Sheet

Each member of the Joint Venture must fill out this form separately. Subcontractor must fill out this form.

| Joint Venture/Subcontractor Information |  |
| --- | --- |
| Bidder’s legal name |  |
| Joint Venture Partner’s or Subcontractor’s legal name |  |
| Joint Venture Partner’s or Subcontractor’s country of constitution |  |
| Joint Venture Partner’s or Subcontractor’s year of constitution |  |
| Joint Venture Partner’s or Subcontractor’s legal address in country of constitution |  |
| Joint Venture Partner’s or Subcontractor’s authorized representative information (name, address, telephone number(s), fax number(s), e-mail address) |  |
| Attached are copies of the following documents: - 1. Articles of incorporation or constitution of the legal entity named above, in accordance with ITB 4.1 and ITB 4.2 - 2. Authorization to represent the firm named above, in accordance with ITB 22.2 - 3. In the case of a government-owned enterprise, documents establishing legal and financial autonomy and compliance with commercial law, in accordance with ITB 4.5 |  |

Subcontractors are those listed in Technical Proposal – Proposed Subcontractors and/or Manufacturers for Major Items of Plant and Services.

Form LIT – 1: Pending Litigation and Arbitration

Each Bidder must fill out this form if so required under Criterion 2.2 of Section 3 (Evaluation and Qualification Criteria) to describe any pending litigation or arbitration formally commenced against it.

In case of a Joint Venture, each Joint Venture Partner must fill out this form separately and provide the Joint Venture Partner’s name below:

Joint Venture Partner: ___________________

| Pending Litigation and Arbitration |  |  |  |
| --- | --- | --- | --- |
| Choose one of the following: - No pending litigation and arbitration. - Below is a description of all pending litigation and arbitration against the Bidder (or each Joint Venture member if Bidder is a Joint Venture). |  |  |  |
| Year | Matter in Dispute | Value of Pending Claim in $ Equivalent | Value of Pending Claim as a Percentage of Net Worth |

- Note -This form shall only be included if Criterion 2.2 of Section 3 (Evaluation and Qualification Criteria) is applicable.

Form FIN - 1: Historical Financial Performance

Each Bidder must fill out this form.

In case of a Joint Venture, each Joint Venture Partner must fill out this form separately and provide the Joint Venture Partner’s name below:

Joint Venture Partner: ___________________

|  | - Financial Data for Previous . . . . . Years [$ Equivalent] |  |  |
| --- | --- | --- | --- |
|  | Year 1: | Year 2: | Year __: |

Information from Balance Sheet

| Total Assets (TA) |  |  |  |
| --- | --- | --- | --- |
| Total Liabilities (TL) |  |  |  |
| Net Worth = TA – TL |  |  |  |
| Current Assets (CA) |  |  |  |
| Current Liabilities (CL) |  |  |  |
| Working Capital = CA – CL |  |  |  |

| Most Recent Working Capital |  | To be obtained for most recent year and carried forward to FIN - 3 Line 1; in case of Joint Ventures, to the corresponding Joint Venture Partner’s FIN – 3. |
| --- | --- | --- |

Information from Income Statement

| Total Revenues |  |  |  |
| --- | --- | --- | --- |
| Profits Before Taxes |  |  |  |
| Profits After Taxes |  |  |  |
| - Attached are copies of financial statements (balance sheets including all related notes, and income statements) for the last . . . . . . . years, as indicated above, complying with the following conditions: - Unless otherwise required by Section 3 of the Bidding Documents, all such documents reflect the financial situation of the legal entity or entities comprising the Bidder and not the Bidder’s parent companies, subsidiaries, or affiliates. - Historical financial statements must be audited by a certified accountant. - Historical financial statements must be complete, including all notes to the financial statements. - Historical financial statements must correspond to accounting periods already completed and audited (no statements for partial periods shall be requested or accepted). |  |  |  |

Form FIN - 2: Average Annual Turnover

Each Bidder must fill out this form.

The information supplied should be the Annual Turnover of the Bidder or each member of a Joint Venture in terms of the amounts billed to clients for each year for work in progress or completed, converted to US dollars at the rate of exchange at the end of the period reported.

In case of a Joint Venture, each Joint Venture Partner must fill out this form separately and provide the Joint Venture Partner’s name below:

Joint Venture Partner: ___________________

| - Annual Turnover Data for the Last . . . . . Years |  |  |  |
| --- | --- | --- | --- |
| Year | Amount Currency | Exchange Rate | $ Equivalent |
| Average Annual Turnover |  |  |  |

Form FIN – 3:  Availability of Financial Resources

Bidders must demonstrate sufficient financial resources, usually comprising of Working Capital supplemented by credit line statements or overdraft facilities and others to meet the Bidder’s financial requirements for

- its current contract commitments, and

- the subject contract.

In case of a Joint Venture, each Joint Venture Partner must fill out this form separately and provide the Joint Venture Partner’s name below:

Joint Venture Partner: ___________________

| Financial Resources |  |  |
| --- | --- | --- |
| No. | Source of financing | Amount ($ equivalent) |
| 1 | Working Capital (to be taken from FIN - 1) |  |
| 2 | Credit Linea |  |
| 3 | Other Financial Resources |  |
| Total Available Financial Resources |  |  |

a 	To be substantiated by a letter from the bank issuing the line of credit.

Form FIN- 4:  Financial Requirements for Current Contract Commitments

Bidders (or each Joint Venture partner) should provide information on their current commitments on all contracts that have been awarded, or for which a letter of intent or acceptance has been received, or for contracts approaching completion, but for which an unqualified, full completion certificate has yet to be issued.

In case of a Joint Venture, each Joint Venture Partner must fill out this form separately and provide the Joint Venture Partner’s name below:

Joint Venture Partner: ___________________

- Current Contract Commitments

| ### No. | ### Name of Contract | ### Employer’s Contact (Address, Tel, Fax) | Contract Completion ### Date | Outstanding Contract Value (X) a | Remaining Contract Period in months (Y) b | Monthly Financial Resources Requirement (X / Y) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |
| Total Monthly Financial Requirement for Current Contract Commitments |  |  |  |  |  | $ . . . . . . . . . . . . . . . . . |

a	Remaining outstanding contract values to be calculated from 28 days prior to the bid submission deadline ($ equivalent based on the foreign exchange rate as of the same date).

b	Remaining contract period to be calculated from 28 days prior to bid submission deadline.

Form FIN - 5: Self-Assessment Tool for Bidder’s Compliance to Financial Resources (Criterion 2.3.3 of Section 3)

This form requires the same information submitted in Forms FIN - 3 and FIN - 4. All conditions of “Available Financial Resources Net of CCC ≥ Requirement for the Subject Contract” must be satisfied to qualify.

Form FIN - 5A: For Single Entities

| For Single Entities: (A) | Total Available Financial Resources from FIN – 3 (B) | Total Monthly Financial Requirement for Current Contract Commitments (CCC) from FIN – 4 (C) | Available Financial Resources Net of CCC D = (B - C) | Requirement for the Subject Contract (E) | Results: Yes or No [D must be greater than or equal to E] (F) |
| --- | --- | --- | --- | --- | --- |
| _________ (Name of Bidder) |  |  |  | . . . . . . . . . . ._ |  |

Form FIN - 5B: For Joint Ventures

| For Joint Ventures: (A) | Total Available Financial Resources from FIN – 3 (B) | Total Monthly Financial Requirement for Current Contract Commitments (CCC) from FIN – 4 (C) | Available Financial Resources Net of CCC D = (B - C) | Requirement for the Subject Contract (E) | Results: Yes or No [D must be greater than or equal to E] (F) |
| --- | --- | --- | --- | --- | --- |
| One Partner: |  |  |  |  |  |
| ____________ (Name of Partner) |  |  |  | . . . . . . . . . . . |  |
| Each Partner: |  |  |  |  |  |
| _____________ (Name of Partner 1) |  |  |  | . . . . . . . . . . . |  |
| _____________ (Name of Partner 2) |  |  |  | . . . . . . . . . . . |  |
| _____________ (Name of Partner 3) |  |  |  | . . . . . . . . . . . |  |
| All partners combined | ∑ D = Sum of available financial resources net of current contract commitments for all partners |  | ∑ D = _______ | . . . . . . . . . . . |  |

- Note -

Form FIN – 5 is made available for use by the bidder as a self-assessment tool, and by the employer as an evaluation work sheet, to determine compliance with the financial resources requirement as stated in 2.3.3. Failure to submit Form FIN - 5 by the Bidder shall not lead to bid rejection.

Form EXP – 1:  Contracts of Similar Size and Nature

Fill out one (1) form per contract.

| - Contract of Similar Size and Nature |  |  |  |
| --- | --- | --- | --- |
| Contract No . . . . . . of . . . . . | Contract Identification |  |  |
| Award Date |  | Completion Date |  |
| Role in Contract | - Contractor | - Management Contractor | - Subcontractor |
| Total Contract Amount | $ |  |  |
| If partner in a Joint Venture or subcontractor, specify participation of total contract amount | Percent of Total | Amount |  |
| Employer’s name Address Telephone number Fax number E-mail |  |  |  |
| - Description of the Similarity in Accordance with Criterion 2.4.1 of Section 3 (Evaluation and Qualification Criteria) |  |  |  |

Form EXP - 2:  Experience in Key Activities

Fill out one (1) form per contract.

| - Contract with Similar Key Activities |  |  |  |
| --- | --- | --- | --- |
| Contract No . . . . . . of . . . . . | Contract Identification |  |  |
| Award Date |  | Completion Date |  |
| Role in Contract | - Contractor | - Management Contractor | - Subcontractor |
| Total Contract Amount | $ |  |  |
| If partner in a Joint Venture or subcontractor, specify participation of total contract amount | Percent of Total | Amount |  |
| Employer’s name Address Telephone number Fax number E-mail |  |  |  |
| - Description of the Key Activities in Accordance with Criterion 2.4.2 of Section 3 (Evaluation and Qualification Criteria) |  |  |  |

Form EXP - 3: Subcontractors

Fill out one (1) form per contract.

| - Contract for the Major Items |  |  |  |
| --- | --- | --- | --- |
| Contract No . . . . . . of . . . . . . | Contract Identification |  |  |
| Award Date |  | Completion Date |  |
| Role in Contract | - Contractor | - Management Contractor | - Subcontractor |
| Total Contract Amount | $ |  |  |
| If partner in a Joint Venture or subcontractor, specify participation of total contract amount | Percent of Total | Amount |  |
| Employers name Address Telephone number Fax number E-mail |  |  |  |
| - Description of the Major Items in Accordance with Criterion 2.5 of Section 3 (Evaluation and Qualification Criteria) |  |  |  |

Section 5 - Eligiblility

This Section contains the list of eligible countries.[list of eligible countries]

Bidders may submit bids if none of the following reasons for exclusion apply:

- participation of a bidder is ruled out by sanctions issued by the United Nations

- The bidder is or was involved as a consultant in the preparation or implementation of the project. The same applies to an enterprise or an individual that is closely connected to the bidder under a company group or a similar business link, or to several enterprises or individuals associated correspondingly. (exception: In BOT projects or turnkey projects a participation of future suppliers or manufacturers may even be desirable);

- failure to submit a declaration of undertaking in accordance with Bid forms

- the bidder is legally barred from the procurement process in the country of the contracting agency on the grounds of previous violations of regulations on fraud and corruption

- the bidders or sub-contractors to be contracted for considerable portions of the contract are enterprises economically intertwined with the contracting agency in the host country and/or state-controlled enterprises that are not legally or financially independent

Section 6 - Employer’s Requirements

Table of Contents

1	Scope of Supply of Plant and Services						6-2

2.	Specifications										6-5

3.  	Drawings										6-10

4.  	Supplementary Information								6-10

5.  	Certificates										6-10

5.1  Form of Completion Certificate	6-10

5.2  Form of Operational Acceptance Certificate	6-10

6. 	Change Orders									6-10

6.1. 	Change Order Procedure	6-10

6.1.1	General	6-10

6.1.2 	Change Order Log	6-10

6.1.3	References for Changes	6-10

6.2	Change Order Forms	6-10

6.2.1	Request for Change Proposal Form	6-10

6.2.2  Estimate for Change Proposal Form	6-10

6.2.3  Acceptance of Estimate Form	6-10

6.2.4  Change Proposal Form	6-10

6.2.5  Change Order Form	6-10

6.2.6  Pending Agreement Change Order Form	6-10

6.2.7  Application for Change Proposal Form	6-10

7. 	Personnel Requirements								6-19

8. 	Equipment Requirements								6-20

### 1. Scope of Supply of Plant and Services

The scope of the Contract is the design and Installation of a Municipal Solid Waste incineration plant with energy recovery power generation at Hithadhoo, Addu City, including all kind of required civil foundation works for all machineries & equipments like boiler, shredder, turbine etc., excluding other civil works like structures main building ,halls, storage building, building foundations, steel structures, supply, all necessary temporary structures for site development, in compliance with the land development and construction conditions, Buildings, annexes, engineering networks. The construction will be made on the basis of the approved Working Design.

The dimensioning quantities are 50 tons/day of residual MSW and it is essential to provide 1MW electricity power to the central grid at Hithadhoo. Waste composition is given in the Table 1 & 2 below and the Table 3 explains the physical parameters of different types of waste.

It is assumed that the waste delivered to the incineration plant will be gathered from households, hotel and resorts

The designed, constructed and delivered operational plant shall fulfil the Employer’s Requirements specified in this Tender Dossier, National standards or international standards recommended by the Environmental Protection Agency, where national standards are non-existed, and the environmental protection legislation.

A complete feasibility study could be provided by the client upon request of the contractor after award

Table 1: Household waste composition

| Waste composition | % | Trend |
| --- | --- | --- |
| Organics | 70% | Constant |
| Garden waste | 30% |  |
| Kitchen waste | 30% |  |
| other organics | 10% |  |
| Paper & cardboard | 7% | Constant |
| Glass | 3% | decrease by 1% |
| Plastics | 5% | increase in the next years probably by 2-3 % |
| Metals | 4% | Constant |
| Hazardous wastes (including clinical) | 2% | Constant |
| Other (inert & dust)/mixed waste | 9% | Decrease |
| Total | 100% |  |

Table 2: Resort waste composition

| Waste composition | % | Trend |
| --- | --- | --- |
| Organics | 74% | Constant |
| Garden waste | 19% |  |
| Kitchen waste | 45% |  |
| other organics | 10% |  |
| Paper & cardboard | 9% | Constant |
| Glass | 5% | Constant |
| Plastics | 5% | Constant |
| Metals | 2% | Constant |
| Hazardous wastes (including clinical) | 0,5% | Constant |
| Other (inert & dust)/mixed waste | 4,5% | Constant |
| Total | 100% |  |

Table 3: Physical parameters of waste

| Waste composition | Calorific value kJ/kg |  | Water content % |  | Glowing loss (dry substance) % |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Min | Max | min | max | min | Max |
| Organics |  |  |  |  |  |  |
| Garden waste | 1.000 | 9.000 | 45 | 85 | 50 | 90 |
| Kitchen waste | 2.500 | 8.500 | 55 | 70 | 90 | 90 |
| other organics | 2.500 | 8.500 | 55 | 70 | 90 | 90 |
| Paper & cardboard | 13.000 | 13.000 | 20 | 20 | 95 | 95 |
| Glass | 0 | 0 | 2 | 2 | 0 | 0 |
| Plastics | 32.500 | 32.500 | 10 | 10 | 95 | 95 |
| Metals | 0 | 0 | 5 | 5 | 0 | 0 |
| Hazardous wastes (including clinical) | 9.500 | 9.500 | 25 | 25 | 75 | 75 |
| Other (inert & dust)/mixed waste | 7.800 | 7.800 | 25 | 25 | 75 | 75 |

### 2. Specifications

| General | The activities of supply in this specification cover the Design, Construction, Manufacturing, Testing, Supply, Installation, Commissioning, Trial Operation, Performance and Acceptance Tests, Performance Guarantees Services, Training, etc. of an incineration plant at Hithadhoo, Addu City, which are described in this document. In this public procurement award documentation (hereinafter referred to tender documents) before commencement of work the approved conceptual design for the plant is to be provided. The Tenderer is requested to submit an offer for the Plant, fulfilling all requirements, regulations and targets of these tender documents. Proposals for admissible significant amendments to the approved Conceptual Design are not admitted. All costs related to agreements and approval by the competent authority of the Working Design prepared by the Contractor, including all admissible substantial amendments, to the approved Conceptual Design, are to be borne by the Contractor. The Contractor shall ensure the compliance of the working design with the conditions of the EIA Decision. |
| --- | --- |
| scope of work and supply | The Contractor shall furnish all labour, materials, plant facilities and equipment, whether of temporary or of permanent nature, to perform the work necessary to design and construct the complete waste to energy plant. The scope of supply includes also all spare and ware parts during the tests on completion, during the Defects Notification Period (DNP) and till issuing the Performance Certificate. |
| design and documentation | Preparing the complete design documentation in English language including the necessary agreements and permits in compliance with the National Law and Regulations, including further amendments |
| working design | The Working Design must be prepared on the basis of the National standards and norms and must obtain the required agreements, statements and permits by the competent authorities. The Contractor may perform additional engineering and geological surveys in order to collect all the necessary information for preparation of the working design within the scope of the contract, if the Contractor decided that the available data are not sufficient. These additional works will have to be approved by the national authorities. |
| as-built documentation | During the construction the Contractor prepares as-built documentation in scope and contents as per the requirements of the National legislation. |
| executing construction installation works and services | Excluded Civil works & other works - Construction of main facility building - Roads and other infrastructure - Construction of all civil works installation such as foundation, halls and sheds - Construction of the plant, including the waste storage areas, the waste feeding system and other possible construction facilities which may be required in compliance with the prepared design and implemented technology. - Air conditioned control room. - Steel structural columns for building - supplying water, discharging of technological and sanitary sewage as well as rainwater, including provision of the necessary storage volumes into the incineration plant - Supply of treated water up to the incineration building. - Supply of diesel up to the incineration facility - supplying electric power and lighting the area - Supply of mobile machineries such as wheel loader, forklifts during the incineration operation. Included Civil works & other works - Construction of concrete foundations and skids for all equipments of within the scope of supplier. - Construction of blow down pit - Delivery and assembly of the complete in to the incineration plant production lines fulfilling the Employer’s Requirements. - Delivery of the remaining machines and equipment necessary for the correct operation of the incineration plant according to the Employer’s Requirements. |
| mechanical and electrical work | The Contractor shall furnish all labour, materials and work necessary to design, manufacture, make factory tests as required, work shop paint, deliver to site of Works, construct, erect, make field tests, make final painting, commissioning, carry out trial run and acceptance tests of all plants and equipment for the incineration plant, including but not limited to - transporting systems like conveyor belts etc. - motors and ancillaries - Steam , condensate, blow down , cooling water, hydraulic oil drain water piping, valves and associated equipment - insulation with stainless steel cladding for all heat media pipes. - All required inter connecting hot air/primary air/flue gas ducts with insulation and cladding. - Fabric compensators for all ducting wherever required. - All steel supports, brackets etc.. - Internal control/power/data/communications cabling within the suppliers product from suppliers main panel with required cable tray/conduit etc.. - fire fighting facilities and tanks, - the incineration unit, not limited to steel structure, all the platforms, steel stairs, plate work, - complete mechanical ventilation system - flue gas treatment facilities with as fans, ducts, filter systems - transformers and auxiliary transformers - voltage switchgears - DC system (rectifier and batteries), UPS installation - Earthling and lightning protection, lighting system, industrial power outlets, cables, cable support structures, fire detection system and other miscellaneous electrical - complete instrumentation and control equipment for the main systems - the complete internal and external fire protection system including supply and installation of wet risers, hose reels, fire hydrants, automatic and manual alarm, extinguishers and foam generator, all the monitoring and fire-fighting equipment. The scope of supply further includes Documents, drawings, etc. in full compliance with the Employer’s requirements including checking of civil, electrical, mechanical and other related engineering drawings with reference to the Contractor's scope of supply All necessary applications and approvals to related competent authorities for electrical, fire protection, construction licence, etc. All necessary equipment and calibrated instruments to carry out the performance tests All necessary motors for ventilators, compressors, valves, gantry cranes, etc. All parts necessary for anchoring, grouting, alignment and installation of equipment, plant and steel structures especially base plates, frames, bolts, bars, bolt sleeves, grouting, etc., the fixing thereof in place, and the responsible supervision of fixing of the embedded parts - first filling and servicing of lubricating oil, grease, etc. - consumables - spare and wear parts for the entire plant - tools required for the maintenance of the entire plant The Contractor must provide periodical supervision team of appropriate qualified experts for the whole Defect Notification Period (DNP), until the issuance of the Performance Certificate The Contractor has to ensure that all manufacturers of stand-alone equipment who will be responsible for repair and maintenance of their equipment after final taking over of the plant are being represented. During installation, commissioning and before taking over certificate, the future operating staff of the Employer shall be trained by the Contractor. Moreover the operation during the DNP and performance tests will be monitored/supervised by the contractor, and in case of any problem the operating staff of the Employer shall be instructed and further trained by the Contractor. The instructions shall be in English language. The Contractor shall make available, for the purpose of instruction, and all information necessary for the effective execution of the instruction programme. The Contractor shall instruct and train the trainees in such a way that the operation, maintenance and, if necessary, repairs to the system can be handled competently by the respective personnel. The Contractor shall provide all required notes, manuals, drawings, training aids etc. to supplement the construction, operation and maintenance instruction manuals and to enable the operating and maintenance staff to efficiently operate and maintain the works. The types of the training aids and brands of the equipment shall be approved by the Engineer. All training materials shall be in English language. |
| services | Start-up, testing, commissioning and trial (reliability) operation of the plant for regular operation, including a guarantee for delivering all the appropriate documents required in compliance with the National Construction Law for the Employer to obtain the permit for the operation. Training the Employer’s personnel in operating the incineration plant must happens during the start-up and test run period. Each trained member of the personnel shall receive an appropriate certificate from the Contractor confirming appropriate training. |
| consumables | The Contractor shall supply within this Contract all necessary consumables initially required (up to issuance of the Take Over Certificate of the whole Plant), such as lubricants, greases, chemicals, etc. except fuel and water for all equipment furnished by him under this Contract. The Contractor shall submit to the Engineer for approval, up to beginning of trial period, a complete tabulated consumables’ list for all consumables required, showing all locations where these consumables are required, the type of consumable, and the quantity for one refill/exchange. |
| special equipment | The Contractor shall supply all necessary special tools for dismantling, maintenance, installation and adjustment of the supplied equipment. Tools and equipment for major inspections and measurements shall be included as well. The tools, wrenches, etc. shall be brand-new and within the guarantee period. They shall be of the forged and polished chrome-vanadium type. Special tools and devices shall be provided with means for ready identification. Suitable hardwood or steel boards arranged for wall mounting as well as tool carts and/or tool boxes shall be included in the delivery. The Contractor submits to the Engineer for approval an itemised list and description of all required tools, auxiliary devices, storage equipment, etc.. A complete list of maintenance equipment and special tools included in the scope of supply shall be submitted with the Bid. The Contractor shall supply to the Employer, along with each item of special equipment supplied, three copies of the Manufacturer's Instructions Catalogue in English language. |
| other work |  |
| clearance of site | Upon receiving the Performance Certificate, the Contractor shall remove any remaining Contractor’s Equipment, surplus material, wreckage, rubbish and Temporary Works from the Site. |
| compliance with the employer’s requirements | All works undertaken, including the prepared designs, completed works, delivered materials, machines and equipment pertaining to the Contract should comply with the requirements of the technical specifications. The Tenderer, on the basis of his knowledge and experience, should also include additional elements of the installation, equipment and operations which are not enumerated in the Employer’s Requirements but are relevant and necessary for ensuring proper functioning of the incineration plant, its efficiency and fulfilling the warranty conditions. The solutions submitted in the Bid shall guarantee the achievement of the objective e.g. the proper functioning of the incineration plant. The properties of the materials and elements of the construction, machines and equipment shall comply with and pertain to the data described in the technical requirements. |
| technical description |  |
| general | The incineration with waste to energy system includes but may not limited to the following. - Waste reception with weighing bridge - Mechanical storage room with odor management with mixing of waste and draft re-circulation to main combustor. - Conveyer system to shredder - Shredder - Fe/N Fe separator - Oversize screener - Mechanical moving floor with sorting - solid waste feeding system with metering bin - Step /moving grate combustion system with steam boiler - Automatic ash removal system with wet slager - secondary combustion chamber - induced draft fan - Primary air fan with flue gas recirculation - Steam turbine with synchronies generator - Air cooler condenser - Condensate collection tank - Condensate transfer pump - Feed water cum de aerator tank. - Chemical dosing system - flue gas cleaning system including feeding of the absorption material and the discharging system of the by products - continuous emission monitoring system - lance for the combustion of waste oil - utilities (compressed air system, portable water, nitrogen system) - auxiliary burner (operated with diesel fuel) - UPS for PLC working - Auxiliary power generator - Distributed control pannel - Complete PLC and SCADA system |
| system description | The system description describes a system developed during the preliminary engineering. It is not intended to be prescriptive. Contractor may propose alternative arrangements provided that the basic system design criteria and system functional requirements are met. The purpose of the incineration system is to reduce the volume of solid waste generated in Zone 6 & 7 (Gaafu Alifu, Gaafu Dhalu Atolls, Fuvamulah and Addu City) The contractor has to give the requirements of the incineration building. This building will only be a weather protection. The control room and the other rooms necessary for the operation plant are located in a separate building which is not part of the contractors supply. The contractor has to specify the area for control room and workshop. The incineration system is designed for an operation time of 330 days/year. The capacity is 2 t/h. Only specialized conveyers, adapted for the transport of municipal waste are permitted for delivery and assembly. |
| Waste Reception, Tipping, Temporally storage, waste handling, and shredding, sorting, transfer conveyer | Wastes from the connected islands in Addu City (Hithadhoo, Maradhoo, Maradhoo-Feydhoo, Feydhoo and Gan International Airport) will be transported using specialized vehicles to the site on daily basis Specialized marine vessels will deliver waste material from other islands in the Zones 6 & 7 on regular basis with each vessel containing approximately 25-40 waste containers. Each container can weigh between 300 kg – 1000 kg. A tractor /wheel loader/truck will be used to transport waste containers from the harbor to the facility where it will be weighed and off-loaded. Once the tractor/wheel loader/truck weighted, it will automatically registered to the system and then tipped in to the temporally storage refuse pit which is around 350 to 400m3 of capacity. The waste will be mixed in the refuse pit. The refuse pit will be designed to store waste for at least two to three days of combustion as waste is only delivered during the day and on working days but plant operates around the clock. The tipping storage hall and refuse area will be closed buildings to prevent dust and odors from escaping in to the environment. In addition, air is continually extracted from the pit to maintain a negative pressure. The extracted air can be serve as combustion air for the combustion system. In case of unscheduled/scheduled stop of the plant it will provided a deodorization unit (dry catalytic method). From the storage pit on words complete process has to be automated and should not require any man power or a wheel loader. Waste will discharge from the storage room to receiving conveyor that will take the waste transfer them to the shredder hopper. Once the shredder hopper is full, the system will deactivate. Once the waste gets low in the hopper, the system will reactivate and the process is repeated. Waste will then be shredded and discharged to the vibration conveyer system to separate ferrous and nonferrous items and this should also include the magnetic and nonferrous separator. Once metal separated from the waste will go to oversize screener unit and oversize waste particles has to go back the shredder by a separate conveyer and small fuel particles has to go to boiler metering bin via an elevated conveyer. As the boiler metering bin calls for waste, the system and conveyors will be activated and waste will be transferred to the metering bin. Once the metering bin is full, the complete floor and conveyors will shut down. As the metering bin fuel level is lowered, the system will be reactivated and the process repeats. |
| Shredder | Single-rotor shredder with 2-fold electric drive motor (with FC). Including slip clutch. Wearing parts easy to change. Feed hopper hydraulic driven. Central lubrication, completely electronically controlled. Should be designed to take Furniture, mattresses and municipal garbage and other bulky waste. Specification - Feed opening 1,7 x 1,8 m or more - Cutting Diameter 750mm or more - Rotor Speed 67 1/min or more - Number of rotor knives 18 pc or more - Number of stator knives 4 pc or more - Max. Outlet Size 350x350 mm or lesser - Drive power less than 2 x 110 kW - Hydraulic aggregate 22 kW or lesser The following minimum scope of supplies refers to the offered conveyor - conveyor belt - carrier idler sets with pulley - substation with pulleys - support frame with supporting steelwork - drive pulley with drive unit - end pulley with tensioning device - life time greased bearings - electric motor with gear box - monitor for motor - end pulley with take-up station - material charging - belt cleaning - material guides - belt guides and centering device - mounting possibilities for ferrous metal separators (where required) - stationary equipment for repairs - safety devices - reciprocating feeders (where required) - pull-wire emergency stop control - bell standstill monitor - internal cabling of all components to local control box In case of scraper chain conveyors, the above mentioned should be applied analogously. In addition to above, the scope of supplies for transfer points will include, but not be limited to chutes with support structure, fully encased with access openings |
| Lock Hopper system /Waste metering bin | To introduce the solid waste into the primary combustion chamber a lock hopper system is foreseen. Fuel feeding system for MSW wastes, consisting of: - 1 hydraulically actuated sealing gate on top of the fuel dosing shaft - 1 fuel dosing shaft: an inclined, vertical shaft made of solid steel plates. - The fuel feeding shaft leads the fuel from the double gate flaps to the grate. - The design of system facilitates the feeding shaft with enlarges at the bottom, Should designed to reduce the risk of material stocking. Including: - Min./Max. level indicator in the fuel dosing shaft - Quenching water injection for the avoidance of burn-backs according to - DIN- and TRD requirements in the fuel dosing shaft - An access door for inside inspection. |
| Combustion chamber and steam boiler | The following design parameters are the basis of the engineering of the combustion chamber cum steam boiler design feed - design feed: 50 t/d (2 t/h) - Step/Oscillating /Reciprocating type grate system with under bed and over bed fire - operation 24 hrs/day, 330 days/ year - feed stream heat value 6,500 - 9,500 kJ/kg (Heat value of each fuel has been mentioned above sheet) - ash content 20 - 30% - humidity of waste 10 - 30% - max. size of the waste 350 mm (after shredder) - ambient temperature 29 - 35 °C - ambient rel. humidity 70 - 90% |
| Primary combustion chamber | The primary combustion chamber (PCC) includes the grate system as specified above . The PCC has a horizontal refractory lined combustion chamber. The combustor temperature is typically maintained at 850°C. The refractory lining is designed for a continuous operating temperature for above 1,400°C. The PCC has to include the following - primary air inlet - waste oil lance (capacity 75 l/h waste oil) incl. waste oil pump system and spray nozzle - pressure and temperature transmitters - The chamber should equipped with sight glasses at each grate section. A inspection - door guarantees the accessibility of the combustion chamber - Complete boiler management system and safety system - There should be a camera for combustion chamber to make easy judgment of the quality of the combustion - Closed, water-filled drag chain de-asher with drag chain, chain tightening equipment and drive unit with gear motor has to be arranged above the water surface. - The water level has to be automatically controlled by a float valve and makes possible the permanent ash discharge out of all grate zones without additional air flow to the combustion chamber - Bottom ash discharge system with adequately size to provide a minimum of 8 hours on operation with the bottom ash removal system out of service. |
| Secondary combustion chamber | The secondary combustion chamber (SCC) is a horizontal refractory lined chamber. The combustion temperature is typically maintained at 850°C. The refractory lining is designed for a continuous operating temperature of above 1,400°C. |
| Primary burner | The primary burner has to be designed for maintaining the temperature in the PCC over 800°C, when the heat value of the input waste is lower than 7,000 KJ/kg. The burner is operated with diesel fuel oil. The primary burner must have a long flame without impingement upon the refractory. The primary burner includes the following - diesel fuel oil supply - combustion air fan - burner fining control system - intermittent pilot system with automatic igniter - flame safety system - fuel oil nozzle The combustion noise from all sources within the system do not exceed 85 dB(A) measured 1 meter horizontally from the equipment. A purging air step after the burner shut down is includes to purge the equipment and ducts of flue gas to minimize condensation of acid gases during cool down. |
| Ash Removal system | The ash conveyor system transports the ash from the discharge end of the PCC to a transportable ash container. An interlock prevents the ash conveyor from operating when the ash container is not in place. The conveyor is actuated with an electric motor gear reducer which provides adequate power under all operating conditions. |
| Ash Containers | In the scope of supply two ash containers are included. The containers have a cover or tangs to minimize ash discharge during storage prior to transport and during transport off-site disposal. The size of the containers allows movement with a standard fork lift but sufficient capacity to retain ash generated in 8 hours at normal waste loading. |
| Flue gas cleaning and treatment | The flue gas cleaning will be done with a dry system using a alkaline absorbents like limestone or sodium bicarbonate. Flue gas cleaning system should be including with Soot Blowers. - set of retractable soot blowers or shot ball cleaning system to remove loose dust SNCR - for NOx reduction due to injection of Urea Solution into the combustion chamber, - Include water dosing tank and fluid UREA Storage Tank. It has to be installed in a frost free area. Bag house Filter (with Lime and activated carbon dosing) The limestone is fed by a pneumatic feeding system into the flue gas. In a bag house filter the absorbents and the dust is separated from the flue gas. The pollutants reach with the absorption material on the surface of the filter tubes. Should be including: - 60m³ Silo for Lime - Big bag dosing station for Activated Carbon - Steel structures, platform, ladder including fall preventions and safety barrior. Specification of the bag house filter Component; Unit. Flue gas flow; Max. 19,500 Nm³/h. pressure loss; 10 mbar. filter surface load; 0,8. design temperature; 170°C. max. temperature; 200°C. The dust and the absorption material has to be transported by a screw conveyor into a big bag. After the filling this big bag is transported by a forklift to the land fill side. The following clean gas emissions must be reacted by the flue gas cleaning (guaranteed values) Parameter; Unit. total dust; 10 mg/Nm³. total hydrocarbons (THC); 10 mg/Nm³. carbon monoxide (CO); 50 mg/Nm³. HCl; 10 mg/Nm³. SO2; 50 mg/Nm³. Cd; 0.05 mg/Nm³. TL; 0.05 mg/Nm³. Pb, Cr (Sb, Cu); 0.5 mg/Nm³. As, Co, Ni (Mn, V, Sn); 0.5 mg/Nm³. Hg; 0.05 mg/Nm³. (Basis = 11 Vol.-% O2, dry flue gas) |
| Main Induced Draft Fan (ID Fan) | The bidder has to Provide an Excess Air Fan to maintain an oxygen concentration set point in the flue gas as measured at the discharge of the induced draft fan. Maintain the oxygen concentration set point by throttling a damper on the discharge or suction of the excess air fan. Design the fan to provide 100% excess air. Design the Excess Air Fan to discharge air into the SCC. Use manual dampers to split the flow to the SCC. Ensure that the combined noise from all sources within the system do not exceed 85 dB(A) measured 1 meter horizontally from the equipment base. Designed as radial forced draft fan with casing made of steel (St 37), gastight welded. Direct motor actuation. Including suction guard, base frame, vibration dampers. Casing with zinc phosphate priming and synthetic resin coating. With coupling between shaft and motor, equipped with vibration sensor |
| Combustion Air Fan | Combustion air fan to suit all combustion processes. Designed as radial forced draft fan with casing made of steel (St 37), gastight welded. Direct motor actuation. Including suction guard, base frame, vibration dampers. Casing with zinc phosphate priming and synthetic resin coating. |
| Cooling air fan | Cooling air fan to cool and protect burner and nozzles in emergency cases. Designed as radial forced draft fan with casing made of steel (St 37), gastight welded. Direct motor actuation. Including suction guard, base frame, vibration dampers. Casing with zinc phosphate priming and synthetic resin coating. |
| Stack | The height of the stack must be calculated in the Final Environment and Social Impact Assessment Report. For price calculation purposes the height of the stack assumed to be 22.5 m. Specification height 22.5 m diameter (inside) 0.5 m or as per the suppliers design material 316 stainless steel The stack is either self-supported or supported within a structural steel frame. The bidder has to Provide the necessary nozzles and taps for collecting manual grab flue gas samples as well as nozzles and brackets necessary to mount continuous monitoring instruments downstream of the APC and upstream of the induced draft fan and common back |
| Continuous emissions monitoring system | A Continuous Emissions Monitoring System (CEMS) and Data Acquisition System (DAS) is installed to monitor and continuously record the following flue gas constituents Total Hydrocarbons (THC) Sulfur Oxides SO2 Dust NOx HCl |
| Compressed Air system | The bidder has to Provide a complete compressed air system as required to support the requirements of the incinerator and the functions of the facility including but not limited to the operation of pneumatic valves and equipment and instrument air. Provide two (2) compressors (one duty, one standby), designed for Ultimate design. Ensure type of compressor selected is suitable for the intended service. Ensure air quality is suitable for the intended service. Provide air filters, Air dryers moisture traps and other ancillary equipment necessary to produce the requisite air quality. Provide air receiver tank appropriately size to allow air compressors to operate intermittently and to retain a sufficient air charge for safe shut down of the plant on loss of power to the air compressors. Ensure the tank is Boiler and Pressure Vessel Code certified and stamped. Provide all instruments necessary for monitoring air pressure and the functions of the installed equipment. Communicate critical alarms and indications to the Distributed control system (DCS). |
| Plant control system | The DCS has an open architecture for facility wide control and monitoring. The DCS has to collect information in the operator control room for monitoring and limited control by operation personnel. Control of individual equipment packages may be supervised by local programmable controllers or trough hardwired panels provided with the equipment. |
| Hardware | The bidder has to Design the DCS to be expandable to meet the future needs of the facility. As a minimum provide 20% spare I/O capacity and 50% spare processing capacity. Provide redundancy in the configuration for components critical to the operation of the DCS or to programmable controller-type devices located in equipment packages including but not limited to power supplies, processors, I/O cards etc. Make the transfer to the redundant or standby components automatic and bumpless. “Critical components” are defined as those which cannot be replaced within 12 hours of failure or those which would negatively affect the overall operation of the plant in any way. Provide a single Uninterruptible Power Supply (UPS) to support the entire DCS and associated operator consoles. Size the UPS to guarantee full control system operation for a minimum of 30 to 45 minutes following a plant power outage to allow for an orderly shutdown of the plant systems. Include control room lighting and other appurtenant equipment necessary to conduct operations in this requirement. Provide fully redundancy for the plant communication data highway and the controller to I/O communication highways with both paths continually active. Ensure no single point of failure can cause complete loss of process control. Interfaces to local equipment systems that have redundant features are not required to be redundant. Contractor also should provide emergency generator to protect equipments when sudden power loss occurs. |
| Degree of Automation | The design may require manual intervention by the operator at equipment local control consoles or panels in some instances. As a minimum communicate trouble alarm to the DCS to identify equipment problems that demand local attention. Furnish the control room to contain the engineering and operation stations arranged in multi-station consoles and equipped with redundant communication ports to both the DCS and the plant Local Area Network (LAN). Ensure each station is capable of being independently powered, shut down, and restarted and that under proper access level authorization each station is capable of providing process monitor and control functions for any portion of the facility. |
| Alarm Philosophy | The bidder has to implement an alarm management system to direct the operators attention to those alarms and systems requiring attention to prevent hazardous situation form developing and to minimize harmful impacts to equipment and personnel. DCS has to be designed to be primary means of displaying alarms. The alarms has to be displayed, properly time and date stamped on the consoles in order of urgency and log to a data historian and alarm printer. All the alarms are has to be displayed on the graphical pages at the top or the bottom of the screen. In order to warn the operator, provision is also made for an acoustic alarm through the speakers of the personal computer. |
| Telephone System | In the main control room, provision has to be made for a central digital telephone system, which can also be used as an intercom between the various work positions in the plant. |
| Monitoring Philosophy | The bidder has to utilize process-like graphic displays at the DCS to accomplish normal operation monitoring and control. Also to provide overview graphics as required facilitating the safe operation of the facility. Security features has to be built into the control consoles to prevent unauthorized access to console functions. The access to specific process displays, variables control points, system configuration and utilities must be limited by tuning key locks and multiple configurable level of password security. The programs in the supervision system has to be configured to carry out the following functions: - Manual or automatic management of the system activation organs. - Monitoring the variables of the process and of the conditions of the plant. - Management of the alarms with signal and printout. - Generating reports. - Diagnostics. - Management of the access levels. - Data archiving. |
| Emergency generator | The plant has to be equipped with an emergency generator to provide the necessary electric power in case of electric black out. |
| Video surveillance | The most important areas of the plant has to be equipped with a video surveillance system. The operators can keep under control these areas and react in case of problems. Among these areas we mention: plant gates; internal road system and maneuvering areas; feeding hopper of the furnace; combustion inside furnace; boiler drum level; bottom ash conveyors; silos area. |
| Energy Recovery and waste to energy | The Energy recovery system includes but may not limited to the following. - Steam engine as package unit including - Steam engine - Generator - net and generator control unit - Synchronizing unit - Bypass pressure relief system - Condenser - Air cooler - Condensate Tank - Condensate Pumps - Degasser - Boiler feed water pump - Boiler water preparation (reserve osmosis system) |
| System Description | The system description describes a system developed during the preliminary engineering. It is not intended to be prescriptive. Contractor may propose alternative arrangements provided that the basic system design criteria and system functional requirements are met. The purpose of the steam engine is to produce enough electricity to feed the Regional Solid waste Management Facility in a closing loop, additional electricity production may be fed into the grid. The contractor has to give the requirements of the building. This building will only be a weather protection. The control room and the other rooms necessary for the operation plant are located in a separate building which is not part of the contractors supply. The contractor has to specify the area for control room and workshop. |
| Design Standards and piping systems | The piping system must correspond to the actual state-of-the-art in the construction, operational safety and material condition of the equipment (EU, British or American standards) at the time of finishing the construction. When dimensioning and arrangement of all parts all thermodynamic, flow and resistance technical requirements, have to be considered. In the construction documents all dimensions and room temperatures must be included. It is to strive for the best possible utilization of space of the building. The subsequent maintenance possibility of building and system components must be observed. The good accessibility the piping and system components must be ensured for assembly, welding, repair and inspection work as well as inspections during operation. In the structural design of the pipeline system, it is noted that the tube systems are not biased. This must be ensured through appropriate measures. If a Bias is required, it has to be agreed. Outgoing from the main strands and not constantly flowed through pipes, for example, Supply line to the safety valves , reducing and overflow stations must be connected to main lines that no condensate return takes place . For this purpose, suitable drainage points should be planned. Adequately dimensioned heat-up and holding lines must be provided. The following minimum distances must be available considering all possible pipelines and pipeline movements: - between thermal insulation and building 100 mm - between adjacent pipe exterior parts including insulation 100 mm horizontal distance between the pipes including insulation and the accessories (e.g. support structure) and the system parts for all operating and committing routes 750 mm clear passage height above the main walkways and main courses 2.300 mm. Required escape routes have to be planned and kept clear. In the design and arrangement of all the pipelines and the establishment of fixed point positions and guides or hangers weight, reaction forces and linear expansion of piping and subsequent parts must be considered. The introduction of forces and moments in subsequent components and aggregates of the water / steam system (eg steam engine, boilers, tanks, pumps, heat exchangers, etc.) must be avoided or are within the permissible values. These parts of the plant may not be provided as fixed points. For collectors the introduced forces and torques must also be limited to the permissible value. Pipelines that pass through walls have to be provided at these locations with thermo wells. Below the building top watertight masonry, penetrations are to be used. Unless pipelines with heat and/ or sound insulation are provided, this must be considered in the pipeline planning. Pipes and heat or sound insulation are possible to run so that the insulation throughout can be attached by flattening or penetrations to other lines or equipment without interruption. The supports must be designed such that deformations of the pipes cause undue stresses in operation and all incidents at any point of the pipes or their holders. The pipes must have under all operating incidents the opportunity to freely stretch around the constructed values. The piping routing must be chosen so that no undue stresses occur as a result of thermal expansions disabled. It take into account also movements on units such as heat exchangers, pumps, etc. By appropriate piping and proper arrangement of suspensions or supporting structures is to ensure that vibrations are so far prevents any impermissible stresses. The pipe supports must be designed such that the pipelines cannot stand out from the supports. The structural design of the pipeline system has to be made taking into account the permissible stress at the connection points. All pipes have to be installed, so that a proper and complete filling, emptying, venting and draining is ensured and that as little drainage points are required. Steam lines are at least in horizontal strands with a sufficient gradient of. 2% in the direction of flow, thus arise for the drainage points clear lows positions. The water and condensate pipes, however, are planning a continuous rise in the horizontal strands, thus resulting unique venting points. Drainage, ventilation shall be so located that no harmful interference to warm the pipes and can occur during operation and the system is not compromised by insufficient drainage of steam lines. All drainage, emptying-, ventilation lines are merging at central locations and are viewable in the hopper or collector open. The respective hand valves are clear and easy to operate at the end of lines, to arrange about 1,2 m above the ground or stage level. Drainage systems, vents, blow down lines each with double shut-off; at vents and drains that need to be in use regularly, the second barrier gets in the flow direction of a motor drive; each second barrier receives a throttling valve plug; separate lines of all blow downs, drains and vents to central stations with uniform sizes and pressure ratings. Cones for drainage and vents should be located at least 2.0 m adjacent to the corresponding shut-off valves and can be observed when operating the valve. The design of fittings includes all fittings; these are included in the scope of supply. For all valves command and installation, requirements of the respective valve manufacturer must be observed. Valves must be clearly laid out, with the same good accessibility for observation, maintenance, repair and possible expansion. They must from the ground or from a main stage are reachable, if necessary, appropriate service platforms shall be provided. Fittings, particularly for drainage and vents are, largely summarize to control positions that need to be accessible during operation. At locations where direct accessibility cannot be guaranteed, spindle extensions are provided. Valves with direct flange mounted drives are basically to arrange with a vertical spindle. If this is not possible, additional supports are to be attached. The minimum distance between fittings hand wheels should be 100 mm in compliance with all sorts of pipeline systems and pipeline movements. There are precautions to avoid inadmissible pressure increases in line sections can be shut off by external warming The changes in length that occur must be able to be absorbed by the pipes, without allowable deformations or excessive stress at the connection points, or to the support structures. It is not allowed to use compensators in pipes higher pressure and higher temperature |
| Supports & Brackets | The pipe wall thickness for dismounts, vents, drains, etc. is possible to adjust the main or base-pipe-wall-thickness. Supports, also high-pressure pipes are to carry out in any case as a reinforced neck. The transition of the weld between nozzle and pipe are ground notch-free with a radius corresponding to the pipe wall thickness, but at least 10 mm execute. The length of weld should be such that at any separation of the connecting lead a faultless weld preparation, welding, heat treatment and possibly final weld inspection is possible. |
| Compounds | Basically welded joints are to be provided. The number of welds is to minimize. The use of flanged joints should be limited to cases where pipes, plant components or assemblies must be designed for operational testing and manufacturing reasons with flanges. |
| Steam Boiler | Steam boiler should be either a hot flue gas (From incinerator) fired waste heat steam boiler or a direct MSW fired step/moving grate type with water wall membrane steam boiler with below features |
| Specification | Total thermal heat capacity approx Max 5.5MWt to 7.00MWt Temperature Steam 380 °C Quantity Steam 8.5 t/h or above Pressure Steam 40 bar (g) Operating pressure max 50 bar(g) Design Pressure 65 bar (g) Flue gas approx 23.000 Nm³/h or according to the suppliers design - Automatic blow down system with TDS controller. - If required Economizer or Air pre heater is optional. - Water Level controller for 24 hours supervision free operation. - Steam soot blower system. - Insulation thickness should not be less than 5" - Boiler cladding material has to be stainless steel. - Boiler has to be supply along with the ladders, platforms and structural steel at operating levels. - Oxygen trim system - Properly sized steam flow metering system - High temperature combustion system camera for viewing in control room - Intermittent Blow down systems. - Boiler construction has to be self-supporting type, which does not require heavy external supporting structure - The boiler has to be bottom self-supported and free to thermally expand in all directions so as to avoid excessive mechanical stress - Including all required interconnecting steam/condensate/blow down piping and insulations. - Attemperator to control the steam temperature over the super heater turn down ratio in accordance with the thermal lay out by injecting condensate. - Boiler has to be manufactured as pee the TUV, ASME Standards including all relevant valves, gauges, instruments etc. |
| Steam Turbine | 1 Steam Turbine Unit for generation of 1MW Net power to the grid from overheated steam (Turbine output = 1MW Net + Total Machine power consumption) Turbine has to be mounted on a Base Frame Turbine should be consisting with integrated lube oil system Turbine should be consisting with Automatic Sealing Steam System - Gross Energy output = 1MW Net + Total power consumption of the plant - Design: Multistage impulse-design steam turbine - Inlet Trip Valve: Emergency Trip Valve for mounting on inlet - Inlet Steam Strainer: Cone design steam strainer - Control Inlet: Nozzle Group Control, 3 valves, hydraulic operated - Blade Design: Inserted and pinned blades - Blade Material: X20Cr13/1.4021, forged, annealed - Rotor: Built-Up Rotor - Balance Quality: G 1,6 - Shaft Material: 30CrNiMo8/1.6580, single forged, annealed - Wheel Material: X20Cr13/1.4021, single forged, annealed - Casing: horizontal split - Casing Material: Cast Steel Sections - GS17CrMo55 - Welded Sections - P265GH - Bearings, radial: Plain bearing, fixed pad, forced feed lubrication - Bearings, axial: Plain bearing, tilting pad, forced feed lubrication - Shaft sealing, steam: Labyrinth - Shaft sealing, oil: Labyrinth - Inlet steam: As per the boiler design - Exhaust steam: As per the design - Speed: 5500 min-1 - Thermal Insulation: Removable matt insulation, mineral wool |
| Gear Box | - Double helical, high speed reduction gear box with curved tooth couplings. - Type: High Speed Gear Box - Tooth: Double helical - Lubrication: Forced feed - Bearings: Plain bearings - Bearing Temperature: 2 x PT 100 per bearing - The gearbox has to be mounted with the main-oil pump for the lubrication system |
| Couplings | - Turbine – Gear Box (HS): Curved tooth coupling, forced feed lubrication - Gear Box – Generator (LS): Curved tooth coupling, grease lubricated - Low speed coupling grease lubricated with torque limiter on low speed - coupling. - Couplings has to be provided with coupling guards |
| Synchronous Generator | - Synchronous, has to be self-excited, 4-pole 50Hz, brushless generator - Type: 3-Phase Synchronous Generator - Excitation: self-excited brushless excitation system - Voltage: 0,4 kV +/- 5% - Frequency: 50 Hz - Power Factor i: 0,8 - Cooling: air cooler - Ambient temperature: max. 42°C - Bearing: sleeve journal bearings - Design: VDE 0530, IEC 34 - Accessory: Anti-Condensation Heaters |
| Condenser | One properly sized Water Cooled Vacuum Condenser for operation as a vacuum condenser. The condenser has to be mounted directly underneath of the turbine and generator set. Package - One shell and tube vacuum condenser - Local accessory package - Cooling Water Inlet / Outlet Thermometer - Pressure Gauge Cooling Water Pressure - Condensate Well Thermometer - Condensing Steam Pressure Gauge - Ejector System with Ejector Condenser and accessories - 2x100% Condensate Pumps with accessories - Condensate Level Control - Internal piping of the components - Steam Side Safety Valve - Mounting Frame for package Design - Shell Design Pressure: Min 3 barg - Tube Design Pressure: Min 6 barg - Tube Design Temperature: Min 100degC Materials - Shell: Carbon Steel Shell - Tubes and Tube Sheets: Carbon steel - Baffles: Carbon Steel - Water Boxes: Carbon Steel |
| Air cooler /Cooling tower | There should be a properly sized V coil type air cooler or with cooling tower with required inter connecting piping, valves, instruments. Including one running one stand by cooling water circulation pumping stations. - cooling water: 90 °C - outlet temperature: 70 °C - Design capacity: Approximately 4000 kW |
| Condensate tank with transfer pumps. | Supplier has to be supplied properly sized condensate collection tank capacity not lower than 4000 liters including with insulation and cladding , one running one stand by steam operate/motor operated condensate transfer pumps to the boiler feed water tank , minimum pressure boosting up to 4 bar |
| De- aerator tank | Dome end type Spray de-aerator system has to be properly sized and supplied and capacity not less than 5000 liters. - Heat the feed water to the saturation temperature corresponding to the steam pressure within the heater. - Reduce feed water oxygen content to 0.005 cc/liter - The de-aerator has to l be constructed of SA516 Grade 70 steel plate with minimum 1/4" thickness or as per the manufactures designed on the designed working pressure. - The de-aerator has to be incorporate a stainless steel spray valve with - 316 stainless steel spring(s) mounted in the spray valve compartment. - The internal direct contact vent condenser, has to be fabricated of stainless steel, shall consist of a separate compartment for concentrating the non-condensable gases before they are released to atmosphere. - The final stage of de-aeration has to be accomplished by using a steam scrubber designed to scrub the water with the entering steam and heat the water to saturation temperature. - De-aerator storage tank has to be provided with de-aerated water that is measured to the overflow level. - De-aerator has to be operable at minimum 2 bas or above . The entire assembly has to be pre-assembled and has to be consist of the following components: - Two (2) Properly sized Centrifugal boiler feed water pumps should be equipped with high temperature mechanical seals. - suction connections with shut off valves, strainers and expansion couplings. - Pressure gauges has to be supplied for the discharge side of the pumps along with recirculation lines. - One (1) pump to be in operation while one (1) pump is in standby. Each pump is to be driven by a TEFC motor as required to meet the required discharge pressure. - One (1) Prefabricated de-aerator steel stand to be not less than 8 feet and has to be sized for the above stated pump operation. - Insulation not less than 3" with stainless steel cladding for entire tank. |
| Execution - Design/ engineering | The bidder has to provide all engineering and design for the incineration and WTE system including the preparation and submittal of al drawings, equipment data sheets, P&ID´s, operation and maintenance manuals and other documents for the supplied equipment 4 (four) weeks after the contract get in force, the bidder has to provide all utility requirement information (amount of potable water, wastewater, power consumption etc.). The contractor has also provided to the civil engineer relevant data like dimensions weights which are necessary for the design of the foundation. The design has to be compliant with all the Maldives government regulations pertaining this work. For stack emission the design has to consider the limits of the European legislation (17. BImSchV, European norm) or similar |
| Factory Testing | Before shipment the bidder hat to do quality control and functional tests without waste to demonstrate the quality of the equipment and the ability to the equipment to meet the requirements. the inspection will be made by a representative of the employer. Part of the Factory Acceptance Test (FAT) is also the test of the controls and the implementation of a full functional control simulation of each completed control panel and MCC (if used).The bidder has to demonstrate the correct operation of each circuit, instrument loop, alarm and function including communication of output via TCP/ IP Ethernet. |
| Construction | The bidder has to Furnish all services, including all labor, materials, tools, supplies, consumables, technical, professional services, equipment, transportation, supervision, office or storage facilities, personal, protective equipment and test equipment necessary and required to complete the incineration system in accordance with the contract terms and conditions. |
| field test and commissioning | Prior to equipment installation the bidder has to check equipment foundations and other site conditions for compliance with requirements for installation. |
| Startup Testing | The bidder has to conduct Site Acceptance Tests (SAT) at the site to demonstrate that performance of incineration system meets the required operational requirements and guarantees. The stack emission test must be performed by an independent company. The bidder has to perform a running test to check for excessive vibrations, leaks and proper operation of the equipment and controls. He has to simulate actual service conditions to the extent possible to verify performer. The bidder has to perform al full functional control simulation of the DCS, control panel and PLC and to demonstrate correct operation of each circuit, instrument loop, alarm and function including communication of outputs via THP/IP Ethernet. |
| Commissioning | The bidder has to perform a 72 hour-test run during commissioning to prove the incineration system performance and compliance with the specification requirements and Maldives government regulations. Each process unit of the incineration system has to be tested at the design conditions. the stack emission test must be performed by an independent company. |
| Training and additional support | The bidder has to provide a training program for the system operators, which also includes the training on the assembly and disassembly of the equipment required maintenance and operation. The training consists of minimum 3 (three) day class room training and 5 (five) days training on site. An additional support should be quoted by providing a periodical inspection and training on the job for 10 days every 2 months during the first 6 months of operation. |
| Guarantees | The following parameters are guaranteed values Parameter; Unit. Throughput; 50TPD (2T/H). Power output net; 1000KW Net to Grid. Temporally waste storage; 350 to 400 m3. transport capacity; 2. t/h. operation time; 330 days/year. emission values; total dust; 10 mg/Nm³. total hydrocarbons (THC); 10 mg/Nm³. carbon monoxide (CO); 50 mg/Nm³. HCl; 10 mg/Nm³. SO2; 50 mg/Nm³. Cd; 0.05 mg/Nm³. TL; 0.05 mg/Nm³. Pb, Cr (Sb, Cu); 0.5 mg/Nm³. As, Co, Ni (Mn, V, Sn); 0.5 mg/Nm³. Hg; 0.05 mg/Nm³. (Basis = 11 Vol.-% O2, dry flue gas) |
| Service Contract | The bidder has to quote a service contract for a periodical maintenance, inspection. The quotation has to be made for 2 years with a possibility of extension and should be based on a bidders experience of yearly maintenances (major maintenance and revision part),. The quotation shall include the sending of adequate engineer on site including flight, transport and accommodation. The quotation should be made as a lump sum for the period of 2 years. Price for this has to be mentioned separately in the tender. |
| Grid Connection | Connection of the Power plant to the external networks will have to be specified according to the Technical Conditions for connection issued by network owners or operators. The connection point and the interface should be defined before commencement of the work. Bidder has to quote for the scope of works for the electrical scope and grid connection detailed in Annexes 2A and 2B and 2C of this document. |

### 3.Drawings

Drawing N°68521_WU_LP_170529_A1_1-500 is attached

The layout drawing is only for information purposes for the tentative positioning and size of the plant, and should be adapted by the contractor for its own design.

### 4.  Supplementary Information

A complete feasibility study could be provided by the client upon request of the contractor after award

Household waste composition

| Waste composition | % | Trend |
| --- | --- | --- |
| Organics | 70% | constant |
| Garden waste | 30% |  |
| Kitchen waste | 30% |  |
| other organics | 10% |  |
| Paper & cardboard | 7% | constant |
| Glass | 3% | decrease by 1% |
| Plastics | 5% | increase in the next years probably by 2-3 % |
| Metals | 4% | constant |
| Hazardous wastes (including clinical) | 2% | constant |
| Other (inert & dust)/mixed waste | 9% | decrease |
| Total | 100% |  |

Resort waste composition

| Waste composition | % | Trend |
| --- | --- | --- |
| Organics | 74% | constant |
| Garden waste | 19% |  |
| Kitchen waste | 45% |  |
| other organics | 10% |  |
| Paper & cardboard | 9% | constant |
| Glass | 5% | constant |
| Plastics | 5% | constant |
| Metals | 2% | constant |
| Hazardous wastes (including clinical) | 0,5% | constant |
| Other (inert & dust)/mixed waste | 4,5% | constant |
| Total | 100% |  |

Physical parameters of waste

| Waste composition | Calorific value kJ/kg |  | Water content % |  | Glowing loss (dry substance) % |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | min | max | min | max | min | max |
| Organics |  |  |  |  |  |  |
| Garden waste | 1.000 | 9.000 | 45 | 85 | 50 | 90 |
| Kitchen waste | 2.500 | 8.500 | 55 | 70 | 90 | 90 |
| other organics | 2.500 | 8.500 | 55 | 70 | 90 | 90 |
| Paper & cardboard | 13.000 | 13.000 | 20 | 20 | 95 | 95 |
| Glass | 0 | 0 | 2 | 2 | 0 | 0 |
| Plastics | 32.500 | 32.500 | 10 | 10 | 95 | 95 |
| Metals | 0 | 0 | 5 | 5 | 0 | 0 |
| Hazardous wastes (including clinical) | 9.500 | 9.500 | 25 | 25 | 75 | 75 |
| Other (inert & dust)/mixed waste | 7.800 | 7.800 | 25 | 25 | 75 | 75 |

### 5. Certificates

5.1  Form of Completion Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Dear Ladies and/or Gentlemen,

Pursuant to GCC Clause 24 (Completion of the Facilities) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . . . .insert date. . . . . ], relating to the [. . . .brief description of the Facilities . . . .], we hereby notify you that the following part(s) of the Facilities was (were) complete on the date specified below, and that, in accordance with the terms of the Contract, the Employer hereby takes over the said part(s) of the Facilities, together with the responsibility for care and custody and the risk of loss thereof on the date mentioned below.

1.	Description of the Facilities or part thereof:  [. . . .description . . . .]

2.	Date of Completion:  [. . . .date . . . .]

However, you are required to complete the outstanding items listed in the attachment hereto as soon as practicable.

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

5.2  Form of Operational Acceptance Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Pursuant to GCC Subclause 25.3 (Operational Acceptance) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . .date. . .], relating to the [. . .brief description of the facilities. . .], we hereby notify you that the Functional Guarantees of the following part(s) of the Facilities were satisfactorily attained on the date specified below.

1.	Description of the Facilities or part thereof:  [. . . description . . .]

2.	Date of Operational Acceptance:  [. . . date . . .]

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

### 6.  Change Orders

6.1	Change Order Procedure

6.1.1	General

6.1.2	Change Order Log

6.1.3	References for Changes

6.2.	Change Order Forms

6.2.1	Request for Change Proposal

6.2.2	Estimate for Change Proposal

6.2.3	Acceptance of Estimate

6.2.4	Change Proposal

6.2.5	Change Order

6.2.6	Pending Agreement Change Order

6.2.7	Application for Change Proposal

6.1. 	Change Order Procedure

6.1.1  General

This section provides samples of procedures and forms for implementing changes in the Facilities during the performance of the Contract in accordance with GCC Clause 39 (Change in the Facilities) of the General Conditions.

6.1.2 Change Order Log

The Contractor shall keep an up-to-date Change Order Log to show the current status of Requests for Change and Changes authorized or pending. Entries of the Changes in the Change Order Log shall be made to ensure that the log is up-to-date. The Contractor shall attach a copy of the current Change Order Log in the monthly progress report to be submitted to the Employer.

6.1.3	References for Changes

(1)	Request for Change as referred to in GCC Clause 39 shall be serially numbered CR-X-nnn.

(2)	Estimate for Change Proposal as referred to in GCC Clause 39 shall be serially numbered CN-X-nnn.

(3)	Acceptance of Estimate as referred to in GCC Clause 39 shall be serially numbered CA-X-nnn.

(4)	Change Proposal as referred to in GCC Clause 39 shall be serially numbered CP-X-nnn.

(5)	Change Order as referred to in GCC Clause 39 shall be serially numbered CO-X-nnn.

Note:

(a)	Requests for Change issued from the Employer’s Home Office and the Site representatives of the Employer shall have the following respective references:

Home Office	CR-H-nnn

Site		CR-S-nnn

(b)	The above number “nnn” is the same for Request for Change, Estimate for Change Proposal, Acceptance of Estimate, Change Proposal and Change Order.

6.2	Change Order Forms

6.2.1  Request for Change Proposal Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to the captioned Contract, you are requested to prepare and submit a Change Proposal for the Change noted below in accordance with the following instructions within [  number  ] days of the date of this letter [or on or before (  date  )].

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Originator of Change:

Employer:  [Name]

Contractor (by Application for Change Proposal No. [Number Refer to Annex 6.2.7])

4.	Brief Description of Change:  [  Description  ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [  Description  ]

6.	Reference drawings and/or technical documents for the request of Change:

Drawing No./Document No.		Description

7.	Detailed conditions or special requirements on the requested Change:  [  Description  ]

8.	General Terms and Conditions:

(a)	Please submit your estimate showing what effect the requested Change will have on the Contract Price.

(b)	Your estimate shall include your claim for the additional time, if any, for completing the requested Change.

(c)	If you have any opinion that is critical to the adoption of the requested Change in connection with the conformability to the other provisions of the Contract or the safety of the Plant or Facilities, please inform us in your proposal of revised provisions.

(d)	Any increase or decrease in the work of the Contractor relating to the services of its personnel shall be calculated.

(e)	You shall not proceed with the execution of the work for the requested Change until we have accepted and confirmed the amount and nature in writing.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.2   Estimate for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to your Request for Change Proposal, we are pleased to notify you of the approximate cost to prepare the below-referenced Change Proposal in accordance with GCC Subclause 39.2.1 of the General Conditions.  We acknowledge that your agreement to the cost of preparing the Change Proposal, in accordance with GCC Subclause 39.2.2, is required before estimating the cost for change work.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Brief Description of Change:  [  Description  ]

4.	Scheduled Impact of Change:  [  Description  ]

5.	Cost for Preparation of Change Proposal:  [  insert costs, which shall be in the currencies of the contract  ]

(a)	Engineering	(Amount)

(i)	Engineer		 hours (hrs) x 	 rate/hr =

(ii)	Draftsperson		 hrs x 	 rate/hr =

Sub-total		 hrs

Total Engineering Cost

(b)	Other Cost

Total Cost (a) + (b)

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.3  Acceptance of Estimate Form

[ Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [ Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby accept your Estimate for Change Proposal and agree that you should proceed with the preparation of the Change Proposal.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Request number/revision  ]

3.	Estimate for Change Proposal No./Rev.:  [  Proposal number/revision  ]

4.	Acceptance of Estimate No./Rev.:  [  Estimate number/revision  ]

5.	Brief Description of Change:  [  Description  ]

6.	Other Terms and Conditions:  In the event that we decide not to order the Change accepted, you shall be entitled to compensation for the cost of preparing the Change Proposal described in your Estimate for Change Proposal mentioned in para. 3 above in accordance with GCC Clause 39 of the General Conditions.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.4  Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

In response to your Request for Change Proposal No. [Number], we hereby submit our proposal as follows:

1.	Title of Change:  [  Name  ]

2.	Change Proposal No./Rev.:  [  Proposal number / revision ]

3.	Originator of Change:	Employer:  [ Name  ] / Contractor:  [  Name  ]

4.	Brief Description of Change:  [  Description  ]

5.	Reasons for Change:  [  Reason  ]

6.	Facilities and/or Item No. of Equipment related to the requested Change:  [  Facilities  ]

7.	Reference drawings and/or technical documents for the requested Change:

[  Drawing/Document No./Description  ]

8.	Estimate of increase/decrease to the Contract Price resulting from the Change Proposal:

Amount

[ insert  amounts in the currencies of the Contract ]

(a)	Direct material

(b)	Major construction equipment

(c)	Direct field labor (Total 	 hrs)

(d)	Subcontracts

(e)	Indirect material and labor

(f)	Site supervision

(g)	Head office technical staff salaries

Process engineer		 hrs @ 	 rate/hr

Project engineer		 hrs @ 	 rate/hr

Equipment engineer		 hrs @ 	 rate/hr

Procurement		 hrs @ 	 rate/hr

Draftsperson		 hrs @ 	  rate/hr

Total			hrs

(h)	Extraordinary costs (computer, travel, etc.)

(i)	Fee for general administration, 	 % of Items

(j)	Taxes and customs duties

Total lump sum cost of Change Proposal		[  Sum of items (a) to (j)  ]

Cost to prepare Estimate for Change Proposal	 	[  Amount payable if Change is not accepted  ]

9.	Additional time for Completion required due to Change Proposal

10.	Effect on the Functional Guarantees

11.	Effect on the other terms and conditions of the Contract

12.	Validity of this Proposal:  within [Number] days after receipt of this Proposal by the Employer

13.	Other terms and conditions of this Change Proposal:

(a)	You are requested to notify us of your acceptance, comments or rejection of this detailed Change Proposal within [Number] days from your receipt of this Proposal.

(b)	The amount of any increase and/or decrease shall be taken into account in the adjustment of the Contract Price.

(c)	Contractor’s cost for preparation of this Change Proposal: [ . . . .insert amount. This cost shall be reimbursed by the employer in case of employer’s withdrawal or rejection of this Change Proposal without default of the contractor in accordance with GCC Clause 39 of the General Conditions . . . . ]

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.5  Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We approve the Change Order for the work specified in the Change Proposal (No. [  number  ]), and agree to adjust the Contract Price, Time for Completion, and/or other conditions of the Contract in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Change Request No./Rev.:  [  Request number / revision  ]

3.	Change Order No./Rev.:  [  Order number / revision  ]

4.	Originator of Change:	Employer:  [Name] / Contractor:  [  Name  ]

5.	Authorized Price:

Ref. No.:  [  Number  ]	Date:  [  Date  ]

Foreign currency portion [  Amount  ]  plus Local currency portion [  Amount  ]

6.	Adjustment of Time for Completion

None		Increase [  Number  ] days	 	Decrease [  Number  ] days

7.	Other effects, if any

Authorized by:  		Date:

Employer

Accepted by:  		Date:

Contractor

6.2.6  Pending Agreement Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We instruct you to carry out the work in the Change Order detailed below in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Employer’s Request for Change Proposal No./Rev.:  [  number/revision  ]	dated:  [ date  ]

3.	Contractor’s Change Proposal No./Rev.:  [  number / revision  ]	dated:  [ date ]

4.	Brief Description of Change:  [ Description ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [ Facilities ]

6.	Reference Drawings and/or technical documents for the requested Change:

[  Drawing / Document No. / Description  ]

7.	Adjustment of Time for Completion:

8.	Other change in the Contract terms:

9.	Other terms and conditions:

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.7  Application for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby propose that the work mentioned below be treated as a Change in the Facilities.

1.	Title of Change:  [  Name  ]

2.	Application for Change Proposal No./Rev.:  [  Number / revision  ]	dated:  [  Date  ]

3.	Brief Description of Change:  [  Description  ]

4.	Reasons for Change:

5.	Order of Magnitude Estimation (amount in the currencies of the Contract): [  Amount  ]

6.	Scheduled Impact of Change:

7.	Effect on Functional Guarantees, if any:

8.	Appendix:

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

- 7.  Personnel Requirements

Using Form PER - 1 and PER - 2 in Section 4 (Bidding Forms), the Bidder must demonstrate that it has personnel who meet the following requirements:

| No. | Position | Total Work Experience [years] | Experience In Similar Work [years] |
| --- | --- | --- | --- |
| 1 | Team leader (civil or mechanical engineer) | Min. 15 years | Min. 10 years |
| 2 | Foreman (civil or mechanical engineer) | Min. 15 years | Min 10 years |
| 3 | Electrician | Min. 10 years | Min 5 years |
| 4 | Heavy vehicle operators | Min. 10 | Min 5 years |
| 5 | Supporting staff | Min 5 years | Min. 2 years |

- 8.  Equipment Requirements

Using Form EQU in Section 4 (Bidding Forms), the Bidder must demonstrate that it has the key equipment listed below:

| No. | Equipment Type and Characteristics | Minimum Number Required |
| --- | --- | --- |
| 1 | Crane (min height) 25 m | 1 |
| 2 | Wheel loader | 1 |
| 3 | Forklift | 2 |
| 4 | Dump trucks | 2 |
| 5 | Roller compactor | 1 |
| 6 | Concrete mixer | 1 |

Section 7 - General Conditions of Contract

The GCC contain general clauses to be applied on all contracts. The GCC in this section, read in conjunction with the Special Conditions of Contract in Section 8 and other documents listed therein, should be a complete document expressing all the rights and obligations of the contracting parties. The General Conditions herein shall not be altered.

## Table of Clauses

A.  Contract and Interpretation	7-3

1.	Definitions	7-3

2.	Contract Documents	7-5

3.	Interpretation	7-5

4.  	Communications	7-7

5.	Law and Language	7-7

6.	Fraud  and Corruption	7-7

B.  Subject Matter of Contract	7-9

7.	Scope of Facilities	7-9

8.	Time for Commencement and Completion	7-9

9.	Contractor’s Responsibilities	7-10

10.	Employer’s Responsibilities	7-11

C.  Payment	7-12

11.	Contract Price	7-12

12.	Terms of Payment	7-12

13.	Securities	7-13

14.	Taxes and Duties	7-14

D.  Intellectual Property	7-14

15.	License/Use of Technical Information	7-14

16.	Confidential Information	7-15

E.   Execution of the Facilities	7-15

17.	Representatives	7-16

18.	Work Program	7-17

19.	Subcontracting	7-18

20.	Design and Engineering	7-19

21.	Procurement	7-21

22.	Installation	7-22

23.	Test and Inspection	7-28

24.	Completion of the Facilities	7-30

25. Commissioning and Operational Acceptance	7-31

F.  Guarantees and Liabilities	7-34

26.	Completion Time Guarantee	7-34

27.	Defect Liability	7-35

28.	Functional Guarantees	7-36

29.	Patent Indemnity	7-37

30.	Limitation of Liability	7-38

G.  Risk Distribution	7-38

31.	Transfer of Ownership	7-38

32.	Care of Facilities	7-39

33.	Loss of or Damage to Property; Accident or Injury to Workers; Indemnification	7-40

34.	Insurance	7-41

35.	Unforeseen Conditions	7-43

36.	Change in Laws and Regulations	7-44

37.	Force Majeure	7-44

38.	War Risks	7-45

H.  Change in Contract Elements	7-47

39.	Change in the Facilities	7-47

40.	Extension of Time for Completion	7-50

41.	Suspension	7-51

42.	Termination	7-52

43.	Assignment	7-57

I.  Claims, Disputes and Arbitration	7-58

44.	Contractor’s Claims	7-58

45. Disputes and Arbitration	7-59

General Conditions of Contract

A.  Contract and Interpretation

| 1. Definitions | 1.1 The following words and expressions shall have the meanings hereby assigned them: “Contract” means the Contract Agreement entered into between the Employer and the Contractor, together with the Contract Documents referred to therein; they shall constitute the Contract, and the term “the Contract” shall in all such documents be construed accordingly. “Contract Documents” means the documents listed in Article 1.1 (Contract Documents) of the Contract Agreement (including any amendments thereto). “GCC” means the General Conditions of Contract. “SCC” means the Special Conditions of Contract. “day” means calendar day. “year” means 365 days. “month” means calendar month. “Party” means the Employer or the Contractor, as the context requires. “Employer” means the person named as such in the SCC and includes the legal successors or permitted assigns of the Employer. “Project Manager” means the person appointed by the Employer in the manner provided in GCC Subclause 17.1 (Project Manager) hereof and named as such in the SCC to perform the duties delegated by the Employer. “Contractor” means the person(s) named as Contractor in the Contract Agreement, and includes the legal successors or permitted assigns of the Contractor. “Contractor’s Representative” means any person nominated by the Contractor and approved by the Employer in the manner provided in GCC Subclause 17.2 (Contractor’s Representative and Construction Manager) hereof to perform the duties delegated by the Contractor. “Construction Manager” means the person appointed by the Contractor’s Representative in the manner provided in GCC Subclause 17.2.4. “Subcontractor,” including manufacturers, means any person to whom execution of any part of the Facilities, including preparation of any design or supply of any Plant, is sub-contracted directly or indirectly by the Contractor, and includes its legal successors or permitted assigns. “Dispute Board” means the person or persons named as such in the SCC appointed by agreement between the Employer and the Contractor to make a decision on or to settle any dispute or difference between the Employer and the Contractor referred to him or her by the parties pursuant to GCC Subclause 45.1 (Dispute Board) hereof. “The Agency” means the financing institution named in the SCC. “Contract Price” means the sum specified in Article 2.1 (Contract Price) of the Contract Agreement, subject to such additions and adjustments thereto or deductions therefrom, as may be made pursuant to the Contract. “Facilities” means the Plant to be supplied and installed, as well as all the Installation Services to be carried out by the Contractor under the Contract. “Plant” means permanent plant, equipment, machinery, apparatus, articles and things of all kinds to be provided and incorporated in the Facilities by the Contractor under the Contract (including the spare parts to be supplied by the Contractor under GCC Subclause 7.3 hereof), but does not include Contractor’s Equipment. “Installation Services” means all those services ancillary to the supply of the Plant for the Facilities, to be provided by the Contractor under the Contract, such as transportation and provision of marine or other similar insurance, inspection, expediting, site preparation works (including the provision and use of Contractor’s Equipment and the supply of all construction materials required), installation, testing, precommissioning, commissioning, operations, maintenance, the provision of operations and maintenance manuals, training, etc. as the case may require. “Contractor’s Equipment” means all facilities, equipment, machinery, tools, apparatus, appliances, or things of every kind required in or for installation, completion and maintenance of Facilities that are to be provided by the Contractor, but does not include Plant, or other things intended to form or forming part of the Facilities. “Country of Origin” means the countries and territories eligible under the rules of the Agency as further elaborated in the SCC. “Site” means the land and other places upon which the Facilities are to be installed, and such other land or places as may be specified in the Contract as forming part of the Site. “Effective Date” means the date of fulfillment of all conditions stated in Article 3 (Effective Date) of the Contract Agreement, upon which the period until the Time for Completion shall be counted from. “Time for Completion” means the time within which Completion of the Facilities as a whole (or of a part of the Facilities where a separate Time for Completion of such part has been prescribed) is to be attained, as referred to in GCC Clause 8 and in accordance with the relevant provisions of the Contract. “Completion” means that the Facilities (or a specific part thereof where specific parts are specified in the Contract) have been completed operationally and structurally and put in a tight and clean condition, that all work in respect of Precommissioning of the Facilities or such specific part thereof has been completed, and that the Facilities or specific part thereof are ready for Commissioning as provided in GCC Clause 24 (Completion) hereof. “Precommissioning” means the testing, checking and other requirements specified in the Employer’s Requirements that are to be carried out by the Contractor in preparation for Commissioning as provided in GCC Clause 24 (Completion) hereof. “Commissioning” means operation of the Facilities or any part thereof by the Contractor following Completion, which operation is to be carried out by the Contractor as provided in GCC Subclause 25.1 (Commissioning) hereof, for the purpose of carrying out Guarantee Test(s). “Guarantee Test(s)” means the test(s) specified in the Employer’s Requirements to be carried out to ascertain whether the Facilities or a specified part thereof is able to attain the Functional Guarantees specified in the Appendix (Functional Guarantees) to the Contract Agreement in accordance with the provisions of GCC Subclause 25.2 (Guarantee Test) hereof. “Operational Acceptance” means the acceptance by the Employer of the Facilities (or any part of the Facilities where the Contract provides for acceptance of the Facilities in parts), which certifies the Contractor’s fulfillment of the Contract in respect of Functional Guarantees of the Facilities (or the relevant part thereof) in accordance with the provisions of GCC Clause 28 (Functional Guarantees) hereof and shall include deemed acceptance in accordance with GCC Clause 25 (Commissioning and Operational Acceptance) hereof. “Defect Liability Period” means the period of validity of the warranties given by the Contractor commencing at Completion of the Facilities or a part thereof, during which the Contractor is responsible for defects with respect to the Facilities (or the relevant part thereof) as provided in GCC Clause 27 (Defect Liability) hereof. |
| --- | --- |
| 2. Contract Documents | 2.1 Subject to Article 1.2 (Order of Precedence) of the Contract Agreement, all documents forming part of the Contract (and all parts thereof) are intended to be correlative, complementary and mutually explanatory. The Contract shall be read as a whole. |
| 3. Interpretation | 3.1 In the Contract, except where the context requires otherwise, - words indicating one gender include all genders; - words indicating the singular also include the plural and words indicating the plural also include the singular; - provisions including the word “agree,” “agreed,” or “agreement” require the agreement to be record in writing; - the word “tender” is synonymous with “bid,” “tenderer” with “Bidder,” and “tender documents” with “Bidding Documents;” and - “written” or “in writing” means handwritten, typewritten, printed or electronically made, and resulting in a permanent record. The marginal words and other headings shall not be taken into consideration in the interpretation of these Conditions. 3.2 Incoterms Unless inconsistent with any provision of the Contract, the meaning of any trade term and the rights and obligations of parties thereunder shall be as prescribed by Incoterms. “Incoterms” means international rules for interpreting trade terms published by the International Chamber of Commerce (latest edition), 38 Cours Albert 1er, 75008 Paris, France. 3.3 Entire Agreement Subject to GCC Subclause 16.4 hereof, the Contract constitutes the entire agreement between the Employer and Contractor with respect to the subject matter of Contract and supersedes all communications, negotiations, and agreements (whether written or oral) of parties with respect thereto made prior to the date of Contract. 3.4 Amendment No amendment or other variation of the Contract shall be effective unless it is in writing, is dated, expressly refers to the Contract, and is signed by a duly authorized representative of each party hereto. 3.5 Independent Contractor The Contractor shall be an independent contractor performing the Contract. The Contract does not create any agency, partnership, joint venture, or other joint relationship between the parties hereto. Subject to the provisions of the Contract, the Contractor shall be solely responsible for the manner in which the Contract is performed. All employees, representatives, or Subcontractors engaged by the Contractor in connection with the performance of the Contract shall be under the complete control of the Contractor and shall not be deemed to be employees of the Employer, and nothing contained in the Contract or in any subcontract awarded by the Contractor shall be construed to create any contractual relationship between any such employees, representatives, or Subcontractors and the Employer. 3.6 Non-Waiver 3.6.1 Subject to GCC Subclause 3.6.2 below, no relaxation, forbearance, delay, or indulgence by either party in enforcing any of the terms and conditions of the Contract or the granting of time by either party to the other shall prejudice, affect, or restrict the rights of that party under the Contract, nor shall any waiver by either party of any breach of Contract operate as waiver of any subsequent or continuing breach of Contract. 3.6.2 Any waiver of a party’s rights, powers, or remedies under the Contract must be in writing, must be dated, and signed by an authorized representative of the party granting such waiver, and must specify the right and the extent to which it is being waived. 3.7 Severability If any provision or condition of the Contract is prohibited or rendered invalid or unenforceable, such prohibition, invalidity, or unenforceability shall not affect the validity or enforceability of any other provisions and conditions of the Contract. 3.8 Country of Origin “Origin” means the place where the plant and component parts thereof are mined, grown, produced, or manufactured, and from which the services are provided. Plant components are produced when, through manufacturing, processing, or substantial or major assembling of components, a commercially recognized product results that is substantially in its basic characteristics or in purpose or utility from its components. |
| 4. Communications | 4.1 Wherever these Conditions provide for the giving or issuing of approvals, certificates, consents, determinations, notices, requests, and discharges, these communications shall be - in writing and delivered against receipt; and - delivered, sent, or transmitted to the address for the recipient’s communications as stated in the Contract Agreement. When a certificate is issued to a Party, the certifier shall send a copy to the other Party. When a notice is issued to a Party, by the other Party or the Project Manager, a copy shall be sent to the Project Manager or the other Party, as the case may be. |
| 5. Law and Language | 5.1 The Contract shall be governed by and interpreted in accordance with laws of the country specified in the SCC. 5.2 The ruling language of the Contract shall be that stated in the SCC. 5.3 The language for communications shall be the ruling language unless otherwise stated in the SCC. |
| 6. Fraud and Corruption | 6.1 ADFD’s Anticorruption Policy requires Borrowers (including beneficiaries of ADFD-financed activity), as well as Bidders, Suppliers, and Contractors under ADFD-financed contracts, observe the highest standard of ethics during the procurement and execution of such contracts. In pursuance of this policy, ADFD - defines, for the purposes of this provision, the terms set forth below as follows: - “corrupt practice” means the offering, giving, receiving, or soliciting, directly or indirectly, anything of value to influence improperly the actions of another party; - “fraudulent practice” means any act or omission, including a misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain a financial or other benefit or to avoid an obligation; - “coercive practice” means impairing or harming, or threatening to impair or harm, directly or indirectly, any party or the property of the party to influence improperly the actions of a party; - “collusive practice” means an arrangement between two or more parties designed to achieve an improper purpose, including influencing improperly the actions of another party; - “obstructive practice” means (a) deliberately destroying, falsifying, altering, or concealing of evidence material to an ADFD investigation; (b) making false statements to investigators in order to materially impede an ADFD investigation; (c) failing to comply with requests to provide information, documents, or records in connection with an Office of Anticorruption and Integrity (OAI) investigation; (d) threatening, harassing, or intimidating any party to prevent it from disclosing its knowledge of matters relevant to the investigation or from pursuing the investigation, or (e) materially impeding ADFDʼs contractual rights of audit or access to information; and - “integrity violation" is any act which violates ADFD’s Anticorruption Policy, including (i) to (v) above and the following: abuse, conflict of interest, violations of ADFD sanctions, retaliation against whistleblowers or witnesses, and other violations of ADFD's Anticorruption Policy, including failure to adhere to the highest ethical standard. - will reject a proposal for award if it determines that the Bidder recommended for award has, directly or through an agent, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices or other integrity violations in competing for the Contract; - will cancel the portion of the financing allocated to a contract if it determines at any time that representatives of the Borrower or of a beneficiary of ADFD-financing engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices or other integrity violations during the procurement or the execution of that contract, without the Borrower having taken timely and appropriate action satisfactory to ADFD to remedy the situation; - will impose remedial actions on a firm or an individual, at any time, in accordance with ADFD’s Anticorruption Policy and Integrity Principles and Guidelines (both as amended from time to time), including declaring ineligible, either indefinitely or for a stated period of time, to participate in ADFD-financed, -administered, or -supported activities or to benefit from an ADFD-financed, -administered, or -supported contract, financially or otherwise, if it at any time determines that the firm or individual has, directly or through an agent, engaged in corrupt, fraudulent, collusive, coercive, or obstructive practices or other integrity violations; and - will have the right to require suppliers and contractors to permit ADFD or its representative to inspect their accounts and records and other documents relating to the bid submission and contract performance and to have them audited by auditors appointed by ADFD. |

B.  Subject Matter of Contract

| 7. Scope of Facilities | 7.1 Unless otherwise expressly limited in the Employer’s Requirements, the Contractor’s obligations cover the provision of all Plant and the performance of all Installation Services required for the design, the manufacture (including procurement, quality assurance, construction, installation, associated civil works, pre-commissioning and delivery) of the Plant and the installation, completion, and commissioning of the Facilities in accordance with the plans, procedures, specifications, drawings, codes, and any other documents as specified in the section Employer’s Requirements. Such specifications include, but are not limited to, the provision of supervision and engineering services; the supply of labor, materials, equipment, spare parts (as specified in GCC Subclause 7.3 below) and accessories; Contractor’s Equipment; construction utilities and supplies; temporary materials, structures, and facilities; transportation (including, without limitation, unloading and hauling to, from and at the Site); and storage, except for those supplies, works, and services that will be provided or performed by the Employer, as set forth in the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement. 7.2 The Contractor shall, unless specifically excluded in the Contract, perform all such work and/or supply all such items and materials not specifically mentioned in the Contract but that can be reasonably inferred from the Contract as being required for attaining Completion of the Facilities as if such work and/or items and materials were expressly mentioned in the Contract. 7.3 In addition to the supply of Mandatory Spare Parts included in the Contract, the Contractor agrees to supply spare parts required for the operation and maintenance of the Facilities for the period specified in the SCC and the provisions, if any, specified in the SCC. However, the identity, specifications, and quantities of such spare parts and the terms and conditions relating to the supply thereof are to be agreed between the Employer and the Contractor, and the price of such spare parts shall be that given in Price Schedule No. 6, which shall be added to the Contract Price. The price of such spare parts shall include the purchase price therefore and other costs and expenses (including the Contractor’s fees) relating to the supply of spare parts. |
| --- | --- |
| 8. Time for Commencement and Completion | 8.1 The Contractor shall commence work on the Facilities within the period specified in the SCC and without prejudice to GCC Subclause 26.2 hereof, the Contractor shall thereafter proceed with the Facilities in accordance with the time schedule specified in the Appendix 4 (Time Schedule) to the Contract Agreement. 8.2 The Contractor shall attain Completion of the Facilities or of a part where a separate time for Completion of such part is specified in the Contract, within the time stated in the SCC or within such extended time to which the Contractor shall be entitled under GCC Clause 40 hereof. |
| 9. Contractor’s Responsibilities | 9.1 The Contractor shall design, manufacture, including associated purchases and/or subcontracting, install, and complete the Facilities in accordance with the Contract. When completed, the Facilities should be fit for the purposes for which they are intended as defined in the Contract. 9.2 The Contractor confirms that it has entered into this Contract on the basis of a proper examination of the data relating to the Facilities, including any data as to boring tests provided by the Employer, and on the basis of information that the Contractor could have obtained from a visual inspection of the Site if access thereto was available and of other data readily available to it relating to the Facilities as of the date 28 days prior to bid submission. The Contractor acknowledges that any failure to acquaint itself with all such data and information shall not relieve its responsibility for properly estimating the difficulty or cost of successfully performing the Facilities. 9.3 The Contractor shall acquire and pay for all permits, approvals, and/or licenses from all local, state, or national government authorities or public service undertakings in the country where the Site is located, which such authorities or undertakings require the Contractor to obtain in its name and which are necessary for the performance of the Contract, including, without limitation, visas for the Contractor’s and Subcontractor’s personnel and entry permits for all imported Contractor’s Equipment. The Contractor shall acquire all other permits, approvals, and/or licenses that are not the responsibility of the Employer under GCC Subclause 10.3 hereof and that are necessary for the performance of the Contract. 9.4 The Contractor shall comply with all laws in force in the country where the Facilities are to be implemented. The laws will include all local, state, national, or other laws that affect the performance of the Contract and bind upon the Contractor. The Contractor shall indemnify and hold harmless the Employer from and against any and all liabilities, damages, claims, fines, penalties, and expenses of whatever nature arising or resulting from the violation of such laws by the Contractor or its personnel, including the Subcontractors and their personnel, but without prejudice to GCC Subclause 10.1 hereof. 9.5 Any plant and services that will be incorporated in or be required for the Facilities and other supplies shall have their origin as specified under GCC Clause 1 (Country of Origin). Any Subcontractors retained by the Contractor shall be from a country as specified in GCC Clause 1 (Country of Origin). - The Contractor shall permit ADFD to inspect the Contractor’s accounts and records relating to the performance of the Contractor and to have them audited by auditors appointed by ADFD, if so required by ADFD. - If the Contractor is a joint venture or consortium of two or more persons, all such persons shall be jointly and severally bound to the Employer for the fulfillment of the provisions of the Contract and shall designate one of such persons to act as a leader with authority to bind the joint venture or consortium. The composition or the constitution of the joint venture or consortium shall not be altered without the prior consent of the Employer. - Protection of the Environment - The Contractor shall take all reasonable steps to protect the environment (both on and off the Site) and to limit damage and nuisance to people and property resulting from pollution, noise, and other results of his operations. - The Contractor shall ensure that emissions, surface discharges, and effluent from the Contractor’s activities shall not exceed the values stated in the Specification or prescribed by applicable Laws. |
| 10. Employer’s Responsibilities | 10.1 All information and/or data to be supplied by the Employer as described in the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement shall be deemed to be accurate, except when the Employer expressly states otherwise. 10.2 The Employer shall be responsible for acquiring and providing legal and physical possession of the Site and access thereto, and for providing possession of and access to all other areas reasonably required for the proper execution of the Contract, including all requisite rights of way, as specified in the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement. The Employer shall give full possession of and accord all rights of access thereto on or before the date(s) specified in that Appendix. 10.3 The Employer shall acquire and pay for all permits, approvals, and/or licenses from all local, state, or national government authorities, or public service undertakings in the country where the Site is located which (a) such authorities or undertakings require the Employer to obtain in the Employer’s name, (b) are necessary for the execution of the Contract, including those required for the performance by both the Contractor and the Employer of their respective obligations under the Contract, and (c) are specified in the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement. 10.4 If requested by the Contractor, the Employer shall use its best endeavors to assist the Contractor in obtaining in a timely and expeditious manner all permits, approvals, and/or licenses necessary for the execution of the Contract from all local, state, or national government authorities, or public service undertakings that such authorities or undertakings require the Contractor or Subcontractors or the personnel of the Contractor or Subcontractors, as the case may be, to obtain. 10.5 Unless otherwise specified in the Contract or agreed upon by the Employer and the Contractor, the Employer shall provide sufficient, properly qualified operating and maintenance personnel; shall supply and make available all raw materials, utilities, lubricants, chemicals, catalysts, other materials and facilities; and shall perform all work and services of whatsoever nature, including those required by the Contractor to properly carry out Pre-commissioning, Commissioning, and Guarantee Tests, all in accordance with the provisions of the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement at or before the time specified in the program furnished by the Contractor under GCC Subclause 18.2 hereof and in the manner thereupon specified or as otherwise agreed upon by the Employer and the Contractor. 10.6 The Employer shall be responsible for the continued operation of the Facilities after Completion, in accordance with GCC Subclause 24.8, and shall be responsible for facilitating the Guarantee Test(s) for the Facilities, in accordance with GCC Subclause 25.2. - All costs and expenses involved in the performance of the obligations under this GCC Clause 10 shall be the responsibility of the Employer, except those incurred by the Contractor with respect to the performance of Guarantee Tests, in accordance with GCC Subclause 25.2. - In the event that the Employer shall be in breach of any of his obligations imposed by the Contract, then the additional cost reasonably incurred by the Contractor in consequence thereof shall be added to the Contract Price. |

C.  Payment

| 11. Contract Price | 11.1 The Contract Price shall be as specified in Article 2 (Contract Price and Terms of Payment) of the Contract Agreement. 11.2 Unless an adjustment clause is provided for in the SCC, the Contract Price shall be a firm lump sum not subject to any alteration, except in the event of a Change in the Facilities or as otherwise provided in the Contract. 11.3 Subject to GCC Subclauses 9.2, 10.1, and 35 hereof, the Contractor shall be deemed to have satisfied itself as to the correctness and sufficiency of the Contract Price, which shall, except as otherwise provided for in the Contract, cover all its obligations under the Contract. |
| --- | --- |
| 12. Terms of Payment | 12.1 The Contract Price shall be paid as specified in Article 2 (Contract Price and Terms of Payment) of the Contract Agreement and in the Appendix (Terms and Procedures of Payment) to the Contract Agreement, which also outlines the procedures to be followed in making application for and processing payments. 12.2 No payment made by the Employer herein shall be deemed to constitute acceptance by the Employer of the Facilities or any part(s) thereof. 12.3 In the event that the Employer fails to make any payment by its respective due date or within the period set forth in the Contract, the Employer shall pay to the Contractor interest on the amount of such delayed payment at the rate(s) shown in the Appendix (Terms and Procedures of Payment) to the Contract Agreement for the period of delay until payment has been made in full, whether before or after judgment or arbitrage award. 12.4 The currency or currencies in which payments are made to the Contractor under this Contract shall be specified in the Appendix (Terms and Procedures of Payment) to the Contract Agreement, subject to the general principle that payments will be made in the currency or currencies in which the Contract Price has been stated in the Contractor’s bid. |
| 13. Securities | 13.1 Issuance of Securities The Contractor shall provide the securities specified below in favor of the Employer at the times, and in the amount, manner, and form specified below. 13.2 Advance Payment Security 13.2.1 The Contractor shall, within 28 days of the notification of contract award, provide a security in an amount equal to the advance payment calculated in accordance with the Appendix (Terms and Procedures of Payment) to the Contract Agreement, and in the same currency or currencies. 13.2.2 The security shall be in the form provided in the Bidding Documents or in another form acceptable to the Employer. The amount of the security shall be reduced in proportion to the value of the Facilities executed by and paid to the Contractor from time to time, and shall automatically become null and void when the full amount of the advance payment has been recovered by the Employer. The security shall be returned to the Contractor immediately after its expiration. 13.3 Performance Security 13.3.1 The Contractor shall, within 28 days of the notification of contract award, provide a security for the due performance of the Contract in the amount specified in the SCC. 13.3.2 The security shall be denominated in the currency or currencies of the Contract, or in a freely convertible currency acceptable to the Employer, and shall be in one of the forms of Agency guarantees provided in the Bidding Documents, as stipulated by the Employer in the SCC, or in another form acceptable to the Employer. - Unless otherwise specified in the SCC, the security shall be reduced by half on the date of the Operational Acceptance. The Security shall become null and void, or shall be reduced pro rata to the Contract Price of a part of the Facilities for which a separate Time for Completion is provided, 540 days after Completion of the Facilities or 365 days after Operational Acceptance of the Facilities, whichever occurs first; provided, however, that if the Defects Liability Period has been extended on any part of the Facilities pursuant to GCC Subclause 27.8 hereof, the Contractor shall issue an additional security in an amount proportionate to the Contract Price of that part. The security shall be returned to the Contractor immediately after its expiration, provided, however, that if the Contractor, pursuant to GCC Subclause 27.10, is liable for an extended defect liability obligation, the performance security shall be extended for the period and up to the amount specified in the SCC. |
| 14. Taxes and Duties | 14.1 The works are exempted from all form of taxes and duties imposed in the country as noted in Article 5 clause 16 of the loan agreement between ADFD and the Government of the Maldives 14.2 If any tax exemptions, reductions, allowances, or privileges may be available to the Contractor in the country where the Site is located, the Employer shall use its best endeavors to enable the Contractor to benefit from any such tax savings to the maximum allowable extent. |

D.  Intellectual Property

| 15. License/Use of Technical Information | 15.1 For the operation and maintenance of the Plant, the Contractor hereby grants a non-exclusive and nontransferable license (without the right to sublicense) to the Employer under the patents, utility models, or other industrial property rights owned by the Contractor or by a third party from whom the Contractor has received the right to grant licenses thereunder, and shall also grant to the Employer a nonexclusive and nontransferable right (without the right to sublicense) to use the know-how and other technical information disclosed to the Employer under the Contract. Nothing contained herein shall be construed as transferring ownership of any patent, utility model, trademark, design, copyright, know-how, or other intellectual property right from the Contractor or any third party to the Employer. 15.2 The copyright in all drawings, documents, and other materials containing data and information furnished to the Employer by the Contractor herein shall remain vested in the Contractor or, if they are furnished to the Employer directly or through the Contractor by any third party, including suppliers of materials, the copyright in such materials shall remain vested in such third party. |
| --- | --- |
| 16. Confidential Information | 16.1 The Employer and the Contractor shall keep confidential and shall not, without the written consent of the other party hereto, divulge to any third party any documents, data or other information furnished directly or indirectly by the other party hereto in connection with the Contract, whether such information has been furnished prior to, during, or following termination of the Contract. Notwithstanding the above, the Contractor may furnish to its Subcontractor(s) such documents, data, and other information it receives from the Employer to the extent required for the Subcontractor(s) to perform its work under the Contract, in which event the Contractor shall obtain from such Subcontractor(s) an undertaking of confidentiality similar to that imposed on the Contractor under this GCC Clause 16. 16.2 The Employer shall not use such documents, data, and other information received from the Contractor for any purpose other than the operation and maintenance of the Facilities. Similarly, the Contractor shall not use such documents, data, and other information received from the Employer for any purpose other than the design, procurement of Plant, construction, or such other work and services as are required for the performance of the Contract. 16.3 The obligation of a party under GCC Subclauses 16.1 and 16.2 above, however, shall not apply to that information, which (a) now or hereafter enters the public domain through no fault of that party; (b) can be proven to have been possessed by that party at the time of disclosure and which was not previously obtained, directly or indirectly, from the other party hereto; and (c) otherwise lawfully becomes available to that party from a third party that has no obligation of confidentiality. 16.4 The above provisions of this GCC Clause 16 shall not in any way modify any undertaking of confidentiality given by either of the parties hereto prior to the date of the Contract in respect of the Facilities or any part thereof. 16.5 The provisions of this GCC Clause 16 shall survive termination, for whatever reason, of the Contract. |

E.   Execution of the Facilities

| 17. Representatives | 17.1 Project Manager If the Project Manager is not named in the Contract, then within 14 days of the Effective Date, the Employer shall appoint and notify the Contractor in writing of the name of the Project Manager. The Employer may from time to time appoint some other person as the Project Manager in place of the person previously so appointed, and shall give notice of the name of such other person to the Contractor without delay. No such appointment shall be made at such a time or in such a manner as to impede the progress of work on the Facilities. Such appointment shall only take effect upon receipt of such notice by the Contractor. The Project Manager shall represent and act for the Employer at all times during the performance of the Contract. All notices, instructions, orders, certificates, approvals, and all other communications under the Contract shall be given by the Project Manager, except as herein otherwise provided. All notices, instructions, information, and other communications given by the Contractor to the Employer under the Contract shall be given to the Project Manager, except as herein otherwise provided. 17.2 Contractor’s Representative and Construction Manager 17.2.1 If the Contractor’s Representative is not named in the Contract, then within 14 days of the Effective Date, the Contractor shall appoint the Contractor’s Representative and shall request the Employer in writing to approve the person so appointed. If the Employer makes no objection to the appointment within 14 days, the Contractor’s Representative shall be deemed to have been approved. If the Employer objects to the appointment within 14 days giving the reason therefor, then the Contractor shall appoint a replacement within 14 days of such objection, and the foregoing provisions of this GCC Subclause 17.2.1 shall apply thereto. 17.2.2 The Contractor’s Representative shall represent and act for the Contractor at all times during the performance of the Contract and shall give to the Project Manager all the Contractor’s notices, instructions, information, and all other communications under the Contract. All notices, instructions, information, and all other communications given by the Employer or the Project Manager to the Contractor under the Contract shall be given to the Contractor’s Representative or, in its absence, its deputy, except as herein otherwise provided. The Contractor shall not revoke the appointment of the Contractor’s Representative without the Employer’s prior written consent, which shall not be unreasonably withheld. If the Employer consents thereto, the Contractor shall appoint some other person as the Contractor’s Representative, pursuant to the procedure set out in GCC Subclause 17.2.1. 17.2.3 The Contractor’s Representative may, subject to the approval of the Employer which shall not be unreasonably withheld, at any time delegate to any person any of the powers, functions and authorities vested in him or her. Any such delegation may be revoked at any time. Any such delegation or revocation shall be subject to a prior notice signed by the Contractor’s Representative, and shall specify the powers, functions, and authorities thereby delegated or revoked. No such delegation or revocation shall take effect unless and until a copy thereof has been delivered to the Employer and the Project Manager. Any act or exercise by any person of powers, functions and authorities so delegated to him or her in accordance with this GCC Subclause 17.2.3 shall be deemed to be an act or exercise by the Contractor’s Representative. 17.2.4 From the commencement of installation of the Facilities at the Site until Completion, the Contractor’s Representative shall appoint a suitable person as the Construction Manager. The Construction Manager shall supervise all work done at the Site by the Contractor and shall be present at the Site throughout normal working hours except when on leave, sick, or absent for reasons connected with the proper performance of the Contract. Whenever the Construction Manager is absent from the Site, the Contractor’s Representative or the Construction Manager shall appoint a suitable person to act as the Construction Manager’s deputy. 17.2.5 The Employer may by notice to the Contractor object to any representative or person employed by the Contractor in the execution of the Contract who, in the reasonable opinion of the Employer, may behave inappropriately, may be incompetent or negligent, or may commit a serious breach of the Site regulations provided under GCC Subclause 22.4. The Employer shall provide evidence of the same, whereupon the Contractor shall remove such person from the Facilities. 17.2.6 If any representative or person employed by the Contractor is removed in accordance with GCC Subclause 17.2.5, the Contractor shall, where required, promptly appoint a replacement. |
| --- | --- |
| 18. Work Program | 18.1 Contractor’s Organization The Contractor shall supply to the Employer and the Project Manager a chart showing the proposed organization to be established by the Contractor for carrying out work on the Facilities within 21 days of the Effective Date. The chart shall include the identities of the key personnel, and the curricula vitae of such key personnel to be employed shall be supplied together with the chart. The Contractor shall promptly inform the Employer and the Project Manager in writing of any revision or alteration of such an organization chart. 18.2 Program of Performance Within 28 days after the Effective Date, the Contractor shall submit to the Project Manager a detailed program of performance of the Contract, made in a form acceptable to the Project Manager and showing the sequence in which it proposes to design, manufacture, transport, assemble, install, and pre-commission the Facilities, as well as the date by which the Contractor reasonably requires that the Employer shall have fulfilled its obligations under the Contract so as to enable the Contractor to execute the Contract in accordance with the program and to achieve Completion, Commissioning, and Acceptance of the Facilities in accordance with the Contract. The program so submitted by the Contractor shall accord with the Time Schedule included in the Appendix (Time Schedule) to the Contract Agreement and any other dates and periods specified in the Contract. The Contractor shall update and revise the program as and when appropriate or when required by the Project Manager, but without modification in the Times for Completion given in the SCC and any extension granted in accordance with GCC Clause 40, and shall submit all such revisions to the Project Manager. 18.3 Progress Report The Contractor shall monitor progress of all the activities specified in the program referred to in GCC Subclause 18.2 above, and supply a progress report to the Project Manager every month. The progress report shall be in a form acceptable to the Project Manager and shall indicate: (a) percentage completion achieved compared with the planned percentage completion for each activity; and (b) where any activity is behind the program, giving comments and likely consequences and stating the corrective action being taken. 18.4 Progress of Performance If at any time the Contractor’s actual progress falls behind the program referred to in GCC Subclause 18.2, or it becomes apparent that it will so fall behind, the Contractor shall, at the request of the Employer or the Project Manager, prepare and submit to the Project Manager a revised program, taking into account the prevailing circumstances, and shall notify the Project Manager of the steps being taken to expedite progress so as to attain Completion of the Facilities within the Time for Completion under GCC Subclause 8.2, any extension thereof entitled under GCC Subclause 40.1, or any extended period as may otherwise be agreed upon between the Employer and the Contractor. 18.5 Procedures The Contract shall be executed in accordance with the Contract Documents including the procedures given in the Forms and Procedures of the Employer’s Requirements. The Contractor may execute the Contract in accordance with its own standard project execution plans and procedures to the extent that they do not conflict with the provisions contained in the Contract. |
| 19.Subcontracting | 19.1 The Appendix 5 (List of Major Items of Plant and Services and List of Approved Subcontractors) to the Contract Agreement specifies major items of plant and services and a list of approved Subcontractors against each item, including manufacturers. Insofar as no Subcontractors are listed against any such item, the Contractor shall prepare a list of Subcontractors for such item for inclusion in such list. The Contractor may from time to time propose any addition to or deletion from any such list. The Contractor shall submit any such list or any modification thereto to the Employer for its approval in sufficient time so as not to impede the progress of work on the Facilities. Such approval by the Employer for any of the Subcontractors shall not relieve the Contractor from any of its obligations, duties, or responsibilities under the Contract. 19.2 The Contractor shall select and employ its Subcontractors for such major items from those listed in the lists referred to in GCC Subclause 19.1. - For items or parts of the Facilities not specified in the Appendix (List of Major Items of Plant and Services and List of Approved Subcontractors for Major Items) to the Contract Agreement, the Contractor may employ such Subcontractors as it may select, at its discretion. - Each subcontract shall include provisions which would entitle the Employer to require the sub-contract to be assigned to the Employer under GCC 19.5 (if and when applicable), or in event of termination by the Employer under GCC 42.2. - If a Sub-contractor's obligations extend beyond the expiry date of the relevant Defects Liability Period and the Project Manager, prior to that date, instructs the Contractor to assign the benefits of such obligations to the Employer, then the Contractor shall do so. |
| 20. Design and Engineering | 20.1 Specifications and Drawings 20.1.1 The Contractor shall execute the basic and detailed design and the engineering work in compliance with the provisions of the Contract, or where not so specified, in accordance with good engineering practice. The Contractor shall be responsible for any discrepancies, errors, or omissions in the specifications, drawings, and other technical documents that it has prepared, whether such specifications, drawings, and other documents have been approved by the Project Manager or not, provided that such discrepancies, errors, or omissions are not because of inaccurate information furnished in writing to the Contractor by or on behalf of the Employer. 20.1.2 The Contractor shall be entitled to disclaim responsibility for any design, data, drawing, specification, or other document, or any modification thereof provided or designated by or on behalf of the Employer, by giving a notice of such disclaimer to the Project Manager. 20.2 Codes and Standards Wherever references are made in the Contract to codes and standards in accordance with which the Contract shall be executed, the edition or the revised version of such codes and standards current at the date 28 days prior to date of bid submission shall apply unless otherwise specified. During Contract execution, any changes in such codes and standards shall be applied subject to approval by the Employer and shall be treated in accordance with GCC Clause 39. 20.3 Approval/Review of Technical Documents by Project Manager 20.3.1 The Contractor shall prepare or cause its Subcontractors to prepare, and furnish to the Project Manager the documents listed in the Appendix (List of Documents for Approval or Review) to the Contract Agreement for its approval or review as specified and in accordance with the requirements of GCC Subclause 18.2 (Program of Performance). Any part of the Facilities covered by or related to the documents to be approved by the Project Manager shall be executed only after the Project Manager’s approval thereof. GCC Subclauses 20.3.2 through 20.3.7 shall apply to those documents requiring the Project Manager’s approval, but not to those furnished to the Project Manager for its review only. 20.3.2 Within 14 days after receipt by the Project Manager of any document requiring the Project Manager’s approval in accordance with GCC Subclause 20.3.1, the Project Manager shall either return one copy thereof to the Contractor with its approval endorsed thereon or shall notify the Contractor in writing of its disapproval thereof and the reasons therefor and the modifications that the Project Manager proposes. If the Project Manager fails to take such action within the said 14 days, then the said document shall be deemed to have been approved by the Project Manager. 20.3.3 The Project Manager shall not disapprove any document, except on the grounds that the document does not comply with the Contract or that it is contrary to good engineering practice. If the Project Manager disapproves a document, he shall specify the reasons for his decision. 20.3.4 If the Project Manager disapproves the document, the Contractor shall modify the document and resubmit it for the Project Manager’s approval in accordance with GCC Subclause 20.3.2. If the Project Manager approves the document subject to modification(s), the Contractor shall make the required modification(s), whereupon the document shall be deemed to have been approved. 20.3.5 If any dispute or difference occurs between the Employer and the Contractor in connection with or arising out of the disapproval by the Project Manager of any document and/or any modification(s) thereto that cannot be settled between the parties within a reasonable period, then such dispute or difference may be referred to an Dispute Board for determination in accordance with GCC Subclause 45.3 hereof. If such dispute or difference is referred to an Dispute Board, the Project Manager shall give instructions as to whether and, if so, how, performance of the Contract is to proceed. The Contractor shall proceed with the Contract in accordance with the Project Manager’s instructions, provided that if the Dispute Board upholds the Contractor’s view on the dispute and if the Employer has not given notice under Subclause 45.3 hereof, then the Contractor shall be reimbursed by the Employer for any additional costs incurred by reason of such instructions and shall be relieved of such responsibility or liability in connection with the dispute and the execution of the instructions as the Dispute Board shall decide, and the Time for Completion shall be extended accordingly. 20.3.6 The Project Manager’s approval, with or without modification of the document furnished by the Contractor, shall not relieve the Contractor of any responsibility or liability imposed upon it by any provisions of the Contract except to the extent that any subsequent failure results from modifications required by the Project Manager. 20.3.7 The Contractor shall not depart from any approved document unless the Contractor has first submitted to the Project Manager an amended document and obtained the Project Manager’s approval thereof, pursuant to the provisions of this GCC Subclause 20.3. If the Project Manager requests any change in any already approved document and/or in any document based thereon, the provisions of GCC Clause 39 shall apply to such request. |
| 21. Procurement | 21.1 Materials Subject to GCC Subclause 14.2, the Contractor shall procure and transport all materials in an expeditious and orderly manner to the Site. 21.2 Employer-Supplied Materials If the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement provides that the Employer shall furnish any specific items to the Contractor, the following provisions shall apply: 21.2.1 The Employer shall, at its own risk and expense, transport each item to the place on or near the Site as agreed upon by the parties and make such item available to the Contractor at the time specified in the program furnished by the Contractor, pursuant to GCC Subclause 18.2, unless otherwise mutually agreed. 21.2.2 Upon receipt of such item, the Contractor shall inspect the same visually and notify the Project Manager of any detected shortage, defect, or default. The Employer shall immediately remedy any shortage, defect, or default, or the Contractor shall, if practicable and possible, at the request of the Employer, remedy such shortage, defect, or default at the Employer’s cost and expense. After inspection, such item shall fall under the care, custody, and control of the Contractor. The provision of this GCC Subclause 21.2.2 shall apply to any item supplied to remedy any such shortage or default or to substitute for any defective item, or shall apply to defective items that have been repaired. 21.2.3 The foregoing responsibilities of the Contractor and its obligations of care, custody, and control shall not relieve the Employer of liability for any undetected shortage, defect, or default, nor place the Contractor under any liability for any such shortage, defect or default whether under GCC Clause 27 or under any other provision of Contract. 21.3 Transportation 21.3.1 The Contractor shall at its own risk and expense transport all the materials and the Contractor’s Equipment to the Site by the mode of transport that the Contractor judges most suitable under all the circumstances. 21.3.2 Unless otherwise provided in the Contract, the Contractor shall be entitled to select any safe mode of transport operated by any person to carry the materials and the Contractor’s Equipment. 21.3.3 Upon dispatch of each shipment of materials and the Contractor’s Equipment, the Contractor shall notify the Employer by telex, cable, facsimile, or electronic means, of the description of the materials and of the Contractor’s Equipment, the point and means of dispatch, and the estimated time and point of arrival in the country where the Site is located, if applicable, and at the Site. The Contractor shall furnish the Employer with relevant shipping documents to be agreed upon between the parties. 21.3.4 The Contractor shall be responsible for obtaining, if necessary, approvals from the authorities for transportation of the materials and the Contractor’s Equipment to the Site. The Employer shall use its best endeavors in a timely and expeditious manner to assist the Contractor in obtaining such approvals, if requested by the Contractor. The Contractor shall indemnify and hold harmless the Employer from and against any claim for damage to roads, bridges, or any other traffic facilities that may be caused by the transport of the materials and the Contractor’s Equipment to the Site. 21.4 Customs Clearance The Contractor shall, at its own expense, handle all imported materials and Contractor’s Equipment at the point(s) of import and shall handle any formalities for customs clearance, subject to the Employer’s obligations under GCC Subclause 14.2, provided that if applicable laws or regulations require any application or act to be made by or in the name of the Employer, the Employer shall take all necessary steps to comply with such laws or regulations. In the event of delays in customs clearance that are not the fault of the Contractor, the Contractor shall be entitled to an extension in the Time for Completion, pursuant to GCC Clause 40. |
| 22. Installation | 22.1 Setting Out/Supervision 22.1.1 Benchmark (a) The Contractor shall be responsible for the true and proper setting-out of the Facilities in relation to bench marks, reference marks, and lines provided to it in writing by or on behalf of the Employer. (b) If, at any time during the progress of installation of the Facilities, any error shall appear in the position, level, or alignment of the Facilities, the Contractor shall forthwith notify the Project Manager of such error and, at its own expense, immediately rectify such error to the reasonable satisfaction of the Project Manager. If such error is based on incorrect data provided in writing by or on behalf of the Employer, the expense of rectifying the same shall be borne by the Employer. 22.1.2 Contractor’s Supervision The Contractor shall give or provide all necessary superintendence during the installation of the Facilities, and the Construction Manager or its deputy shall be constantly on the Site to provide full-time superintendence of the installation. The Contractor shall provide and employ only technical personnel who are skilled and experienced in their respective callings and supervisory staff who are competent to adequately supervise the work at hand. 22.2 Labor 22.2.1 Engagement of Staff and Labor (a) Except as otherwise stated in the Specification, the Contractor shall make arrangements for the engagement of all staff and labor, local or otherwise, and for their payment, housing, feeding, and transport. (b) The Contractor shall provide and employ on the Site in the installation of the Facilities such skilled, semi-skilled, and unskilled labor as is necessary for the proper and timely execution of the Contract. The Contractor is encouraged to use local labor that has the necessary skills. (c) The Contractor shall be responsible for obtaining all necessary permit(s) and/or visa(s) from the appropriate authorities for the entry of all labor and personnel to be employed on the Site into the country where the Site is located. The Employer will, if requested by the Contractor, use his best endeavors in a timely and expeditious manner to assist the Contractor in obtaining any local, state, national, or government permission required for bringing in the Contractor’s personnel. (d) The Contractor shall at its own expense provide the means of repatriation to all of its and its Subcontractor’s personnel employed on the Contract at the Site to the place where they were recruited or to their domicile. It shall also provide suitable temporary maintenance of all such persons from the cessation of their employment on the Contract to the date programmed for their departure. In the event that the Contractor defaults in providing such means of transportation and temporary maintenance, the Employer may provide the same to such personnel and recover the cost of doing so from the Contractor. 22.2.2 Persons in the Service of Employer The Contractor shall not recruit, or attempt to recruit, staff and labor from amongst the Employer’s Personnel. 22.2.3 Labor Laws (a) The Contractor shall comply with all the relevant labor Laws applicable to the Contractor’s Personnel, including Laws relating to their employment, health, safety, welfare, immigration, and emigration, and shall allow them all their legal rights. (b) The Contractor shall at all times during the progress of the Contract use its best endeavors to prevent any unlawful, riotous, or disorderly conduct or behavior by or amongst its employees and the labor of its Subcontractors. (c) The Contractor shall, in all dealings with its labor and the labor of its Subcontractors currently employed on or connected with the Contract, pay due regard to all recognized festivals, official holidays, religious, or other customs and all local laws and regulations pertaining to the employment of labor. 22.2.4 Rates of Wages and Conditions of Labor (a) The Contractor shall pay rates of wages, and observe conditions of labor, which are not lower than those established for the trade or industry where the work is carried out. If no established rates or conditions are applicable, the Contractor shall pay rates of wages and observe conditions which are not lower than the general level of wages and conditions observed locally by employers whose trade or industry is similar to that of the Contractor. (b) The Contractor shall inform the Contractor’s Personnel about their liability to pay personal income taxes in the Country in respect of such of their salaries, wages, and allowances as are chargeable under the Laws for the time being in force, and the Contractor shall perform such duties in regard to such deductions thereof as may be imposed on him by such Laws. 22.2.5 Working Hours (a) No work shall be carried out on the Site on locally recognized days of rest, or outside the normal working hours stated in the SCC, unless (i) otherwise stated in the Contract; (ii) the Project Manager gives consent; or (iii the work is unavoidable, or necessary for the protection of life or property or for the safety of the Works, in which case the Contractor shall immediately advise the Project Manager. (b) If and when the Contractor considers it necessary to carry out work at night or on public holidays so as to meet the Time for Completion and requests the Project Manager’s consent thereto, the Project Manager shall not unreasonably withhold such consent. (c) This Subclause shall not apply to any work which is customarily carried out by rotary or double shifts. 22.2.6 Facilities for Staff and Labor (a) Except as otherwise stated in the Specification, the Contractor shall provide and maintain all necessary accommodation and welfare facilities for the Contractor’s Personnel. The Contractor shall also provide facilities for the Employer’s Personnel as stated in the Specification. (b) The Contractor shall not permit any of the Contractor’s Personnel to maintain any temporary or permanent living quarters within the structures forming part of the Permanent Works. 22.2.7 Health and Safety (a) The Contractor shall at all times take all reasonable precautions to maintain the health and safety of the Contractor’s Personnel. In collaboration with local health authorities, the Contractor shall ensure that medical staff, first aid facilities, sick bay, and ambulance service are available at all times at the Site and at any accommodation for Contractor’s and Employer’s Personnel, and that suitable arrangements are made for all necessary welfare and hygiene requirements and for the prevention of epidemics. (b) The Contractor shall appoint an accident prevention officer at the Site, responsible for maintaining safety and protection against accidents. This person shall be qualified for this responsibility, and shall have the authority to issue instructions and take protective measures to prevent accidents. Throughout the performance of the Contract, the Contractor shall provide whatever is required by this person to exercise this responsibility and authority. (c) The Contractor shall send to the Project Manager, details of any accident as soon as practicable after its occurrence. The Contractor shall maintain records and make reports concerning health, safety, and welfare of persons, and damage to property, as the Project Manager may reasonably require. 22.2.8 Funeral Arrangements In the event of the death of any of the Contractor’s personnel or accompanying members of their families, the Contractor shall be responsible for making the appropriate arrangements for their return or burial, unless otherwise specified in the SCC. 22.2.9 Records of Contractor’s Personnel The Contractor shall keep accurate records of the Contractor’s personnel, including the number of each class of Contractor’s Personnel on the Site and the names, ages, gender, hours worked, and wages paid to all workers. These records shall be summarized on a monthly basis in a form approved by the Project Manager and shall be available for inspection by the Project Manager until the Contractor has completed all work. 22.2.10 Supply of Foodstuff The Contractor shall arrange for the provision of a sufficient supply of suitable food as may be stated in the Specification at reasonable prices for the Contractor’s Personnel for the purposes of or in connection with the Contract. 22.2.11 Supply of Water The Contractor shall, having regard to local conditions, provide on the Site an adequate supply of drinking and other water for the use of the Contractor’s Personnel. 22.2.12 Measures against Insect and Pest Nuisance The Contractor shall at all times take the necessary precautions to protect the Contractor’s Personnel employed on the Site from insect and pest nuisance, and to reduce their danger to health. The Contractor shall comply with all the regulations of the local health authorities, including use of appropriate insecticide. 22.2.13 Alcoholic Liquor or Drugs The Contractor shall not, otherwise than in accordance with the Laws of the Country, import, sell, give barter, or otherwise dispose of any alcoholic liquor or drugs, or permit or allow importation, sale, gift barter, or disposal by Contractor's Personnel. 22.2.14 Arms and Ammunition The Contractor shall not give, barter, or otherwise dispose of, to any person, any arms or ammunition of any kind, or allow Contractor's Personnel to do so. 22.2.15 Prohibition of All Forms of Forced or Compulsory Labor The contractor shall not employ "forced or compulsory labor" in any form. "Forced or compulsory labor" consists of all work or service, not voluntarily performed, that is extracted from an individual under threat of force or penalty. 22.2.16 Prohibition of Harmful Child Labor The Contractor shall not employ any child to perform any work that is economically exploitative, or is likely to be hazardous to, or to interfere with, the child's education, or to be harmful to the child's health or physical, mental, spiritual, moral, or social development. 22.3 Contractor’s Equipment 22.3.1 All Contractor’s Equipment brought by the Contractor onto the Site shall be deemed to be intended to be used exclusively for the execution of the Contract. The Contractor shall not remove the same from the Site without the Project Manager’s consent that such Contractor’s Equipment is no longer required for the execution of the Contract. 22.3.2 Unless otherwise specified in the Contract, upon completion of the Facilities, the Contractor shall remove from the Site all Equipment brought by the Contractor onto the Site and any surplus materials remaining thereon. 22.3.3 The Employer will, if requested, use its best endeavors to assist the Contractor in obtaining any local, state or national government permission required by the Contractor for the export of the Contractor’s Equipment imported by the Contractor for use in the execution of the Contract that is no longer required for the execution of the Contract. 22.4 Site Regulations and Safety The Employer and the Contractor shall establish Site regulations setting out the rules to be observed in the execution of the Contract at the Site and shall comply therewith. The Contractor shall prepare and submit to the Employer, with a copy to the Project Manager, proposed Site regulations for the Employer’s approval, which approval shall not be unreasonably withheld. Such Site regulations shall include, but shall not be limited to, rules in respect of security, safety of the Facilities, gate control, sanitation, medical care, and fire prevention. 22.5 Opportunities for Other Contractors 22.5.1 The Contractor shall, upon written request from the Employer or the Project Manager, give all reasonable opportunities for carrying out the work to any other contractors employed by the Employer on or near the Site. 22.5.2 If the Contractor, upon written request from the Employer or the Project Manager, makes available to other contractors any roads or ways the maintenance for which the Contractor is responsible, permits the use by such other contractors of the Contractor’s Equipment, or provides any other service of whatsoever nature for such other contractors, the Employer shall fully compensate the Contractor for any loss or damage caused or occasioned by such other contractors in respect of any such use or service, and shall pay to the Contractor reasonable remuneration for the use of such equipment or the provision of such services. 22.5.3 The Contractor shall also so arrange to perform its work as to minimize, to the extent possible, interference with the work of other contractors. The Project Manager shall determine the resolution of any difference or conflict that may arise between the Contractor and other contractors and the workers of the Employer in regard to their work. 22.5.4 The Contractor shall notify the Project Manager promptly of any defects in the other Contractors’ work that come to its notice, and that could affect the Contractor’s work. The Project Manager shall determine the corrective measures, if any, required to rectify the situation after inspection of the Facilities. Decisions made by the Project Manager shall be binding on the Contractor. 22.6 Emergency Work If, by reason of an emergency arising in connection with and during the execution of the Contract, any protective or remedial work is necessary as a matter of urgency to prevent damage to the Facilities, the Contractor shall immediately carry out such work. If the Contractor is unable or unwilling to do such work immediately, the Employer may do or cause such work to be done as the Employer may determine is necessary in order to prevent damage to the Facilities. In such event the Employer shall, as soon as practicable after the occurrence of any such emergency, notify the Contractor in writing of such emergency, the work done and the reasons therefor. If the work done or caused to be done by the Employer is work that the Contractor was liable to do at its own expense under the Contract, the reasonable costs incurred by the Employer in connection therewith shall be paid by the Contractor to the Employer. Otherwise, the cost of such remedial work shall be borne by the Employer. 22.7 Site Clearance 22.7.1 Site Clearance in Course of Performance In the course of carrying out the Contract, the Contractor shall keep the Site reasonably free from all unnecessary obstruction, store, or remove any surplus materials, clear away any wreckage, rubbish, or temporary works from the Site, and remove any Contractor’s Equipment no longer required for execution of the Contract. 22.7.2 Clearance of Site after Completion After Completion of all parts of the Facilities, the Contractor shall clear away and remove all wreckage, rubbish, and debris of any kind from the Site, and shall leave the Site and Facilities in a clean and safe condition. 22.8 Watching and Lighting The Contractor shall provide and maintain at its own expense all lighting, fencing, and watching when and where necessary for the proper execution and the protection of the Facilities, or for the safety of the owners and occupiers of adjacent property and for the safety of the public. |
| 23. Test and Inspection | 23.1 The Contractor shall at its own expense carry out at the place of manufacture and/or on the Site all such tests and/or inspections of the Plant and any part of the Facilities as are specified in the Contract. 23.2 The Employer and the Project Manager or their designated representatives shall be entitled to attend the aforesaid test and/or inspection, provided that the Employer shall bear all costs and expenses incurred in connection with such attendance including, but not limited to, all traveling and board and lodging expenses. 23.3 Whenever the Contractor is ready to carry out any such test and/or inspection, the Contractor shall give a reasonable advance notice of such test and/or inspection and of the place and time thereof to the Project Manager. The Contractor shall obtain from any relevant third party or manufacturer any necessary permission or consent to enable the Employer and the Project Manager or their designated representatives to attend the test and/or inspection. 23.4 The Contractor shall provide the Project Manager with a certified report of the results of any such test and/or inspection. If the Employer or Project Manager or their designated representatives fails to attend the test and/or inspection, or if it is agreed between the parties that such persons shall not do so, then the Contractor may proceed with the test and/or inspection in the absence of such persons, and may provide the Project Manager with a certified report of the results thereof. 23.5 The Project Manager may require the Contractor to carry out any test and/or inspection not required by the Contract, provided that the Contractor’s reasonable costs and expenses incurred in the carrying out of such test and/or inspection shall be added to the Contract Price. Further, if such test and/or inspection impedes the progress of work on the Facilities and/or the Contractor’s performance of its other obligations under the Contract, due allowance will be made in respect of the Time for Completion and the other obligations so affected. 23.6 If any Plant or any part of the Facilities fails to pass any test and/or inspection, the Contractor shall either rectify or replace such Plant or part of the Facilities and shall repeat the test and/or inspection upon giving a notice under GCC Subclause 23.3. 23.7 If any dispute or difference of opinion shall arise between the parties in connection with or arising out of the test and/or inspection of the Plant or part of the Facilities that cannot be settled between the parties within a reasonable period of time, it may be referred to an Dispute Board for determination in accordance with GCC Subclause 45.3. 23.8 The Contractor shall afford the Employer and the Project Manager, at the Employer’s expense, access at any reasonable time to any place where the Plant are being manufactured or the Facilities are being installed, in order to inspect the progress and the manner of manufacture or installation, provided that the Project Manager shall give the Contractor a reasonable prior notice. 23.9 The Contractor agrees that neither the execution of a test and/or inspection of Plant or any part of the Facilities, nor the attendance by the Employer or the Project Manager, nor the issue of any test certificate pursuant to GCC Subclause 23.4, shall release the Contractor from any other responsibilities under the Contract. 23.10 No part of the Facilities or foundations shall be covered up on the Site without the Contractor carrying out any test and/or inspection required under the Contract. The Contractor shall give a reasonable notice to the Project Manager whenever any such parts of the Facilities or foundations are ready or about to be ready for test and/or inspection; such test and/or inspection and notice thereof shall be subject to the requirements of the Contract. 23.11 The Contractor shall uncover any part of the Facilities or foundations, or shall make openings in or through the same as the Project Manager may from time to time require at the Site, and shall reinstate and make good such part or parts. If any parts of the Facilities or foundations have been covered up at the Site after compliance with the requirement of GCC Subclause 23.10 and are found to be executed in accordance with the Contract, the expenses of uncovering, making openings in or through, reinstating, and making good the same shall be borne by the Employer, and the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been delayed or impeded in the performance of any of its obligations under the Contract. |
| 24. Completion of the Facilities | 24.1 As soon as the Facilities or any part thereof has, in the opinion of the Contractor, been completed operationally and structurally and put in a tight and clean condition as specified in the Employer’s Requirements, excluding minor items not materially affecting the operation or safety of the Facilities, the Contractor shall so notify the Employer in writing. 24.2 Within 7 days after receipt of the notice from the Contractor under GCC Subclause 24.1, the Employer shall supply the operating and maintenance personnel specified in the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement for Pre-commissioning of the Facilities or any part thereof. Pursuant to the Appendix (Scope of Works and Supply by the Employer) to the Contract Agreement, the Employer shall also provide, within the said 7-day period, the raw materials, utilities, lubricants, chemicals, catalysts, facilities, services, and other matters required for Pre-commissioning of the Facilities or any part thereof. 24.3 As soon as reasonably practicable after the operating and maintenance personnel have been supplied by the Employer and the raw materials, utilities, lubricants, chemicals, catalysts, facilities, services, and other matters have been provided by the Employer in accordance with GCC Subclause 24.2, the Contractor shall commence Pre-commissioning of the Facilities or the relevant part thereof in preparation for Commissioning, subject to GCC Subclause 25.5. 24.4 As soon as all works in respect of Pre-commissioning are completed and, in the opinion of the Contractor, the Facilities or any part thereof is ready for Commissioning, the Contractor shall so notify the Project Manager in writing. 24.5 The Project Manager shall, within 14 days after receipt of the Contractor’s notice under GCC Subclause 24.4, either issue a Completion Certificate in the form specified in the Employer’s Requirements (Forms and Procedures), stating that the Facilities or that part thereof have reached Completion as of the date of the Contractor’s notice under GCC Subclause 24.4, or notify the Contractor in writing of any defects and/or deficiencies. If the Project Manager notifies the Contractor of any defects and/or deficiencies, the Contractor shall then correct such defects and/or deficiencies, and shall repeat the procedure described in GCC Subclause 24.4. If the Project Manager is satisfied that the Facilities or that part thereof have reached Completion, the Project Manager shall, within 7 days after receipt of the Contractor’s repeated notice, issue a Completion Certificate stating that the Facilities or that part thereof have reached Completion as of the date of the Contractor’s repeated notice. If the Project Manager is not so satisfied, then it shall notify the Contractor in writing of any defects and/or deficiencies within 7 days after receipt of the Contractor’s repeated notice, and the above procedure shall be repeated. 24.6 If the Project Manager fails to issue the Completion Certificate and fails to inform the Contractor of any defects and/or deficiencies within 14 days after receipt of the Contractor’s notice under GCC Subclause 24.4 or within 7 days after receipt of the Contractor’s repeated notice under GCC Subclause 24.5, or if the Employer makes use of the Facilities or part thereof, then the Facilities or that part thereof shall be deemed to have reached Completion as of the date of the Contractor’s notice or repeated notice, or as of the Employer’s use of the Facilities, as the case may be. 24.7 As soon as possible after Completion, the Contractor shall complete all outstanding minor items so that the Facilities are fully in accordance with the requirements of the Contract, failing which the Employer will undertake such completion and deduct the costs thereof from any monies owing to the Contractor. 24.8 Upon Completion, the Employer shall be responsible for the care and custody of the Facilities or the relevant part thereof, together with the risk of loss or damage thereto, and shall thereafter take over the Facilities or the relevant part thereof. |
| 25. Commissioning and Operational Acceptance | 25.1 Commissioning 25.1.1 Commissioning of the Facilities or any part thereof shall be commenced by the Contractor immediately after issue of the Completion Certificate by the Project Manager, pursuant to GCC Subclause 24.5, or immediately after the date of the deemed Completion, under GCC Subclause 24.6. 25.1.2 The Employer shall supply the operating and maintenance personnel and all raw materials, utilities, lubricants, chemicals, catalysts, facilities, services, and other matters required for Commissioning. 25.1.3 In accordance with the requirements of the Contract, the Contractor’s and Project Manager’s advisory personnel shall attend the Commissioning, including the Guarantee Test, and shall advise and assist the Employer. 25.2 Guarantee Test 25.2.1 Subject to GCC Subclause 25.5, the Guarantee Test and repeats thereof shall be conducted by the Contractor during Commissioning of the Facilities or the relevant part thereof to ascertain whether the Facilities or the relevant part can attain the Functional Guarantees specified in the Appendix (Functional Guarantees) to the Contract Agreement. The Employer shall promptly provide the Contractor with such information as the Contractor may reasonably require in relation to the conduct and results of the Guarantee Test and any repeats thereof. 25.2.2 If for reasons not attributable to the Contractor, the Guarantee Test of the Facilities or the relevant part thereof cannot be successfully completed within the period from the date of Completion specified in the SCC or any other period agreed upon by the Employer and the Contractor, the Contractor shall be deemed to have fulfilled its obligations with respect to the Functional Guarantees, and GCC Subclauses 28.2 and 28.3 shall not apply. 25.3 Operational Acceptance 25.3.1 Subject to GCC Subclause 25.4 below, Operational Acceptance shall occur in respect of the Facilities or any part thereof when (a) the Guarantee Test has been successfully completed and the Functional Guarantees are met; or (b) the Guarantee Test has not been successfully completed or has not been carried out for reasons not attributable to the Contractor within the period from the date of Completion specified in the SCC, or any other agreed upon period as specified in GCC Subclause 25.2.2 above; or (c) the Contractor has paid the liquidated damages specified in GCC Subclause 28.3 hereof; and (d) any minor items mentioned in GCC Subclause 24.7 hereof relevant to the Facilities or that part thereof have been completed. 25.3.2 At any time after any of the events set out in GCC Subclause 25.3.1 have occurred, the Contractor may give a notice to the Project Manager requesting the issue of an Operational Acceptance Certificate in the form provided in the Employer’s Requirements (Forms and Procedures) in respect of the Facilities or the part thereof specified in such notice as of the date of such notice. 25.3.3 The Project Manager shall, after consultation with the Employer, and within 7 days after receipt of the Contractor’s notice, issue an Operational Acceptance Certificate. 25.3.4 If within 7 days after receipt of the Contractor’s notice, the Project Manager fails to issue the Operational Acceptance Certificate or fails to inform the Contractor in writing of the justifiable reasons why the Project Manager has not issued the Operational Acceptance Certificate, the Facilities or the relevant part thereof shall be deemed to have been accepted as of the date of the Contractor’s said notice. 25.4 Partial Acceptance 25.4.1 If the Contract specifies that Completion and Commissioning shall be carried out in respect of parts of the Facilities, the provisions relating to Completion and Commissioning including the Guarantee Test shall apply to each such part of the Facilities individually, and the Operational Acceptance Certificate shall be issued accordingly for each such part of the Facilities. 25.4.2 If a part of the Facilities comprises facilities such as buildings, for which no Commissioning or Guarantee Test is required, then the Project Manager shall issue the Operational Acceptance Certificate for such facility when it attains Completion, provided that the Contractor shall thereafter complete any outstanding minor items that are listed in the Operational Acceptance Certificate. 25.5 Delayed Pre-Commissioning and/or Guarantee Test 25.5.1 In the event that the Contractor is unable to proceed with the Pre-commissioning of the Facilities pursuant to Subclause 24.3, or with the Guarantee Test pursuant to Subclause 25.2, for reasons attributable to the Employer either on account of non availability of other facilities under the responsibilities of other contractor(s), or for reasons beyond the Employer’s control, the provisions leading to “deemed” completion of activities such as Completion, pursuant to GCC Subclause 24.6, and Operational Acceptance, pursuant to GCC Subclause 25.3.4, and Contractor’s obligations regarding Defect Liability Period, pursuant to GCC Subclause 27.2, Functional Guarantee, pursuant to GCC Clause 28, and Care of Facilities, pursuant to GCC Clause 32, and GCC Clause 41.1, Suspension, shall not apply. In this case, the following provisions shall apply. 25.5.2 When the Contractor is notified by the Project Manager that he will be unable to proceed with the activities and obligations pursuant to above Subclause 25.5.1, the Contractor shall be entitled to the following: (a) the Time of Completion shall be extended for the period of suspension without imposition of liquidated damages pursuant to GCC Subclause 26.2; (b) payments due to the Contractor in accordance with the provision specified in the Appendix (Terms and Procedures of Payment) to the Contract Agreement, which would not have been payable in normal circumstances due to noncompletion of the subject activities, shall be released to the Contractor against submission of a security in the form of a bank guarantee of equivalent amount acceptable to the Employer, and which shall become null and void when the Contractor will have complied with its obligations regarding those payments, subject to the provision of Subclause 25.5.3 below; (c) the expenses towards the above security and extension of other securities under the contract, of which validity needs to be extended, shall be reimbursed to the Contractor by the Employer; (d) the additional charges towards the care of the Facilities pursuant to GCC Subclause 32.1 shall be reimbursed to the Contractor by the Employer for the period between the notification mentioned above and the notification mentioned in Subclause 25.5.4 below. The provision of GCC Subclause 33.2 shall apply to the Facilities during the same period. 25.5.3 In the event that the period of suspension under above Subclause 25.5.1 actually exceeds 180 days, the Employer and Contractor shall mutually agree to any additional compensation payable to the Contractor. 25.5.4 When the Contractor is notified by the Project Manager that the plant is ready for Pre-commissioning, the Contractor shall proceed without delay in performing all the specified activities and obligations under the contract. |

F.  Guarantees and Liabilities

| 26. Completion Time Guarantee | 26.1 The Contractor guarantees that it shall attain Completion of the Facilities (or a part for which a separate time for completion is specified) within the Time for Completion specified in the SCC pursuant to GCC Subclause 8.2, or within such extended time to which the Contractor shall be entitled under GCC Clause 40 hereof. 26.2 If the Contractor fails to attain Completion of the Facilities or any part thereof within the Time for Completion or any extension thereof under GCC Clause 40, the Contractor shall pay to the Employer liquidated damages in the amount specified in the SCC as a percentage rate of the Contract Price or the relevant part thereof. The aggregate amount of such liquidated damages shall in no event exceed the amount specified as “Maximum” in the SCC as a percentage rate of the Contract Price. Once the “Maximum” is reached, the Employer may consider termination of the Contract, pursuant to GCC Subclause 42.2.2. Such payment shall completely satisfy the Contractor’s obligation to attain Completion of the Facilities or the relevant part thereof within the Time for Completion or any extension thereof under GCC Clause 40. The Contractor shall have no further liability whatsoever to the Employer in respect thereof. However, the payment of liquidated damages shall not in any way relieve the Contractor from any of its obligations to complete the Facilities or from any other obligations and liabilities of the Contractor under the Contract. Save for liquidated damages payable under this GCC Subclause 26.2, the failure by the Contractor to attain any milestone or other act, matter or thing by any date specified in the Appendix (Time Schedule) to the Contract Agreement and/or other program of work prepared pursuant to GCC Subclause 18.2 shall not render the Contractor liable for any loss or damage thereby suffered by the Employer. 26.3 If the Contractor attains Completion of the Facilities or any part thereof before the Time for Completion or any extension thereof under GCC Clause 40, the Employer shall pay to the Contractor a bonus in the amount specified in the SCC. The aggregate amount of such bonus shall in no event exceed the amount specified as “Maximum” in the SCC. |
| --- | --- |
| 27. Defect Liability | 27.1 The Contractor warrants that the Facilities or any part thereof shall be free from defects in the design, engineering, materials, and workmanship of the Plant supplied and of the work executed. 27.2 The Defect Liability Period shall be 540 days from the date of Completion of the Facilities (or any part thereof) or 1 year from the date of Operational Acceptance of the Facilities (or any part thereof), whichever first occurs, unless specified otherwise in the SCC pursuant to GCC Subclause 27.10. If during the Defect Liability Period any defect should be found in the design, engineering, materials, and workmanship of the Plant supplied or of the work executed by the Contractor, the Contractor shall promptly, in consultation and agreement with the Employer regarding appropriate remedying of the defects, and at its cost, repair, replace, or otherwise make good as the Contractor shall determine at its discretion, such defect as well as any damage to the Facilities caused by such defect. The Contractor shall not be responsible for the repair, replacement, or making good of any defect or of any damage to the Facilities arising out of or resulting from any of the following causes: (a) improper operation or maintenance of the Facilities by the Employer, (b) operation of the Facilities outside specifications provided in the Contract, or (c) normal wear and tear. 27.3 The Contractor’s obligations under this GCC Clause 27 shall not apply to: (a) any materials that are supplied by the Employer under GCC Subclause 21.2, are normally consumed in operation, or have a normal life shorter than the Defect Liability Period stated herein; (b) any designs, specifications or other data designed, supplied, or specified by or on behalf of the Employer or any matters for which the Contractor has disclaimed responsibility herein; or (c) any other materials supplied or any other work executed by or on behalf of the Employer, except for the work executed by the Employer under GCC Subclause 27.7. 27.4 The Employer shall give the Contractor a notice stating the nature of any such defect together with all available evidence thereof, promptly following the discovery thereof. The Employer shall afford all reasonable opportunity for the Contractor to inspect any such defect. 27.5 The Employer shall afford the Contractor all necessary access to the Facilities and the Site to enable the Contractor to perform its obligations under this GCC Clause 27. The Contractor may, with the consent of the Employer, remove from the Site any Plant or any part of the Facilities that are defective if the nature of the defect, and/or any damage to the Facilities caused by the defect, is such that repairs cannot be expeditiously carried out at the Site. 27.6 If the repair, replacement or making good is of such a character that it may affect the efficiency of the Facilities or any part thereof, the Employer may give to the Contractor a notice requiring that tests of the defective part of the Facilities shall be made by the Contractor immediately upon completion of such remedial work, whereupon the Contractor shall carry out such tests. If such part fails the tests, the Contractor shall carry out further repair, replacement or making good, as the case may be, until that part of the Facilities passes such tests. The tests shall be agreed upon by the Employer and the Contractor. 27.7 If the Contractor fails to commence the work necessary to remedy such defect or any damage to the Facilities caused by such defect within a reasonable time (which shall in no event be considered to be less than 15 days), the Employer may, following notice to the Contractor, proceed to do such work, and the reasonable costs incurred by the Employer in connection therewith shall be paid to the Employer by the Contractor or may be deducted by the Employer from any monies due the Contractor or claimed under the Performance Security. 27.8 If the Facilities or any part thereof cannot be used by reason of such defect and/or making good of such defect, the Defect Liability Period of the Facilities or such part, as the case may be, shall be extended by a period equal to the period during which the Facilities or such part cannot be used by the Employer because of any of the aforesaid reasons. 27.9 Except as provided in GCC Clauses 27 and 33, the Contractor shall be under no liability whatsoever and howsoever arising, and whether under the Contract or at law, in respect of defects in the Facilities or any part thereof, the Plant, design, or engineering, or work executed that appear after Completion of the Facilities or any part thereof, except where such defects are the result of the gross negligence, fraud, criminal, or willful action of the Contractor. 27.10 In addition, any such component of the Facilities and during the period of time as may be specified in the SCC shall be subject to an extended Defect Liability Period. Such obligation of the Contractor shall be in addition to the Defect Liability Period specified under GCC Subclause 27.2. |
| 28. Functional Guarantees | 28.1 The Contractor guarantees that during the Guarantee Test, the Facilities and all parts thereof shall attain the Functional Guarantees specified in the Appendix (Functional Guarantees) to the Contract Agreement, subject to, and upon the conditions therein specified. 28.2 If, for reasons attributable to the Contractor, the minimum level of the Functional Guarantees specified in the Appendix (Functional Guarantees) to the Contract Agreement are not met either in whole or in part, the Contractor shall at its cost and expense make such changes, modifications, and/or additions to the Plant or any part thereof as may be necessary to meet at least the minimum level of such Guarantees. The Contractor shall notify the Employer upon completion of the necessary changes, modifications, and/or additions, and shall request the Employer to repeat the Guarantee Test until the minimum level of the Guarantees has been met. If the Contractor eventually fails to meet the minimum level of Functional Guarantees, the Employer may consider termination of the Contract, pursuant to GCC Subclause 42.2.2. 28.3 If, for reasons attributable to the Contractor, the Functional Guarantees specified in the Appendix (Functional Guarantees) to the Contract Agreement are not attained either in whole or in part, but the minimum level of the Functional Guarantees specified in the said Appendix to the Contract Agreement is met, the Contractor shall, at the Contractor’s option, either (a) make such changes, modifications, and/or additions to the Facilities or any part thereof that are necessary to attain the Functional Guarantees at its cost and expense, and shall request the Employer to repeat the Guarantee Test or (b) pay liquidated damages to the Employer in respect of the failure to meet the Functional Guarantees in accordance with the provisions in the Appendix (Functional Guarantees) to the Contract Agreement. 28.4 The payment of liquidated damages under GCC Subclause 28.3, up to the limitation of liability specified in the Appendix (Functional Guarantees) to the Contract Agreement, shall completely satisfy the Contractor’s guarantees under GCC Subclause 28.3, and the Contractor shall have no further liability whatsoever to the Employer in respect thereof. Upon the payment of such liquidated damages by the Contractor, the Project Manager shall issue the Operational Acceptance Certificate for the Facilities or any part thereof in respect of which the liquidated damages have been so paid. |
| 29. Patent Indemnity | 29.1 The Contractor shall, subject to the Employer’s compliance with GCC Subclause 29.2, indemnify and hold harmless the Employer and its employees and officers from and against any and all suits, actions, or administrative proceedings, claims, demands, losses, damages, costs, and expenses of whatsoever nature, including attorney’s fees and expenses, which the Employer may suffer as a result of any infringement or alleged infringement of any patent, utility model, registered design, trademark, copyright, or other intellectual property right registered or otherwise existing at the date of the Contract by reason of (a) the installation of the Facilities by the Contractor or the use of the Facilities in the country where the Site is located, and (b) the sale of the products produced by the Facilities in any country. Such indemnity shall not cover any use of the Facilities or any part thereof other than for the purpose indicated by or to be reasonably inferred from the Contract, any infringement resulting from the use of the Facilities or any part thereof, or any products produced thereby in association or combination with any other equipment, plant, or materials not supplied by the Contractor, pursuant to the Contract Agreement. 29.2 If any proceedings are brought or any claim is made against the Employer arising out of the matters referred to in GCC Subclause 29.1, the Employer shall promptly give the Contractor a notice thereof, and the Contractor may at its own expense and in the Employer’s name conduct such proceedings or claim and any negotiations for the settlement of any such proceedings or claim. If the Contractor fails to notify the Employer within 28 days after receipt of such notice that it intends to conduct any such proceedings or claim, then the Employer shall be free to conduct the same on its own behalf. Unless the Contractor has so failed to notify the Employer within the 28-day period, the Employer shall make no admission that may be prejudicial to the defense of any such proceedings or claim. The Employer shall, at the Contractor’s request, afford all available assistance to the Contractor in conducting such proceedings or claim, and shall be reimbursed by the Contractor for all reasonable expenses incurred in so doing. 29.3 The Employer shall indemnify and hold harmless the Contractor and its employees, officers, and Subcontractors from and against any and all suits, actions or administrative proceedings, claims, demands, losses, damages, costs, and expenses of whatsoever nature, including attorney’s fees and expenses, which the Contractor may suffer as a result of any infringement or alleged infringement of any patent, utility model, registered design, trademark, copyright, or other intellectual property right registered or otherwise existing at the date of the Contract arising out of or in connection with any design, data, drawing, specification, or other documents or materials provided or designed by or on behalf of the Employer. |
| 30. Limitation of Liability | 30.1 Except in cases of criminal negligence or willful misconduct, (a) the Contractor shall not be liable to the Employer, whether in contract, tort, or otherwise, for any indirect or consequential loss or damage, loss of use, loss of production, or loss of profits or interest costs, provided that this exclusion shall not apply to any obligation of the Contractor to pay liquidated damages to the Employer, and (b) the aggregate liability of the Contractor to the Employer, whether under the Contract, in tort or otherwise, shall not exceed a multiple of the Contract Price specified in the SCC or, if a multiple is not so specified, the total Contract Price, provided that this limitation shall not apply to the cost of repairing or replacing defective equipment, or to any obligation of the Contractor to indemnify the Employer with respect to patent infringement. |

G.  Risk Distribution

| 31. Transfer of Ownership | 31.1 Ownership of the Plant (including spare parts) to be imported into the country where the Site is located shall be transferred to the Employer upon loading on to the mode of transport to be used to convey the Plant from the country of origin to that country. 31.2 Ownership of the Plant (including spare parts) procured in the country where the Site is located shall be transferred to the Employer when the Plant are brought on to the Site. 31.3 Ownership of the Contractor’s Equipment used by the Contractor and its Subcontractors in connection with the Contract shall remain with the Contractor or its Subcontractors. 31.4 Ownership of any Plant in excess of the requirements for the Facilities shall revert to the Contractor upon Completion of the Facilities or at such earlier time when the Employer and the Contractor agree that the Plant in question are no longer required for the Facilities. 31.5 Notwithstanding the transfer of ownership of the Plant, the responsibility for care and custody thereof together with the risk of loss or damage thereto shall remain with the Contractor pursuant to GCC Clause 32 (Care of Facilities) hereof until Completion of the Facilities or the part thereof in which such Plant are incorporated. |
| --- | --- |
| 32. Care of Facilities | 32.1 The Contractor shall be responsible for the care and custody of the Facilities or any part thereof until the date of Completion of the Facilities pursuant to GCC Clause 24 or, where the Contract provides for Completion of the Facilities in parts, until the date of Completion of the relevant part, and shall make good at its own cost any loss or damage that may occur to the Facilities or the relevant part thereof from any cause whatsoever during such period. The Contractor shall also be responsible for any loss or damage to the Facilities caused by the Contractor or its Subcontractors in the course of any work carried out, pursuant to GCC Clause 27. Notwithstanding the foregoing, the Contractor shall not be liable for any loss or damage to the Facilities or that part thereof caused by reason of any of the matters specified or referred to in paragraphs (a), (b) and (c) of GCC Subclauses 32.2 and 38.1. 32.2 If any loss or damage occurs to the Facilities or any part thereof or to the Contractor’s temporary facilities by reason of (a) insofar as they relate to the country where the Site is located, nuclear reaction, nuclear radiation, radioactive contamination, pressure wave caused by aircraft or other aerial objects, or any other occurrences that an experienced contractor could not reasonably foresee, or if reasonably foreseeable could not reasonably make provision for or insure against, insofar as such risks are not normally insurable on the insurance market and are mentioned in the general exclusions of the policy of insurance, including War Risks and Political Risks, taken out under GCC Clause 34 hereof; or (b) any use or occupation by the Employer or any third party other than a Subcontractor, authorized by the Employer of any part of the Facilities; or (c) any use of or reliance upon any design, data, or specification provided or designated by or on behalf of the Employer, or any such matter for which the Contractor has disclaimed responsibility herein, the Employer shall pay to the Contractor all sums payable in respect of the Facilities executed, notwithstanding that the same be lost, destroyed, or damaged, and will pay to the Contractor the replacement value of all temporary facilities and all parts thereof lost, destroyed, or damaged. If the Employer requests the Contractor in writing to make good any loss or damage to the Facilities thereby occasioned, the Contractor shall make good the same at the cost of the Employer in accordance with GCC Clause 39. If the Employer does not request the Contractor in writing to make good any loss or damage to the Facilities thereby occasioned, the Employer shall either request a change in accordance with GCC Clause 39, excluding the performance of that part of the Facilities thereby lost, destroyed or damaged, or, where the loss or damage affects a substantial part of the Facilities, the Employer shall terminate the Contract pursuant to GCC Subclause 42.1 hereof. 32.3 The Contractor shall be liable for any loss of or damage to any Contractor’s Equipment, or any other property of the Contractor used or intended to be used for purposes of the Facilities, except (i) as mentioned in GCC Subclause 32.2 with respect to the Contractor’s temporary facilities, and (ii) where such loss or damage arises by reason of any of the matters specified in GCC Subclauses 32.2 (b) and (c) and 38.1. 32.4 With respect to any loss or damage caused to the Facilities or any part thereof or to the Contractor’s Equipment by reason of any of the matters specified in GCC Subclause 38.1, the provisions of GCC Subclause 38.3 shall apply. |
| 33. Loss of or Damage to Property; Accident or Injury to Workers; Indemnification | 33.1 Subject to GCC Subclause 33.3, the Contractor shall indemnify and hold harmless the Employer and its employees and officers from and against any and all suits, actions, or administrative proceedings, claims, demands, losses, damages, costs, and expenses of whatsoever nature, including attorney’s fees and expenses, in respect of the death or injury of any person or loss of or damage to any property other than the Facilities whether accepted or not, arising in connection with the supply and installation of the Facilities and by reason of the negligence of the Contractor or its Subcontractors, or their employees, officers, or agents, except any injury, death, or property damage caused by the negligence of the Employer, its contractors, employees, officers, or agents. 33.2 If any proceedings are brought or any claim is made against the Employer that might subject the Contractor to liability under GCC Subclause 33.1, the Employer shall promptly give the Contractor a notice thereof and the Contractor may at its own expense and in the Employer’s name conduct such proceedings or claim and any negotiations for the settlement of any such proceedings or claim. If the Contractor fails to notify the Employer within 28 days after receipt of such notice that it intends to conduct any such proceedings or claim, then the Employer shall be free to conduct the same on its own behalf. Unless the Contractor has so failed to notify the Employer within the 28-day period, the Employer shall make no admission that may be prejudicial to the defense of any such proceedings or claim. The Employer shall, at the Contractor’s request, afford all available assistance to the Contractor in conducting such proceedings or claim, and shall be reimbursed by the Contractor for all reasonable expenses incurred in so doing. 33.3 The Employer shall indemnify and hold harmless the Contractor and its employees, officers, and Subcontractors from any liability for loss of or damage to property of the Employer, other than the Facilities not yet taken over, that is caused by fire, explosion, or any other perils, in excess of the amount recoverable from insurances procured under GCC Clause 34, provided that such fire, explosion, or other perils were not caused by any act or failure of the Contractor. 33.4 The party entitled to the benefit of an indemnity under this GCC Clause 33 shall take all reasonable measures to mitigate any loss or damage which has occurred. If the party fails to take such measures, the other party’s liabilities shall be correspondingly reduced. |
| 34. Insurance | 34.1 To the extent specified in the Appendix (Insurance Requirements) to the Contract Agreement, the Contractor shall at its expense take out and maintain in effect, or cause to be taken out and maintained in effect, during the performance of the Contract, the insurances set forth below in the sums and with the deductibles and other conditions specified in the said Appendix. The identity of the insurers and the form of the policies shall be subject to the approval of the Employer, who should not unreasonably withhold such approval. (a) Cargo Insurance During Transport Covering loss or damage occurring while in transit from the Contractor’s or Subcontractor’s works or stores until arrival at the Site, to the Plant (including spare parts therefor) and to the Contractor’s Equipment. (b) Installation All Risks Insurance Covering physical loss or damage to the Facilities at the Site, occurring prior to Completion of the Facilities, with an extended maintenance coverage for the Contractor’s liability in respect of any loss or damage occurring during the Defect Liability Period while the Contractor is on the Site for the purpose of performing its obligations during the Defect Liability Period. (c) Third Party Liability Insurance Covering bodily injury or death suffered by third parties including the Employer’s personnel, and loss of or damage to property occurring in connection with the supply and installation of the Facilities. (d) Automobile Liability Insurance Covering use of all vehicles used by the Contractor or its Subcontractors, whether or not owned by them, in connection with the execution of the Contract. (e) Workers’ Compensation In accordance with the statutory requirements applicable in any country where the Contract or any part thereof is executed. (f) Employer’s Liability In accordance with the statutory requirements applicable in any country where the Contract or any part thereof is executed. (g) Other Insurances Such other insurances as may be specifically agreed upon by the parties hereto as listed in the Appendix (Insurance Requirements) to the Contract Agreement. 34.2 The Employer shall be named as co-insured under all insurance policies taken out by the Contractor pursuant to GCC Subclause 34.1, except for the Third Party Liability, Workers’ Compensation, and Employer’s Liability Insurances, and the Contractor’s Subcontractors shall be named as co-insureds under all insurance policies taken out by the Contractor pursuant to GCC Subclause 34.1 except for the Cargo Insurance During Transport, Workers’ Compensation, and Employer’s Liability Insurances. All insurer’s rights of subrogation against such co-insureds for losses or claims arising out of the performance of the Contract shall be waived under such policies. 34.3 The Contractor shall, in accordance with the provisions of the Appendix (Insurance Requirements) to the Contract Agreement, deliver to the Employer certificates of insurance or copies of the insurance policies as evidence that the required policies are in full force and effect. The certificates shall provide that no less than 21 days’ notice shall be given to the Employer by insurers prior to cancellation or material modification of a policy. 34.4 The Contractor shall ensure that, where applicable, its Subcontractor(s) shall take out and maintain in effect adequate insurance policies for their personnel and vehicles and for work executed by them under the Contract, unless such Subcontractors are covered by the policies taken out by the Contractor. 34.5 The Employer shall at its expense take out and maintain in effect during the performance of the Contract those insurances specified in the Appendix (Insurance Requirements) to the Contract Agreement, in the sums and with the deductibles and other conditions specified in the said Appendix. The Contractor and the Contractor’s Subcontractors shall be named as co-insureds under all such policies. All insurers’ rights of subrogation against such co-insureds for losses or claims arising out of the performance of the Contract shall be waived under such policies. The Employer shall deliver to the Contractor satisfactory evidence that the required insurances are in full force and effect. The policies shall provide that not less than 21 days’ notice shall be given to the Contractor by all insurers prior to any cancellation or material modification of the policies. If so requested by the Contractor, the Employer shall provide copies of the policies taken out by the Employer under this GCC Subclause 34.5. 34.6 If the Contractor fails to take out and/or maintain in effect the insurances referred to in GCC Subclause 34.1, the Employer may take out and maintain in effect any such insurances and may from time to time deduct from any amount due the Contractor under the Contract any premium that the Employer shall have paid to the insurer, or may otherwise recover such amount as a debt due from the Contractor. If the Employer fails to take out and/or maintain in effect the insurances referred to in GCC 34.5, the Contractor may take out and maintain in effect any such insurances and may from time to time deduct from any amount due the Employer under the Contract any premium that the Contractor shall have paid to the insurer, or may otherwise recover such amount as a debt due from the Employer. If the Contractor fails to or is unable to take out and maintain in effect any such insurances, the Contractor shall nevertheless have no liability or responsibility towards the Employer, and the Contractor shall have full recourse against the Employer for any and all liabilities of the Employer herein. 34.7 Unless otherwise provided in the Contract, the Contractor shall prepare and conduct all and any claims made under the policies effected by it pursuant to this GCC Clause 34, and all monies payable by any insurers shall be paid to the Contractor. The Employer shall give to the Contractor all such reasonable assistance as may be required by the Contractor. With respect to insurance claims in which the Employer’s interest is involved, the Contractor shall not give any release or make any compromise with the insurer without the prior written consent of the Employer. With respect to insurance claims in which the Contractor’s interest is involved, the Employer shall not give any release or make any compromise with the insurer without the prior written consent of the Contractor. |
| 35. Unforeseen Conditions | 35.1 If, during the execution of the Contract, the Contractor shall encounter on the Site any physical conditions other than climatic conditions, or artificial obstructions that could not have been reasonably foreseen prior to the date of the Contract Agreement by an experienced contractor on the basis of reasonable examination of the data relating to the Facilities including any data as to boring tests, provided by the Employer, and on the basis of information that it could have obtained from a visual inspection of the Site if access thereto was available, or other data readily available to it relating to the Facilities, and if the Contractor determines that it will in consequence of such conditions or obstructions incur additional cost and expense or require additional time to perform its obligations under the Contract that would not have been required if such physical conditions or artificial obstructions had not been encountered, the Contractor shall promptly, and before performing additional work or using additional Plant or Contractor’s Equipment, notify the Project Manager in writing of (a) the physical conditions or artificial obstructions on the Site that could not have been reasonably foreseen; (b) the additional work and/or Plant and/or Contractor’s Equipment required, including the steps which the Contractor will or proposes to take to overcome such conditions or obstructions; (c) the extent of the anticipated delay; and (d) the additional cost and expense that the Contractor is likely to incur. On receiving any notice from the Contractor under this GCC Subclause 35.1, the Project Manager shall promptly consult with the Employer and Contractor and decide upon the actions to be taken to overcome the physical conditions or artificial obstructions encountered. Following such consultations, the Project Manager shall instruct the Contractor, with a copy to the Employer, of the actions to be taken. 35.2 Any reasonable additional cost and expense incurred by the Contractor in following the instructions from the Project Manager to overcome such physical conditions or artificial obstructions referred to in GCC Subclause 35.1 shall be paid by the Employer to the Contractor as an addition to the Contract Price. - If the Contractor is delayed or impeded in the performance of the Contract because of any such physical conditions or artificial obstructions referred to in GCC Subclause 35.1, the Time for Completion shall be extended in accordance with GCC Clause 40. |
| 36. Change in Laws and Regulations | 36.1 If, after the date 28 days prior to the date of Bid submission, in the country where the Site is located, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated, or changed, which shall be deemed to include any change in interpretation or application by the competent authorities, that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the performance of any of its obligations under the Contract. Notwithstanding the foregoing, such additional or reduced costs shall not be separately paid or credited if the same has already been accounted for in the price adjustment provisions where applicable, in accordance with the SCC, pursuant to GCC Subclause 11.2. |
| 37. Force Majeure | 37.1 “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the party affected, and shall include, without limitation, the following: (a) war, hostilities, or warlike operations whether a state of war be declared or not, invasion, act of foreign enemy and civil war; (b) rebellion, revolution, insurrection, mutiny, usurpation of civil or military government, conspiracy, riot, civil commotion, and terrorist acts; (c) confiscation, nationalization, mobilization, commandeering or requisition by or under the order of any government or de jure or de facto authority or ruler or any other act or failure to act of any local state or national government authority; (d) strike, sabotage, lockout, embargo, import restriction, port congestion, lack of usual means of public transportation and communication, industrial dispute, shipwreck, shortage or restriction of power supply, epidemics, quarantine, and plague; (e) earthquake, landslide, volcanic activity, fire, flood or inundation, tidal wave, typhoon or cyclone, hurricane, storm, lightning, or other inclement weather condition, nuclear, and pressure waves or other natural or physical disaster; and (f) shortage of labor, materials, or utilities where caused by circumstances that are themselves Force Majeure. 37.2 If either party is prevented, hindered, or delayed from or in performing any of its obligations under the Contract by an event of Force Majeure, then it shall notify the other in writing of the occurrence of such event and the circumstances thereof within 14 days after the occurrence of such event. 37.3 The party who has given such notice shall be excused from the performance or punctual performance of its obligations under the Contract for so long as the relevant event of Force Majeure continues and to the extent that such party’s performance is prevented, hindered, or delayed. The Time for Completion shall be extended in accordance with GCC Clause 40. 37.4 The party or parties affected by the event of Force Majeure shall use reasonable efforts to mitigate the effect thereof upon its or their performance of the Contract and to fulfill its or their obligations under the Contract, but without prejudice to either party’s right to terminate the Contract under GCC Subclauses 37.6 and 38.5. 37.5 No delay or nonperformance by either party hereto caused by the occurrence of any event of Force Majeure shall (a) constitute a default or breach of the Contract; or (b) give rise to any claim for damages or additional cost or expense occasioned thereby, subject to GCC Subclauses 32.2, 38.3 and 38.4 if and to the extent that such delay or nonperformance is caused by the occurrence of an event of Force Majeure. 37.6 If the performance of the Contract is substantially prevented, hindered, or delayed for a single period of more than 60 days or an aggregate period of more than 120 days on account of one or more events of Force Majeure during the currency of the Contract, the parties will attempt to develop a mutually satisfactory solution, failing which either party may terminate the Contract by giving a notice to the other, but without prejudice to either party’s right to terminate the Contract under GCC Subclause 38.5. 37.7 In the event of termination pursuant to GCC Subclause 37.6, the rights and obligations of the Employer and the Contractor shall be as specified in GCC Subclauses 42.1.2 and 42.1.3. 37.8 Notwithstanding GCC Subclause 37.5, Force Majeure shall not apply to any obligation of the Employer to make payments to the Contractor herein. |
| 38. War Risks | 38.1 “War Risks” shall mean any event specified in paragraphs (a) and (b) of GCC Subclause 37.1 and any explosion or impact of any mine, bomb, shell, grenade, or other projectile, missile, munitions or explosive of war, occurring or existing in or near the country (or countries) where the Site is located. 38.2 Notwithstanding anything contained in the Contract, the Contractor shall have no liability whatsoever for or with respect to (a) destruction of or damage to Facilities, Plant, or any part thereof; (b) destruction of or damage to property of the Employer or any third party; or (c) injury or loss of life if such destruction, damage, injury or loss of life is caused by any war risks, and the Employer shall indemnify and hold the Contractor harmless from and against any and all claims, liabilities, actions, lawsuits, damages, costs, charges, or expenses arising in consequence of or in connection with the same. 38.3 If the Facilities or any Plant or Contractor’s Equipment or any other property of the Contractor used or intended to be used for the purposes of the Facilities shall sustain destruction or damage by reason of any war risks, the Employer shall pay the Contractor for (a) any part of the Facilities or the Plant so destroyed or damaged to the extent not already paid for by the Employer and so far as may be required by the Employer, and as may be necessary for completion of the Facilities; (b) replacing or making good any Contractor’s Equipment or other property of the Contractor so destroyed or damaged; and (c) replacing or making good any such destruction or damage to the Facilities or the Plant or any part thereof. If the Employer does not require the Contractor to replace or make good any such destruction or damage to the Facilities, the Employer shall either request a change in accordance with GCC Clause 39, excluding the performance of that part of the Facilities thereby destroyed or damaged or, where the loss, destruction, or damage affects a substantial part of the Facilities, shall terminate the Contract, pursuant to GCC Subclause 42.1. If the Employer requires the Contractor to replace or make good on any such destruction or damage to the Facilities, the Time for Completion shall be extended in accordance with GCC 40. 38.4 Notwithstanding anything contained in the Contract, the Employer shall pay the Contractor for any increased costs or incidentals to the execution of the Contract that are in any way attributable to, consequent on, resulting from, or in any way connected with any war risks, provided that the Contractor shall as soon as practicable notify the Employer in writing of any such increased cost. 38.5 If during the performance of the Contract any war risks shall occur that financially or otherwise materially affect the execution of the Contract by the Contractor, the Contractor shall use its reasonable efforts to execute the Contract with due and proper consideration given to the safety of its and its Subcontractors’ personnel engaged in the work on the Facilities, provided, however, that if the execution of the work on the Facilities becomes impossible or is substantially prevented for a single period of more than sixty (60) days or an aggregate period of more than one hundred and twenty (120) days on account of any war risks, the parties will attempt to develop a mutually satisfactory solution, failing which either party may terminate the Contract by giving a notice to the other. 38.6 In the event of termination pursuant to GCC Subclauses 38.3 or 38.5, the rights and obligations of the Employer and the Contractor shall be specified in GCC Subclauses 42.1.2 and 42.1.3. |

H. Change in Contract Elements

| 39. Change in the Facilities | 39.1 Introducing a Change 39.1.1 Subject to GCC Subclauses 39.2.5 and 39.2.7, the Employer shall have the right to propose, and subsequently require, that the Project Manager order the Contractor from time to time during the performance of the Contract to make any change, modification, addition, or deletion to, in or from the Facilities hereinafter called “Change,” provided that such Change falls within the general scope of the Facilities and does not constitute unrelated work and that it is technically practicable, taking into account both the state of advancement of the Facilities and the technical compatibility of the Change envisaged with the nature of the Facilities as specified in the Contract. 39.1.2 The Contractor may from time to time during its performance of the Contract propose to the Employer with a copy to the Project Manager, any Change that the Contractor considers necessary or desirable to improve the quality, efficiency, or safety of the Facilities. The Employer may at its discretion approve or reject any Change proposed by the Contractor, provided that the Employer shall approve any Change proposed by the Contractor to ensure the safety of the Facilities. 39.1.3 Notwithstanding GCC Subclauses 39.1.1 and 39.1.2, no change made necessary because of any default of the Contractor in the performance of its obligations under the Contract shall be deemed to be a Change, and such change shall not result in any adjustment of the Contract Price or the Time for Completion. 39.1.4 The procedure on how to proceed with and execute Changes is specified in GCC Subclauses 39.2 and 39.3, and further details and forms are provided in the Employer’s Requirements (Forms and Procedures). 39.2 Changes Originating from Employer 39.2.1 If the Employer proposes a Change pursuant to GCC Subclause 39.1.1, it shall send to the Contractor a “Request for Change Proposal,” requiring the Contractor to prepare and furnish to the Project Manager as soon as reasonably practicable a “Change Proposal,” which shall include the following: (a) brief description of the Change, (b) effect on the Time for Completion, (c) estimated cost of the Change, (d) effect on Functional Guarantees (if any), (e) effect on the Facilities, and (f) effect on any other provisions of the Contract. 39.2.2 Prior to preparing and submitting the “Change Proposal,” the Contractor shall submit to the Project Manager an “Estimate for Change Proposal,” which shall be an estimate of the cost of preparing and submitting the Change Proposal. Upon receipt of the Contractor’s Estimate for Change Proposal, the Employer shall do one of the following: (a) accept the Contractor’s estimate with instructions to the Contractor to proceed with the preparation of the Change Proposal, (b) advise the Contractor of any part of its Estimate for Change Proposal that is unacceptable and request the Contractor to review its estimate (c) advise the Contractor that the Employer does not intend to proceed with the Change. 39.2.3 Upon receipt of the Employer’s instruction to proceed under GCC Subclause 39.2.2 (a), the Contractor shall, with proper expedition, proceed with the preparation of the Change Proposal, in accordance with GCC Subclause 39.2.1. 39.2.4 The pricing of any Change shall, as far as practicable, be calculated in accordance with the rates and prices included in the Contract. If such rates and prices are inequitable, the parties thereto shall agree on specific rates for the valuation of the Change. 39.2.5 If before or during the preparation of the Change Proposal it becomes apparent that the aggregate effect of compliance therewith and with all other Change Orders that have already become binding upon the Contractor under this GCC Clause 39 would be to increase or decrease the Contract Price as originally set forth in Article 2 (Contract Price) of the Contract Agreement by more than 15%, the Contractor may give a written notice of objection thereto prior to furnishing the Change Proposal as aforesaid. If the Employer accepts the Contractor’s objection, the Employer shall withdraw the proposed Change and shall notify the Contractor in writing thereof. The Contractor’s failure to so object shall neither affect its right to object to any subsequent requested Changes or Change Orders herein, nor affect its right to take into account, when making such subsequent objection, the percentage increase or decrease in the Contract Price that any Change not objected to by the Contractor represents. 39.2.6 Upon receipt of the Change Proposal, the Employer and the Contractor shall mutually agree upon all matters therein contained. Within 14 days after such agreement, the Employer shall, if it intends to proceed with the Change, issue the Contractor with a Change Order. If the Employer is unable to reach a decision within 14 days, it shall notify the Contractor with details of when the Contractor can expect a decision. If the Employer decides not to proceed with the Change for whatever reason, it shall, within the said period of 14 days, notify the Contractor accordingly. Under such circumstances, the Contractor shall be entitled to reimbursement of all costs reasonably incurred by it in the preparation of the Change Proposal, provided that these do not exceed the amount given by the Contractor in its Estimate for Change Proposal submitted in accordance with GCC Subclause 39.2.2. 39.2.7 If the Employer and the Contractor cannot reach agreement on the price for the Change, an equitable adjustment to the Time for Completion, or any other matters identified in the Change Proposal, the Employer may nevertheless instruct the Contractor to proceed with the Change by issue of a “Pending Agreement Change Order.” Upon receipt of a Pending Agreement Change Order, the Contractor shall immediately proceed with effecting the Changes covered by such Order. The parties shall thereafter attempt to reach agreement on the outstanding issues under the Change Proposal. If the parties cannot reach agreement within 60 days from the date of issue of the Pending Agreement Change Order, then the matter may be referred to the Dispute Board in accordance with the provisions of GCC Subclause 45.3. 39.3 Changes Originating from Contractor 39.3.1 If the Contractor proposes a Change pursuant to GCC Subclause 39.1.2, the Contractor shall submit to the Project Manager a written “Application for Change Proposal,” giving reasons for the proposed Change and including the information specified in GCC Subclause 39.2.1. Upon receipt of the Application for Change Proposal, the parties shall follow the procedures outlined in GCC Subclauses 39.2.6 and 39.2.7. However, should the Employer choose not to proceed, the Contractor shall not be entitled to recover the costs of preparing the Application for Change Proposal. |
| --- | --- |
| 40. Extension of Time for Completion | 40.1 The Time(s) for Completion specified in the SCC shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 39; (b) any occurrence of Force Majeure as provided in GCC Clause 37, unforeseen conditions as provided in GCC Clause 35, or other occurrence of any of the matters specified or referred to in paragraphs (a), (b) and (c) of GCC Subclause 32.2; (c) any suspension order given by the Employer under GCC Clause 41 hereof or reduction in the rate of progress pursuant to GCC Subclause 41.2; or (d) any changes in laws and regulations as provided in GCC Clause 36; or (e) any default or breach of the Contract by the Employer, or any activity, act or omission of the Employer, or the Project Manager, or any other contractors employed by the Employer; or (f) any other matter specifically mentioned in the Contract; or (g) any delay on the part of a sub-contractor, provided such delay is due to a cause for which the Contractor himself would have been entitled to an extension of time under this Subclause by such period as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. 40.2 Except where otherwise specifically provided in the Contract, the Contractor shall submit to the Project Manager a notice of a claim for an extension of the Time for Completion, together with particulars of the event or circumstance justifying such extension as soon as reasonably practicable after the commencement of such event or circumstance. As soon as reasonably practicable after receipt of such notice and supporting particulars of the claim, the Employer and the Contractor shall agree upon the period of such extension. In the event that the Contractor does not accept the Employer’s estimate of a fair and reasonable time extension, the Contractor shall be entitled to refer the matter to a Dispute Board, pursuant to GCC Subclause 45.3. 40.3 The Contractor shall at all times use its reasonable efforts to minimize any delay in the performance of its obligations under the Contract. In all cases where the Contractor has given a notice of a claim for an extension of time under GCC 40.2, the Contractor shall consult with the Project Manager in order to determine the steps (if any) which can be taken to overcome or minimize the actual or anticipated delay. The Contractor shall there after comply with all reasonable instructions, which the Project Manager shall give in order to minimize such delay. If compliance with such instructions shall cause the Contractor to incur extra costs and the Contractor is entitled to an extension of time under GCC 40.1, the amount of such extra costs shall be added to the Contract Price. |
| 41. Suspension | 41.1 The Employer may request the Project Manager, by notice to the Contractor, to order the Contractor to suspend performance of any or all of its obligations under the Contract. Such notice shall specify the obligation of which performance is to be suspended, the effective date of the suspension and the reasons therefor. The Contractor shall thereupon suspend performance of such obligation, except those obligations necessary for the care or preservation of the Facilities, until ordered in writing to resume such performance by the Project Manager. If, by virtue of a suspension order given by the Project Manager, other than by reason of the Contractor’s default or breach of the Contract, the Contractor’s performance of any of its obligations is suspended for an aggregate period of more than 90 days, then at any time thereafter and provided that at that time such performance is still suspended, the Contractor may give a notice to the Project Manager requiring that the Employer shall, within 28 days of receipt of the notice, order the resumption of such performance or request and subsequently order a change in accordance with GCC Clause 39, excluding the performance of the suspended obligations from the Contract. If the Employer fails to do so within such period, the Contractor may, by a further notice to the Project Manager, elect to treat the suspension, where it affects a part only of the Facilities, as a deletion of such part in accordance with GCC Clause 39 or, where it affects the whole of the Facilities, as termination of the Contract under GCC Subclause 42.1. 41.2 If (a) the Employer has failed to pay the Contractor any sum due under the Contract within the specified period, has failed to approve any invoice or supporting documents without just cause pursuant to the Appendix (Terms and Procedures of Payment) to the Contract Agreement, or commits a substantial breach of the Contract, the Contractor may give a notice to the Employer that requires payment of such sum, with interest thereon as stipulated in GCC Subclause 12.3, requires approval of such invoice or supporting documents, or specifies the breach and requires the Employer to remedy the same, as the case may be. If the Employer fails to pay such sum together with such interest, fails to approve such invoice or supporting documents or give its reasons for withholding such approval, or fails to remedy the breach or take steps to remedy the breach within 14 days after receipt of the Contractor’s notice; or (b) the Contractor is unable to carry out any of its obligations under the Contract for any reason attributable to the Employer, including but not limited to the Employer’s failure to provide possession of or access to the Site or other areas in accordance with GCC Subclause 10.2, or failure to obtain any governmental permit necessary for the execution and/or completion of the Facilities, then the Contractor may by 14 days’ notice to the Employer suspend performance of all or any of its obligations under the Contract, or reduce the rate of progress. 41.3 If the Contractor’s performance of its obligations is suspended, or the rate of progress is reduced pursuant to this GCC Clause 41, then the Time for Completion shall be extended in accordance with GCC Subclause 40.1, and any and all additional costs or expenses incurred by the Contractor as a result of such suspension or reduction shall be paid by the Employer to the Contractor in addition to the Contract Price, except in the case of suspension order or reduction in the rate of progress by reason of the Contractor’s default or breach of the Contract. 41.4 During the period of suspension, the Contractor shall not remove from the Site any Plant, any part of the Facilities or any Contractor’s Equipment, without the prior written consent of the Employer. |
| 42. Termination | 42.1 Termination for Employer’s Convenience 42.1.1 The Employer may at any time terminate the Contract for any reason by giving the Contractor a notice of termination that refers to this GCC Subclause 42.1. 42.1.2 Upon receipt of the notice of termination under GCC Subclause 42.1.1, the Contractor shall, either immediately or upon the date specified in the notice of termination, (a) cease all further work, except for such work as the Employer may specify in the notice of termination for the sole purpose of protecting that part of the Facilities already executed, or any work required to leave the Site in a clean and safe condition; (b) terminate all subcontracts, except those to be assigned to the Employer pursuant to paragraph (d) (ii) below; (c) remove all Contractor’s Equipment from the Site, repatriate the Contractor’s and its Subcontractors’ personnel from the Site, remove from the Site any wreckage, rubbish and debris of any kind, and leave the whole of the Site in a clean and safe condition; and (d) subject to the payment specified in GCC Subclause 42.1.3, (i) deliver to the Employer the parts of the Facilities executed by the Contractor up to the date of termination; (ii) to the extent legally possible, assign to the Employer all right, title and benefit of the Contractor to the Facilities and to the Plant as of the date of termination, and, as may be required by the Employer, in any subcontracts concluded between the Contractor and its Subcontractors; and (iii) deliver to the Employer all non-proprietary drawings, specifications and other documents prepared by the Contractor or its Subcontractors as at the date of termination in connection with the Facilities. 42.1.3 In the event of termination of the Contract under GCC Subclause 42.1.1, the Employer shall pay to the Contractor the following amounts: (a) the Contract Price, properly attributable to the parts of the Facilities executed by the Contractor as of the date of termination; (b) the costs reasonably incurred by the Contractor in the removal of the Contractor’s Equipment from the Site and in the repatriation of the Contractor’s and its Subcontractors’ personnel; (c) any amounts to be paid by the Contractor to its Subcontractors in connection with the termination of any subcontracts, including any cancellation charges; (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition pursuant to paragraph (a) of GCC Subclause 42.1.2; and (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. 42.2 Termination for Contractor’s Default 42.2.1 The Employer, without prejudice to any other rights or remedies it may possess, may terminate the Contract forthwith in the following circumstances by giving a notice of termination and its reasons therefor to the Contractor, referring to this GCC Subclause 42.2: (a) if the Contractor becomes bankrupt or insolvent, has a receiving order issued against it, compounds with its creditors, or, if the Contractor is a corporation, a resolution is passed or order is made for its winding up, other than a voluntary liquidation for the purposes of amalgamation or reconstruction, a receiver is appointed over any part of its undertaking or assets, or if the Contractor takes or suffers any other analogous action in consequence of debt; (b) if the Contractor assigns or transfers the Contract or any right or interest therein in violation of the provision of GCC Clause 43; and (c) if the Contractor, in the judgment of the Employer has engaged in corrupt or fraudulent practices, as defined in GCC Clause 6, in competing for or in executing the Contract. 42.2.2 If the Contractor (a) has abandoned or repudiated the Contract; (b) has without valid reason failed to commence work on the Facilities promptly or has suspended, other than pursuant to GCC Subclause 41.2, the progress of Contract performance for more than 28 days after receiving a written instruction from the Employer to proceed; (c) persistently fails to execute the Contract in accordance with the Contract or persistently neglects to carry out its obligations under the Contract without just cause; (d) refuses or is unable to provide sufficient materials, services or labor to execute and complete the Facilities in the manner specified in the program furnished under GCC Subclause 18.2 at rates of progress that give reasonable assurance to the Employer that the Contractor can attain Completion of the Facilities by the Time for Completion as extended; then the Employer may, without prejudice to any other rights it may possess under the Contract, give a notice to the Contractor, stating the nature of the default and requiring the Contractor to remedy the same. If the Contractor fails to remedy or to take steps to remedy the same within 14 days of its receipt of such notice, then the Employer may terminate the Contract forthwith by giving a notice of termination to the Contractor that refers to this GCC Subclause 42.2. 42.2.3 Upon receipt of the notice of termination under GCC Subclauses 42.2.1 or 42.2.2, the Contractor shall, either immediately or upon such date as is specified in the notice of termination, (a) cease all further work, except for such work as the Employer may specify in the notice of termination for the sole purpose of protecting that part of the Facilities already executed, or any work required to leave the Site in a clean and safe condition; (b) terminate all subcontracts, except those to be assigned to the Employer pursuant to paragraph (d) below; (c) deliver to the Employer the parts of the Facilities executed by the Contractor up to the date of termination; (d) to the extent legally possible, assign to the Employer all right, title and benefit of the Contractor to the Facilities and to the Plant as of the date of termination, and, as may be required by the Employer, in any subcontracts concluded between the Contractor and its Subcontractors; and (e) deliver to the Employer all drawings, specifications and other documents prepared by the Contractor or its Subcontractors as of the date of termination in connection with the Facilities. 42.2.4 The Employer may enter upon the Site, expel the Contractor, and complete the Facilities itself or by employing any third party. The Employer may, to the exclusion of any right of the Contractor over the same, take over and use with the payment of a fair rental rate to the Contractor, with all the maintenance costs to the account of the Employer and with an indemnification by the Employer for all liability including damage or injury to persons arising out of the Employer’s use of such equipment, any Contractor’s Equipment owned by the Contractor and on the Site in connection with the Facilities for such reasonable period as the Employer considers expedient for the supply and installation of the Facilities. Upon completion of the Facilities or at such earlier date as the Employer thinks appropriate, the Employer shall give notice to the Contractor that such Contractor’s Equipment will be returned to the Contractor at or near the Site and shall return such Contractor’s Equipment to the Contractor in accordance with such notice. The Contractor shall thereafter without delay and at its cost remove or arrange removal of the same from the Site. 42.2.5 Subject to GCC Subclause 42.2.6, the Contractor shall be entitled to be paid the Contract Price attributable to the Facilities executed as of the date of termination, the value of any unused or partially used Plant on the Site, and the costs, if any, incurred in protecting the Facilities and in leaving the Site in a clean and safe condition pursuant to paragraph (a) of GCC Subclause 42.2.3. Any sums due the Employer from the Contractor accruing prior to the date of termination shall be deducted from the amount to be paid to the Contractor under this Contract. 42.2.6 If the Employer completes the Facilities, the cost of completing the Facilities by the Employer shall be determined. If the sum that the Contractor is entitled to be paid, pursuant to GCC Subclause 42.2.5, plus the reasonable costs incurred by the Employer in completing the Facilities, exceeds the Contract Price, the Contractor shall be liable for such excess. If such excess is greater than the sums due the Contractor under GCC Subclause 42.2.5, the Contractor shall pay the balance to the Employer, and if such excess is less than the sums due the Contractor under GCC Subclause 42.2.5, the Employer shall pay the balance to the Contractor. The Employer and the Contractor shall agree, in writing, on the computation described above and the manner in which any sums shall be paid. 42.3 Termination by Contractor 42.3.1 If (a) the Employer has failed to pay the Contractor any sum due under the Contract within the specified period, has failed to approve any invoice or supporting documents without just cause pursuant to the Appendix (Terms and Procedures of Payment) to the Contract Agreement, or commits a substantial breach of the Contract, the Contractor may give a notice to the Employer that requires payment of such sum, thereon as stipulated in GCC Subclause 12.3, requires approval of such invoice or supporting documents, or specifies the breach and requires the Employer to remedy the same, as the case may be. If the Employer fails to pay such sum, fails to approve such invoice or supporting documents or give its reasons for withholding such approval, fails to remedy the breach or take steps to remedy the breach within 14 days after receipt of the Contractor’s notice; or (b) the Contractor is unable to carry out any of its obligations under the Contract for any reason attributable to the Employer, including but not limited to the Employer’s failure to provide possession of or access to the Site or other areas or failure to obtain any governmental permit necessary for the execution and/or completion of the Facilities; then the Contractor may give a notice to the Employer thereof, and if the Employer has failed to pay the outstanding sum, to approve the invoice or supporting documents, to give its reasons for withholding such approval, or to remedy the breach within 28 days of such notice, or if the Contractor is still unable to carry out any of its obligations under the Contract for any reason attributable to the Employer within 28 days of the said notice, the Contractor may by a further notice to the Employer referring to this GCC Subclause 42.3.1, forthwith terminate the Contract. 42.3.2 The Contractor may terminate the Contract forthwith by giving a notice to the Employer to that effect, referring to this GCC Subclause 42.3.2, if the Employer becomes bankrupt or insolvent, has a receiving order issued against it, compounds with its creditors, or, being a corporation, if a resolution is passed or order is made for its winding up (other than a voluntary liquidation for the purposes of amalgamation or reconstruction), a receiver is appointed over any part of its undertaking or assets, or if the Employer takes or suffers any other analogous action in consequence of debt. 42.3.3 If the Contract is terminated under GCC Subclauses 42.3.1 or 42.3.2, then the Contractor shall immediately (a) cease all further work, except for such work as may be necessary for the purpose of protecting that part of the Facilities already executed, or any work required to leave the Site in a clean and safe condition; (b) terminate all subcontracts, except those to be assigned to the Employer pursuant to paragraph (d) (ii); (c) remove all Contractor’s Equipment from the Site and repatriate the Contractor’s and its Subcontractors’ personnel from the Site; and (d) subject to the payment specified in GCC Subclause 42.3.4, (i) deliver to the Employer the parts of the Facilities executed by the Contractor up to the date of termination; (ii) to the extent legally possible, assign to the Employer all right, title and benefit of the Contractor to the Facilities and to the Plant as of the date of termination, and, as may be required by the Employer, in any subcontracts concluded between the Contractor and its Subcontractors; and (iii) deliver to the Employer all drawings, specifications and other documents prepared by the Contractor or its Subcontractors as of the date of termination in connection with the Facilities. 42.3.4 If the Contract is terminated under GCC Subclauses 42.3.1 or 42.3.2, the Employer shall pay to the Contractor all payments specified in GCC Subclause 42.1.3, and reasonable compensation for all loss, except for loss of profit, or damage sustained by the Contractor arising out of, in connection with or in consequence of such termination. 42.3.5 Termination by the Contractor pursuant to this GCC Subclause 42.3 is without prejudice to any other rights or remedies of the Contractor that may be exercised in lieu of or in addition to rights conferred by GCC Subclause 42.3. 42.4 In this GCC Clause 42, the expression “Facilities executed” shall include all work executed, Installation Services provided, and all Plant acquired, or subject to a legally binding obligation to purchase, by the Contractor and used or intended to be used for the purpose of the Facilities, up to and including the date of termination. 42.5 In this GCC Clause 42, in calculating any monies due from the Employer to the Contractor, account shall be taken of any sum previously paid by the Employer to the Contractor under the Contract, including any advance payment paid pursuant to the Appendix (Terms and Procedures of Payment) to the Contract Agreement. |
| 43. Assignment | 43.1 Neither the Employer nor the Contractor shall, without the express prior written consent of the other party which consent shall not be unreasonably withheld, assign to any third party the Contract or any part thereof, or any right, benefit, obligation or interest therein or thereunder, except that the Contractor shall be entitled to assign either absolutely or by way of charge any monies due and payable to it or that may become due and payable to it under the Contract. |

I.  Claims, Disputes, and Arbitration

| 44. Contractor’s Claims | 44.1 If the Contractor considers himself to be entitled to any extension of the Time for Completion and/or any additional payment, under any Clause of these Conditions or otherwise in connection with the Contract, the Contractor shall submit a notice to the Project Manager, describing the event or circumstance giving rise to the claim. The notice shall be given as soon as practicable, and not later than 28 days after the Contractor became aware, or should have become aware, of the event or circumstance. If the Contractor fails to give notice of a claim within such period of 28 days, the Time for Completion shall not be extended, the Contractor shall not be entitled to additional payment, and the Employer shall be discharged from all liability in connection with the claim. Otherwise, the following provisions of this Subclause shall apply. The Contractor shall also submit any other notices, which are required by the Contract, and supporting particulars for the claim, all as relevant to such event or circumstance. The Contractor shall keep such contemporary records as may be necessary to substantiate any claim, either on the Site or at another location acceptable to the Project Manager. Without admitting the Employer’s liability, the Project Manager may, after receiving any notice under this Subclause, monitor the record keeping and/or instruct the Contractor to keep further contemporary records. The Contractor shall permit the Project Manager to inspect all these records, and shall (if instructed) submit copies to the Project Manager. Within 42 days after the Contractor became aware (or should have become aware) of the event or circumstance giving rise to the claim, or within such other period as may be proposed by the Contractor and approved by the Project Manager, the Contractor shall send to the Project Manager a fully detailed claim, which includes full supporting particulars of the basis of the claim and of the extension of time and/or additional payment claimed. If the event or circumstance giving rise to the claim has a continuing effect, - this fully detailed claim shall be considered as interim; - the Contractor shall send further interim claims at monthly intervals, giving the accumulated delay and/or amount claimed, and such further particulars as the Project Manager may reasonably require; and - the Contractor shall send a final claim within 28 days after the end of the effects resulting from the event or circumstance, or within such other period as may be proposed by the Contractor and approved by the Project Manager. Within 42 days after receiving a claim or any further particulars supporting a previous claim, or within such other period as may be proposed by the Project Manager and approved by the Contractor, the Project Manager shall respond with approval, or with disapproval and detailed comments. He may also request any necessary further particulars, but shall nevertheless give his response on the principles of the claim within such time. Each payment certificate shall include such amounts for any claim as have been reasonably substantiated as due under the relevant provision of the Contract. Unless and until the particulars supplied are sufficient to substantiate the whole of the claim, the Contractor shall only be entitled to payment for such part of the claim as he has been able to substantiate. The Project Manager shall agree with the Contractor or estimate: (i) the extension (if any) of the Time for Completion (before or after its expiry) in accordance with GCC Clause 40, and/or (ii) the additional payment (if any) to which the Contractor is entitled under the Contract. The requirements of this Subclause are in addition to those of any other Subclause, which may apply to a claim. If the Contractor fails to comply with this or another Subclause in relation to any claim, any extension of time and/or additional payment shall take account of the extent (if any) to which the failure has prevented or prejudiced proper investigation of the claim, unless the claim is excluded under the second paragraph of this Subclause. In the event that the Contractor and the Employer cannot agree on any matter relating to a claim, either party may refer the matter to the Dispute Board pursuant to GCC 45 hereof. |
| --- | --- |
| 45. Disputes and Arbitration | ### 45.1 Appointment of the Dispute Board Disputes shall be referred to a Dispute Board for decision in accordance with GCC Subclause 45.3. The Parties shall appoint a Dispute Board by the date stated in the SCC. The Dispute Board shall comprise, as stated in the SCC, either one or three suitably qualified persons (“the members”), each of whom shall be fluent in the language for communication defined in the Contract and shall be a professional experienced in the type of activities involved in the performance of the Contract and with the interpretation of contractual documents. If the number is not so stated and the Parties do not agree otherwise, the Dispute Board shall comprise three persons, one of whom shall serve as chairman. If the Parties have not jointly appointed the Dispute Board 21 days before the date stated in the SCC and the Dispute Board is to comprise three persons, each Party shall nominate one member for the approval of the other Party. The first two members shall recommend and the Parties shall agree upon the third member, who shall act as chairman. However, if a list of potential members is included in the SCC, the members shall be selected from those on the list, other than anyone who is unable or unwilling to accept appointment to the Dispute Board. The agreement between the Parties and either the sole member or each of the three members shall incorporate by reference the General Conditions of Dispute Board Agreement contained in the Appendix to these General Conditions, with such amendments as are agreed between them. The terms of the remuneration of either the sole member or each of the three members, including the remuneration of any expert whom the Dispute Board consults, shall be mutually agreed upon by the Parties when agreeing the terms of appointment of the member or such expert (as the case may be). Each Party shall be responsible for paying one-half of this remuneration. If a member declines to act or is unable to act as a result of death, disability, resignation or termination of appointment, a replacement shall be appointed in the same manner as the replaced person was required to have been nominated or agreed upon, as described in this Subclause. The appointment of any member may be terminated by mutual agreement of both Parties, but not by the Employer or the Contractor acting alone. Unless otherwise agreed by both Parties, the appointment of the Dispute Board (including each member) shall expire when the Operational Acceptance Certificate has been issued in accordance with GCC Clause 25.3. |
|  | ### 45.2 Failure to Agree Dispute Board If any of the following conditions apply, namely: - the Parties fail to agree upon the appointment of the sole member of the Dispute Board by the date stated in the first paragraph of GCC Subclause 45.1; - either Party fails to nominate a member (for approval by the other Party) of a Dispute Board of three persons by such date; - the Parties fail to agree upon the appointment of the third member (to act as chairman) of the Dispute Board by such date; or - the Parties fail to agree upon the appointment of a replacement person within 42 days after the date on which the sole member or one of the three members declines to act or is unable to act as a result of death, disability, resignation, or termination of appointment; then the appointing entity or official named in the SCC shall, upon the request of either or both of the Parties and after due consultation with both Parties, appoint this member of the Dispute Board. This appointment shall be final and conclusive. Each Party shall be responsible for paying one-half of the remuneration of the appointing entity or official. |
|  | ### 45.3 Obtaining Dispute Board’s Decision If a dispute (of any kind whatsoever) arises between the Parties in connection with the performance of the Contract, including any dispute as to any certificate, determination, instruction, opinion or valuation of the Project Manager, either Party may refer the dispute in writing to the Dispute Board for its decision, with copies to the other Party and the Project Manager. Such reference shall state that it is given under this Subclause. For a Dispute Board of three persons, the Dispute Board shall be deemed to have received such reference on the date when it is received by the chairman of the Dispute Board. Both Parties shall promptly make available to the Dispute Board all such additional information, further access to the Site, and appropriate facilities, as the Dispute Board may require for the purposes of making a decision on such dispute. The Dispute Board shall be deemed to be not acting as arbitrator(s). Within 84 days after receiving such reference, or within such other period as may be proposed by the Dispute Board and approved by both Parties, the Dispute Board shall give its decision, which shall be reasoned and shall state that it is given under this Subclause. The decision shall be binding on both Parties, who shall promptly give effect to it unless and until it shall be revised in an amicable settlement or an arbitral award as described below. Unless the Contract has already been abandoned, repudiated or terminated, the Contractor shall continue to proceed with the performance of the Facilities in accordance with the Contract. If either Party is dissatisfied with the Dispute Board’s decision, then either Party may, within 28 days after receiving the decision, give notice to the other Party of its dissatisfaction and intention to commence arbitration. If the Dispute Board fails to give its decision within the period of 84 days (or as otherwise approved) after receiving such reference, then either Party may, within 28 days after this period has expired, give notice to the other Party of its dissatisfaction and intention to commence arbitration. In either event, this notice of dissatisfaction shall state that it is given under this Subclause, and shall set out the matter in dispute and the reason(s) for dissatisfaction. Except as stated in GCC Subclauses 45.6 and 45.7, neither Party shall be entitled to commence arbitration of a dispute unless a notice of dissatisfaction has been given in accordance with this Subclause. If the Dispute Board has given its decision as to a matter in dispute to both Parties, and no notice of dissatisfaction has been given by either Party within 28 days after it received the Dispute Board’s decision, then the decision shall become final and binding upon both Parties. |
|  | ### 45.4 Amicable Settlement Where notice of dissatisfaction has been given under GCC Subclause 45.3 above, both Parties shall attempt to settle the dispute amicably before the commencement of arbitration. However, unless both Parties agree otherwise, arbitration may be commenced on or after the fifty-sixth day after the day on which notice of dissatisfaction and intention to commence arbitration was given, even if no attempt at amicable settlement has been made. |
|  | ### 45.5 Arbitration Unless settled amicably, any dispute in respect of which the Dispute Board’s decision (if any) has not become final and binding shall be finally settled by international arbitration. Unless otherwise agreed by both Parties, - (a) arbitration proceedings shall be conducted as stated in the Special Conditions; - (b) if no arbitration proceedings is so stated, the dispute shall be finally settled by institutional arbitration under the Rules of Arbitration of the International Chamber of Commerce; - (c) the dispute shall be settled by three arbitrators; and - (d) the arbitration shall be conducted in the language for communications defined in GCC Subclause 5.3. The arbitrator(s) shall have full power to open up, review and revise any certificate, determination, instruction, opinion or valuation of the Project Manager, and any decision of the Dispute Board, relevant to the dispute. Nothing shall disqualify the Project Manager from being called as a witness and giving evidence before the arbitrator(s) on any matter whatsoever relevant to the dispute. Neither Party shall be limited in the proceedings before the arbitrator(s) to the evidence or arguments previously put before the Dispute Board to obtain its decision, or to the reasons for dissatisfaction given in its notice of dissatisfaction. Any decision of the Dispute Board shall be admissible in evidence in the arbitration. Arbitration may be commenced prior to or after completion of the Works. The obligations of the Parties, the Project Manager and the Dispute Board shall not be altered by reason of any arbitration being conducted during the progress of the Works. |
|  | ### 45.6 Failure to Comply with Dispute Board’s Decision - In the event that a Party fails to comply with a Dispute Board decision which has become final and binding, then the other Party may, without prejudice to any other rights it may have, refer the failure itself to arbitration under GCC Subclause 45.5. GCC Subclauses 45.3 and 45.4 shall not apply to this reference. |
|  | ### 45.7 Expiry of Dispute Board’s Appointment If a dispute arises between the Parties in connection with the performance of the Contract, and there is no Dispute Board in place, whether by reason of the expiry of the Dispute Board’s appointment or otherwise, - (a) GCC Subclauses 45.3 and 45.4 shall not apply, and (b) the dispute may be referred directly to arbitration under GCC Subclause 45.5. |

# APPENDIX A

# General Conditions of Dispute Board Agreement

### 1	Definitions

Each “Dispute Board Agreement” is a tripartite agreement by and between

- the “Employer”;

- the “Contractor”; and

- the “Member” who is defined in the Dispute Board Agreement as being

(i)	the sole member of the "Dispute Board" and, where this is the case, all references to the “Other Members” do not apply; or

(ii)	one of the three persons who are jointly called the “Dispute Board” and, where this is the case, the other two persons are called the “Other Members”.

The Employer and the Contractor have entered (or intend to enter) into a contract, which is called the "Contract" and is defined in the Dispute Board Agreement, which incorporates this Appendix. In the Dispute Board Agreement, words and expressions which are not otherwise defined shall have the meanings assigned to them in the Contract.

### 2	General Provisions

Unless otherwise stated in the Dispute Board Agreement, it shall take effect on the latest of the following dates:

- (a)	the Commencement Date defined in the Contract;

- (b)	when the Employer, the Contractor and the Member have each signed the Dispute Board Agreement; or

- (c)	when the Employer, the Contractor and each of the Other Members (if any) have respectively each signed a dispute board agreement.

This employment of the Member is a personal appointment. At any time, the Member may give not less than 70 days’ notice of resignation to the Employer and to the Contractor, and the Dispute Board Agreement shall terminate upon the expiry of this period.

### 3	Warranties

The Member warrants and agrees that he/she is and shall be impartial and independent of the Employer, the Contractor and the Project Manager. The Member shall promptly disclose, to each of them and to the Other Members (if any), any fact or circumstance which might appear inconsistent with his/her warranty and agreement of impartiality and independence.

When appointing the Member, the Employer and the Contractor relied upon the Member’s representations that he/she is

- (a)	experienced in the work, which the Contractor is to carry out under the Contract,

- (b)	experienced in the interpretation of contract documentation, and

- (c)	fluent in the language for communications defined in the Contract.

### 4	General Obligations of the Member

The Member shall

- (a)	have no interest financial or otherwise in the Employer, the Contractor or the Project Manager, nor any financial interest in the Contract except for payment under the Dispute Board Agreement;

- (b)	not previously have been employed as a consultant or otherwise by the Employer, the Contractor, or the Project Manager, except in such circumstances as were disclosed in writing to the Employer and the Contractor before they signed the Dispute Board Agreement;

- (c)	have disclosed in writing to the Employer, the Contractor, and the Other Members (if any), before entering into the Dispute Board Agreement and to his/her best knowledge and recollection, any professional or personal relationships with any director, officer, or employee of the Employer, the Contractor, or the Project Manager, and any previous involvement in the overall project of which the Contract forms part;

- (d)	not, for the duration of the Dispute Board Agreement, be employed as a consultant or otherwise by the Employer, the Contractor, or the Project Manager, except as may be agreed in writing by the Employer, the Contractor, and the Other Members (if any);

- (e)	comply with the annexed procedural rules and with GCC Subclause 45.3;

- (f)	not give advice to the Employer, the Contractor, the Employer’s Personnel, or the Contractor’s Personnel concerning the conduct of the Contract, other than in accordance with the annexed procedural rules;

- (g)	not while a Member enter into discussions or make any agreement with the Employer, the Contractor, or the Project Manager regarding employment by any of them, whether as a consultant or otherwise, after ceasing to act under the Dispute Board Agreement;

- (h)	ensure his/her availability for all site visits and hearings as are necessary;

- (i)	become conversant with the Contract and with the progress of the Facilities (and of any other parts of the project of which the Contract forms part) by studying all documents received, which shall be maintained in a current working file;

- (j)	treat the details of the Contract and all the Dispute Board’s activities and hearings as private and confidential, and not publish or disclose them without the prior written consent of the Employer, the Contractor, and the Other Members (if any); and

- (k)	be available to give advice and opinions on any matter relevant to the Contract when requested by both the Employer and the Contractor, subject to the agreement of the Other Members (if any).

### 5	General Obligations of the Employer and the Contractor

The Employer, the Contractor, the Employer’s Personnel and the Contractor’s Personnel shall not request advice from or consultation with the Member regarding the Contract, otherwise than in the normal course of the Dispute Board’s activities under the Contract and the Dispute Board Agreement. The Employer and the Contractor shall be responsible for compliance with this provision, by the Employer’s Personnel and the Contractor’s Personnel respectively.

The Employer and the Contractor undertake to each other and to the Member that the Member shall not, except as otherwise agreed in writing by the Employer, the Contractor, the Member and the Other Members (if any)

- (a)	be appointed as an arbitrator in any arbitration under the Contract;

- (b)	be called as a witness to give evidence concerning any dispute before arbitrator(s) appointed for any arbitration under the Contract; or

- (c)	be liable for any claims for anything done or omitted in the discharge or purported discharge of the Member’s functions, unless the act or omission is shown to have been in bad faith.

The Employer and the Contractor hereby jointly and severally indemnify and hold the Member harmless against and from claims from which he is relieved from liability under the preceding paragraph.

Whenever the Employer or the Contractor refers a dispute to the Dispute Board under GCC Subclause 45.3, which will require the Member to make a site visit and attend a hearing, the Employer or the Contractor shall provide appropriate security for a sum equivalent to the reasonable expenses to be incurred by the Member. No account shall be taken of any other payments due or paid to the Member.

### 6	Payment

The Member shall be paid as follows, in the currency named in the Dispute Board Agreement:

- (a)	a retainer fee per calendar month, which shall be considered as payment in full for

(i)	being available on 28 days’ notice for all site visits and hearings;

(ii)	becoming and remaining conversant with all project developments and maintaining relevant files;

(iii)	all office and overhead expenses including secretarial services, photocopying and office supplies incurred in connection with his duties; and

(iv)	all services performed hereunder except those referred to in sub-paragraphs (b) and (c) of this Clause.

- The retainer fee shall be paid with effect from the last day of the calendar month in which the Dispute Board Agreement becomes effective; until the last day of the calendar month in which the Taking-Over Certificate is issued for the whole of the Works.

- With effect from the first day of the calendar month following the month in which Taking-Over Certificate is issued for the whole of the Works, the retainer fee shall be reduced by one-third. This reduced fee shall be paid until the first day of the calendar month in which the Member resigns or the Dispute Board Agreement is otherwise terminated.

- (b)	a daily fee, which shall be considered as payment in full for

(i)	each day or part of a day up to a maximum of 2 days’ travel time in each direction for the journey between the Member’s home and the site, or another location of a meeting with the Other Members (if any);

(ii)	each working day on site visits, hearings, or preparing decisions; and

(iii)	each day spent reading submissions in preparation for a hearing.

- (c)	all reasonable expenses, including necessary travel expenses (air fare in less than first class, hotel and subsistence and other direct travel expenses) incurred in connection with the Member’s duties, as well as the cost of telephone calls, courier charges, facsimiles, and telexes, and use of the internet: a receipt shall be required for each item in excess of 5%  of the daily fee referred to in sub-paragraph (b) of this Clause;

- (d)	any taxes properly levied in the Country on payments made to the Member (unless a national or permanent resident of the Country) under this Clause 6.

- The retainer and daily fees shall be as specified in the Dispute Board Agreement. Unless it specifies otherwise, these fees shall remain fixed for the first 24 calendar months, and shall thereafter be adjusted by agreement between the Employer, the Contractor and the Member, at each anniversary of the date on which the Dispute Board Agreement became effective.

- If the parties fail to agree on the retainer fee or the daily fee, the appointing entity or official named in the SCC shall determine the amount of the fees to be used.

- The Member shall submit invoices for payment of the monthly retainer and air fares quarterly in advance. Invoices for other expenses and for daily fees shall be submitted following the conclusion of a site visit or hearing. All invoices shall be accompanied by a brief description of activities performed during the relevant period and shall be addressed to the Contractor.

- The Contractor shall pay each of the Member’s invoices in full within 56 calendar days after receiving each invoice and shall apply to the Employer (in the Statements under the Contract) for reimbursement of one-half of the amounts of these invoices. The Employer shall then pay the Contractor in accordance with the Contract.

- If the Contractor fails to pay to the Member the amount to which he/she is entitled under the Dispute Board Agreement, the Employer shall pay the amount due to the Member and any other amount which may be required to maintain the operation of the Dispute Board; and without prejudice to the Employer’s rights or remedies. In addition to all other rights arising from this default, the Employer shall be entitled to reimbursement of all sums paid in excess of one-half of these payments, plus all costs of recovering these sums and financing charges calculated at the rate specified in accordance with GCC Subclause 12.3.

- If the Member does not receive payment of the amount due within 70 days after submitting a valid invoice, the Member may (i) suspend his/her services (without notice) until the payment is received, and/or (ii) resign his/her appointment by giving notice under Clause 7.

### 7	Termination

At any time: (i) the Employer and the Contractor may jointly terminate the Dispute Board Agreement by giving 42 days’ notice to the Member, or (ii) the Member may resign as provided for in Clause 2.

If the Member fails to comply with the Dispute Board Agreement, the Employer and the Contractor may, without prejudice to their other rights, terminate it by notice to the Member. The notice shall take effect when received by the Member.

If the Employer or the Contractor fails to comply with the Dispute Board Agreement, the Member may, without prejudice to his other rights, terminate it by notice to the Employer and the Contractor. The notice shall take effect when received by them both.

Any such notice, resignation and termination shall be final and binding on the Employer, the Contractor and the Member. However, a notice by the Employer or the Contractor, but not by both, shall be of no effect.

### 8	Default of the Member

If the Member fails to comply with any of his obligations under Clause 4 concerning his impartiality or independence in relation to the Employer or the Contractor, he/she shall not be entitled to any fees or expenses hereunder and shall, without prejudice to their other rights, reimburse each of the Employer and the Contractor for any fees and expenses received by the Member and the Other Members (if any), for proceedings or decisions (if any) of the Dispute Board which are rendered void or ineffective by the said failure to comply.

### 9	Disputes

- Any dispute or claim arising out of or in connection with this Dispute Board Agreement, or the breach, termination or invalidity thereof, shall be finally settled by institutional arbitration. If no other arbitration institute is agreed, the arbitration shall be conducted under the Rules of Arbitration of the International Chamber of Commerce by one arbitrator appointed in accordance with these Rules of Arbitration.

## Annex  - DISPUTE BOARD GUIDELINES

1. 	Unless otherwise agreed by the Employer and the Contractor, the Dispute Board shall visit the site at intervals of not more than 140 days, including times of critical construction events, at the request of either the Employer or the Contractor. Unless otherwise agreed by the Employer, the Contractor, and the Dispute Board, the period between consecutive visits shall not be less than 70 days, except as required to convene a hearing as described below.

2.	The timing of and agenda for each site visit shall be as agreed jointly by the Dispute Board, the Employer, and the Contractor, or in the absence of agreement, shall be decided by the Dispute Board. The purpose of site visits is to enable the Dispute Board to become and remain acquainted with the progress of the Works and of any actual or potential problems or claims, and, as far as reasonable, to prevent potential problems or claims from becoming disputes.

3.	Site visits shall be attended by the Employer, the Contractor, and the Project Manager and shall be coordinated by the Employer in cooperation with the Contractor. The Employer shall ensure the provision of appropriate conference facilities and secretarial and copying services. At the conclusion of each site visit and before leaving the site, the Dispute Board shall prepare a report on its activities during the visit and shall send copies to the Employer and the Contractor.

4.	The Employer and the Contractor shall furnish to the Dispute Board one copy of all documents which the Dispute Board may request, including Contract documents, progress reports, variation instructions, certificates, and other documents pertinent to the performance of the Contract. All communications between the Dispute Board and the Employer or the Contractor shall be copied to the other Party. If the Dispute Board comprises three persons, the Employer and the Contractor shall send copies of these requested documents and these communications to each of these persons.

5.	If any dispute is referred to the Dispute Board in accordance with GCC Subclause 45.3, the Dispute Board shall proceed in accordance with GCC Subclause 45.3 and these Guidelines. Subject to the time allowed to give notice of a decision and other relevant factors, the Dispute Board shall

- (a)	act fairly and impartially as between the Employer and the Contractor, giving each of them a reasonable opportunity of putting his case and responding to the other’s case; and

- (b)	adopt procedures suitable to the dispute, avoiding unnecessary delay or expense.

6.	The Dispute Board may conduct a hearing on the dispute, in which event it will decide on the date and place for the hearing and may request that written documentation and arguments from the Employer and the Contractor be presented to it prior to or at the hearing.

7.	Except as otherwise agreed in writing by the Employer and the Contractor, the Dispute Board shall have power to adopt an inquisitorial procedure, to refuse admission to hearings or audience at hearings to any persons other than representatives of the Employer, the Contractor, and the Project Manager, and to proceed in the absence of any party who the Dispute Board is satisfied received notice of the hearing; but shall have discretion to decide whether and to what extent this power may be exercised.

8.	The Employer and the Contractor empower the Dispute Board, among other things, to

- (a)	establish the procedure to be applied in deciding a dispute;

- (b)	decide upon the Dispute Board’s own jurisdiction, and as to the scope of any dispute referred to it;

- (c)	conduct any hearing as it thinks fit, not being bound by any rules or procedures other than those contained in the Contract and these Guidelines;

- (d)	take the initiative in ascertaining the facts and matters required for a decision;

- (e)	make use of its own specialist knowledge, if any;

- (f)	decide upon the payment of financing charges in accordance with the Contract;

- (g)	decide upon any provisional relief such as interim or conservatory measures;

- (h)	open up, review and revise any certificate, decision, determination, instruction, opinion or valuation of the Project Manager, relevant to the dispute; and

- (i)	appoint, should the Dispute Board so consider necessary and the Parties agree, a suitable expert at the cost of the Parties to give advice on a specific matter relevant to the dispute.

9.	The Dispute Board shall not express any opinions during any hearing concerning the merits of any arguments advanced by the Parties. Thereafter, the Dispute Board shall make and give its decision in accordance with GCC Subclause 45.3, or as otherwise agreed by the Employer and the Contractor in writing. If the Dispute Board comprises three persons

- (a)	it shall convene in private after a hearing, in order to have discussions and prepare its decision;

- (b)	it shall endeavour to reach a unanimous decision: if this proves impossible the applicable decision shall be made by a majority of the Members, who may require the minority Member to prepare a written report for submission to the Employer and the Contractor; and

- (c)	if a Member fails to attend a meeting or hearing, or to fulfil any required function, the other two Members may nevertheless proceed to make a decision, unless

(i)	either the Employer or the Contractor does not agree that they do so, or

(ii)	the absent Member is the chairman and he/she instructs the other Members to not make a decision.

Section 8 - Special Conditions of Contract

The following Special Conditions of Contract (SCC) shall supplement the General Conditions of Contract (GCC). Whenever there is a conflict, the provisions herein shall prevail over those in the GCC.  The clause number of the SCC is the corresponding clause number of the GCC.

Table of Clauses

1.	Definitions	8-2

5.	Law and Language	8-2

7.	Scope of Facilities	8-2

8.	Time for Commencement and Completion	8-2

11.	Contract Price	8-2

13. 	Securities	8-3

22	Installation	8-3

25.	Commissioning and Operational Acceptance	8-4

26.	Completion Time Guarantee	8-4

27.	Defect Liability	8-4

30.	Limitation of Liability	8-4

45.	Disputes and Arbitration	8-5

46.	Eligibility	8-5

| ### 1. Definitions |  |
| --- | --- |
|  | The Employer is: Ministry of Environment and Energy Republic of the Maldives The Project Manager is: To be inserted The Funding’s are: Abu Dhabi Fund for Development (ADFD) Country of Origin: According Section Eligibility list |
| ### 5. Law and Language |  |
|  | 5.1 The Contract shall be interpreted in accordance with the laws of: Maldives |
|  | 5.2 The ruling language is: English/Dhivehi |
|  | 5.3 The language for communications is: English |
| ### 7. Scope of Facilities |  |
|  | 7.3 The Contractor agrees to supply spare parts for a period of years: 2 years The Contractor shall carry sufficient inventories to ensure an ex-stock supply of consumable spares for the Plant. Other spare parts and components shall be supplied as promptly as possible, but at the most within 6 months of placing the order and opening the letter of credit. In addition, in the event of termination of the production of spare parts, advance notification will be made to the Employer of the pending termination, with sufficient time to permit the Employer to procure the needed requirement. Following such termination, the Contractor will furnish to the extent possible and at no cost to the Employer the blueprints, drawings and specifications of the spare parts, if requested. |
| ### 8. Time for Commencement and Completion |  |
|  | 8.1 The Contractor shall commence work on the Facilities within 14 days from the Effective Date for determining Time for Completion as specified in the Contract Agreement. |
|  | 8.2 The Time for Completion of the whole of the Facilities shall be 365days from the Effective Date as described in the Contract Agreement. Time for Completion for parts of the Facilities: 3 months for site clearance and concrete foundations and slabs |
| ### 11. Contract Price |  |
|  | 11.2 The Contract Price shall be adjusted in accordance with the provisions of Appendix 2 (Price Adjustment) to the Contract Agreement. |
| ### 13. Securities |  |
|  | 13.3.1 The amount of performance security, as a percentage of the Contract Price for the Facility or for the part of the Facility for which a separate Time for Completion is provided, shall be: 10% of the contract sum |
|  | 13.3.2 The performance security shall be in the form of the contract guarantee. as per form included in Section 9 (Contract Forms). |
|  | 13.3.3 The performance security shall not be reduced on the date of the Operational Acceptance. |
| ### 22. Installation |  |
|  | 22.2 Labor 22.2.5 Working Hours (a) Normal working hours are: from 8 am to 5 pm with 1 hr lunch break. |
| ### 25. Commissioning and Operational Acceptance |  |
|  | 25.2.2 The Guarantee Test of the Facilities shall be successfully completed within .14 days from the date of Completion. |
| ### 26. Completion Time Guarantee |  |
|  | 26.2 Applicable rate for liquidated damages: 0,5 % per week Maximum deduction for liquidated damages: 5% of contract price |
|  | 26.3 No bonus will be given for earlier Completion of the Facilities or part thereof. |
| ### 27. Defect Liability |  |
|  | 27.10 The critical components covered under the extended defect liability are - refractory line - steamboiler - steam engine and the period shall be 24,000 operating hours |
| ### 30. Limitation of Liability |  |
|  | 30.1 (b) The multiplier of the Contract Price is: _________________________________ |
| ### 45. Disputes and Arbitration |  |
|  | 45.1 The Dispute Board shall be appointed within 28 days after the Effective Date. The Dispute Board shall be a dispute board of 3 members List of potential Dispute Board members is: _________________________________ |
|  | 45.2 Appointment (if not agreed) to be made by: ___________________________________ |
|  | 45.5 Rules of procedure for arbitration proceedings: (a) Contracts with foreign contractors: International arbitration shall be conducted in accordance with the rules of the Singapore International Arbitration Centre (SIAC) shall apply. Arbitration shall be administered by SIAC The place of arbitration shall be the place of the institution administering the arbitration. (b) Contracts with contractors being nationals of the Employer’s country: Maldives |
| 46. | Eligibility |
|  | 46.1 The Contractor shall have the nationality of an ADFD member country. The Contractor shall be deemed to have the nationality of a country if the Contractor is a citizen or is constituted, incorporated, or registered, and operates in conformity with the provisions of the laws of that country. This criterion shall also apply to the determination of the nationality of proposed subcontractors or suppliers for any part of the Contract including related services. 46.2 The materials, equipment and services to be supplied under the Contract shall have their origin in eligible source countries and all expenditures under the Contract will be limited to such materials, equipment, and services. At the Employer’s request, the Contractor may be required to provide evidence of the origin of materials, equipment and services. 46.3 For purposes of SCC 46.2, “origin” means the place where the materials and equipment are mined, grown, produced or manufactured, and from which the services are provided. Materials and equipment are produced when, through manufacturing, processing, or substantial or major assembling of components, a commercially recognized product results that differs substantially in its basic characteristics or in purpose or utility from its components. |

Section 9 - Contract Forms

Table of Forms

Notification of Award	9-2

Contract Agreement	9-3

Appendix 1 -  Terms and Procedures of Payment	9-6

Appendix 2  -  Insurance Requirements	9-10

Appendix 3  -  Time Schedule	9-13

Appendix 4  -  List of Major Items of Plant and Services and List of Approved Subcontractors	9-14

Appendix 5  -  Scope of Works and Supply by the Employer	9-15

Appendix 6  -  List of Documents for Approval or Review	9-16

Appendix 7  -  Functional Guarantees	9-17

Performance Security 	9-19

Advance Payment Security 	9-21

# Notification of Award

[  Employer's letterhead  ]

Letter of Acceptance

[  date  ]

To:  [  Name and address of the contractor  ]

This is to notify you that your Bid dated [  date  ] for execution of the [  name of the contract and identification number, as given in the Bid Data Sheet  ] for the Contract Price in the aggregate of [  amounts in words and figures  ] [  name of currency  ], as corrected and modified in accordance with the Instructions to Bidders is hereby accepted by our Agency.

You are requested to furnish the Performance Security within 28 days in accordance with the Conditions of Contract, using for that purpose one of the Performance Security Forms included in Section 9 (Contract Forms) of the Bidding Document.

Authorized Signature:

Name and Title of Signatory:

Name of Agency:

Attachment:  Contract Agreement

# Contract Agreement

THIS AGREEMENT made on the [  insert number  ] day of [  insert month  ], [  insert year  ],

BETWEEN

(1) [  name of the employer  ], a corporation incorporated under the laws of [  country of the employer  ] and having its principal place of business at [  address of the employer  ] (hereinafter called “the Employer”), and (2) [  name of the contractor  ], a corporation incorporated under the laws of [  country of the contractor  ] and having its principal place of business at [  address of the contractor  ] (hereinafter called “the Contractor”).

WHEREAS the Employer desires to engage the Contractor to design, manufacture, test, deliver, install, complete and commission certain Facilities, viz. [  list of facilities  ] (“the Facilities”) and the Contractor have agreed to such engagement upon and subject to the terms and conditions hereinafter appearing.

NOW IT IS HEREBY AGREED as follows:

| Article 1 Contract Documents | 1.1 Contract Documents (Reference GCC Clause 2) The following documents shall constitute the Contract between the Employer and the Contractor, and each shall be read and construed as an integral part of the Contract: (a) This Contract Agreement and the Appendixes hereto (b) Letter of Bid and Price Schedules submitted by the Contractor (c) Special Conditions of Contract (d) List of Eligible Countries that was specified in Section 5 of the Bidding Document (e) General Conditions of Contract (f) Specifications (g) Drawings (h) Other completed Bidding Forms submitted with the Letter of Bid (i) Any other documents forming part of the Employer’s Requirements (j) Any other documents shall be added here 1.2 Order of Precedence (Reference GCC Clause 2) In the event of any ambiguity or conflict between the Contract Documents listed above, the order of precedence shall be the order in which the Contract Documents are listed in Article 1.1 (Contract Documents) above. 1.3 Definitions (Reference GCC Clause 1) Capitalized words and phrases used herein shall have the same meanings as are ascribed to them in the General Conditions. |
| --- | --- |

| Article 2 Contract Price and Terms of Payment | 2.1 Contract Price (Reference GCC Clause 11) The Employer hereby agrees to pay to the Contractor the Contract Price in consideration of the performance by the Contractor of its obligations hereunder. The Contract Price shall be the aggregate of [. . . amounts of foreign currency in words . . . ], [. . . amounts in figures. . . ] as specified in Price Schedule No. 5 (Grand Summary), [. . . amounts of local currency in words . . . ], [. . . amounts in figures. . . ], or such other sums as may be determined in accordance with the terms and conditions of the Contract. 2.2 Terms of Payment (Reference GCC Clause 12) The terms and procedures of payment according to which the Employer will reimburse the Contractor are given in the Appendix (Terms and Procedures of Payment) hereto. The Employer shall instruct its bank to issue an irrevocable confirmed documentary credit made available to the Contractor in a bank in the country of the Contractor. The credit shall be for an amount of [. . . amount equal to the total named in Schedule 1 less the advance payment to be made for plant and mandatory spare parts supplied from abroad. . . ]; and shall be subject to the Uniform Customs and Practice for Documentary Credits 1993 Revision, ICC Publication No. 500.2 In the event that the amount payable under Schedule No. 1 is adjusted in accordance with GCC 11.2 or with any of the other terms of the Contract, the Employer shall arrange for the documentary credit to be amended accordingly |
| --- | --- |
| Article 3 Effective Date | 3.1 Effective Date (Reference GCC Clause 1) The Effective Date upon which the period until the Time for Completion of the Facilities shall be counted from is the date when all of the following conditions have been fulfilled: (a) This Contract Agreement has been duly executed for and on behalf of the Employer and the Contractor. (b) The Contractor has submitted to the Employer the performance security and the advance payment guarantee. (c) The Employer has paid the Contractor the advance payment. (d) The Contractor has been advised that the documentary credit referred to in Article 2.2 above has been issued in its favor. Each party shall use its best efforts to fulfill the above conditions for which it is responsible as soon as practicable. 3.2 If the conditions listed under 3.1 are not fulfilled within 2 months from the date of this Contract notification because of reasons not attributable to the Contractor, the parties shall discuss and agree on an equitable adjustment to the Contract Price and the Time for Completion and/or other relevant conditions of the Contract. |
| _________________________________ 2 Or Uniform Customs and Practice for Documentary Credits 2007 Revision, ICC Publication No. 600 (or the latest version). |  |
| Article 4 Communications | 4.1 The address of the Employer for notice purposes, pursuant to GCC 4.1 is: [ Employer's address ]. 4.2 The address of the Contractor for notice purposes, pursuant to GCC 4.1 is: [ Contractor's address ]. |
| Article 5. Appendixes | 5.1 The Appendixes listed in the attached List of Appendixes shall be deemed to form an integral part of this Contract Agreement. 5.2 Reference in the Contract to any Appendix shall mean the Appendixes attached hereto, and the Contract shall be read and construed accordingly. |

IN WITNESS WHEREOF the Employer and the Contractor have caused this Agreement to be duly executed by their duly authorized representatives the day and year first above written.

Signed by, for and on behalf of the Employer

[  Signature  ]

[  Title  ]

in the presence of

[  Signature  ]

[  Title  ]

Signed by, for and on behalf of the Contractor

[  Signature  ]

[  Title  ]

in the presence of

[  Signature  ]

[  Title  ]

APPENDIXES

Appendix 1 -	Terms and Procedures of Payment

Appendix 2 -	Insurance Requirements

Appendix 3 -	Time Schedule

Appendix 4 -	List of Major Items of Plant and Services and List of Approved Subcontractors

Appendix 5 -	Scope of Works and Supply by the Employer

Appendix 6 -	List of Documents for Approval or Review

Appendix 7 -	Functional Guarantees

# Appendix 1  -  Terms and Procedures of Payment

In accordance with the provisions of GCC Clause 12 (Terms of Payment), the Employer shall pay the Contractor in the following manner and at the following times, based on the Price Breakdown given in the section on Price Schedules.  Payments will be made in the currencies quoted by the Bidder unless otherwise agreed between the parties.  Applications for payment in respect of part deliveries may be made by the Contractor as work proceeds.

(A)  Terms of Payment

Schedule No. 1 Plant and Mandatory Spare Parts Supplied from Abroad

In respect of plant and mandatory spare parts supplied from abroad, the following payments shall be made:

Ten percent (10%) of the total CIP amount as an advance payment against receipt of invoice and an irrevocable advance payment security for the equivalent amount made out in favor of the Employer.  The advance payment security may be reduced in proportion to the value of the plant and mandatory spare parts delivered to the site, as evidenced by delivery documents.

Eighty percent (80%) of the total or pro rata CIP or amount upon Incoterm “CIP,” upon delivery to the site within 45 days after receipt of invoice.

Five percent (5%) of the total or pro rata CIP or amount upon issue of the Completion Certificate, within 45 days after receipt of invoice.

Five percent (5%) of the total or pro rata CIP or amount upon issue of the Operational Acceptance Certificate, within 45 days after receipt of invoice.

Schedule No. 2 Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country

In respect of plant and mandatory spare parts supplied from within the Employer’s country, the following payments shall be made:

Ten percent (10%) of the total EXW amount as an advance payment against receipt of invoice, and an irrevocable advance payment security for the equivalent amount made out in favor of the Employer. The advance payment security may be reduced in proportion to the value of the plant and mandatory spare parts delivered to the site, as evidenced by delivery documents.

Eighty percent (80%) of the total or pro rata EXW amount upon Incoterm “Ex-Works,” upon delivery to the site within 45 days after receipt of invoice.

Five percent (5%) of the total or pro rata EXW amount upon issue of the Completion Certificate, within 45 days after receipt of invoice.

Five percent (5%) of the total or pro rata EXW amount upon issue of the Operational Acceptance Certificate, within 45 days after receipt of invoice.

Schedule No. 3 Design Services

In respect of design services for both the foreign currency and the local currency portions, the following payments shall be made:

Ten percent (10%) of the total design services amount as an advance payment against receipt of invoice and an irrevocable advance payment security for the equivalent amount made out in favor of the Employer.

Ninety percent (90%) of the total or pro rata design services amount upon acceptance of design by the Project Manager within 45 days after receipt of invoice.

Schedule No. 4 Installation and Other Services

In respect of installation services for both the foreign and local currency portions, the following payments shall be made:

Ten percent (10%) of the total installation and other services amount as an advance payment against receipt of invoice and an irrevocable advance payment security for the equivalent amount made out in favor of the Employer.  The advance payment security may be reduced in proportion to the value of work performed by the Contractor as evidenced by the invoices for installation services.

Eighty percent (80%) of the measured value of work performed by the Contractor, as identified in the said Program of Performance, during the preceding month, as evidenced by the Employer’s authorization of the Contractor’s application, will be made monthly within 45 days after receipt of invoice.

Five percent (5%) of the total or pro rata value of installation services performed by the Contractor as evidenced by the Employer’s authorization of the Contractor’s monthly applications, upon issue of the Completion Certificate, within 45 days after receipt of invoice.

Five percent (5%) of the total or pro rata value of installation services performed by the Contractor as evidenced by the Employer’s authorization of the Contractor’s monthly applications, upon issue of the Operational Acceptance Certificate, within 45 days after receipt of invoice.

Schedule No. 5 Service contract

The service contract should be concluded for a two year maintenance and control service including the sending of adequate and qualified personnel for periodical review and maintenance including travel days, transport of specific equipment etc. Payment should be made against invoice with documentation proof (tickets, reimbursable, per diem, etc..)

(B)  Payment Procedures

When applying for certification and making payments, the procedures shall be as follows:

- Payment against monthly statement according to the terms of payment with deduction of the advance payment in pro-rata

- Additional services according separate service contract (the bidder should provide a suggestion or a sample of a service contract

# Appendix 2  -  Insurance Requirements

(A)  Types of Insurance to Be Taken Out by the Contractor

In accordance with the provisions of GCC Clause 34, the Contractor shall at its expense take out and maintain in effect, or cause to be taken out and maintained in effect, during the performance of the Contract, the types of insurance set forth below in the sums and with the deductibles and other conditions specified.  The identity of the insurers and the form of the policies shall be subject to the approval of the Employer, such approval not to be unreasonably withheld.

(a)  Cargo Insurance

Covering loss or damage occurring, while in transit from the supplier’s or manufacturer’s works or stores until arrival at the Site, to the Facilities (including spare parts therefore) and to the construction equipment to be provided by the Contractor or its Subcontractors.

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| [in currency(ies)] | [in currency(ies)] | [names] | [place] | [place] |

(b)  Installation All Risks Insurance

Covering physical loss or damage to the Facilities at the Site, occurring prior to completion of the Facilities, with an extended maintenance coverage for the Contractor’s liability in respect of any loss or damage occurring during the defect liability period while the Contractor is on the Site for the purpose of performing its obligations during the defect liability period.

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| [in currency(ies)] | [in currency(ies)] | [names] | [place] | [place] |

(c)  Third Party Liability Insurance

Covering bodily injury or death suffered by third parties (including the Employer’s personnel) and loss of or damage to property (including the Employer’s property and any parts of the Facilities that have been accepted by the Employer) occurring in connection with the supply and installation of the Facilities.

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| [in currency(ies)] | [in currency(ies)] | [names] | [place] | [place] |

(d)  Automobile Liability Insurance

Covering use of all vehicles used by the Contractor or its Subcontractors (whether owned by them or not) in connection with the supply and installation of the Facilities.  Comprehensive insurance in accordance with statutory requirements.

(e)  Workers’ Compensation

In accordance with the statutory requirements applicable in any country where the Facilities or any part thereof is executed.

(f)  Employer’s Liability

In accordance with the statutory requirements applicable in any country where the Facilities or any part thereof is executed.

(g) Other Insurance

The Contractor is also required to take out and maintain at its own cost the following types of insurance:

Details:

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| [in currency(ies)] | [in currency(ies)] | [names] | [place] | [place] |

The Employer shall be named as co-insured under all insurance policies taken out by the Contractor pursuant to GCC Subclause 34.1, except for the Third Party Liability, Workers’ Compensation, and Employer’s Liability Insurance, and the Contractor’s Subcontractors shall be named as co-insureds under all insurance policies taken out by the Contractor pursuant to GCC Subclause 34.1, except for the Cargo, Workers’ Compensation and Employer’s Liability Insurance. All insurer’s rights of subrogation against such co-insureds for losses or claims arising out of the performance of the Contract shall be waived under such policies.

(B)  Types of Insurance to Be Taken Out by the Employer

The Employer shall at its expense take out and maintain in effect during the performance of the Contract the following insurance policies.

Details:

| Amount | Deductible limits | Parties insured | From | To |
| --- | --- | --- | --- | --- |
| [in currency(ies)] | [in currency(ies)] | [names] | [place] | [place] |

# Appendix 3  -  Time Schedule

# Appendix 4  -  List of Major Items of Plant and Services and List of Approved Subcontractors

A list of major items of plant and services is provided below.

The following Subcontractors and Manufacturers are approved for carrying out the item of the facilities indicated.  Where more than one Subcontractor is listed, the Contractor is free to choose between them, but it must notify the Employer of its choice in good time prior to appointing any selected Subcontractor.  In accordance with GCC Subclause 19.1, the Contractor is free to submit proposals for Subcontractors for additional items from time to time.  No Subcontracts shall be placed with any such Subcontractors for additional items until the Subcontractors have been approved in writing by the Employer and their names have been added to this list of Approved Subcontractors.

| Major Items of Plant and Services | Approved Subcontractors and Manufacturers | Nationality |
| --- | --- | --- |

# Appendix 5  -  Scope of Works and Supply by the Employer

The following personnel, facilities, works, and supplies will be provided or supplied by the Employer, and the provisions of GCC Clauses 10, 21, and 24 shall apply as appropriate.

All personnel, facilities, works, and supplies will be provided by the Employer in good time so as not to delay the performance of the Contractor, in accordance with the approved Time Schedule and Program of Performance pursuant to GCC Subclause 18.2.

Unless otherwise indicated, all personnel, facilities, works, and supplies will be provided free of charge to the Contractor.

| Personnel | Charge to Contractor (if any) |
| --- | --- |

| Facilities | Charge to Contractor (if any) |
| --- | --- |

| Works | Charge to Contractor (if any) |
| --- | --- |

| Supplies | Charge to Contractor (if any) |
| --- | --- |

# Appendix 6  -  List of Documents for Approval or Review

Pursuant to GCC Subclause 20.3.1, the Contractor shall prepare, or cause its Subcontractor to prepare, and present to the Project Manager in accordance with the requirements of GCC Subclause 18.2 (Program of Performance), the following documents for

(A)  Approval

1.

2.

3.

(B)  Review

1.

2.

3.

# Appendix 7  -  Functional Guarantees

1.	General

This Appendix sets out

(a)	the functional guarantees referred to in GCC Clause 28 (Functional Guarantees)

(b)	the preconditions to the validity of the functional guarantees, either in production and/or consumption, set forth below

(c)	the minimum level of the functional guarantees

(d)	the formula for calculating liquidated damages for failure to attain the functional guarantees.

2.	Preconditions

The Contractor gives the functional guarantees (specified herein) for the facilities, subject to the following preconditions being fully satisfied:

3.	Functional Guarantees

Subject to compliance with the foregoing preconditions, the Contractor guarantees as follows:

3.1	Production Capacity

3.2	Raw Materials and Utilities Consumption

4.	Failure in Guarantees and Liquidated Damages

4.1	Failure to Attain Guaranteed Production Capacity

If the production capacity of the facilities attained in the guarantee test, pursuant to GCC Subclause 25.2, is less than the guaranteed figure specified in para. 3.1 above, but the actual production capacity attained in the guarantee test is not less than the minimum level specified in para. 4.3 below, and the Contractor elects to pay liquidated damages to the Employer in lieu of making changes, modifications and/or additions to the Facilities, pursuant to GCC Subclause 28.3, then the Contractor shall pay liquidated damages at the rate of . . . . . . . .for every complete 1% of the deficiency in the production capacity of the Facilities, or at a proportionately reduced rate for any deficiency, or part thereof, of less than a complete 1%.

4.2	Raw Materials and Utilities Consumption in Excess of Guaranteed Level

If the actual measured figure of specified raw materials and utilities consumed per unit (or their average total cost of consumption) exceeds the guaranteed figure specified in para. 3.2 above (or their specified average total cost of consumption), but the actual consumption attained in the guarantee test, pursuant to GCC Subclause 25.2, is not more than the maximum level specified in para. 4.3 below, and the Contractor elects to pay liquidated damages to the Employer in lieu of making changes, modifications and/or additions to the Facilities pursuant to GCC Subclause 28.3, then the Contractor shall pay liquidated damages at the rate of . . . . . . . . for every complete 1% of the excess consumption of the Facilities, or part thereof, of less than a complete 1%.

4.3	Minimum Levels

Notwithstanding the provisions of this paragraph, if as a result of the guarantee test(s), the following minimum levels of performance guarantees (and consumption guarantees) are not attained by the Contractor, the Contractor shall at its own cost make good any deficiencies until the Facilities reach any of such minimum performance levels, pursuant to GCC Subclause 28.2:

(a)	production capacity of the Facilities attained in the guarantee test:  95% of the guaranteed production capacity

and/or

(b)	average total cost of consumption of all the raw materials and utilities of the Facilities:  105% of the guaranteed figures.

4.4	Limitation of Liability

Subject to para. 4.3 above, the Contractor’s aggregate liability to pay liquidated damages for failure to attain the functional guarantees shall not exceed . . . percent ( . . .  %) of the Contract price

- Performance Security

Bankʼs name, and address of issuing branch or office

Beneficiary: 	Name and address of the employer

Date:

Performance Guarantee No.:

We have been informed that . . . . . name of the contractor. . . . . (hereinafter called “the Contractor”) has entered into Contract No. . . . . . reference number of the contract. . . . . dated . . . . . . . .with you, for the execution of . . . . . . name of contract and brief description of plant and services. . . . . (hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, a performance guarantee is required.

At the request of the Contractor, we . . . . . name of the bank. . . . . hereby irrevocably undertake to pay you any sum or sums not exceeding in total an amount of . . . . . name of the currency and amount in words. . . . . . (. . . . . amount in figures. . . . . ) such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of your first demand in writing accompanied by a written statement stating that the Contractor is in breach of its obligation(s) under the Contract, without your needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire no later than the earlier of

(a)	18 months after our receipt of

(i) 	a copy of the Completion Certificate; or

(ii) 	a registered letter from the Contractor, attaching a copy of the notice to the project manager that the Facilities are ready for commissioning, and stating that 14 days have elapsed from receipt of such notice (or 7 days have elapsed if the notice was a repeated notice) and the project manager has failed to issue a Completion Certificate or inform the Contractor in writing of any defects or deficiencies; or

(iii) 	a registered letter from the Contractor stating that no Completion Certificate has been issued but the Employer is making use of the Facilities; or

(b) 	the ____ day of _____, 2___.

Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees, ICC Publication No. 458 (or ICC Publication No. 758 as applicable), except that subparagraph (ii) of Sub-Article 20(a) is hereby excluded.

. . . . . . . . . . . . . . . . . . . . . . . . . . . . 
Signature(s) and seal of bank (where appropriate)

-- Note to Bidder --

If the institution issuing the performance security is located outside the country of the employer, it shall have a correspondent financial institution located in the country of the employer to make it enforceable.

Advance Payment Security

Bankʼs name, and address of issuing branch or office

Beneficiary: 	Name and address of the employer

Date:

Advance Payment Guarantee No.:

We have been informed that . . . . . name of the contractor. . . . . (hereinafter called "the Contractor") has entered into Contract No. . . . . . reference number of the contract. . . . . dated . . . . . . . .with you, for the execution of . . . . . . name of contract and brief description of plant and services. . . . . (hereinafter called "the Contract").

Furthermore, we understand that, according to the Conditions of the Contract, an advance payment in the sum . . . . . name of the currency and amount in words. . . . . . (. . . . . amount in figures. . . . . ) is to be made against an advance payment guarantee.

At the request of the Contractor, we . . . . . name of the bank. . . . . hereby irrevocably undertake to pay you any sum or sums not exceeding in total an amount of . . . . . name of the currency and amount in words. . . . . . (. . . . . amount in figures. . . . . ) upon receipt by us of your first demand in writing accompanied by a written statement stating that the Contractor is in breach of its obligation under the Contract because the Contractor used the advance payment for purposes other than the costs of mobilization in respect of the Works.

It is a condition for any claim and payment under this guarantee to be made that the advance payment referred to above must have been received by the Contractor on its account number . . . . . contractorʼs account number. . . . . at . . . . . name and address of the bank. . . . . .

The maximum amount of this guarantee shall be progressively reduced by the amount of the advance payment repaid by the Contractor as indicated in copies of interim statements or payment certificates, which shall be presented to us. This guarantee shall expire, at the latest, upon our receipt of a copy of the interim payment certificate, indicating that 80% of the Contract Price has been certified for payment, or on the . . . day of . . . . . . , . . . . ,  whichever is earlier. Consequently, any demand for payment under this guarantee must be received by us at this office on or before that date.

This guarantee is subject to the Uniform Rules for Demand Guarantees, ICC Publication No. 458 (or ICC Publication No. 758 as applicable).

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 
Signature(s) and seal of bank (where appropriate)

-- Note to Bidder --

If the institution issuing the advance payment security is located outside the country of the employer, it shall have a correspondent financial institution located in the country of the employer to make it enforceable.

ANNEX 1 – WITHDRAWAL PROCEDURE

ANNEX 2A – BILL OF QUANTITIES FOR ELECTRICAL GRID CONNECTION

| Item | Description | Qty | Unit | Rate USD | Amount USD |
| --- | --- | --- | --- | --- | --- |
| 1 Supply & installation of Synchronizing panel including below switchgear & |  | 1 | Item |  |  |
|  | accessories in powder coated, metal, free standing enclosure (Form 3b) with |  |  |  |  |
|  | necessary internal wiring |  |  |  |  |
|  | 01 no. 1600Amp 4P 70kA adjustable motorized ACB complete with shunt, UVT |  |  |  |  |
|  | and auxiliary For G1 (Diesel Generator 01) |  |  |  |  |
|  | 01 no. 630Amp 4P 36kA adjustable motorized MCCB complete with shunt, UVT |  |  |  |  |
|  | and auxiliary For G2 (Diesel Generator 02) |  |  |  |  |
|  | 01 no. 3200Amp 4P 70kA adjustable motorized ACB complete with shunt, UVT |  |  |  |  |
|  | and auxiliary For G3 W2E Turbine |  |  |  |  |
|  | 01 no. 3200Amp 4P 70kA adjustable ACB complete with shunt, UVT |  |  |  |  |
|  | For 1000kW Load (outgoing feeder for step up TF) |  |  |  |  |
|  | 01 no. 1250Amp 4P 70kA adjustable MCCB complete with shunt, UVT |  |  |  |  |
|  | For 600kW Load |  |  |  |  |
|  | 01 no. 125Amp 4P 25kA adjustable MCCB complete with shunt, UVT |  |  |  |  |
|  | For 60kW Load |  |  |  |  |
|  | 01 no. 250Amp 4P 36kA adjustable MCCB complete with shunt, UVT |  |  |  |  |
|  | For 100kW Load |  |  |  |  |
|  | 01 no. 63Amp 4P 18kA adjustable MCCB complete with shunt, UVT |  |  |  |  |
|  | For 25kW Load |  |  |  |  |
|  | 01 no. 250Amp 4P 36kA adjustable MCCB complete with shunt, UVT |  |  |  |  |
|  | For Spare 1 - 100kW Load |  |  |  |  |
|  | 01 no. 125Amp 4P 25kA adjustable MCCB complete with shunt, UVT |  |  |  |  |
|  | For Spare 2 - 60kW Load |  |  |  |  |
|  | 01 no. 63Amp 4P 18kA adjustable MCCB complete with shunt, UVT |  |  |  |  |
|  | For Spare 3 - 25kW Load |  |  |  |  |
|  | 11 nos. Earth Fault Relays |  |  |  |  |
|  | 11 nos. Phase Failure Relay |  |  |  |  |
|  | 11 nos. Digital Power Analyzer |  |  |  |  |
|  | 11 nos. Over Current Relay |  |  |  |  |
|  | 04 nos. Hour meter |  |  |  |  |
|  | 04 nos. Power factory meter |  |  |  |  |
|  | 04 nos. Frequency meter |  |  |  |  |
|  | 04 nos. Synchronizing and load sharing module Deep Sea 8810 |  |  |  |  |
|  | 04 nos. RPM meter |  |  |  |  |
|  | 12 nos. Digital ammeters AC |  |  |  |  |
|  | 12 nos. Digital voltmeters AC |  |  |  |  |
|  | 04 nos. Analogue ammeter DC |  |  |  |  |
|  | 04 nos. Analogue voltmeter DC |  |  |  |  |
|  | 03 nos. KRAL flow meter |  |  |  |  |
|  | 04 nos. CT type analogue kW meter |  |  |  |  |
|  | 04 nos. CT type analogue kWh meter |  |  |  |  |
|  | 04 nos. Emergency push button |  |  |  |  |
|  | 1 lot.. LED indicators |  |  |  |  |
|  | 01 lot. AC current transformers |  |  |  |  |
|  | 01 lot. DC current transformers |  |  |  |  |
|  | 04 nos. 100kA TPN surge arrestors with 125A HRC fuses |  |  |  |  |
|  | 01 lot. 150mmx12.5mm TPN+E tinned copper bus bar for main chamber |  |  |  |  |
|  | 01 lot. Suitable sizes of TPN tinned copper bus bar for outgoing feeders |  |  |  |  |

- Programming of Deep Sea units, testing & commissioning of complete panel (Sync & distribution)

| 2 | Supply, lay & connect feeder cable from Sync. panel to G1 using | 36 | Mts |  |  |
| --- | --- | --- | --- | --- | --- |
|  | with 4x4C 240sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  |  |  |
|  | cable trench. |  |  |  |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 3 | Supply, lay & connect feeder cable from Sync. panel to G2 using | 36 | Mts |  |  |
|  | with 2x4C 240sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  |  |  |
|  | cable trench. |  |  |  |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 4 | Supply, lay & connect feeder cable from Sync. Panel to G3 turbine | 66 | Mts |  |  |
|  | using with 7x4C 300sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  |  |  |
|  | cable trench. |  |  |  |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 5 | Supply, lay & connect feeder cable from Sync. Panel to 1500kW feeder | 70 | Mts |  |  |
|  | (step up TF) using with 7x4C 300sq.mm CU/XLPE/SWA/PVC + 25mmx3mm |  |  |  |  |
|  | copper tape in cable trench. |  |  |  |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 6 | Supply, lay & connect feeder cable from Sync. Panel to 600kW feeder | 0 | Mts | Length to be |  |
|  | using with 3x4C 240sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  | finalized in |  |
|  | cable trench. |  |  | Future but please mentioned the rate per meter |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 7 | Supply, lay & connect feeder cable from Sync. Panel to 60kW feeder | 0 | Mts | Length to be |  |
|  | using with 4C 50sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  | finalised in |  |
|  | cable trench. |  |  | Future but please mentioned the rate per meter |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 8 | Supply, lay & connect feeder cable from Sync.panel to 100kW feeder | 0 | Mts | Length to be |  |
|  | using with 4C 120sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  | finalised in |  |
|  | cable trench. |  |  | Future but please mentioned the rate per meter |  |
|  | Rate includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 9 | Supply, lay & connect feeder cable from Sync.panel to 25kW feeder | 0 | Mts | Length to be |  |
|  | using with 4C 25sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  | finalised in |  |
|  | cable trench. |  |  | Future but please mentioned the rate per meter |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 10 | Supply, lay & connect feeder cable from Sync.panel to Spare Feeder 1 - 100kW | 0 | Mts | Length to be |  |
|  | using with 4C 120sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  | finalised in |  |
|  | cable trench. |  |  | Future but please mentioned the rate per meter |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 11 | Supply, lay & connect feeder cable from Sync.panel to Spare Feeder 2 - 60kW | 0 | Mts | Length to be |  |
|  | using with 4C 50sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  | finalised in |  |
|  | cable trench. |  |  | Future but please mentioned the rate per meter |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 12 | Supply, lay & connect feeder cable from Sync.panel to Spare Feeder 3 - 25kW | 0 | Mts | Length to be |  |
|  | using with 4C 25sq.mm CU/XLPE/SWA/PVC + 25mmx3mm copper tape in |  |  | finalised in |  |
|  | cable trench. |  |  | Future but please mentioned the rate per meter |  |
|  | Rate should includes charges for excavation, backfilling, laying of sand bed, concrete |  |  |  |  |
|  | tiles, warning tapes, lugs, gland, vynil end caps, nut & bolts, ties, crimping etc. |  |  |  |  |
| 13 | Supply, lay & connect control cables from Sync. panel to G1, G2, G3 and 1500kW | 1 | Lot |  |  |
|  | Load feeder using with 3C 1.5sq.mm CU/PVC/SWA/PVC in cable trench. |  |  |  |  |
| 14 | Supply & installation of earth electrode 16mmDx3000mmL solid copper rods | 2 | No. |  |  |
|  | in radial arrangement (as per the recommended procedure) and connecting |  |  |  |  |
|  | same to Synchronising panel & step up transformer using 25mmx3mmT |  |  |  |  |
|  | copper tape. Earth resisitance should be below 5 Ohms as per the IEE regulation |  |  |  |  |
| 15 | Supply & installation of 2000kVA, 0.415kV to 11kV, Dyn11, dry type, cast resin, | 1 | Item |  |  |
|  | indoor, step up transformer with Al/Al winding with off load tap changers and |  |  |  |  |
|  | factory fitted IP21 enclosure |  |  |  |  |
| 16 | Supply & installation of 11kV, 630Amp, 21kA for 3 seconds, indoor type, | 1 | Item |  |  |
|  | motorised operated, extensible Ring Main Unit with over current / earth fault. |  |  |  |  |
|  | Type : two motorised vaccum circuit breakers feeders |  |  |  |  |
| 17 | End termination & commissioning of step up Transformer & Ring mains unit | 1 | Item |  |  |

ANNEX 2B – PROCESS FLOOR DIAGRAM FOR ADDU 50TPD W2E 1MW NET POWER PLANT

ANNEX 2C – 50TPD ELECTRICAL SYNC PANEL DESIGN

Whether as a Contractor, Subcontractor, Consultant, Manufacturer or Supplier, or Service Provider; or in any other capacity (different names are used depending on the particular Bidding Document).

Use one of the two options as appropriate.

If none has been paid or is to be paid, indicate “None.”

All italicized text is for use in preparing this form and shall be deleted from the final document.

Or 758 as applicable.

Whether as a Contractor, Subcontractor, Consultant, Manufacturer or Supplier, or Service Provider; or in any other capacity (different names are used depending on the particular Bidding Document).

Tables of Adjustment Data may be added if the contract provides for price adjustment (see GCC 11).

All italicized text is for guidance on how to prepare this demand guarantee and shall be deleted from the final document.

The guarantor shall insert an amount representing the percentage of the contract price specified in the contract and denominated either in the currency(ies) of the contract or a freely convertible currency acceptable to the employer.

Or the same or similar to this clause specified in the Uniform Rules for Demand Guarantees, ICC Publication No. 758, where applicable.

All italicized text serves as a guide for preparing this demand guarantee and shall be deleted from the final document.

The guarantor shall insert an amount representing the amount of the advance payment denominated either in the currency(ies) of the advance payment as specified in the contract, or in a freely convertible currency acceptable to the employer.

Footnote 2.

Insert the expected expiration date of the time for completion. The employer should note that in the event of an extension of the time for completion of the contract, the employer would need to request an extension of this guarantee from the guarantor. Such request must be in writing and must be made prior to the expiration date established in the guarantee. In preparing this guarantee, the employer might consider adding the following text to the form, at the end of the penultimate paragraph: “The Guarantor agrees to a one-time extension of this guarantee for a period not to exceed [6 months][1 year], in response to the Employer’s written request for such extension, such request to be presented to the Guarantor before the expiry of the guarantee.”