## Project CoverSheet
BILL OF QUANTITIES
SEWERAGE SYSTEM IN GDH.MADAVELI
CLIENT : MINISTRY OF ENVIRONMENT AND ENERGY

## main summary
SUMMARY OF BILLS OF QUANTITIES
MADAVELI SEWERAGE SYSTEM
| DESCRIPTION | AMOUNT (MRF)
| Bill №: 01 - GENERAL BOQ | 0
| Bill №: 02 - SEWERAGE SYSTEM | 0
| TOTAL AMOUNT | 0

## Preamble
MADAVELI SEWERAGE SYSTEM
Preamble Notes
1 | General Notes
1.1 | The Bill of Quantities shall be read in conjunction with the Instruction to Bidders, General Conditions of Contract, Appendix to bid, Technical Specification and Tender Drawings.
1.2 | List of Materials to be supplied by employer is stated in 03-Material list. Only these materials will be supplied by employer and bidders should provide any other materials required in Addissions and omissions bill of Material list. Rates for any other materials required ( which are not specified in addisions or omissions) should be included in the labor rates.
1.3 | The bidders shall provide the quanitites and price/rates for the materials listed in 03-Material list based on the BOQ and Drawings. Employer will provide the materials based on these quantites and bidder shall be responsible for any shortage of materials.
1.4 | The rates and prices tendered in the priced Bill of Quantities shall, except in so far as it is otherwise provided under the Contract, include all constructional plant, labour, supervision, materials, transportation, installation/erection, profit, together with all general risks, liabilities and obligations set out or implied in the bidding document.
1.5 | The rates and prices shall be quoted entirely in Maldivian Rufiyaa.
1.6 | A rate or price shall be entered against each item in the Bill of Quantities, whether quantities are stated or not. The cost of items against which the Contractor has failed to enter a rate or price shall be deemed to be covered by other rates and prices entered in the Bill of Quantities and no separate payment shall be made for such un-priced items.
1.7 | The whole cost of complying with the provisions of the Contract shall be included in the items provided in the priced Bill of Quantities, and where no items are provided but required for completion of contract works, the cost shall be deemed to be distributed among the rates and prices entered for the related item of work.
1.8 | General directions and descriptions of work and materials are not necessarily repeated or summarized in the Bill of Quantities. The Bidder shall refer to relevant sections of the Contract Document to fully understand the item requirements before entering rates or prices against each item in the Bill of Quantities.

## 01 general BoQ
MADAVELI SEWERAGE SYSTEM
01 GENERAL WORKS
BILL OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BILL NO. 01 - GENERAL AND PRELIMINARIES
1.1.00 | Project Management cost
1.1.01 | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings & similar. | 1 | Item |  | 0
1.2.00 | Contractual Requirements
1.2.01 | Provide & Maintain all necessary Insurances, Guarantees and Securities. | 1 | Item |  | 0
1.3.00 | Specified Requirements
1.3.01 | Provision and Erection of Notice Boards 3m x 4m size as per drawing and specification, including complete cost and conveyanceof materials, labour charges, & etc. | 1 | Item |  | 0
1.3.02 | Provision of photographs of important activities of the work during the progress of work as directed by the Engineer. | 1 | Item |  | 0
1.3.03 | Provision of videograph of the progress of works, one video tape not more than 30 minutes duration showing the progress during evey month. | 1 | Item |  | 0
1.3.04 | Submission of shop drawings for approval by the Engineer prior to commencement of work | 1 | Item |  | 0
1.3.05 | Detailed survey of each plot and prepare site layout and identify household catchpit and obtain Homeowner & Contractor agreement for each house | 1 | Item |  | 0
1.3.06 | Provision and maintaining of adequately equipped Laboratory services as required for site control on the quality of materials and the works as required by the engineer; | 1 | Item |  | 0
1.3.07 | Survey of the area of sea outfall | 1 | Item |  | 0
1.3.08 | Preperation of the electrical drawings and obtaining approval from MEA | 1 | Item |  | 0
1.4.00 | Temporary Works
1.4.01 | Provision of Temporary storage facilites for plant, Equipment and materials | 1 | Item |  | 0
1.5.00 | Dewatering
1.5.01 | Dewatering as required as per EPA regulation 2013/R-1697 | 1 | Item |  | 0
1.4.00 | TOTAL OF BILL №: 01 - Carried Over To Summary |  |  |  | 0
BILL NO. 02 - SITE PREPARATION
2.1.00 | Clearing grass, bushes, shrubs, saplings, uprooting rank vegetation all along the pipeline route and removal & disposal of rubbish to approved tips anywhere in the island as directed by the Engineer-in-charge | 1 | Item |  | 0
2.2.00 | Cutting of trees, including trunks, branching and removal of stumps, roots, stacking of serviceable materials with all lifts and up to all lead within project area and earthfilling in the depression/pit, including excavation & backfilling
2.2.01 | Girth size up to 300mm | 1 | item |  | 0
2.2.02 | Girth size from 300mm to 600mm | 1 | item |  | 0
2.2.03 | Girth size from 600mm to above | 1 | item |  | 0
2.3.00 | Dismantling of existig structures like pillars, walls, slabs and any other structure constructed of Brick or coral stone masonry, cement concrete, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material | 1 | item |  | 0
2.5.0 | TOTAL OF BILL №: 02 - Carried Over To Summary |  |  |  | 0
BILL NO. 03 - DECOMISSIONING
3.1.00 | Decomissioning of existing septic tanks and small bore gravity sewers upon completion and testing and comissioning of new system. Rates shall include for removal of all the existing sludge from the septic tanks and soak wells using proper equiment such as sucker truck; and transfer the contents to STP/Location specified by Engineer. Once all the content has been thoroughly removed the septic tanks should be backfilled with adequate material and compacted | 1 | item |  | 0
3.2.00 | TOTAL OF BILL №: 03 - Carried Over To Summary |  |  |  | 0
BILL NO. 04 - OPERATIONAL COST
4.1.00 | Operational cost for a period of one year for Sewerage systems | 12 | months |  | 0
4.2.00 | TOTAL OF BILL №: 04 - Carried Over To Summary |  |  |  | 0
BILL NO. 05 - SUMMARY ,GENERAL BOQ
5.1.01 | BILL NO. 01 - GENERAL AND PRELIMINARIES |  |  |  | 0
5.1.02 | BILL NO. 02 - SITE PREPARATION |  |  |  | 0
5.1.03 | BILL NO. 03 - DECOMISSIONING |  |  |  | 0
5.1.04 | BILL NO. 04 - OPERATIONAL COST |  |  |  | 0
| TOTAL OF BILL №: 05 - Carried Over To Summary |  |  |  | 0

## 02 sewarage system
MADAVELI SEWERAGE SYSTEM
02 SEWERAGE SYSTEM
BILL OF QUANTITIES
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (4 nos.)
1.1.00 | General Notes
(a) Cement for all structural works shall be Sulphate resistant portland cement to BS4027:1996 unless specified otherwise
(b) All structural reinforcement steel shall be epoxy coated reinforcement to ASTM A775 / A775M andTwo coats of Bitumastic paint shall be applied on the external surfaces of all structures below ground level.
(c) rates shall include the pump sump, valve chamber, control panel cabinet and valves, fittings inside the valve chamber and vent structures
(d) All internal concrete surfaces shall be protected with epoxy coating of thickness 500 microns
(e) Bituminous coating shall be provided to all external surfaces of concrete works below ground
(f) Rates shall include for formwork, cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
1.2.01 | Excavation and sinking of concrete caissions of 1400 mm dia x 3000 mm at at the PS locations, as detailed in the drawing, sealing the bottom and ballasting against the buoyancy | 7 | nos |  | 0
1.2.01 | Supply and installation of the GRP wet wells for the pump stations and filling the gap with Gr15 concrete as detailed in the drawing. | 7 | nos |  | 0
1.2.03 | Construction of the concrete cover slab with DI MH covers for pump access into the well. | 7 | nos |  | 0
1.2.04 | Constructioin of concrete foundation for the vent pipe as per the detaioled drawing. | 7 | nos |  | 0
| TOTAL OF BILL №: 01 - Carried Over To Summary |  |  |  | 0
BILL NO. 02 - INSTALLATION OF PUMPS
2.1.00 | General Notes
(a) Rates shall include for installation as per approved drawings
b) rates shall include costs for Power cable, duckfoot bend, dischage connection, guide bars and 6m of stainless steel lifting chain, level control switches as per drawing and specifications.
(b) Rates shall include for all internal piping and connections as per detail
2.2.00 | Installation of Pumps
2.2.01 | Submersible Pumps 1.4 kW (Pump Station 01) - Pump Capacity, 2.0 l/s, Head=6 m each | 2 | nos |  | 0
2.2.02 | Submersible Pumps 1.4 kW (Pump Station 02) - Pump Capacity, 2.0 l/s, Head=6 m each | 2 | nos |  | 0
2.2.03 | Submersible Pumps 1.4 kW (Pump Station 03) - Pump Capacity, 2.0 l/s, Head=6 m each | 2 | nos |  | 0
2.2.04 | Submersible Pumps 1.4 kW (Pump Station 04) - Pump Capacity, 2.0 l/s, Head=6 m each | 2 | nos |  | 0
2.2.05 | Submersible Pumps 1.4 kW (Pump Station 05) - Pump Capacity, 2.0 l/s, Head=6 m each | 2 | nos |  | 0
2.2.06 | Submersible Pumps 1.4 kW (Pump Station 06) - Pump Capacity, 2.0 l/s, Head=6 m each | 2 | nos |  | 0
2.2.07 | Submersible Pumps 1.4 kW (Pump Station 07) - Pump Capacity, 2.0 l/s, Head=6 m each | 2 | nos |  | 0
2.2.08 | Submersible Pumps 4.9kW (Sea Outfall) - Pump Capacity | 2 | nos |  | 0
Q = 11.0 l/s, H = 15.0 M or Equvialent
2.3.00 | Vent structures
2.3.01 | Supply and installation of vent structure as per the drawing | 7 | nos. |  | 0
2.4.00 | Monitoring system for Pump stations including all necessary cabling and wiring or GSM modules. | 1 | Item |  | 0
2.5.00 | laying and Installation of Pumping Main
2.5.01 | Pumping main 90 mm dia. HDPE PE100 SDR11 PN16 pipe | 1262 | m |  | 0
2.5.02 | Pumping main 160mm dia. HDPE PE100 SDR11 PN16 pipe | 200 | m |  | 0
| TOTAL OF BILL №: 02 - Carried Over To Summary |  |  |  | 0
BILL NO. 03 - MECHANICAL AND ELECTRICAL WORKS
3.1.00 | General Notes
(a) The rate shall include for any necessary excavation of trenches, backfilling after laying and testing, jointing, installing house connection wyes on the main line, dewatering if absolutely necessarry, and any other required accessories, including dismantling of road layers and reinstatement after works
(b) The rate shall include for making good any areas affected by below works
3.2.00 | Main feeder cable from island grid to control panels (4 pump stations and admin building/STP) including , materials and accessories required for complete works
3.2.01 | 70 mm2 4-Core armoured cable (Gen room to Control room and to PS Feeder) | 210 | m |  | 0
3.2.02 | 25 mm2 4-Core armoured cable (feeder to PS) | 80 | m |  | 0
3.3.00 | Control Panel with necessary cabling and control wiring as per approved details (4 Pump staions , STP and admin building) | 1 | Item |  | 0
3.4.00 | Control panel board for the pump station, complete with the float swich pump control, overload relay, EFR, Warning beacon,General indicators such as Amp, Voltage, Phase indicators etc. | 4 | nos |  | 0
3.4.00 | Preparation of electrical drawings and obtaining approval from MEA | 1 | Item |  | 0
3.5.00 | Testing and Commissioning of the complete electrical system. | 1 | Item |  | 0
| TOTAL OF BILL №: 03 - Carried Over To Summary |  |  |  | 0
BILL NO. 04 - GRAVITY SEWER MAINS
4.1.00 | General Notes
(a) The rate for pipe laying shall comprise excavation of trenches, backfilling after laying and testing, jointing pipes, installing house connection wyes on the main line, dewatering if absolutely necessarry, providing granular bedding for pipe laying, including dismantling of road layers and reinstatement after works
(b) all gravity sewer pipes shall be UPVC to BS EN1401-1:2009.
(c) All gravity sewer mains shall be 160mm dia UPVC of wall thickness & stiffness rated to SN4 & SDR41.
(d) All gravity house laterals shall be 110mm dia UPVC of wall thickness & stiffness rated to SN4 & SDR41.
(e) All gravity sewer mains shall have minimum 0.4% slope unless specified
(f) All gravity sewer pipes shall be jointed using rubber ring push fit jointing method & rubber rings comply with BS 2494 (type2).
(h) All sewer pipes shall be buried under earth cover of minimum 0.6 meters.
4.2.00 | Pipe laying
All pipes are measured in linear meters on plan veiw. Contractor shall adjust for slopes
4.2.01 | 160mm dia, uPVC gravity sewer main (SN4, SDR41) | 10137 | m |  | 0
4.3.00 | Maintenance shaft
(a) Rates shall include for installation of all connections, concrete protections and necessary ancillary items, as per drawing and technical specifications
4.3.01 | 600mm dia. PE/PP Maintenance shaft with concrete protection | 97 | nos. |  | 0
4.4.00 | House Connection
4.4.01 | Laying of Lateral house connection to main network, not exceeding maximum distance of 6m, including provision and installation of 315mm dia. uPVC House inspection chamber as per detail drawing | 387 | nos. |  | 0
4.5.00 | Clean out
(a) Rates shall include for all connections, concrete protections and necessary ancillary items, as per drawing and technical specifications
4.5.01 | 160mm dia. uPVC clean out | 52 | nos. |  | 0
| TOTAL OF BILL №: 04 - Carried Over To Summary |  |  |  | 0
BILL NO. 05 - ADMIN BUILDING
5.1.00 | General Notes
(a) Lean concrete shall be GRADE C15 and all structural concrete shall be GRADE C30
(b) All concrete below ground in contact with ground water shall be done using SRC with waterproofing admixture
(c) Bituminous coating shall be provided to all exposed concrete surfaces
(d) Rates shall include for excavation in all types of hard & soft soils and removing, transporting & stacking the excavated material anywhere in the island and as directed by the Engineer, backfilling with excavated materials from stacks, watering consolidation
5.2.00 | Admin / Control building as per the drawing and the specifications.
Following works to be incorporated:
Eaxacations for foundations, back filling under floors, concrete works, cement block masonary,
Zn Alum roof on GI steel truss as shown in the drawing, Aluminium doors and windows
All meachanical and electrical works associated with the building as per drawings and technical specification
All plumbing and drainage works associated with the building as per drawings and technical specification
All plumbing and drainage fittings and fixtures associated with the building as per drawings and technical specification
| TOTAL AREA UNDER ROOF = 6.0 M SPAN X 18.85 M LONG ( 113.10 SQM) | 1 | item |  | 0
5.3.0 | Fire detection and protection
Provision of fire detection and protection as per drawings
5.3.01 | 5kg capacity dry chemical powder type Fire Extinguisher | 3 | nos. |  | 0
5.3.02 | 2kg capacity CO2 Fire Extinguisher | 3 | nos. |  | 0
5.3.03 | Installation of fire blanket | 1 | nos. |  | 0
5.4 | Parking Shed (6m x 3.5m) | 1 | nos. |  | 0
5.5 | Boundary Wall and gate | 1 | nos. |  | 0
| TOTAL OF BILL №: 05 - Carried Over To Summary |  |  |  | 0
BILL NO. 06- SEA OUTFALL
6.1.00 | Installation of outfall pipeline with concrete ballast block, anchoring and necessary concrete protection as per drawing
6.1.01 | 160mm dia, HDPE sea outfall pipe (PE 100, PN16, SDR11). The maximum depth of diffuser head from MSL is 15m | 210 | m |  | 0
| TOTAL OF BILL №: 06 - Carried Over To Summary |  |  |  | 0
BILL NO. 07- STP.
7.1.01 | Excavations for foundations | 320.54 | M3 |  | 0
7.1.02 | Grade 30 concrete in foundations, tank bases and walls on G1000 polythene membrane | 186.5 | M3 |  | 0
7.1.03 | Form work for the foundations, tank bases and walls (Approx) | 920 | m2 |  | 0
7.1.04 | Steel reinforcement work for the structures | 16.115 | MT |  | 0
7.1.05 | Water proofing of the tanks | 1 | item |  | 0
7.1.06 | Hydraulic testing of tanks for leakages | 1 | item |  | 0
7.1.07 | Pninting the internal walls with a epoxy paint resistant to sewer contamination | 1 | item |  | 0
7.1.08 | Painting the external walls with a weather shield paint, 2 coats. | 1 | item |  | 0
7.1.09 | All internal plumbing work as per the detailed drawing. | 1 | item |  | 0
7.1.10 | Construction of Sludge drying bed , 8.4 m Long x 4.2 m wide x 2.5 m ht ( As per the drawing) | 1 | item |  | 0
7.1.11 | Supply and installation of pumps- EQT -AT (0.2m3/min) | 2 | nos |  | 0
7.1.12 | Supply and installation of pumps- CWT - SOF (0.2m3/min) | 2 | nos |  | 0
7.1.13 | Supply and installation of pumps- SHT - SDB (0.1m3/min) | 2 | nos |  | 0
7.1.14 | Supply and installation of pumps- SDB - AT (0.1m3/min) | 2 | nos |  | 0
7.1.15 | Supply and installation of Air blowers , 2.53m3/min | 3 | nos |  | 0
7.1.16 | Fine bubble areators (EPDM) (200 mm dia), including piping from air blowers to areators | 44 | nos |  | 0
7.1.17 | Supply and installation of a electrical control panel as per the detailed drawing | 1 | nos |  | 0
7.1.18 | Supply and Installation of all level sensors for the pumps as detailed in the drawing | 2 | nos |  | 0
7.1.19 | Supply and installation of water flow meters (Digital) 0.2m3/min) at the EQT/AT pipe line | 2 | nos. |  | 0
| TOTAL OF BILL №: 07 - Carried Over To Summary |  |  |  | 0
BILL NO. 08- SUPPLY OF O&M EQUIPMENT AND SPARES
8.1.00 | Safety Tools
Supply and Delivery of the following safety equipments and tools:
8.1.01 | Wooden First Aid Box | 1 | Nr. |  | 0
8.1.02 | Fire Bucket sand with 3 nos. of round bottom buckets. | 5 | Nr. |  | 0
8.1.03 | Rubber mat of 1.1kV grade of size 6mm thick. | 4 | Nr. |  | 0
8.1.04 | Fire Safety Rules chart. | 1 | Nr. |  | 0
8.1.05 | Shock Treatment Chart | 1 | Nr. |  | 0
8.2.00 | Maintenance Tools
| Supply and Delivery of standard maintenance tools / equipments including manuals and catalogues to Engineer's approval. | 1 | set |  | 0
| TOTAL OF BILL №: 08 - Carried Over To Summary |  |  |  | 0
BILL NO. 09 - TESTING AND COMMISSIONING
9.1.00 | Preparation ofall O&M manuals, training documents and as-built drawings | 1 | item |  | 0
9.2.00 | Provision of two year warranty of system including all required maintenance and provision of spare parts during this period | 1 | item |  | 0
9.3.00 | Training of employeer's nominnes in operation and maintainance as per employer's requirement | 1 | Item |  | 0
9.4.00 | Testing and comissioning of system | 1 | item |  | 0
| TOTAL OF BILL №: 9 - Carried Over To Summary |  |  |  | 0
SUMMARY OF BOQ
| BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (4 nos.) |  |  |  | 0
| BILL NO. 02 - INSTALLATION OF PUMPS |  |  |  | 0
| BILL NO. 03 - MECHANICAL AND ELECTRICAL WORKS |  |  |  | 0
| BILL NO. 04 - GRAVITY SEWER MAINS |  |  |  | 0
| BILL NO. 05 - ADMIN BUILDING |  |  |  | 0
| BILL NO. 06- SEA OUTFALL |  |  |  | 0
| BILL NO. 07 - STP |  |  |  | 0
| BILL NO. 08- SUPPLY OF O&M EQUIPMENT AND SPARES |  |  |  | 0
| BILL NO. 09- TESTING AND COMMISSIONING |  |  |  | 0
| TOTAL SUMMARY OF BOQ, SEWERAGE SYSTEM |  |  |  | 0