## Prelim and GR
PROVISION OF SEWERAGE FACILITIES IN 5 ISLANDS AND – S. HULHUDHOO & S. MEEDHOO
ITEM | DESCRIPTION | QTY | UNIT | UNIT RATE | TOTAL
|  |  |  | USD | USD
PRELIMINARIES & GENERAL REQUIREMENTS
Generally
The Contractor shall allow here for all costs
for mobilization as a lumpsum amount, or in a
breakup provided by the contractor, for all items
in this contract which includes the requirements
as set in contract documents and drawings including
any regulatory requirements to complete the works
A | Expenditure incurred in complying with the clauses
in the Introduction, Invitation for Bids, Instruction to
Bidders, Bidding Data, Appendix to Bid, Qualification
| Instruction, Form of Agreement & Form of Security | Item | L.S.
B | Expenditure incurred in complying with the clauses
| in the General & Particular Contract Conditions | Item | L.S.
C | Ditto - in section 01000 ; Introduction | Item | L.S.
D | Ditto - in section 01110 : Summary of Works | Item | L.S.
E | Ditto - in section 01200 :Payment, Program and Measurements | Item | L.S.
F | Ditto - in section 01310 : Project Coordination | Item | L.S.
G | Ditto - in section 01320 : Progress Schedule | Item | L.S.
H | Ditto - in section 01330 : Submittals | Item | L.S.
I | Ditto - in section 01450 : Quality Control | Item | L.S.
J | Ditto - in section 01500 : Construction Facilities &
| Temporary Controls | Item | L.S.
K | Ditto - in section 01600 : Materials & Equipments | Item | L.S.
L | Ditto - in section 01720 : Field Engineering | Item | L.S.
M | Ditto - in section 01750 : Starting of Systems | Item | L.S.
N | Ditto - in section 01770 : Contract Close Out | Item | L.S.
O | Ditto - in section 01780 : Data Operation and | Item | L.S.
Maintenance
| PAGE TOTAL |  |  |  | 0
PRELIMINARIES & GENERAL REQUIREMENTS
Bill Collection
| Page 1 |  |  |  | 0
Total for Preliminaries & General Requirements
| Carried to GENERAL SUMMARY |  |  |  | 0

## Sewerage
PROVISION OF SEWERAGE FACILITIES IN 5 ISLANDS AND – S. HULHUDHOO & S. MEEDHOO
ITEM | DESCRIPTION | QTY | UNIT | UNIT RATE | TOTAL
|  |  |  | USD | USD
SEWERAGE SYSTEM
COLLECTION SYSTEM
Site Preparation - Specification Section 02200
A | Site clearance for the gravity sewerage works, protection of existing plants, trees, services and utilities. | Item | LS
Sanitary Sewerage - Specification Section 02530
Pipework
| 150mm dia UPVC pipe laying in trenches for the gravirty sewer including excavation, shoring, dewatering to lines and levels, 5 cm thick sand bedding protection as indicated in drawings, connections, testing, putting marker tapes, protection of adjacent structure and backfilling to make up levels,complete to the satisfaction of Engineer (Ref. Spec. 02240, 02260, 02315, 02316, 02318, 03300) all as specified and shown on drawings. |  |  |  |  | 31224
B | Depth Upto 750mm from GL | 11489 | m
C | Depth Above 750mm and below 1500mm from GL | 8749 | m
D | Depth Above 1500mm from GL | 10986 | m
E | Bypass pipe 160mm OD with Non return valve for each Lifting station | 5300 | m
Maintenance Shaft
F | Supply and installation of 150 mm UPVC MS (Maintenance shaft) with BS EN 124 450mm dia cast iron manhole frame and cover assembly, according to the detail shown in the drawings of MS (Maintenance shaft) with all necessary pipe and fittings, including excavation, shoring and dewatering. (Ref. Spec. 02240, 02260, 02315, 02316, 02530). | 49 | No
Manholes
| Supply & Installation of 1000mm dia FRP Manhole including excavation, shoring, dewatering to lines and levels, cast iron covers and frame, concrete works, FRP pipe rings, all other supports & protection as indicated in drawings, connections, testing, protection of adjacent structure and backfilling to make up levels, complete to the satisfaction of Engineer (Ref. Spec. 02240, 02260, 02315, 02316, 02530, 02631, 03100, 03200, 03300, 05500) all as specified and shown on drawings. |  |  |  |  | 392
252
G | Depth Upto 750mm from GL (600mm dia) | 311 | No
H | Depth Above 750mm and below 1500mm from GL (1000mmdia) | 150 | No
I | Depth Above 1500mm and below 1800mm GL (1500mm dia) | 70 | No
J | Depth Above 1800mm from GL (1800mm dia) | 37 | No
PAGE TOTAL
COLLECTION SYSTEM (contd..)
Inspection Chambers
A | Supply & installation of 600mm x 600mm x 750mm HDPE Inspection Chamber for house connection with adequate connections for current & future expansion, supports, protection fixings & covers, complete including concrete works, connections to gravity sewer (connection to household is not part of this contract) all as specified and shown on drawings. (Ref. Spec. 02240, 02260, 02315, 02316) | 1810 | No
LIFTING STATION & PRESSURE MAINS
Packaged Submersible Lift Stations - Specification Section 11170
Supply, install & commission waterproof GRP Packaged lifting station, 1800mm dia, to locations as noted in drawings, including excavations, shoring, dewatering, concrete works, protection, support, heavy duty grating covers, controls, instrumentation, emergency back up facility, power connections, spares and tools for 1 year, chain, pulley hooks steps, etc, finish and complete for the following lifting station as noted. (Ref. Spec. 02240, 02260, 02315, 02316, 02530, 03100, 03200, 03300, 05500) all as specified and shown on drawings.
B | Lifting Station as above - LS1 | 1 | No
C | Lifting Station as above - LS2 | 1 | No
D | Lifting Station as above - LS3 | 1 | No
E | Lifting Station as above - LS4 | 1 | No
B | Lifting Station as above - LS5 | 1 | No
C | Lifting Station as above - LS6 | 1 | No
D | Lifting Station as above - LS7 | 1 | No
E | Lifting Station as above - LS8 | 1 | No
B | Lifting Station as above - LS9 | 1 | No
C | Lifting Station as above - LS10 | 1 | No
D | Lifting Station as above - LS11 | 1 | No
E | Lifting Station as above - LS12 | 1 | No
G | Shade for Duplex Pump Control Panel including the frames and supports, excavation if required, concrete bases, finish and complete, all as specified and shown on drawings. | 12 | No
H | PVC Coated Chain Link Fencing all around the lifting station and pumping station including 1800mm wide gate, pad locks, support, excavation, concrete works, backfilling all as specifed and shown on drawings. | 600 | m
PAGE TOTAL
LIFTING STATION & PRESSURE MAINS (contd..)
A | 110mm diameter HDPE Pressure pipes for pumped mains from lifting station to pumping station, with all necessary fittings including fusion welding, excavation, shoring, dewatering, pipe protection, supports, thrust blocks, backfilling, pressure testing, putting marker tapes etc as required for the complete works (Ref. Spec. 02240, 02260, 02315, 02316, 03100, 03200, 03300), all as specifed and shown on drawings. | 19821 | m
PUMPING STATION
E | Pumping Station including Protective grid, access cover double sealed, shade (inclusive of frames & supports, concrete bases and finish), 150mm diameter UPVC vent pipe etc as specified and shown on drawings. | 1 | No
F | Supply and install two submersible pumps both working, non clog and stainless steel impeller with cast iron body complete with all necessary controls, float switches and safety features as specified and shown on drawings. | 1 | No
Sewer Jetting Equipment
G | The Sewer Jetting Equipment shall include the following, high pressure hoses, Suitable for cleaning out house connections with inspection chamber located on private land with little access or working space between the boundary wall and the superstructure, etc as per mechanical requirements. | 1 | No
PAGE TOTAL
TREATMENT FACILITY (PROVISIONAL)
The treatment process shall be extended aeration, tender documents related to the same are indicative. The contractor shall ensure that all equipments and fixtures are in line with manufacturer's specifications.
A | RCC Collection Well, indicative size of 12000mm x 5000mm x 3200mm below or above grade to manufacture standards including all civil works to house 2 submersible pumps (operating one at a time), controls, instrumentation and emergency back up facility, power connections, spares and tools, chain, pulley hooks steps, etc complete, watertight construction (pumps & controls measured elsewhere) | 1 | No.
B | Compact Waste Water Treatment plant of capacity 3387m3/day expandable upto 5034 m3/day in future with appropriate provision, employing activated sludge aeration process including splitter box, aeration and settling tank, six months capacity sludge tank, necessary piping controls, instrumentation, power connection, emergency backup facility for uniterrupted operation, including all civil works like RCC tanks, excavation, shoring, dewatering, backfilling all inclusive in strict compliance with the manufacturer, above or below grade, complete within the allocated site boundaries (Sludge Tank measured elsewhere) | 1 | No
C | RCC Effluent Manholel, indicative size of 2000mm x 2000mm x 4000mm below grade including all civil works to house 2 submersible pumps (opearting one at a time), controls, instrumentation, emergency back up facility, power connections, spares and tools, chain, pulley hooks steps, etc complete, watertight construction (pumps & controls measured elsewhere) | 1 | No
D | 160mm HDPE Pressure pipes for pumped mains from Effluent Pumping Station to Sea Outfall including excavation, shoring, dewatering, reef trench, sleevs, ballast, supports, thrust blocks, backfilling, testing as appropriate for the completion of this work | 300 | m
E | Pavement all around the treatment facility, width to be1.2m | 1 | LS
F | RCC Sludge Tank, indicative size of 11000mm x 5000mm x 2000mm below grade including all civil works with necessary waterstoppers, protection, heavy duty man hole covers etc complete with all piping associated | 1 | No.
|  |  | PAGE TOTAL |  | 0
TREATMENT FACILITY (contd..)
A | Hardscaping and Lanscaping to match the local | Item | LS
standards, to the level shown in drawings
B | PVC Coated Chain Link Fencing all around the lifting | 100 | m
station inlcuding 2.5 m wide double gate, pad locks,
support, excavation, concreteing, backfilling
C | Suply and install two submersible pumps one working | 1 | Set
one standby, non clog, 6.9 l/s capacity with grinder and
stainless steel impeller with cast iron body complete
with all necessary controls, float switches and safety
features - Inlet Well Pump, as specified and shown on drawings.
D | Suply and install two submersible pumps one working | 1 | Set
one standby, non clog, 6.9l/s capacity and stainless
steel impeller with cast iron body complete with all
necessary controls, float switches and safety features
Effluent Well Pump, as specified and shown on drawings.
E | Provision of sludge pump to dispose stabilized & | 1 | LS
digested sludge including piping and connection to
effluent outfall line, change over valves, support and the
like complete, as specified and shown on drawings.
SUNDRIES
F | Operate and Maintain the complete system for One year including attending & rectification of defects, including provision of tools and spares as required and handing over the works with manual, spares complete. | Item | LS
PAGE TOTAL
SEWERAGE SYSTEM
Bill Collection
Page 3
Page 4
Page 5
Page 6
Page 7
Total for Sewerage System
Carried to GENERAL SUMMARY

## Civil Works
PROVISION OF SEWERAGE FACILITIES IN 5 ISLANDS AND – S. HULHUDHOO & S. MEEDHOO
ITEM | DESCRIPTION | QTY | UNIT | UNIT RATE | TOTAL
|  |  |  | USD | USD
CIVIL WORKS
Site Preparation - Specification Section 02200
A | Site clearance for the water supply works, protection of existing plants, trees, services and utilities. | LS | Item
ADMIN BUILDING
G | RCC Admin Building (1 No.), overall size approximately 6000mm x 2500mm, inclusive of all fittings like split A/c, sanitary ware, kitchen equipment and other electromechanical items and furnitures. This item shall include the design and approval of the building from all disciplines to make it functional all as shown on Drawings. | LS | Item
H | PVC Coated Chain Link Fencing all around the Building Site inlcuding 3000mm wide gate, pad locks, support excavation, concrete works, backfilling all as specifed and shown on drawings. | 100 | m
PAGE TOTAL
ADMIN BUILDING (contd..)
CIVIL WORKS
A | Site clearance for the works, protection of existing plants, trees, services and utilities. | 100 | m2
B | Excavation for foundation, maximum depth not exceeding 1000mm, in all kinds of subsurface material, backfilling of the selected excavated material inside and around the building, to the levels and densities as directed by the Engineer. | 9 | m3
Plain concrete 14MPa @ 28 Days using Sulphate Resisting Cement (TYPE V ) including formwork and additives.
C | 50mm thick blinding under foundation as per drawings. | 21 | m2
Reinforced concrete 30MPa @ 28 days using Ordinary Portland Cement (Type I) including formwork, reinforcement, water stops, expansion and construction joints, joint filler, sealants and additives and fair face finish as specified and shown on drawings
D | Footings including concrete filling around footings. | 0.588 | m3
E | Beams | 0.96 | m3
F | 150 mm thick Slab-on-grade | 1.5 | m3
G | 150 mm Thick Suspended Slab | 1.5 | m3
H | Columns | 0.48 | m3
I | SUNDRIES - Allow for supporting bases, plinths and the like to all mechanical and electrical equipment. | LS | Item
J | 200mm thick cement sand block walls | 60 | m2
K | Waterproofing membrane, each 4 mm thick (Two layers), as specifed and shown on drawings. | LS | Item
L | Type - D1,Wood Door including frame, (1600 x 2100) mm Overall Size as per door schedule. | 1 | No.
M | Type - D2,Wood Door including frame, (900 x 2100) mm Overall Size as per door schedule. | 1 | No.
N | Type - D3,Wood Door including frame, (800 x 2100) mm Overall Size as per door schedule. | 1 | No.
PAGE TOTAL
ADMIN BUILDING (contd..)
CIVIL WORKS (contd..)
A | Type - W1, Aluminum Double Glass Window including frame (1000 x 1500) mm Overall Size , as specified and shown on drawings | 1 | No.
B | 20mm thick sand cement plaster to concrete or block walls and columns to receive paint finish, (including internal Painting) | 286 | m2
C | Epoxy Paint flooring as per drawings. | 30 | m2
D | Non-Slip Ceramic Tiles 200x200 mm Thick as per drawings. | 5 | m2
E | Ceramic Tiles (400 x 200) mm for Skirting as per Drawings | 40 | m2
F | 200 x 300 mm Ceramic Wall Tiles as per Drawings | 30 | m2
G | 600 x 600 mm Perforated Gypsum Tiles for ceiling | 30 | m2
H | Paint with 2 under coat with two coat of putty External plastered wall surfaces | 70 | m2
PAGE TOTAL
WATER SUPPLY SYSTEM
Bill Collection
Page 9
Page 10
Page 11
Page 12
Page 13
Page 14
Total for Water Supply System
Carried to GENERAL SUMMARY

## Electrical works
PROVISION OF SEWERAGE FACILITIES IN 5 ISLANDS AND – S. HULHUDHOO & S. MEEDHOO
ITEM | DESCRIPTION | QTY | UNIT | UNIT RATE | TOTAL
|  |  |  | USD | USD
ELECTRICAL WORKS
Basic Electrical Materials and Methods
Basic Electrical Requirements
A | Supply, installation, testing and commissioning of the following items of work (unless specifically stated otherwise) including all materials, labour, tools, accessories, etc. required for proper operation and completion of each item as per specification | Item | LS
Main Feeder Cables
Supply and install and test the following switchboad from MLTP to Motor starter panel and Generator, motor starter panel to DBs and Pumps inclusive of cable on galvanized steel cable tray and support, cable tray and underground installation. Rate to include cable tray, excavation and backfilling installation work, UPVC sleev and road crossing pipe sleev complete protective marker and indication. Termination juncitin box, support bracket, cable gland and termination work, protective eart and accessories necessary for complete installation
B | 2x4C X 150mm² CU/XLPE/SWA/PVC from ATS to Panel | 20 | m
C | 4C X 25mm² CU/XLPE/SWA/PVC from ATS to Panel | 35 | m
D | 4C X 10mm² CU/XLPE/SWA/PVC from ATS to Panel | 38 | m
E | 4 X 25 + 1 X 16mm² CU/PVC in 50mm PVc lay in tray | 14 | m
F | 4 X 16 + 1 X 6mm² CU/PVC in 38mm PVc in Duct | 33 | m
G | 4 X 10.0 + 1 X 6.0mm² CU/PVC in 38mm G.I conduit | 10 | m
H | 4 X 6.0 + 1 X 4.0mm² CU/PVC in 25mm PVc Duct | 152 | m
I | 4 X 6.0 + 1 X 4.0mm² CU/PVC in 25mm PVc conduit | 22 | m
J | 4 X 4.0 + 1 X 2.5mm² CU/PVC in 25mm G.I conduit | 50 | m
Supply, install and connect the following including wiring, conduits, accessories, etc. all as specified and as required for proper operation
K | 5A 2/3pin switched socket outlet - W/P | 2 | No.
L | 15A 3pin switched socket outlet | 1 | No.
PAGE TOTAL
ELECTRICAL WORKS (contd..)
A | 13A 3pinTwin switched socket outlet | 7 | No.
B | 13A 3pinTwin switched socket outlet - W/P | 6 | No.
C | 20A Junction box with 20A DPSW | 2 | No.
D | Exhaust fan point | 3 | No.
E | Light points | 41 | No.
Distribution Equipment
Supply, install and connect the following motor starter panel with all necessary accessories, interconnections etc., all as shown in the drawings, as specified and as required for proper operation:-
F | Motor Starter Panel | 2 | No
Supply, install & connect the following MCB distribution boards with all necessary accessories, inter-connection, etc., including cables / wires, onduit/duct/tray all as shown on the drawings, as specified and as required for proper operation:-
G | DB - OFFICE | 1 | No
H | DB - EX W/P | 1 | No
I | DB - TP | 1 | No
Emergency Standby Power System
J | Supply, install, connect and commission automatic mains failure standby diesel generating set rated 33kVA rating (portable type) at 0.8 P.F., 50 Hz, 415 Volt complete with diesel engines, generator control panel, batteries, starter,motors, exhaust piping, silencers, 8 hrs built-in base daily fuel tank, vibration isolators, earthing, standard spares, tools, etc., all as shown on the drawings, as specified and as required for proper operation | 2 | No
PAGE TOTAL
ELECTRICAL WORKS (contd..)
A | Supply, install, connect and commission automatic mains failure standby diesel generating set rated 180kVA rating at 0.8 P.F., 50 Hz, 415 Volt complete with diesel engines, generator control panel, batteries, starter,motors, exhaust piping, silencers, 8 hrs built-in base daily fuel tank, vibration isolators, earthing, standard spares, tools, etc., all as shown on the drawings, as specified and as required for proper operation | 1 | No
B | Supply, install, connect and commission automatic mains failure standby diesel generating set rated 55kVA rating at 0.8 P.F., 50 Hz, 415 Volt complete with diesel engines, generator control panel, batteries, starter,motors, exhaust piping, silencers, 8 hrs built-in base daily fuel tank, vibration isolators, earthing, standard spares, tools, etc., all as shown on the drawings, as specified and as required for proper operation | 1 | No
C | Supply, install and connect the 550A, 4 Pole Automatic Transfer Switch (ATS) panel with manual - double bypass - isolation complete with all necessary protection, measuring instruments, accessories interconnection, indicator lamps, etc., all as shown on the drawings, as specified and as required for proper operation | 1 | No
D | Supply, install and connect the 100A, 4 Pole Automatic Transfer Switch (ATS) panel with manual - double bypass - isolation complete with all necessary protection, measuring instruments, accessories interconnection, indicator lamps, etc., all as shown on the drawings, as specified and as required for proper operation | 1 | No
E | Supply, install and connect the 60A, 4 Pole Automatic Transfer Switch (ATS) panel with manual - double bypass - isolation complete with all necessary protection, measuring instruments, accessories interconnection, indicator lamps, etc., all as shown on the drawings, as specified and as required for proper operation | 4 | No
F | Testing and commissioning of the completed installations | Item | LS
PAGE TOTAL
ELECTRICAL WORKS (contd..)
Light Fittings
Supply, install & connect complete in position and in an operable manner the following light fittings complete with lamps, fluorescent tubes, control gears, reflectors, fixings, switches, light point, accessories & connnections all complete as specified and as required for proper operation:
A | Light Fitting Type -70W IP-65 Halogen lamp Mounted on 6M height post | 18 | No
B | 1X40W surface mounted fluorescent light fitting | 13 | No
C | 1X40W wall mounted fluorescent light fitting-w/p | 9 | No
D | 1X60W surface mounted fluorescent downlight-w/p | 1 | No
EARTHING SYSTEM
E | Supply, install and connect complete in position earthing system including copper tapes, earth electrodes, earthing pits, etc., as required inclusive of all fixings and accessories all as shown on the drawings, as specified and as required for proper operation:- | Item | LS
Earthing point with electrode/test point, cover, etc. complete as required for the system
Running copper tape, CU/PVC wire earthing network bonding of entire installation complete in all respects as required for the earthing and bonding system
LIGHTNING PROTECTION SYSTEM
Supply, install, connect and test complete lightning protection system with earth rods, earth pit, clips, conduitsand all required accessories, etc.as shown on the drawings and as required for proper operation.
F | Lightning protection earthing point with electrode/test point complete as required for the system. | 1 | No.
G | Running 3x25mm copper tape air termination network, down conductors, earth termination network, bonding of entire installation to lightning protection system, all required joints, connections, test clamps, etc. all as required for the lightning protection | L.S | L.S
NOTE: The earthing methods and the area requirements for earth pit and copper shall be done as per the manufacturers recommendations.
PAGE TOTAL
ELECTRICAL WORKS (contd..)
Telephone System
Supply, install and connect all the telephone system including telephone terminal cabinets, terminal blocks, terminations and identifications etc.,including conduits, wiring, conduit fittings etc., all as shown on the drawings & as required for proper operation
A | TTB - Telephone Terminal Box | 1 | No.
B | Single Outlet for Telephone (RJ-45) | 2 | No.
C | Single Outlet for Data (RJ-45) | 2 | No.
PAGE TOTAL
ELECTRICAL WORKS
Bill Collection
Page 16
Page 17
Page 18
Page 19
Page 20
Total for Electrical Works
Carried to GENERAL SUMMARY

## Daywork
PROVISION OF SEWERAGE FACILITIES IN 5 ISLANDS AND – S. HULHUDHOO & S. MEEDHOO
ITEM | DESCRIPTION | QTY | UNIT | UNIT RATE | TOTAL
|  |  |  | USD | USD
DAY WORKS
GENERAL PRINCIPLES
A | In accordance with General Conditions of Contract, certain works may be executed on day works In such a case the works must be ordered in writing by the Engineer and they will be administered strictly in accordance with the above clause.
B | The signature of the Engineer on Day work Records will be for record purposes only and the Engineer reserves the right to measure and value any works for which day work records may have been kept.
C | The Contractor will be paid for day works carried out during the course of the Contract while other operations are in progress by him. Profits & overheads will be stated as a percentage addition in the item provided for the same at the end of the Labor, Material, and Plant sections of the Day works Section.
D | Time engaged in the actual works will be allowed. In the event of labor or plant having been brought to the site specially for the item of Day works then a reasonable allowance will be made for travelling time. This allowance for travelling time will be agreed before the day work item is executed.
E | The percentage for profit and overheads will include for the use and waste of hand tools & of all non-mechanical plant, stagings, scaffolding, tarpaulins, use of electric light, power and water for the works, and all special inducements for working in Maldives. Unless specifically authorized in writing by the Engineer, non-productive overtime or special rates for overtime will not be admissible. The cost of all
supervisory staff, including engineer foreman, clerks,
appliance are to be included in the percentage
addition for profit and overheads.
| PAGE TOTAL |  |  |  | 0
LABOUR RATES
A | The day work rates agreed for labor shall be the net amount payable
| Allow the Provisional Sum of USD 5,000,00 (United States Dollars Five thousand only) for labor in Day work |  |  |  | 5000
B | Allowance to be added for overhead and
profits............................ %
C | Tenderers are required to insert hereunder a list of operatives together with their net hourly rates to be used in calculating the cost of work executed on a day work basis :-
Operative Rate per hour
MATERIAL RATES
The day work rates agreed for labour shall be the net amount payable
D | Materials used on day work will be as specified for the Works. The rates shall be the lowest current net manufacturers C.I.F. price, plus a reasonable allowance for customs, port handling charges, delivery to site and storing and protection
| Allow the Provisional Sum of USD 5,000.00 (United States Dollar Five Thousand only) for materials in Day work |  |  |  | 5000
E | Allowance to be added for overhead and
profits............................ %
| PAGE TOTAL |  |  |  | 10000
PLANT AND RATES
A | The definition of hire terms will be as follows:-
1) Hourly hire - Any hour of any period less than eight (8) hours.
2) Daily hire - An eight (8) hour day.
Should more than eight (8) hours be worked consecutively (excluding normal breaks, etc.) for excess hours will be paid for as a direct proportion of the daily hire rate.
B | Plant hire rates are to include for drivers, attendants, operators, maintenance in proper working order at all times, attendance in starting up and shutting down, refueling and all fuel and power, oils, greases, and cleaning materials, replacement and/or sharpening of tools and all other ancillary items including consumable spares.
Note: Payment will not be made for mechanics on maintenance time.
C | Allow the Provisional Sum of USD 5,000.000 (United States Dollar Five Thousand only) for Plant in Day work |  |  |  | 5000
D | Allowance to be added for overhead and
profits............................ %
E | Tenderers are required to insert hereunder a list of plant together with hourly and daily hire rates to be used in calculating the cost of work executed on a day work basis :-
Plant Hourly Rate Daily Rate
| PAGE TOTAL |  |  |  | 5000
DAY WORKS
Bill Collection
Page 21
Page 22
Page 23
Total for DAY WORKS
Carried to GENERAL SUMMARY

## Adjustment
PROVISION OF SEWERAGE FACILITIES IN 5 ISLANDS AND – S. HULHUDHOO & S. MEEDHOO
ITEM | DESCRIPTION | QTY | UNIT | UNIT RATE | TOTAL
|  |  |  | USD | USD
TENDERERS ADJUSTMENT
A | The accuracy of the quantities given in this Bills of Quantities is not guaranteed and the Contractor should satisfy himself as to their accuracy
B | Any adjustments that he may consider necessary should be written below and on similar continuation sheets if required, and the net amount of the adjustments is to be carried to the Summary.
ADDITIONS
1
2
3
4
5
6
OMISSIONS
1
2
3
4
5
6
| PAGE TOTAL |  |  |  | 0
TENDERERS ADJUSTMENT
Bill Collection
Page 25
Total for Tenderer's Adjustments
| Carried to GENERAL SUMMARY |  |  |  | 0

## summary
PROVISION OF SEWERAGE FACILITIES IN 5 ISLANDS AND – S. HULHUDHOO & S. MEEDHOO
GENERAL SUMMARY
NO | CONTENTS |  | PAGE NO | TOTAL
USD
1 | PRELIMINARIES & GENERAL REQUIREMENTS
2 | SEWERAGE SYATEM
3 | CIVIL WORKS
4 | ELECTRICAL WORKS
5 | DAY WORKS
6 | TENDERER'S ADJUSTMENTS
|  | TOTAL | USD
| Tenderers Final Discount |  | USD
GRAND TOTAL, CARRIED TO FORM OF TENDER |  |  | USD
| Signature of the Tenderer : |  | Date :
#REF!