## Cover (2)
BILL OF QUANTITIES
B. THULHAADHOO HOSPITAL/ ACCOMMODATION BLOCK / SERVICES BLOCK
CLIENT : MINISTRY OF HEALTH, GOVERNEMNT OF MALDIVES

## BOQ Summary
SUMMARY OF BILL OF QUANTITIES
Project: HA. HORAFUSHI HOSPITAL / ACCOMMODATION BLOCK / SERVICES BLOCK | Date:
Version:
Client: | Prepared by:
DESCRIPTION |  | AMOUNT (MVR) | %
Bill №: 01 - PRELIMINARIES
Bill №: 02 - EXCAVATION AND FILLING
Bill №: 03 - INSITU CONCRETE WORKS
Bill №: 04 - MASONRY
Bill №: 05 - CARPENTRY
Bill №: 06 - STRUCTURAL METAL WORKS
Bill №: 07 - CEILING
Bill №: 08 - WINDOWS, SCREENS & LIGHTS
Bill №: 09 - DOORS, SHUTTERS & HATCHES
Bill №: 10 - DECORATIONS
Bill №: 11 - FINISHES
Bill №: 12 - ROOFING
Bill №: 13 - HYDRAULICS AND DRAINAGE
Bill №: 14 - ELECTRICAL INSTALLATIONS
Bill №: 15- INSULATION, FIRE STOPPING & FIRE PROTECTION
Bill №: 16 - SOLAR PANEL
Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS
Bill №: 18- ADDITIONS AND OMMISIONS
TOTAL AMOUNT
NOTES to BoQ:

## BOQ for tender
0
BILL OF QUANTITIES
ITEM |  |  |  | DESCRIPTION |  | UNIT | QTY | MATERIAL RATE | LABOUR RATE | AMOUNT
1.0.00 |  |  |  | Bill №: 01 - PRELIMINARIES
1.1.00 | GENERAL NOTES
Abbreviations
|  |  | m | - metre
|  |  | nr | - numbers
|  |  | m3 | - cubic metres
|  |  | m2 | - square metres
|  |  | lm | - linear metre
|  |  | t | - tons
|  |  | inc. | - including
|  |  | mm | - millimetre
|  |  | SS | - stainless steel
|  |  | GI | - galvanized iron
1.2.00 | SITE MANAGEMENT COSTS
|  |  |  | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings & similar. |  | item | 1
1.3.00 | SIGN BOARD
|  |  |  | Allow for sign board. |  | nr | 1
1.4.00 | CLEAN-UP
|  |  |  | Allow for clean-up upon completion of works. |  | item | 1
1.5.00 | INSURANCE, BONDS, GUARANTEES AND WARRANTIES
|  |  |  | Insurance as stated in the general conditions. |  | item | 1
1.6.00 | INSPECTION TRIPS
| Arrange inspection trip to PMU team. Each inspection trip takes 2 days. Contractor has to arrange following for trips; (a) Air tickets for 2 person: Male'/Sh. Funadhoo /Male' by air (normal fair), (b) sea transport, Sh. Funadhoo/Sh. Milandhoo/Sh. Funadhoo by speed boat. (c) Land transport from Airport /Accomodation/Airport. (d) Accommodations (2 Air-condition room) per trip. |  |  |  |  | Item | 10
1.6.00 | TOTAL OF BILL №: 01 - Carried Over To Summary
2.0.00 |  |  |  | Bill №: 02 - EXCAVATION AND FILLING
2.1.00 | GENERAL
|  |  | (a) | Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating, and disposing surplus soil.
2.2.00 | SITE CLEARING
2.2.1 |  |  |  | Clear the site area from Trees, rubbish and vegetable matter, stumps, and roots. Rates must include EIA to remove or reallocate trees. The contractor must survey the site before bidding. |  | m2 | 2281.49
2.3.00 | EXCAVATION
Excavation quantities are measured to the faces of concrete members. Rates shall include for all the additional excavation required to place the formwork. Rates shall include for backfilling.
2.3.1 |  |  |  | Excavation for Foundation pads / beam |  | m3 | 494.1305
2.4.00 | FILLING
Rate shall include for: levelling, grading, trimming, compacting and similar
2.4.01 |  |  |  | Compacted earth filling under ground screed. |  | m2 | 2002.08
2.4.02 |  |  |  | 100mm thick coarse aggregate layer under foundation |  | m2 | 2002.08
2.4.03 |  |  |  | 50mm thick sand blinding below ground slab |  | m2 | 2002.08
2.5.00 | DAMP-PROOF MEMBRANE
Rate shall include for: dressing around and sealing to all penetrations.
2.5.01 |  |  |  | Water Proof Membrane - DPM |  | m2 | 839.15
2.5.02 |  |  |  | Bituminous coating |  | m2 | 2085.115
2.6.00 | DE-WATERING
2.6.01 |  |  |  | De-watering the excavation until completion of concrete work as required |  | item | 1
2.7.00 | TOTAL OF BILL №: 02 - Carried Over To Summary
3.0.00 |  |  |  | Bill №: 03 - INSITU CONCRETE WORKS
3.1.00 | GENERAL
|  |  | (a) | Rates shall include for: placing in position, making good after removal of formwork, mortar touch up to all concrete and casting in all required items; additional concrete required to conform to structural and excavated tolerances
|  |  | (b) | Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6.
|  |  | (c) | All structural concrete shall be GRADE M25 and lean concrete shall be GRADE C15
|  |  | (d) | Rates shall include for: concrete, formwork, reinforcement, cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
|  |  | (e) | Rates shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork.
|  |  | (f) | Rates shall include for: cleaning, fabrication, placing the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
|  |  | (g) | All reinforcing bars shall be high strength bars.
|  |  | (h) | Slab soffits to be finished fairfaced, use plasteciser and formwork with reducing agent.
|  |  | (i) | Waterproofing shall be added to all areas specified.
|  |  | (j) | All works complete as per drawing and specification
3.1.01 |  |  |  | Allow for Concrete Testing. |  | item | 1
3.2.00 | MASS CONCRETE
Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
3.2.01 |  |  | 50 | mm Lean Concrete (Foundations) |  | m3 | 50.0505
REINFORCED INSITU CONCRETE
3.3.00 | SUB-STRUCTURE
FOUNDATION PADS
3.3.01 | 1000 | x | 1000 | x 250mm Foundation pads, F1 |  | m3 | 0.75
3.3.02 | 1400 | x | 1400 | x 300mm Foundation pads, F2 |  | m3 | 2.36
3.3.03 | 1700 | x | 1700 | x 300mm Foundation pads, F3 |  | m3 | 1.74
3.3.04 | 2100 | x | 2100 | x 325mm Foundation pads, F4 |  | m3 | 15.77
3.3.05 | 2400 | x | 2400 | x 400mm Foundation pads, F5 |  | m3 | 41.48
3.3.06 | 2500 | x | 2500 | x 350mm Foundation pads, F6 |  | m3 | 21.88
3.3.07 | 2800 | x | 2800 | x 425mm Foundation pads, F7 |  | m3 | 66.64
3.3.08 | 3000 | x | 3000 | x 475mm Foundation pads, F8 |  | m3 | 64.13
3.3.09 | 3500 | x | 3500 | x 600mm Foundation pads, F9 |  | m3 | 14.7
3.3.10 | 750 | x | 750 | x 250mm Foundation pads, F10 |  | m3 | 1.13
3.3.11 | 1500 | x | 2100 | x 350mm Foundation pads, F11 |  | m3 | 1.11
3.3.12 | 4000 | x | 7000 | x 300mm Foundation pads, ST |  | m3 | 9.35
3.3.13 | 1200 | x | 1200 | x 300mm Foundation pads, F11 - Accommodation block |  | m3 | 1.73
3.3.14 | 1400 | x | 1400 | x 300mm Foundation pads, F12 - Accommodation block |  | m3 | 2.36
3.3.15 | 1800 | x | 1800 | x 350mm Foundation pads, F13 - Accommodation block |  | m3 | 6.81
3.3.16 | 750 | x | 750 | x 250mm Foundation pads, F14 - Services block |  | m3 | 1.69
FOUNDATION BEAMS
3.3.17 | 450 | x | 250 | mm Foundation beam, TB |  | m3 | 87.95
3.3.18 | 400 | x | 250 | mm Foundation beam, TB2 - Accommodation block |  | m3 | 8.27
3.3.19 | 350 | x | 200 | mm Foundation beam, TB3 - Services block |  | m3 | 5.43
RC KICKER (STAIRCASE)
3.3.20 | 1350 | x | 250 | mm wide kicker |  | m3 | 0.29
3.3.21 | 2100 | x | 300 | mm wide kicker |  | m3 | 0.54
3.3.22 | 850 | x | 250 | mm wide kicker - Accommodation block |  | m3 | 0.19
3.4.0 | GROUND FLOOR
COLUMNS
3.4.01 | 350 | x | 350 | mm Concrete columns C1 |  | m3 | 14.79
3.4.02 | 375 | x | 375 | mm Concrete columns C2 |  | m3 | 1
3.4.03 | 350 | x | 350 | mm Concrete columns C3 |  | m3 | 10.88
3.4.04 | 350 | x | 350 | mm Concrete columns C4 |  | m3 | 8.27
3.4.05 |  |  | 400 | mm dia Concrete columns C6 |  | m3 | 3.57
3.4.06 |  |  | 200 | mm dia Concrete columns C7 |  | m3 | 0.79
3.4.07 | 250 | x | 300 | mm Concrete columns C7- Accommodation building |  | m3 | 3.63
3.4.08 | 250 | x | 300 | mm Concrete columns C8 - Services Block |  | m3 | 3.92
SLABS
3.4.09 |  |  | 150 | mm thk Concrete ground Slab |  | m3 | 300.32
3.4.10 |  |  | 150 | mm thk Concrete ground Slab - Accommodation block |  | m3 | 18.33
3.4.11 |  |  | 150 | mm thk Concrete ground Slab - Services block |  | m3 | 20.67
3.4.12 |  |  | 200 | mm thk Ramp Slab |  | m3 | 4.14
3.4.13 |  |  | 200 | mm thk Pool slab |  | m3 | 5.4
STAIRS
3.4.13 |  |  |  | Staircase - main building |  | m3 | 3.7339
3.4.14 |  |  |  | Staircase - accommodation block |  | m3 | 1.4859
RC WALLS
3.4.15 |  |  | 150 | mm RC wall X ray room |  | m3 | 12.8332
3.4.16 |  |  | 100 | mm RC Ramp wall |  | m3 | 1.87
3.4.17 |  |  | 150 | mm RC Pool wall |  | m3 | 4.55
3.5.0 | FIRST FLOOR
BEAMS
3.5.01 | 750 | x | 300 | mm Beam B1 |  | m3 | 1.5
3.5.02 | 700 | x | 300 | mm Beam B2 |  | m3 | 1.46
3.5.03 | 650 | x | 300 | mm Beam B3 |  | m3 | 6.18
3.5.04 | 600 | x | 300 | mm Beam B4 |  | m3 | 1.23
3.5.05 | 575 | x | 300 | mm Beam B5 |  | m3 | 6.3
3.5.06 | 550 | x | 300 | mm Beam B6 |  | m3 | 44.08
3.5.07 | 550 | x | 300 | mm Beam B7 |  | m3 | 24.54
3.5.08 | 550 | x | 300 | mm Beam B8 |  | m3 | 0.54
3.5.09 | 450 | x | 300 | mm Beam B10 |  | m3 | 3.42
3.5.10 | 550 | x | 300 | mm Beam CB1 |  | m3 | 0.14
3.5.11 | 550 | x | 300 | mm Beam CB2 |  | m3 | 0.08
3.5.12 | 550 | x | 300 | mm Beam CB3 |  | m3 | 0.1
3.5.13 | 700 | x | 300 | mm Beam B2A |  | m3 | 0.99
3.5.14 | 550 | x | 300 | mm Beam B3A |  | m3 | 5.01
3.5.15 | 450 | x | 200 | mm Beam B11 - Accommodation block |  | m3 | 0.9
3.5.16 | 450 | x | 200 | mm Beam B12 - Accommodation block |  | m3 | 1.2
3.5.17 | 450 | x | 200 | mm Beam B13 - Accommodation block |  | m3 | 2.74
ROOF BEAM
3.5.18 | 300 | x | 200 | mm Beam RB6 - Services block |  | m3 | 4.77
COLUMNS
3.5.19 | 350 | x | 350 | mm Concrete columns C1 |  | m3 | 10.38
3.5.20 | 375 | x | 375 | mm Concrete columns C2 |  | m3 | 0.55
3.5.21 | 350 | x | 350 | mm Concrete columns C3 |  | m3 | 11.8
3.5.22 | 350 | x | 350 | mm Concrete columns C4 |  | m3 | 8.97
3.5.23 |  |  | 400 | mm dia Concrete columns C6 |  | m3 | 3.87
3.5.24 | 250 | x | 300 | mm Concrete columns C7- Accommodation building |  | m3 | 2.84
SLABS
3.5.25 |  |  | 140 | mm thk Concrete Slab |  | m3 | 36.11
3.5.26 |  |  | 160 | mm thk Concrete Slab |  | m3 | 253.89
3.5.27 |  |  | 165 | mm thk Concrete Slab |  | m3 | 61.95
3.5.28 |  |  | 135 | mm thk Concrete Slab - Accommodation block |  | m3 | 15.75
3.5.29 |  |  | 140 | mm thk Concrete Slab - Accommodation block |  | m3 | 5.24
STAIRS
3.4.30 |  |  |  | Staircase - main building |  | m3 | 3.7339
RC WALLS
3.4.31 |  |  | 100 | mm RC wall - balcony wall with coping |  | m3 | 13.755
3.6.0 | TERRACE FLOOR
BEAMS
3.6.01 | 750 | x | 300 | mm Beam B1 |  | m3 | 2.85
3.6.02 | 575 | x | 300 | mm Beam B5 |  | m3 | 0.81
3.6.03 | 550 | x | 300 | mm Beam B6 |  | m3 | 43.25
3.6.04 | 550 | x | 300 | mm Beam B7 |  | m3 | 22.41
3.6.05 | 550 | x | 300 | mm Beam B8 |  | m3 | 2.78
3.6.06 | 450 | x | 300 | mm Beam B10 |  | m3 | 3.31
3.6.07 | 550 | x | 300 | mm Beam CB2 |  | m3 | 0.18
3.6.08 | 550 | x | 300 | mm Beam CB3 |  | m3 | 0.08
3.6.09 | 550 | x | 300 | mm Beam CB4 |  | m3 | 0.65
3.6.10 | 750 | x | 300 | mm Beam B1A |  | m3 | 2.25
ROOF BEAM
3.6.11 | 300 | x | 200 | mm Beam RB5 - Accommodation block |  | m3 | 2.42
COLUMNS
3.6.12 | 350 | x | 350 | mm Concrete columns C1 |  | m3 | 1.4
3.6.13 | 350 | x | 350 | mm Concrete columns C3 |  | m3 | 0.35
3.6.14 | 350 | x | 350 | mm Concrete columns C4 |  | m3 | 0.35
3.6.15 |  |  | 400 | mm dia Concrete columns C6 |  | m3 | 2.87
SLABS
3.6.16 |  |  | 140 | mm thk Concrete Slab |  | m3 | 31.15
3.6.17 |  |  | 160 | mm thk Concrete Slab |  | m3 | 251.86
RC WALLS
3.6.18 |  |  | 100 | mm RC wall - parapet with coping |  | m3 | 30
3.7.0 | ROOF LEVEL
BEAMS
3.7.01 | 1000 | x | 350 | mm Beam RB1 |  | m3 | 3.78
3.7.02 | 600 | x | 300 | mm Beam RB2 |  | m3 | 2.49
3.7.03 | 450 | x | 200 | mm Beam RB3 |  | m3 | 0.35
3.7.04 | 450 | x | 200 | mm Beam RB4 |  | m3 | 2.2
SLABS
3.7.05 |  |  | 140 | mm thk Concrete Slab |  | m3 | 16.24
3.7.06 |  |  | 130 | mm thk Concrete Slab |  | m3 | 7.41
3.8.00 | OTHER WORKS
Lintel and Sill beams
3.8.01 | 150 | x | 150 | mm Lintel Beam LB | item | item | 1
3.8.02 | 150 | x | 150 | mm Sill Beam SB | item | item | 1
RC TANK
3.8.03 |  |  |  | Fire water tank, 9000gallons | item | no | 1
3.9.0 | Ground Water Well
3.9.1 |  |  | Completion of RC Concrete Groundwater well, Diameter of the well is 2 mete rand thickness of the well is 100mm, the water level must be a minimum of 2 meters in low tide, reinforcement of the well is 10mm bars 250X250mm B/W. The rate also must include a 150mm thick RC slab. |  |  | Item | 1
3.10.00 | BOUNDARY WALL 1.2METER HEIGHT.
3.10.1 |  |  | 150mm thick Solid block single wall 1.2m Height of boundary wall (from ground level ) surrounded by the land area with oil based paint system with textured finish, Rates must includes to remove existing Boundary fence with masonary walls and foundation. Footing: 600 x 600mm (T10 @150 BW) Foundation Beam: 300 x 200mm (4T12, R6@150) Columns (at 3.5M span): 200 x 200mm (4T12, R6@150) Foundation Depth: 750mm Capping Beam: 150 x 150mm (4T10, R6@150) |  |  | meter | 395
3.10.00 |  |  |  | TOTAL OF BILL №: 03 - Carried Over To Summary
4.0.00 |  |  |  | Bill №: 04 - MASONRY
4.1.00 | GENERAL
|  |  | (a) | Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leavingholes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashing, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good.
|  |  | (b) | Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:5 i.e. cement: river sand) shall be of OPC & free form salt.
|  |  | (c) | Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance.
|  |  | (d) | Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance.
|  |  | (e) | All works complete as per drawing and specification
4.2.00 | BRICK WORK
150mm thk masonry solid block wall including making of bricks, bricks laid to form alternate courses of headers and stretchers, laid on and inc. mortar. (EXTERNAL WALLS)
4.2.01 |  |  |  | GROUND FLOOR |  | m2 | 983.6
4.2.02 |  |  |  | FIRST FLOOR |  | m2 | 663.635
4.2.03 |  |  |  | TERRACE FLOOR |  | m2 | 86.25
150mm thk masonry solid block wall including making of bricks, bricks laid to form alternate courses of headers and stretchers, laid on and inc. mortar (INTERNAL WALLS).
4.2.04 |  |  |  | GROUND FLOOR |  | m2 | 175.615
4.2.05 |  |  |  | FIRST FLOOR |  | m2 | 179.99
4.2.06 |  |  |  | TERRACE FLOOR |  | m2 | 14.43
4.3.00 | PLASTERING
20mm thk cement plaster on external surface as specified on the drawing. Waterproofed with Sika product or equivalent.
4.3.01 |  |  |  | GROUND FLOOR |  | m2 | 1152.0625
4.3.02 |  |  |  | FIRST FLOOR |  | m2 | 1054.862
4.3.03 |  |  |  | TERRACE FLOOR |  | m2 | 723.85
16mm thk cement plaster on internal surface as specified on the drawing
4.3.04 |  |  |  | GROUND FLOOR |  | m2 | 2136.384
4.3.05 |  |  |  | FIRST FLOOR |  | m2 | 1462.594
4.3.06 |  |  |  | TERRACE FLOOR |  | m2 | 150.385
4.4.00 | CEMENT SCREED
50mm thk cement screed waterproofed with SIKA product or equivalent
4.4.01 |  |  |  | GROUND FLOOR |  | m2 | 2235.39
4.4.02 |  |  |  | FIRST FLOOR |  | m2 | 1766.15
4.4.03 |  |  |  | TERRACE FLOOR |  | m2 | 1516.7
4.5.00 |  |  |  | TOTAL OF BILL №: 04 - Carried Over To Summary
5.0.00 |  |  |  | Bill №: 05 - CARPENTRY
5.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
|  |  | (b) | All works complete as per drawing and specification
5.2.00 | FIXED FURNITURE
Fixed counter/furniture as per drawing
GROUND FLOOR
5.2.01 |  |  |  | Nurse station counter - OPD |  | no | 1
5.2.02 |  |  |  | Nurse station counter - Trolley exchange |  | no | 1
5.2.03 |  |  |  | Nurse station counter - Suspected ward |  | no | 1
5.2.04 |  |  |  | Nurse station counter - Isolation ward |  | no | 1
5.2.05 |  |  |  | Xray room cubical with counter |  | no | 1
5.2.06 |  |  |  | Main Reception counter |  | no | 1
5.2.07 |  |  |  | Flu clinic counter |  | no | 1
5.2.08 |  |  |  | Pharmacy counter |  | no | 1
FIRST FLOOR
5.2.09 |  |  |  | Nurse station counter - NICU |  | no | 1
5.2.10 |  |  |  | Nurse station counter - Ward |  | no | 1
5.2.11 |  |  |  | Wardrobe - private rooms |  | no | 4
5.2.12 |  |  |  | Reception counter |  | no | 1
5.3.00 | DRY WALL
USG boral impactstop wall board wall as specified in the drawing. (INTERNAL WALLS)
5.3.01 |  |  |  | GROUND FLOOR |  | m2 | 1875.81
5.3.02 |  |  |  | FIRST FLOOR |  | m2 | 1442.13
5.4.00 | TIMBER ROOF FRAMING
5.4.01 | 18 | x | 250 | mm Facia Board (Fiber cement board). |  | m | 64.3
Supplying and installation of Furniture
5.4.02 |  |  |  | Office Table, 1200mm ( table should be solid wood) with drawer. |  | No | 20
5.4.03 |  |  |  | Office Table 1500mm ( table should be solid wood) with drawer. |  | No | 4
5.4.04 |  |  |  | Executive chair, high back |  | No | 10
5.4.05 |  |  |  | Secretary chair , high back. |  | No | 15
5.4.06 |  |  |  | Secretary chair , Low back. |  | No | 20
5.4.07 |  |  |  | Meeting room chair Material: Iron/Aluminum Surface treatment: Spray painting finished. Seat and back: Hight-density sponge, minimum 2.5" thick seat cushion |  | No | 50
5.4.08 |  |  |  | Folding Meeting Table, 1400X600mm, Specifications: Lockable castorsm Aluminum components Feature: Chrome with polished aluminum feet, Easy tilt mechanism for compact storage, Table surface: Scratch resistant, Natural Ash. |  | NO | 15
5.4.09 |  |  |  | Supply and installation of 4 seater Airport Bench set, Armrest/Leg/bracket: Die-casting molding of high strength aluminum alloy. Seat: Numerical control hydraulic molding of high quality cold rolling steel plate. Sponge: Cold consolidation and foam-forming of high density and super soft PU. Beam: metal tube with a diamond shape. Coating: Electrostatic coating after Rust-proof treatment, electroplated polishing. |  | no | 20
5.4.10 |  |  |  | Design and Fabrication of Wooden shelves at Medical Store room, length of Shelf is 1.2M, Width is 0.4m and heigh is 2M, 18mm thick Plywood with both side paint to be used. Frame with 4 shelf, |  | No | 20
FIXED FURNITURE
Fixed counter/furniture as per drawing
GROUND FLOOR
5.4.11 |  |  |  | Main Reception counter |  | no | 1
5.4.12 |  |  |  | Nurse station counter - isolation ward |  | no | 1
5.4.13 |  |  |  | Nurse station counter - suspected ward |  | no | 1
5.4.14 |  |  |  | Nurse station counter - emergency department |  | no | 1
5.4.15 |  |  |  | Triage counter |  | no | 1
5.4.16 |  |  |  | Xray room cubical with counter with LED glass |  | no | 1
5.4.17 |  |  |  | Pharmacy counter |  | no | 1
FIRST FLOOR
5.4.18 |  |  |  | Laboratory working area |  | no | 1
5.4.19 |  |  |  | Centeral reception counter |  | no | 1
5.4.20 |  |  |  | Nurse station counter - labour |  | no | 1
5.4.21 |  |  |  | Nurse station counter - NICU |  | no | 1
5.4.22 |  |  |  | Wardrobe - private rooms |  | no | 2
Supplying and installation of Furniture
5.4.23 |  |  |  | Double bed, |  | Item | 2
5.4.24 |  |  |  | Single bed, |  | Item | 8
5.4.25 |  |  |  | Wordrobe 2 door panel, |  | Item | 8
5.4.26 |  |  |  | Dressing table, |  | Item | 8
5.4.27 |  |  |  | Double mattress, 6 inch thick. |  | Item | 2
5.4.28 |  |  |  | Single mattress, 6 inch thick. |  | Item | 8
5.4.29 |  |  |  | Dining table, for 4 people with chairs |  | Item | 4
5.4.30 |  |  |  | Sofa set, 1 sofa for 2 person and 1 sofa for 1 person with coffee table. |  | Item | 4
5.4.31 |  |  |  | Sofa set, 1 sofar for 2 person and 2 sofa for 1 person with coffee table. |  | Item | 4
5.4.32 |  |  |  | Display TV 65" with TV reck |  | Item | 8
5.4.33 |  |  |  | Electric stove, No of burners 3. |  | Item | 8
5.4.34 |  |  |  | Automatic washing machine, minimum 8KG |  | Item | 8
Kitchen cupbord
5.4.35 |  |  |  | Design and fabrication of kichen cupboard with over hed cupbord. Rates includes to sink and hood, length of kitchen cupboard is same as floor plan. |  | Item | 4
5.5.00 |  |  |  | TOTAL OF BILL №: 05 - Carried Over To Summary
6.0.00 |  |  |  | Bill №: 06 - STRUCTURAL METAL WORKS
6.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all fabrication work, welding, marking, drilling for bolts incl. those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
|  |  | (b) | Rates shall include for fabrication and erection and temporary supports and fixing into position.
|  |  | (c) | All works complete as per drawing and specification
6.2.00 |  |  |  | Staircase Handrailing - Main building
SS/Timber railing handle, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
6.2.01 |  |  |  | Ground to First Floor |  | m | 9.75
6.2.02 |  |  |  | First - Terrace Floor |  | m | 11.12
6.3.00 |  |  |  | Staircase Handrailing - Accommodation block
SS/Timber railing handle, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
6.3.01 |  |  |  | Ground to First Floor |  | m | 6.95
6.4.00 |  |  |  | Glass Handrailing
SS SHS railing handle with 12mm thick tempered glass, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
6.4.01 |  |  |  | Balcony railing - Main building |  | m | 28.1
6.4.02 |  |  |  | Balcony railing - Accommodation building |  | m | 38
6.5.00 |  |  |  | Ramp Handrailing
SS pipe railing handle, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
6.5.01 |  |  |  | Ramp |  | m | 21.1
6.6.00 |  |  |  | Roof Truss / Framing
Steel truss with GI pipe top , bottom chord and GI pipe diagonal member with 50mm thick bracingas per drawing.
Accommodation Block
6.6.01 |  |  | 6900 | mm trruss span, TR1 |  | no | 8
6.6.02 |  |  |  | 50x100x2mm C purlins |  | m | 331.1
6.6.03 |  |  |  | Bracing pipe Top and Bottom |  | m | 47.3
Service Block
6.6.07 |  |  | 7750 | mm trruss span, TR2 |  | no | 10
6.6.08 |  |  |  | 50x100x2mm C purlins |  | m | 331.1
6.6.09 |  |  |  | Bracing pipe Top and Bottom |  | m | 47.3
Portico
6.6.10 |  |  | 6000 | mm trruss span, TR1 |  | no | 4
6.6.11 |  |  | 6300 | mm trruss span, TR2 |  | no | 1
6.6.12 |  |  | 7434 | mm trruss span, TR3 |  | no | 1
6.6.13 |  |  | 4391 | mm trruss span, TR4 |  | no | 1
6.6.14 |  |  | 2088 | mm trruss span, TR5 |  | no | 1
6.6.15 |  |  | 2822 | mm trruss span, TR6 |  | no | 1
6.6.16 |  |  | 5265 | mm trruss span, TR7 |  | no | 4
6.6.17 |  |  | 2662 | mm trruss span, TR7 |  | no | 1
6.6.18 |  |  | 4746 | mm trruss span, TR8 |  | no | 2
6.6.19 |  |  | 6854 | mm trruss span, TR9 |  | no | 2
6.6.20 |  |  |  | 50x100x2mm C purlins |  | m | 350.5
6.9.00 |  |  |  | ALUMINIUM FINS
Steel grill as per drawing
TERRACE FLOOR
6.9.01 |  |  |  | 1700mm x 6000mm |  | no | 2
6.9.02 |  |  |  | 825mm x 6000mm |  | no | 1
6.10.00 |  |  |  | TOTAL OF BILL №: 06 - Carried Over To Summary
7.0.00 |  |  |  | Bill №: 07 - CEILING
7.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
|  |  | (b) | All works complete as per drawing and specification
7.2.00 |  |  |  | CEILING
False flat ceiling with 12mm calcium silicate board under 50x50mm ceiling joist as per drawing - CF01
7.2.01 |  |  |  | Ground floor |  | m2 | 166.1
7.2.02 |  |  |  | First floor |  | m2 | 195.2
7.2.03 |  |  |  | Terrace floor |  | m2 | 34.2
False flat ceiling with 12mm thick gypsum board under 50x50mm ceiling joist as per drawing - CF02
7.2.04 |  |  |  | Ground floor |  | m2 | 1782.9
7.2.05 |  |  |  | First floor |  | m2 | 1448.3
7.3.00 |  |  |  | TOTAL OF BILL №: 07 - Carried Over To Summary
8.0.00 |  |  |  | Bill №: 08 - WINDOWS, SCREENS & LIGHTS
8.1.00 | GENERAL
|  |  | (a) | Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
|  |  | (b) | Rates shall include for door frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings.
|  |  | (c) | Sizes are given overall outside dimensions of actual doors and windows.
|  |  | (d) | Thickness and sizes of glass panels are shown on the Drawings and doors and windows schedule
|  |  | (e) | Rates shall include for all painting as specified
|  |  | (f) | Rates shall include all items specified in the door schedule and specification.
|  |  | (g) | Frames and sashes to be minimum 60 micron black powder coated aluminium other wise specified.
|  |  | (h) | Thickness of aluminum profile must be minimum 2mm thick.
|  |  | (i) | All works complete as per drawing and specification
8.3.00 | WINDOWS
8.3.01 | 1300 | x | 3000 | SF1 - Aluminium frame window |  | nr | 1
8.3.02 | 1500 | x | 3000 | SF1a - Aluminium frame window |  | nr | 2
8.3.03 | 1500 | x | 2100 | SF1b - Aluminium frame window |  | nr | 2
8.3.04 | 2000 | x | 3000 | SF2 - Aluminium frame window |  | nr | 6
8.3.05 | 3300 | x | 3000 | SF3 - Aluminium frame window |  | nr | 1
8.3.06 | 4125 | x | 3000 | SF3a - Aluminium frame window |  | nr | 1
8.3.07 | 3375 | x | 3000 | SF4 - Aluminium frame window |  | nr | 2
8.3.08 | 700 | x | 600 | V1 - Aluminium frame window |  | nr | 6
8.3.09 | 800 | x | 1400 | V2 - Aluminium frame window |  | nr | 8
8.3.10 | 2000 | x | 1200 | V3 - Aluminium frame window |  | nr | 14
8.3.11 | 1000 | x | 1000 | W1 - Aluminium frame window |  | nr | 7
8.3.12 | 1000 | x | 1000 | W1b - Aluminium frame window |  | nr | 1
8.3.13 | 1825 | x | 1000 | W2 - Aluminium frame window |  | nr | 2
8.3.14 | 5700 | x | 1300 | W2a - Aluminium frame window |  | nr | 2
8.3.15 | 2000 | x | 1000 | W2b - Aluminium frame window |  | nr | 3
8.3.16 | 1200 | x | 600 | W2c - Aluminium frame window |  | nr | 2
8.3.17 | 2500 | x | 2000 | W3 - Aluminium frame window |  | nr | 1
8.3.18 | 3000 | x | 2000 | W3a - Aluminium frame window |  | nr | 2
8.3.19 | 2400 | x | 1000 | W3b - Aluminium frame window |  | nr | 27
8.3.20 | 2150 | x | 1000 | W4 - Aluminium frame window |  | nr | 4
8.3.21 | 3650 | x | 1000 | W4b - Aluminium frame window |  | nr | 2
8.3.22 |  |  |  | Supply and complete installation of top quality Hospital grade bed side curtain including railing/Track. Length of rail/track is 6870mm, |  | Item | 41
8.3.23 |  |  |  | Supply and complete installation of window curtains and vertical bliends |  | Item | 1
8.4.00 |  |  |  | TOTAL OF BILL №: 08 - Carried Over To Summary
9.0.00 |  |  |  | Bill №: 09 - DOORS, SHUTTERS & HATCHES
9.1.00 | GENERAL
|  |  | (a) | Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
|  |  | (b) | Rates shall include for door frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings.
|  |  | (c) | Sizes are given overall outside dimensions of actual doors and windows.
|  |  | (d) | Thickness and sizes of glass panels are shown on the Drawings and doors and windows schedule.
|  |  | (e) | Rates shall include for all painting as specified
|  |  | (f) | Rates shall include all items specified in the door schedule and specification.
|  |  | (g) | Frames and sashes to be 25-60 micron black powder coated aluminium other wise specified.
|  |  | (g) | All solid timber doors are teak timber or equivalent.
9.2.00 | DOORS
9.2.01 | 2000 | x | 3000 | AD1 - Aluminium frame door |  | nr | 3
9.2.02 | 2000 | x | 3000 | AD2 - Aluminium frame door |  | nr | 2
9.2.03 | 1200 | x | 3000 | AD3 - Aluminium frame door |  | nr | 3
9.2.04 | 1000 | x | 3000 | AD4 - Aluminium frame door |  | nr | 2
9.2.05 | 1000 | x | 2100 | AD5 - Aluminium frame door |  | nr | 8
9.2.06 | 1000 | x | 2100 | AD5a - Aluminium frame door |  | nr | 6
9.2.07 | 1500 | x | 2100 | AD6 - Aluminium frame door |  | nr | 8
9.2.08 | 4500 | x | 3000 | AD7 - Aluminium frame door |  | nr | 1
9.2.09 | 2000 | x | 3000 | AD8 - Aluminium frame door |  | nr | 7
9.2.10 | 800 | x | 2100 | D1 - Timber frame door |  | nr | 8
9.2.11 | 800 | x | 2100 | D2 - Timber frame door |  | nr | 10
9.2.12 | 2000 | x | 2000 | G1 - Wrought iron gate |  | nr | 2
9.2.13 | 3000 | x | 2000 | G2 - Wrought iron gate |  | nr | 1
9.2.14 | 1500 | x | 2100 | LD1 - Solid timber door |  | nr | 2
9.2.15 | 1200 | x | 2100 | O - opening curve |  | nr | 2
9.2.16 | 1000 | x | 2100 | PD1 - Plywood door |  | nr | 23
9.2.17 | 800 | x | 2100 | PD2 - Plywood door |  | nr | 29
9.2.18 | 700 | x | 2100 | PD3 - Plywood door |  | nr | 2
9.2.19 | 3500 | x | 2400 | RS1 - Roller shutter door |  | nr | 1
9.2.20 | 1500 | x | 2100 | TD1 - Aluminium door |  | nr | 5
9.2.21 | 1000 | x | 2100 | TD2 - Timber door |  | nr | 31
9.2.22 | 1000 | x | 2100 | TD3 - Timber door |  | nr | 35
9.2.23 | 800 | x | 2100 | TD4 - Timber door |  | nr | 25
9.2.24 | 800 | x | 2100 | TD5 - Timber door |  | nr | 18
9.2.25 | 1150 | x | 2100 | TD6 - Timber door |  | nr | 4
9.2.26 | 1500 | x | 2100 | TD7 - Timber door |  | nr | 4
9.2.27 | 1500 | x | 2100 | TD8 - Timber door |  | nr | 4
9.2.28 | 1500 | x | 2100 | TD9 - Timber door |  | nr | 1
9.3.00 |  |  |  | TOTAL OF BILL №: 09 - Carried Over To Summary
10.0.00 |  |  |  | Bill №: 10 - DECORATIONS
10.1.00 | GENERAL
|  |  | (a) | Rates shall include for: the provision, erection and removal of scaffolding, preparation, wall putty application, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door & window furniture.
|  |  | (b) | All painting work shall be carried in accordance with the Specifications.
10.2.00 |  |  |  | WALL PAINTING
EXTERNAL SURFACES: Exterior grade paint finish as specified - WF01
10.2.01 |  |  |  | GROUND FLOOR |  | m2 | 1265.135
10.2.02 |  |  |  | FIRST FLOOR |  | m2 | 909.37
10.2.03 |  |  |  | TERRACE FLOOR |  | m2 | 720.66
INTERNAL SURFACES: Interior grade paint finish as specified - WF03
10.2.04 |  |  |  | GROUND FLOOR |  | m2 | 3847.24
10.2.05 |  |  |  | FIRST FLOOR |  | m2 | 3907.05
10.2.06 |  |  |  | TERRACE FLOOR |  | m2 | 117.9
INTERNAL SURFACES: Latex paint finish as specified - WF04
10.2.07 |  |  |  | GROUND FLOOR |  | m2 | 415.12
10.3.00 |  |  |  | VINYLE FINISH
INTERNAL SURFACES: Vinyl wall finish as specified - WF05
10.3.01 |  |  |  | GROUND FLOOR |  | m2 | 1718.93
10.4.00 |  |  |  | LAMINATE FINISH
INTERNAL SURFACES: High pressure laminate wall finish as specified - WF07
10.4.01 |  |  |  | FIRST FLOOR |  | m2 | 34.86
10.5.00 |  |  |  | CLADDING
Aluminium wall cladding - WF02
10.5.01 |  |  |  | GROUND FLOOR |  | m2 | 74.96
10.5.02 |  |  |  | FIRST FLOOR |  | m2 | 5.2
10.6.00 |  |  |  | CEILING PAINTING
Anti microbial paint coatings as specified in specification and finishing schedule - CF01
10.6.01 |  |  |  | GROUND FLOOR |  | m2 | 166.1
10.6.02 |  |  |  | FIRST FLOOR |  | m2 | 195.2
10.6.03 |  |  |  | TERRACE FLOOR |  | m2 | 34.2
Anti microbial paint coatings as specified in specification and finishing schedule - CF02
10.6.04 |  |  |  | GROUND FLOOR |  | m2 | 1782.9
10.6.05 |  |  |  | FIRST FLOOR |  | m2 | 1448.3
Emulsion paint finish ground smoothing with putty as specified in specification and finishing schedule - CF03
10.6.06 |  |  |  | GROUND FLOOR |  | m2 | 246.2
10.6.07 |  |  |  | FIRST FLOOR |  | m2 | 80
10.6.08 |  |  |  | TERRACE FLOOR |  | m2 | 61.1
10.7.00 |  |  |  | TOTAL OF BILL №: 10 - Carried Over To Summary
11.0.00 |  |  |  | Bill №: 11 - FINISHES
11.1.00 | GENERAL
|  |  | (a) | Rates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing.
11.2.00 |  |  |  | FLOOR PAINTING
Grey epoxy paint finish on Screed with waterproofing - FF11
11.2.01 |  |  |  | Ground Floor |  | m2 | 28.4
11.2.02 |  |  |  | First Floor |  | m2 | 53
11.2.03 |  |  |  | Terrace Floor |  | m2 | 1482.5
Grey epoxy paint finish on Screed - FF12
11.2.04 |  |  |  | Ground Floor |  | m2 | 64.64
11.2.05 |  |  |  | First Floor |  | m2 | 84.1
11.2.06 |  |  |  | Terrace floor |  | m2 | 34.2
11.3.00 |  |  |  | FLOOR TILING
1200 x 1200mm polished full body homogeneous floor tile - FF01
11.3.01 |  |  |  | Ground Floor |  | m2 | 21.3
11.3.02 |  |  |  | First Floor |  | m2 | 49.9
1200 x 1200 Semi polished full body homogeneous floor tile - FF02
11.3.03 |  |  |  | Ground Floor |  | m2 | 649.6
11.3.04 |  |  |  | First Floor |  | m2 | 407.8
800 x 800 Semi polished full body homogeneous floor tile - FF03
11.3.05 |  |  |  | Ground Floor |  | m2 | 257.9
11.3.06 |  |  |  | First Floor |  | m2 | 300.5
600 x 600 Matte full body homogeneous non slip floor tile - FF04
11.3.07 |  |  |  | Ground Floor |  | m2 | 438.6
11.3.08 |  |  |  | First Floor |  | m2 | 188.4
600 x 600 Matte full body homogeneous non slip outdoor floor tile - FF05
11.3.09 |  |  |  | Ground Floor |  | m2 | 248.6
11.3.10 |  |  |  | First Floor |  | m2 | 51.3
600 x 600 Matte full body homogeneous non slip floor tile - FF06
11.3.11 |  |  |  | Ground Floor |  | m2 | 84.1
11.3.12 |  |  |  | First Floor |  | m2 | 85.25
300 x 1200 full body Matte homogeneous Tiles - Staircase - FF07
11.3.13 |  |  |  | Ground Floor |  | m2 | 18.1
11.3.14 |  |  |  | First Floor |  | m2 | 16.7
Homogeneous vinyl flooring for sterile area - FF08
11.3.15 |  |  |  | Ground Floor |  | m2 | 206.9
11.3.16 |  |  |  | First Floor |  | m2 | 503.5
Homogeneous mosaic tile finish - FF13
11.3.17 |  |  |  | Ground Floor |  | m2 | 44.2
Permanently Static dissipative pressed homogeneous vinyl flooring for sterile area - FF09
11.3.18 |  |  |  | Ground Floor |  | m2 | 217.25
11.3.19 |  |  |  | First Floor |  | m2 | 25.7
11.4.00 |  |  |  | PAVING
Paver block - FF10
11.4.01 |  |  |  | Ground Floor |  | m2 | 512
11.5.00 |  |  |  | WALL TILING
300 x 600 Matte full body Homogeneous wall Tiles upto ceiling height - WF06
11.5.01 |  |  |  | Ground Floor |  | m2 | 706.09
11.5.02 |  |  |  | First Floor |  | m2 | 613.99
11.6.00 |  |  |  | TOTAL OF BILL №: 11 - Carried Over To Summary
12.0.00 |  |  |  | Bill №: 12 - ROOFING
12.1.00 | GENERAL
|  |  | (a) | Rates shall include for: fair edges, dressing over angel fillets, roof sealant, turning into grooves, all other labours, circular edges, nails, screws and other fixings and laps.
|  |  | (b) | All works complete as per drawing and specification
12.2.00 |  |  |  | ROOF COVERING
12.2.01 |  |  |  | BHP Lysaght Trimdek Hi-Ten or equivalent roofing sheet, over C purlin frame including all fixings, fixed in accordance with manufacturer's instructions. Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent |  | m² | 384.7005
12.2.02 |  |  |  | 50mm mineral wool insulation inbetween C sections |  | m² | 384.7005
12.2.03 |  |  |  | 12mm clear polycarbonate sheet on top of portico purlins as specified in the drawing |  | m² | 216
12.3.00 |  |  |  | CAPPING
12.3.01 |  |  |  | Lysaght ridge Flashing as per drawing, Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent |  | m | 47.7
12.3.02 |  |  |  | Lysaght Flashing as per drawing, Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent |  | m | 34
12.4.00 |  |  |  | GUTTER
12.4.01 |  |  |  | Gutter 200 x 250mm with gutter strap fixed to purlins, Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent |  | m | 47.7
12.5.00 |  |  |  | DRAIN PIPE
12.5.01 |  |  |  | 75mm dia. Drain pipe with wiremesh gutter strainer |  | item | 1
12.6.00 |  |  |  | FASCIA BOARD
12.6.01 | 18 | x | 200 | mm Fascia Board ( fiber cement board). |  | item | 1
12.6.00 |  |  |  | TOTAL OF BILL №: 12 - Carried Over To Summary
13.0.00 |  |  |  | Bill №: 13 - HYDRAULICS AND DRAINAGE
13.1.00 | HYDRAULICS
13.2.00 | GENERAL
|  |  | (a) | Rates shall include for: sockets, running joints, connectors, elbows, junctions, valves, reducers, expansion joints; backnuts and similar; incidental fittings, clips, saddles, brackets, straps, hangers, screws, nails and fixing complete including cutting and forming holes; excavating, laying pipes and backfilling trenches.
|  |  | (b) | Rate shall also includes the provision for pipe marking, and tagging as indicated in the specifications.
|  |  | (c) | Rate shall also includes the provisional sum for testing such as but not limited to hydrostatic pressure test for pressure line, and gravity leak test for all gravity lines which was stipulated in the specifications., chlorination/disinfection of network and tanks, and testing and commissioning.
|  |  | (d) | Rate includes the complete delivery of the system and is of working condition.
|  |  | (e) | All pipe work and fittings shall be uPVC.
|  |  | (f) | All works complete as per drawing and specification
13.3.00 |  |  |  | FRESH WATER SUPPLY NETWORK
13.3.01 |  |  |  | GROUND FLOOR |  | item | 1
13.3.02 |  |  |  | FIRST FLOOR |  | item | 1
13.4.00 |  |  |  | HOT WATER SUPPLY PIPEWORK
13.4.01 |  |  |  | GROUND FLOOR |  | item | 1
13.4.02 |  |  |  | FIRST FLOOR |  | item | 1
13.5.00 |  |  |  | RAIN PIPEWORK
13.5.01 |  |  |  | GROUND FLOOR |  | item | 1
13.5.02 |  |  |  | FIRST FLOOR |  | item | 1
13.5.03 |  |  |  | TERRACE FLOOR |  | item | 1
13.6.00 |  |  |  | SANITARY FITTINGS
Sanitary fittings including installations as per drawings
COMMON AREAS /GENERAL TOILETS :
13.6.01 |  |  |  | Floor drain gully trap |  | nr | 56
13.6.02 |  |  |  | Floor drain gully trap FG |  | nr | 73
13.6.03 |  |  |  | Floor clean out |  | nr | 36
13.6.04 |  |  |  | Ceiling clean out |  | nr | 22
13.6.05 |  |  |  | Water closet (Anti bacterial type), dual top flush |  | nr | 40
13.6.06 |  |  |  | Muslim Shower |  | nr | 40
13.6.07 |  |  |  | Wash basin |  | nr | 36
13.6.08 |  |  |  | Wash basin tap |  | nr | 36
13.6.09 |  |  |  | Mirror set |  | nr | 36
13.6.10 |  |  |  | Basin with built in cupboard and granite top - dirty / clean utility |  | nr | 16
13.6.11 |  |  |  | Basin elbow turn tap - dirty / clean utility / autoclave |  | nr | 16
13.6.12 |  |  |  | ceramic laboratory sink 620x480x255mm with sink with built in cupboard and granite top |  | nr | 7
13.6.13 |  |  |  | Sink elbow turn tap |  | nr | 7
13.6.14 |  |  |  | Sink with built in cupboard and granite top - private room |  | nr | 4
13.6.15 |  |  |  | Sink elbow turn tap - private room |  | nr | 4
13.6.16 |  |  |  | Shower |  | nr | 19
13.6.17 |  |  |  | Water heater |  | nr | 4
13.6.18 |  |  |  | Hose bibb |  | nr | 7
13.6.19 |  |  |  | Railing set (horizontal & vertical) |  | nr | 19
ACCOMMODATION TOILETS :
13.6.22 |  |  |  | Water closet (Anti bacterial type), dual top flush |  | nr | 6
13.6.23 |  |  |  | Muslim Shower |  | nr | 6
13.6.24 |  |  |  | Wash basin |  | nr | 6
13.6.25 |  |  |  | Toilet paper holder |  | nr | 6
13.6.26 |  |  |  | Soap holder |  | nr | 6
13.6.27 |  |  |  | Mirror set |  | nr | 6
13.6.28 |  |  |  | Sink with built in kitchen cupboard and granite top |  | nr | 4
13.6.29 |  |  |  | Sink tap |  | nr | 4
13.6.30 |  |  |  | Railing set |  | nr | 6
13.6.31 |  |  |  | Floor drain gully trap |  | nr | 4
13.6.32 |  |  |  | Floor drain gully trap FG |  | nr | 17
13.6.33 |  |  |  | Floor clean out |  | nr | 6
13.6.34 |  |  |  | Water heater |  | nr | 6
13.6.35 |  |  |  | Ceiling/Wall clean out |  | nr | 14
DRAINAGE
13.7.00 |  |  |  | GENERAL
|  |  | (a) | Rates shall include for: excavation, maintaining faces of drain pipe trenches and pits, backfilling, disposal of surplus spoil; bends, junctions, reducers, expansion joints and all joints and other incidental materials.
|  |  | (b) | All pipeworks shall be uPVC.
|  |  | (c) | All works complete as per drawing and specification
13.8.00 |  |  |  | DRAINAGE PIPEWORKS
13.8.01 |  |  |  | GROUND FLOOR |  | item | 1
13.8.02 |  |  |  | FIRST FLOOR |  | item | 1
13.9.00 |  |  |  | WATER METERS
13.9.01 |  |  |  | MWSC Water Meters |  | item | 1
13.10.00 |  |  |  | OTHERS
13.10.01 |  |  |  | Greese trap |  | item | 1
13.10.02 |  |  |  | Manhole |  | item | 1
13.10.03 |  |  |  | Area Drain 300x300mm |  | nr | 23
13.10.04 |  |  |  | Scupper drain outlet |  | nr | 19
13.11.00 |  |  |  | VALVES FOR PIPE LINES
13.11.01 |  |  |  | Gate vale |  | nr | 114
13.11.02 |  |  |  | Check valves |  | nr | 2
13.12.00 |  |  |  | WATER PUMP
13.12.01 |  |  |  | Designg supply and installation of Ground water pump, Deavy or equivalent. |  | Item | 2
13.12.02 |  |  |  | Designg supply and installation of Fresh water pump, Deavy or equivalent. |  | Item | 2
13.13.00 |  |  |  | SCRUB SINK
13.13.01 |  |  |  | Supply and Complete instalaation of Scrub sink, Inspital SK90.02 dual sink or equivalent. |  | Item | 1
13.14.00 |  |  |  | TOTAL OF BILL №: 13 - Carried Over To Summary
14.0.00 |  |  |  | Bill №: 14 - ELECTRICAL INSTALLATIONS
14.1.00 | GENERAL
|  |  | (a) | Design, provide and install electrical network for the entire building complete in accordance to standards set by the local governing body STELCO / FENAKA.
|  |  | (b) | The following items and description and the drawings HULS -01 to HULS-05 are given as a guidance as to the nature of the information required to be returned by the contractor. Should they not be appropriate the contractor should provide a similar BOQ using the Additions/Ommisions sheets provided at the back of this BOQ.
|  |  | (c) | The cost shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
|  |  | (d) | The cost shall also include for trenching including: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil.
|  |  | (e) | Rates for electrical isolators, conduits, fittings, equipment and similar items shall include for: all fixings to various building surfaces.
|  |  | (f) | A light fixture is measured as one point; switch end of wire is not included in the quantity.
|  |  | (g) | A point wiring for power points is measured (regardless of 1 gang, 2 gang etc) as one point for each socket outlet; other end of wire is not included in the quantity.
|  |  | (h) | Contractor shall provide all cabling, wiring, conduits, etc. within the site boundaries. Cabling, wiring, conduits etc. outside the site boundaries are not included under this Contract.
|  |  | (i) | All works complete as per drawing and specification
14.2.00 | MAINS CONNECTION & BOARD
14.2.01 |  |  |  | Completion of 3 phase electrical main. |  | item | 1
14.2.01 |  |  |  | Panel board |  | nr | 1
14.3.00 | ELECTRICAL BOARDS
Complete installation, including for all cabling, wiring, connections, earthing, painting, testing and similar of:
14.3.01 |  |  |  | Light, Power & AC Distribution Board |  | nr | 55
14.4.00 | ELECTRICAL WIRING
Electrical wiring with copper conductor cable in conduits in walls and in casing on soffits of slab as specified to:
14.4.01 |  |  |  | Wiring To Lights, Fittings socket |  | pt | 1850
14.5.00 | LIGHTING
14.5.01 |  |  |  | LED recessed light type 1 (18W) |  | nr | 24
14.5.02 |  |  |  | LED recessed light type 2 (12W) |  | nr | 115
14.5.03 |  |  |  | 600x600 LED square diffuser with T5 fitting (12W) |  | nr | 350
14.5.04 |  |  |  | LED down light (18W) weatherproof |  | nr | 8
14.5.05 |  |  |  | Outdoor Wall light 12W weather proof |  | nr | 41
14.5.06 |  |  |  | Troffer diffuser with T5 fitting 28W |  | nr | 47
14.5.07 |  |  |  | LED strip cover light IP65 (8W) |  | nr | 45
14.5.08 |  |  |  | LED recessed light type 3 (12W) |  | nr | 83
14.5.09 |  |  |  | LED indoor wall light up/dn (8W) |  | nr | 1
14.5.10 |  |  |  | LED outdoor wall light up/dn (8W) weatherproof |  | nr | 27
14.5.11 |  |  |  | LED spike light (3W) |  | nr | 15
14.6.00 | SWITCHES
13.6.01 |  |  |  | Light switch 1gang |  | nr | 211
13.6.02 |  |  |  | Light switch 2gang |  | nr | 118
13.6.03 |  |  |  | Light switch 3gang |  | nr | 27
13.6.04 |  |  |  | Fan switch |  | nr | 11
14.7.00 | SOCKETS
14.7.01 |  |  |  | 13A power outlet |  | nr | 270
14.7.02 |  |  |  | 13A Twin socket outlet |  | nr | 256
14.7.03 |  |  |  | 13A UPS socket outlet |  | nr | 72
14.7.04 |  |  |  | 8 power points on envirom head wall |  | nr | 78
14.7.05 |  |  |  | 15A power point |  | nr | 10
14.7.06 |  |  |  | Flex. power outlet w/ cover plate (exhaust fan) |  | nr | 11
14.7.07 |  |  |  | power over ethernet outlet |  | nr | 13
14.7.08 |  |  |  | 13A sockets for toilets |  | nr | 6
14.8.00 | FAN
14.8.01 |  |  |  | Ceiling Fan |  | nr | 11
14.9.00 | IT
14.9.01 |  |  |  | Two gang TV socket outlet |  | nr | 8
14.9.02 |  |  |  | Paging mic |  | nr | 15
14.9.03 |  |  |  | Volume controller |  | nr | 15
14.9.04 |  |  |  | Ceiling speaker |  | nr | 67
14.9.05 |  |  |  | Wall speaker |  | nr | 9
14.9.06 |  |  |  | Hone speaker |  | nr | 25
14.9.07 |  |  |  | Proximity card reader |  | nr | 33
14.9.08 |  |  |  | exit switch |  | nr | 33
14.9.09 |  |  |  | emergency door release |  | nr | 33
14.9.10 |  |  |  | nurse station panel room indicator |  | nr | 15
14.9.11 |  |  |  | electromagnetic lock |  | nr | 33
14.9.12 |  |  |  | door bell button |  | nr | 8
14.9.13 |  |  |  | door bell receiver |  | nr | 8
14.9.14 |  |  |  | theater control panel |  | nr | 1
14.9.15 |  |  |  | Supply and complete installation of OT light. Inspital OT light, model LD20.53, Double Head with Arm Mounted 24” Medical Monitor (With Camera) |  | Item | 1
14.9.16 |  |  |  | HDMA cable for projector |  | nr | 2
14.9.31 |  |  |  | Supply and complete installatioon of Server with Server Rack (24 U) as per specifications |  | Item | 1
14.9.32 |  |  |  | Supply and complete installatioon of 24 port, Double layer Manageable network switch as per Specifications |  | Item | 8
14.10.00 | SECURTIY SYSTEM
CCTV security system to manufacturers detail & Door access system (Door Operating/ access system with CCTV Camera
14.10.01 |  |  |  | Close circuit television |  | nr | 13
14.10.02 |  |  |  | Close circuit television pullbox |  | nr | 1
14.10.03 |  |  |  | Centralization module |  | nr | 24
14.10.04 |  |  |  | Nurse call |  | nr | 41
14.10.05 |  |  |  | Pilot light |  | nr | 33
14.10.06 |  |  |  | TEL / DATA terminal cabinet |  | nr | 1
14.10.07 |  |  |  | Main distribution frame -TTC |  | nr | 1
14.10.08 |  |  |  | TEL/DATA outlet |  | nr | 70
14.10.09 |  |  |  | Private automated branch exchange |  | nr | 1
14.10.10 |  |  |  | DVD 16 channel |  | nr | 1
14.10.11 |  |  |  | Cabling wires and conduits as per drawing |  | item | 1
14.10.12 |  |  |  | Design supply and installation of IP PABX with IP telephone. |  | Item | 1
14.10.13 |  |  |  | Supply and complete installation of Computer system as per specifications |  | Item | 15
14.10.14 |  |  |  | Supply and complete installation of 65" QLED TV, LG or Equivalent at meting room. Any cast or chrome cast must support. |  | Item | 4
14.10.15 |  |  |  | Supplying of Canon Monochrome Multi-Functional Device, Image runner iR 2630i, (A4 & A3 sze) 3 in 1 printer or equivalent. |  | Item | 3
14.11.00 | AIR CONDITION AND VENTILATION
General
(a) Rates shall include for supplying and complete installation of air-conditioning systems; including all pipework, electrical wiring, insulation, stands for outdoor units etc.
(b)All AC Equipments must be VRV/VRF or Central systems which have the capacity to control & operate multiple indoor units
(c) Contractor shall provide Shop Drawings for Consultants' Approval for all electrical units including lighting, power, ACMV systems.
(d) The Brand of AC Equipment specified or to be proposed should demonstrate that it is adequate to cater for highly corrosive environment of Maldives.
(e)The brand or AC Equipment specified should demonstrate all specs below from manufacturer's catalogue /spec sheet.
(d) Proposed system brand and models shall be detailed in Contractor's quotation. Contractor shall propose design and manufacturer's specification sheets of models/units proposed, detailing minimum of below information.
Outdoor Specifications
(a)The Outdoor Unit Shall be factory assembled with Weather Proof casing, constructed from Heavy Gauge Mild Steel Panels and coated with Anti Corrosive Epoxy resin finish. The unit should be completely factory wired and tested and shall be fitted with all necessary controls and switch gear.
(b) All outdoor units need to be VRV or Central systems which have the capacity to control & operate multiple indoor units
(c) All outdoor units needs to have aluminium fins with 105+2 μm thickness, with special Anti corrosive coating of 1.3 ± 0. 35 μm thickness and an outside Hydrophilic layer coating of 0.35 ± 0. 07 μm thickness.
(d) The proposed outdoor or outdoor set specifications should detail Energy Efficiency Ratio (EER) kw/kwh not less than 4.5kw
(e) The brand of AC Equipment proposed should have Outdoor Environment sensor for Compressor Control and adjustment
(f) The Brand of AC Equipment proposed should have an outdoor or outdoor sets of Sound Pressure Level below 60dB (A)
(g)All Outdoor units shall be with inverter compressors and be able to operate even in the event of failure of one compressor.
(H) All outdoor units shall be equipped with high efficiency optimized heat exchangers with variable heat exchanger circuits
(i)The outdoor units shall be provided with its own microprocessor control panels
(j) Service and Parts Replacement Warranty of minimum 12 months for the proposed system should be proposed by the AC Manufacturer
(k) The Outdoot should have a high external static pressure (75Pa or higher)
(l) The Scroll Compressor should have Back Pressure control mechanism to minimize refrigerant load and operational loss.
(m) Outdoor refrigerant type shall be R410A or R32
Indoor Specifications
(a) The address of the indoor unit shall be set automatically in case of individual and group control
(b) Wired centralized control shall be set by liquid crystal remote controller
(c) The fan shall be a dual suction, aerodynamically designed turbo, multi blade centrifugal type fan which shall be statically & dynamically balanced to ensure low noise and vibration free operation. The fan shall be direct driven, mounted directly on motor shaft having support from the unit housing.
(d) The cooling coil shall be made out of seamless copper tubes and have continuous aluminum fins. The tubes shall be staggered in the direction of airflow and shall be hydraulically/ mechanically expanded to bond to the fins. Each coil shall be factory tested at 21kg/sqm air pressure under water.
(e) Each unit shall have a cleanable type filter fixed to an integrally moulded plastic frame. The filter shall be a slide out type and shall be neatly inserted.
(f) Automatic Sensors to control airflow and direction of the airflow by detecting human presence
(i) Each unit shall be provided with a hand held multi-function remote controller. The controller shall be able to change fan speed and angle of swing, temperature and mode (Optional).
(J) Each Unit shall have service Ball valves for After sale service and future Isolation of FCU
(h) The proposed indoor unit should have an indoor Sound Pressure Level below 30dB (A)
(f) All AC Fresh air duct systems must have an H14 Hepa filters attached with 99.99% efficiency on Supply & Return Duct as well
Refrigerant Piping
(a) All refrigerant piping for the air conditioning system shall be constructed from Hard seamless copper up to outer diameter of 41.3 mm and hard drawn copper above outer diameter of41.3 mm. Fittings shall have silver-soldered joints and connections to equipment shall us compression fittings.
(b) All joints in copper piping shall be swag joints using low temperature brazing and or silver solder. Before joining any copper pipe or fittings, its interiors shall be thoroughly cleaned by passing a clean cloth via wire or cable through its entire length. The piping shall be continuously kept clean of dirt etc. while constructing the joints. Subsequently, it shall be thoroughly blown out using nitrogen.
(c) After the refrigerant piping installation has been completed, the refrigerant piping system shall be pressure tested using nitrogen at pressure of 580 PSIG. Pressure shall be maintained in the system for 24 hours. The system shall then be evacuated to minimum vacuum of 700mm hg and held for 24 hours.
(d) The thickness of copper piping shall as per Standard ASTM B280-03
Refrigerant Pipe Insulation
(a) The whole of the liquid and suction refrigerant lines including all fittings, valves etc. shall be insulated with 25mm thick insulation for all copper sizes. Insulation shall be closed cell elastomeric nitrile rubber.
(b) To protect nitrile rubber of exposed piping from degrading due ultra violet rays & atmospheric conditons, it shall be covered polyshield coating with at least two coats of resin and hardener (Make-Polybond /Paramount Polytreat). Fiberglass tape shall be helically wound & painted with two coats of resin with hardener to give smooth & plain finish.
(c) All insulation has to be wrapped in Aluminium Fiber Foil Tape or sheet
Ducting & Ventilation System
(a) All Conceal Duct Indoor System shall be connected to a Duct Ventilation system which shall be designed to provide the most appropriate air flow for designed Air-condition areas
(b) The Duct System shall be made with Pre-Insulated Panels with the below specs - Panel Thickness: 20 – 30mm - Foam Density: 45-48kg/m3 - Aluminium thickness: 80/80m - Alimunium Type: Embossed - The Boards should be Anti-Bacterial, Anti Fungus & Fire Restiant
(c) All supplier & Return Diffusers shall be - The Supply and return air diffusers/grills shall be made of extruded aluminum section with flush fixed pattern - White Powder Coated RAL9010 or 9016 standard - Supply Diffusers shall be with opposed Blade Volume dampers - Thickness of frame should not be less than 1.2mm. The core of the diffuser is 0.9mm thick pressed aluminum.
(d) All ducts shall be installed generally as per the drawings and in strict accordance with approved shop drawings to be prepared by the Contractor.
Rates shall include for complete installation of units
14.11.01 |  |  |  | Air Handling Unit |  | nr | 14
14.11.2 |  |  |  | 4 way cassette unit |  | nr | 40
nr
14.11.03 |  |  |  | Wall mounted AC unit |  | nr | 47
14.11.04 |  |  |  | Fresh air/exhaust air fan, 100CFM |  | nr | 1
14.11.05 |  |  |  | Fresh air/exhaust air fan, 165CFM |  | nr | 1
14.11.06 |  |  |  | Fresh air/exhaust air fan, 245CFM |  | nr | 2
14.11.07 |  |  |  | Fresh air/exhaust air fan, 210CFM |  | nr | 1
14.11.08 |  |  |  | Fresh air/exhaust air fan, 645CFM |  | nr | 1
14.11.09 |  |  |  | Fresh air/exhaust air fan, 500CFM |  | nr | 1
14.11.10 |  |  |  | Fresh air/exhaust air fan, 125CFM |  | nr | 1
14.11.11 |  |  |  | Fresh air/exhaust air fan, 175CFM |  | nr | 1
14.11.12 |  |  |  | Fresh air/exhaust air fan, 85CFM |  | nr | 1
14.11.13 |  |  |  | Fresh air/exhaust air fan, 145CFM |  | nr | 1
14.11.14 |  |  |  | Fresh air/exhaust air fan, 335CFM |  | nr | 1
14.11.15 |  |  |  | Fresh air/exhaust air fan, 130CFM |  | nr | 1
14.11.16 |  |  |  | Fresh air/exhaust air fan, 450CFM |  | nr | 1
14.11.17 |  |  |  | Fresh air/exhaust air fan, 1300CFM |  | nr | 1
14.11.18 |  |  |  | Fresh air/exhaust air fan, 485CFM |  | nr | 1
14.11.19 |  |  |  | Fresh air/exhaust air fan, 200CFM |  | nr | 1
14.11.20 |  |  |  | Fresh air/exhaust air fan, 235CFM |  | nr | 1
14.11.21 |  |  |  | Fresh air/exhaust air fan, 100CFM |  | nr | 1
14.11.22 |  |  |  | Fresh air/exhaust air fan, 475CFM |  | nr | 1
14.11.23 |  |  |  | Fresh air/exhaust air fan, 614CFM |  | nr | 1
14.11.24 |  |  |  | Fresh air/exhaust air fan, 290CFM |  | nr | 1
14.11.25 |  |  |  | Fresh air/exhaust air fan, 870CFM |  | nr | 1
14.11.26 |  |  |  | Fresh air/exhaust air fan, 900CFM |  | nr | 2
14.11.27 |  |  |  | Wall mounted fan, 70CFM |  | nr | 1
14.11.28 |  |  |  | Wall mounted fan, 50CFM |  | nr | 6
14.11.29 |  |  |  | Wall mounted fan, 210CFM |  | nr | 2
14.11.30 |  |  |  | Wall mounted fan, 250CFM |  | nr | 1
14.11.31 |  |  |  | Wall mounted fan, 200CFM |  | nr | 2
14.11.32 |  |  |  | Wall mounted fan, 110CFM |  | nr | 1
14.11.33 |  |  |  | Wall mounted fan, 80CFM |  | nr | 1
14.11.34 |  |  |  | Wall mounted fan, 75CFM |  | nr | 2
14.11.35 |  |  |  | Wall mounted fan, 145CFM |  | nr | 1
14.11.36 |  |  |  | Wall mounted fan, 65CFM |  | nr | 1
14.11.37 |  |  |  | Wall mounted fan, 60CFM |  | nr | 1
14.11.38 |  |  |  | Ceiling mounted exhaust fan, 60CFM |  | nr | 1
14.11.39 |  |  |  | Ceiling mounted exhaust fan, 50CFM |  | nr | 1
14.11.40 |  |  |  | Return air diffuser without damper |  | nr | 43
14.11.41 |  |  |  | Supply air diffuser with damper |  | nr | 48
14.11.42 |  |  |  | Exhaust air grill |  | nr | 83
14.11.43 |  |  |  | Volume controller damper |  | item | 1
14.11.44 |  |  |  | UV lamp |  | nr | 3
14.11.45 |  |  |  | 150mm width supply and return air grill |  | item | 1
14.11.46 |  |  |  | Refrigent pipes with insulation |  | item | 1
14.11.47 |  |  |  | AC drain pipes with insulation |  | item | 1
14.11.48 |  |  |  | Supply air duct with thermal insulation |  | item | 1
14.11.49 |  |  |  | Return air duct with thermal insulation |  | item | 1
14.11.50 |  |  |  | exhaust air duct |  | item | 1
14.11.51 |  |  |  | Fresh air duct |  | item | 1
14.12.00 | LIGHTENING PROTECTION SYSTEM
14.12.01 |  |  |  | Lightning protection system complete as specified in the drawing | item | item | 1
14.13.00 | QUEUE NUMBERING SYSTEM
14.13.01 |  |  |  | Design Supply and complete installation of Queue Number System for Reception counter, OPD rooms, X-Ray, Vaccination, Procedure rooms, Treatment room, Laboratory. incluing all hardwear, wiring as required for all floors all inclusive installation and commissioning.design, supply and install according to hospital operators’ demand/specifications. |  | item | 1
14.14.00 |  |  |  | TOTAL OF BILL №: 14 - Carried Over To Summary
15.00.00 |  |  |  | Bill №: 15- INSULATION, FIRE STOPPING & FIRE PROTECTION
15.1.00 | GENERAL
|  |  | (a) | Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
|  |  | (b) | Rates for cable conduits, fittings, equipment and similar items shall include for: all fixings to various building surfaces
|  |  | (c) | Rates shall include for all necessary electrical wiring and accessories required for completion as per drawing and specification
|  |  | (d) | All items shall be supply and complete installation
|  |  | (e) | All works complete as per drawing and specification
15.2.00 | DRY RISER SYSTEM
15.2.01 |  |  |  | Dry riser system including breeching inlet |  | item | 1
15.3.00 | FIRE FIGHTING SYSTEM
15.3.01 |  |  |  | 2Kg Carbondioxide fire Extinguishers |  | nr | 32
15.3.02 |  |  |  | 9Liters H2O fire Extinguishers |  | nr | 25
15.3.03 |  |  |  | 2Kg DCP fire Extinguishers |  | nr | 1
15.3.04 |  |  |  | 6Kg DCP fire Extinguishers |  | nr | 1
15.3.05 |  |  |  | Smoke detectors |  | nr | 289
15.3.06 |  |  |  | Heat detectors |  | nr | 9
15.3.07 |  |  |  | Manual call point |  | nr | 15
15.3.08 |  |  |  | Fire Alarm control panel |  | nr | 1
15.3.09 |  |  |  | Fire Blancket |  | nr | 6
15.3.10 |  |  |  | Fire alarm sounder with strobe light 95DB |  | nr | 15
15.3.11 |  |  |  | Hose reel 30m with cabinet FHRC |  | nr | 10
15.3.12 |  |  |  | Emergency light |  | nr | 20
15.3.13 |  |  |  | Exit light |  | nr | 19
15.3.14 |  |  |  | Fire pump system consist of electrical duty pump and diesel stand by pump |  | set | 1
15.3.15 |  |  |  | 25mm air release valve |  | nr | 2
15.3.16 |  |  |  | Fire resistance cable |  | item | 1
15.3.17 |  |  |  | MWSC water mete |  | nr | 1
15.3.18 |  |  |  | Fire rated door 90min |  | nr | 2
15.4.00 |  |  |  | TOTAL OF BILL №: 15 - Carried Over To Summary
16.0.00 |  |  |  | Bill №: 16 - SOLAR PANEL
16.1.00 | GENERAL
|  |  | (a) | The price includes all builders’ works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites approved by the engineer to complete the job successfully. • All the following items include supply, install, commission and operate of the complete PV solar system
|  |  | (b) | The contractor shall submit for approval technical data regarding the panels to the consultant prior to procuring the solar panels
|  |  | (c) | All the following items include supply, install, commission and operate of the complete solar panel system
|  |  | (d) | All works complete as per drawing and specification
16.2.00 | SOLAR PANELS
16.2.01 |  |  |  | Design supply and complete installation of solar panels as per drawing and connect to the grid. | 217 | item | 1
16.3.00 |  |  |  | TOTAL OF BILL №: 16 - Carried Over To Summary
17.0.00 |  |  |  | Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS
OXYGEN & MEDICAL AIR FOR ALL BEDS
17.01.00 | GENERAL
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rates shall include for: Design, supply and install according to hospital operators’ demand/specifications. screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
17.02.00 | OXYGEN DELIVERY SYSTEM
Design supply and complete installation of Piped and tested oxygen delivery system from the Oxygen bank as per Specifications and manufactures guidelines, instructions. Oxygen bank, capacity to connect minimum 6 jumbo cylinder. System to be insttaled as per manufactures standards.
17.02.1 |  |  |  | ER area |  | Item | 10
17.02.2 |  |  |  | SUSPECTED ISOLATION ROOM |  | Item | 4
17.02.3 |  |  |  | GYNY WARD |  | Item | 4
17.02.4 |  |  |  | NICU WARD |  | Item | 2
17.02.5 |  |  |  | PEDIATRIC WARD |  | Item | 4
17.02.6 |  |  |  | MALE WARD |  | Item | 4
17.02.7 |  |  |  | PRIVATE ROOM |  | Item | 4
17.02.8 |  |  |  | LABOUR ROOM |  | Item | 3
17.02.9 |  |  |  | OPERATION THEATER |  | Item | 4
17.02.10 |  |  |  | FEMALE WARD |  | Item | 4
17.02.11 |  |  |  | TREATMENT ROOM |  | Item | 1
MEDICAL AIR SYSTEM
Design supply and complete installation of Piped and tested Medical air system from medical air plant as per Specifications and manufactures guidelines, instructions.. Oxygen bank, capacity to connect minimum 12 jumbo cylinder. System to be insttaled as per manufactures standards.
17.02.12 |  |  |  | ER area |  | Item | 10
17.02.13 |  |  |  | SUSPECTED ISOLATION ROOM |  | Item | 4
17.02.14 |  |  |  | GYNY WARD |  | Item | 4
17.02.15 |  |  |  | NICU WARD |  | Item | 2
17.02.16 |  |  |  | PEDIATRIC WARD |  | Item | 4
17.02.17 |  |  |  | MALE WARD |  | Item | 4
17.02.18 |  |  |  | PRIVATE ROOM |  | Item | 4
17.02.19 |  |  |  | LABOUR ROOM |  | Item | 3
17.02.20 |  |  |  | OPERATION THEATER |  | Item | 4
17.02.21 |  |  |  | FEMALE WARD |  | Item | 4
17.02.22 |  |  |  | TREATMENT ROOM |  | Item | 1
VACUME SYTEM
Design supply and complete installation of Piped and tested vacuum system from a central vacuum system as per Specifications and manufactures guidelines, instructions..
17.02.23 |  |  |  | ER area |  | Item | 10
17.02.24 |  |  |  | SUSPECTED ISOLATION ROOM |  | Item | 4
17.02.25 |  |  |  | GYNY WARD |  | Item | 4
17.02.26 |  |  |  | NICU WARD |  | Item | 2
17.02.27 |  |  |  | PEDIATRIC WARD |  | Item | 4
17.02.28 |  |  |  | MALE WARD |  | Item | 4
17.02.29 |  |  |  | PRIVATE ROOM |  | Item | 4
17.02.30 |  |  |  | LABOUR ROOM |  | Item | 3
17.02.31 |  |  |  | OPERATION THEATER |  | Item | 4
17.02.32 |  |  |  | FEMALE WARD |  | Item | 4
17.02.33 |  |  |  | TREATMENT ROOM |  | Item | 1
BED HEAD UNITS
17.02.34 |  |  |  | Supply and complete installation of Bed head units, with control panels , each unit must includes 13amp 4 single sockets, 15amp 1 single socket with 2 USB port, 1 network point, Obsevatuion light and other necessary accessories. |  | Item | 44
OXYGEN GENERATOR
17.02.35 |  |  |  | Design, supply and complete installation of Oxygen generator with manifold, capacity of Generator must be minimun 15m3 per day.(Approve by Client), also filling component must be installed, |  | Item | 1
OXYGEN PLANT SHED
17.02.36 |  |  |  | Constrion of Oxygen bank and Oxygen generator, Vaccum and medical air plant, Shed, Size of the shed will be proposed by the Contractor. |  | Item | 1
17.3.00 |  |  |  | TOTAL OF BILL №: 17- Carried Over To Summary
18.0.00 |  |  |  | Bill №: 18 - ADDITIONS AND OMMISIONS
18.1.00 | ADDITIONS
18.1.01 |  |  |  | Bill №: 01 - PRELIMINARIES
18.1.02 |  |  |  | Bill №: 02 - EXCAVATION AND FILLING
18.1.03 |  |  |  | Bill №: 03 - INSITU CONCRETE WORKS
18.1.04 |  |  |  | Bill №: 04 - MASONRY
18.1.05 |  |  |  | Bill №: 05 - CARPENTRY
18.1.06 |  |  |  | Bill №: 06 - STRUCTURAL METAL WORKS
18.1.07 |  |  |  | Bill №: 07 - CEILING
18.1.08 |  |  |  | Bill №: 08 - WINDOWS, SCREENS & LIGHTS
18.1.09 |  |  |  | Bill №: 09 - DOORS, SHUTTERS & HATCHES
18.1.10 |  |  |  | Bill №: 10 - DECORATIONS
18.1.11 |  |  |  | Bill №: 11 - FINISHES
18.1.12 |  |  |  | Bill №: 12 - ROOFING
18.1.13 |  |  |  | Bill №: 13 - HYDRAULICS AND DRAINAGE
18.1.14 |  |  |  | Bill №: 14 - ELECTRICAL INSTALLATIONS
18.1.15 |  |  |  | Bill №: 15- INSULATION, FIRE STOPPING & FIRE PROTECTION
18.1.16 |  |  |  | Bill №: 16 - SOLAR PANEL
18.1.17 |  |  |  | Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS
TOTAL
18.2.00 | OMISSIONS
18.2.01 |  |  |  | Bill №: 01 - PRELIMINARIES
18.2.02 |  |  |  | Bill №: 02 - EXCAVATION AND FILLING
18.2.03 |  |  |  | Bill №: 03 - INSITU CONCRETE WORKS
18.2.04 |  |  |  | Bill №: 04 - MASONRY
18.2.05 |  |  |  | Bill №: 05 - CARPENTRY
18.2.06 |  |  |  | Bill №: 06 - STRUCTURAL METAL WORKS
18.2.07 |  |  |  | Bill №: 07 - CEILING
18.2.08 |  |  |  | Bill №: 08 - WINDOWS, SCREENS & LIGHTS
18.2.09 |  |  |  | Bill №: 09 - DOORS, SHUTTERS & HATCHES
18.2.10 |  |  |  | Bill №: 10 - DECORATIONS
18.2.11 |  |  |  | Bill №: 11 - FINISHES
18.2.12 |  |  |  | Bill №: 12 - ROOFING
18.2.13 |  |  |  | Bill №: 13 - HYDRAULICS AND DRAINAGE
18.2.14 |  |  |  | Bill №: 14 - ELECTRICAL INSTALLATIONS
18.2.15 |  |  |  | Bill №: 15- INSULATION, FIRE STOPPING & FIRE PROTECTION
18.2.16 |  |  |  | Bill №: 16 - SOLAR PANEL
18.2.17 |  |  |  | Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS
TOTAL
17.3.00 |  |  |  | TOTAL OF BILL №: 17 - Carried Over To Summary