## Cover
include template cover page and document control page

## BOQ Summary
SUMMARY OF BILL OF QUANTITIES |  |  |  | 1.29 | factor for extra & waste | 1.05
Project: HDh Makunudhoo Health Center | Date: | 26th March 2022
Version:
Client: Ministry of Health | Prepared by:
DESCRIPTION |  | AMOUNT (MVR) | %
Bill №: 01 - PRELIMINARIES |  | 0
Bill №: 02 - GROUND WORKS |  | 0
Bill №: 03 - CONCRETE WORKS |  | 0
Bill №: 04 - MASONRY & PLASTERING |  | 0
Bill №: 05 - STRUCTURAL METAL WORKS |  | 0
Bill №: 06 - CARPENTRY |  | 0
Bill №: 07 - RAILINGS |  | 0
Bill №: 08 - CEILING |  | 0
Bill №: 09 - WINDOWS, SCREENS & LIGHTS |  | 0
Bill №: 10 - DOORS, SHUTTERS & HATCHES |  | 0
Bill №: 11 - DECORATIONS |  | 0
Bill №: 12 - FINISHES |  | 0
Bill №: 13 - ROOFING |  | 0
Bill №: 14 - HYDRAULICS AND DRAINAGE |  | 0
Bill №: 15 - ELECTRICAL INSTALLATIONS |  | 0
Bill №: 16 - INSULATION, FIRE STOPPING & FIRE PROTECTION |  | 0
Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS |  | 0
Bill №: 18 - ADDITIONS AND OMMISIONS
Sub Total |  | 0
GST |  | 0
GRAND TOTAL AMOUNT |  | 0
NOTES to BoQ:

## BOQ for tender
0
BILL OF QUANTITIES
ITEM |  |  |  | DESCRIPTION | UNIT | QTY | MATERIAL RATE | LABOUR RATE | AMOUNT
1.0.00 |  |  |  | Bill №: 01 - PRELIMINARIES
1.1.00 | GENERAL NOTES
Abbreviations
|  |  | m | - metre
|  |  | nr | - numbers
|  |  | m3 | - cubic metres
|  |  | m2 | - square metres
|  |  | lm | - linear metre
|  |  | t | - tons
|  |  | inc. | - including
|  |  | mm | - millimetre
|  |  | SS | - stainless steel
|  |  | GI | - galvanized iron
1.2.00 | SITE MANAGEMENT COSTS
|  |  |  | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings & similar. | item | 1
1.3.00 | SIGN BOARD
|  |  |  | Allow for sign board. | nr | 1
1.4.00 | CLEAN-UP
|  |  |  | Allow for clean-up upon completion of works. | item | 1
1.5.00 | INSURANCE, BONDS, GUARANTEES AND WARRANTIES
|  |  |  | Insurance as stated in the general conditions. | item | 1
1.6.00 | INSPECTION TRIPS
| Arrange inspection trip to PMU team. Each inspection trip takes 2 days. Contractor has to arrange following for trips; (a) Air tickets for 2 person: Male'/Hdh. Kulhudhuffushi/Male' by air (normal fair), (b) Speed boat transfer from Hdh. Kulhudhuffushi/Hdh. Makunudhoo/Hdh. Kulhudhuffushi. (C) Accommodations (2 Air-condition room) per trip. |  |  |  | Item | 8
1.6.00 | TOTAL OF BILL №: 01 - Carried Over To Summary
2.0.00 |  |  |  | Bill №: 02 - EXCAVATION AND FILLING
2.1.00 | GENERAL
|  |  | (a) | Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating, and disposing surplus soil.
2.2.00 | SITE CLEARING
|  |  |  | Clear the site area from Trees, rubbish and vegetable matter, stumps, and roots. Rates must include EIA to remove or reallocate trees. The contractor must survey the site before bidding. | m2 | 3716.12
2.3.00 | EXCAVATION
Excavation quantities are measured to the faces of concrete members. Rates shall include for all the additional excavation required to place the formwork. Rates shall include for backfilling.
2.3.01 |  |  |  | Excavation for Foundation Raft | m3 | 1472.42
2.4.00 | FILLING
Rate shall include for: levelling, grading, trimming, compacting and similar
2.4.01 |  |  |  | Compacted earth filling under ground slab | m2 | 2643.58
2.4.02 |  |  |  | 150mm thick coarse aggregate layer under slab | m2 | 2643.58
2.5.00 | DAMP-PROOF MEMBRANE
Rate shall include for: dressing around and sealing to all penetrations.
2.5.01 |  |  |  | Water Proof Membrane | m2 | 2643.58
2.6.00 | DE-WATERING
2.6.01 |  |  |  | De-watering the excavation until completion of concrete work as required | item | 1
2.7.00 | TOTAL OF BILL №: 02 - Carried Over To Summary
3.0.00 |  |  |  | Bill №: 03 - INSITU CONCRETE WORKS
3.1.00 | GENERAL
|  |  | (a) | Rates shall include for: placing in position, making good after removal of formwork, mortar touch up to all concrete and casting in all required items; additional concrete required to conform to structural and excavated tolerances
|  |  | (b) | Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6.
|  |  | (c) | All structural concrete shall be GRADE C30 and lean concrete shall be GRADE C15
|  |  | (d) | Rates shall include for: concrete, formwork, reinforcement, cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
|  |  | (e) | Rates shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork.
|  |  | (f) | Rates shall include for: cleaning, fabrication, placing the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
|  |  | (g) | All reinforcing bars shall be high strength bars.
|  |  | (h) | Slab soffits to be finished fairfaced, use plasteciser and formwork with reducing agent.
|  |  | (i) | Waterproofing shall be added to all areas specified.
3.1.01 |  |  |  | Allow for Concrete Testing. | item | 1
3.2.00 | MASS CONCRETE
Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
3.2.01 |  |  | 50 | mm Lean Concrete (Foundations) | m3 | 36.94
REINFORCED INSITU CONCRETE
3.3.00 | SUB-STRUCTURE
FOUNDATION PADS
3.3.01 | 2600 | x | 2600 | x 525mm Foundation pads, F1 | m3 | 14.2
3.3.02 | 1950 | x | 1950 | x 400mm Foundation pads, F2 | m3 | 21.294
3.3.03 | 2200 | x | 2200 | x 400mm Foundation pads, F3 | m3 | 158.76
3.3.04 | 1700 | x | 1700 | x 400mm Foundation pads, F4 | m3 | 20.81
3.3.05 | 1450 | x | 1450 | x 400mm Foundation pads, F5 | m3 | 67.28
3.3.06 | 2450 | x | 2450 | x 475mm Foundation pads, F6 | m3 | 8.56
3.3.07 | 900 | x | 900 | x 350mm Foundation pads, F7 | m3 | 0.57
3.3.08 | 2000 | x | 1500 | x 400mm Foundation pads, F8 | m3 | 6
3.3.09 | 3100 | x | 1900 | x 400mm Foundation pads, F9 | m3 | 2.36
FOUNDATION BEAMS
3.3.10 | 450 | x | 200 | mm Foundation beam, TB1 | m3 | 61.76
3.3.11 | 450 | x | 200 | mm Foundation beam, TB2 | m3 | 65.18
3.4.00 | GROUND FLOOR
COLUMNS
3.4.01 | 450 | x | 450 | mm Concrete columns C1 | m3 | 1.71
3.4.02 | 350 | x | 350 | mm Concrete columns C2 | m3 | 33.96
3.4.03 | 350 | x | 350 | mm Concrete columns C3 | m3 | 6.18
3.4.04 | 300 | x | 300 | mm Concrete columns C4 | m3 | 18.15
3.4.05 | 250 | x | 250 | mm Concrete columns C5 | m3 | 16.54
3.4.06 |  |  | 550 | mm dia. Concrete columns C6 | m3 | 8
3.4.06 |  |  | 550 | mm dia. Concrete columns C7 | m3 | 4
SLABS
3.4.07 |  |  | 150 | mm thk Concrete Slab on ground fill | m3 | 396.54
RAMPS
3.4.08 |  |  | 180 | mm thk RAMP Slab | m3 | 11.78
STAIRS
2.4.09 |  |  |  | Staircase 01 | m3 | 2.32
2.4.10 |  |  |  | Staircase 02 | m3 | 1.86
2.4.11 |  |  |  | Staircase 03 | m3 | 1.86
RC WALLS
3.4.12 |  |  | 200 | mm thk RC wall with lead shield by supplier | m3 | 18.71
3.5.00 | FIRST FLOOR
BEAMS
3.5.01 | 550 | x | 225 | mm Beam B1 | m3 | 0.93
3.5.02 | 550 | x | 225 | mm Beam B1a | m3 | 0.42
3.5.03 | 550 | x | 225 | mm Beam B1b | m3 | 2.07
3.5.04 | 550 | x | 300 | mm Beam B2 | m3 | 3
3.5.05 | 550 | x | 250 | mm Beam B4 | m3 | 30.73
3.5.06 | 550 | x | 250 | mm Beam B4a | m3 | 2.33
3.5.07 | 550 | x | 250 | mm Beam B4b | m3 | 7.98
3.5.08 | 550 | x | 225 | mm Beam B5 | m3 | 45.29
3.5.09 | 650 | x | 225 | mm Beam B5a | m3 | 11.27
3.5.10 | 500 | x | 200 | mm Beam B6 | m3 | 13.77
3.5.11 | 500 | x | 200 | mm Beam B6a | m3 | 0.13
3.5.12 | 450 | x | 200 | mm Beam B7 | m3 | 1.08
3.5.13 | 450 | x | 200 | mm Beam B7a | m3 | 0.12
3.5.14 | 450 | x | 200 | mm Beam B8 | m3 | 22.39
3.5.15 | 450 | x | 200 | mm Beam B8a | m3 | 1.96
3.5.16 | 450 | x | 200 | mm Beam B10 | m3 | 2.32
3.5.17 | 700 | x | 300 | mm Beam B11 | m3 | 3.4
3.5.18 | 700 | x | 300 | mm Beam B11a | m3 | 1.12
3.5.19 | 700 | x | 300 | mm Beam B11b | m3 | 5.82
3.5.20 | 450 | x | 200 | mm Beam CB1 | m3 | 0.67
3.5.21 | 550 | x | 225 | mm Beam CB2 | m3 | 0.75
SLABS
3.5.22 |  |  | 150 | mm thk Concrete Slab | m3 | 286.33
3.5.23 |  |  | 160 | mm thk Concrete Slab | m3 | 15.85
COLUMNS
3.5.24 | 450 | x | 450 | mm Concrete columns C1 | m3 | 1.62
3.5.25 | 350 | x | 350 | mm Concrete columns C2 | m3 | 32.34
3.5.26 | 350 | x | 350 | mm Concrete columns C3 | m3 | 5.88
3.5.27 | 300 | x | 300 | mm Concrete columns C4 | m3 | 14.4
3.5.28 | 250 | x | 250 | mm Concrete columns C5 | m3 | 8.25
3.5.29 |  |  | 550 | mm dia. Concrete columns C6 | m3 | 3.81
STAIRS
3.5.30 |  |  |  | Staircase 01 | m3 | 2.32
3.6.00 | TERRACE FLOOR
BEAMS
3.6.01 | 550 | x | 300 | mm Beam B2 | m3 | 2.2
3.6.02 | 550 | x | 250 | mm Beam B4 | m3 | 27.46
3.6.03 | 550 | x | 250 | mm Beam B4a | m3 | 2.33
3.6.04 | 550 | x | 250 | mm Beam B4b | m3 | 7.32
3.6.05 | 550 | x | 225 | mm Beam B5 | m3 | 44.68
3.6.06 | 650 | x | 225 | mm Beam B5a | m3 | 10.56
3.6.07 | 500 | x | 200 | mm Beam B6 | m3 | 6.17
3.6.08 | 500 | x | 200 | mm Beam B6a | m3 | 0.13
3.6.09 | 450 | x | 200 | mm Beam B7 | m3 | 1.08
3.6.10 | 450 | x | 200 | mm Beam B7a | m3 | 0.12
3.6.11 | 450 | x | 200 | mm Beam B8 | m3 | 18.76
3.6.12 | 450 | x | 200 | mm Beam B10 | m3 | 2.32
3.6.13 | 700 | x | 300 | mm Beam B11 | m3 | 3.4
3.6.14 | 700 | x | 300 | mm Beam B11a | m3 | 1.12
3.6.15 | 700 | x | 300 | mm Beam B11b | m3 | 5.82
3.6.16 | 450 | x | 200 | mm Beam CB1 | m3 | 0.67
3.6.17 | 550 | x | 225 | mm Beam CB2 | m3 | 0.75
SLABS
3.6.18 |  |  | 150 | mm thk Concrete Slab | m3 | 258.14
3.6.19 |  |  | 160 | mm thk Concrete Slab | m3 | 11.1
COLUMNS
3.6.20 | 350 | x | 350 | mm Concrete columns C2 | m3 | 1.52
3.6.21 | 350 | x | 350 | mm Concrete columns C3 | m3 | 0.38
3.6.22 | 300 | x | 300 | mm Concrete columns C4 | m3 | 0.28
3.7.00 | ROOF
BEAMS
3.7.01 | 500 | x | 200 | mm Beam B6 | m3 | 2.54
3.7.02 | 450 | x | 200 | mm Beam B8 | m3 | 0.49
SLABS
3.7.03 |  |  | 150 | mm thk Concrete Slab | m3 | 8
3.9.0 | Ground Water Well
|  |  | Completion of RC Concrete Groundwater well, Diameter of the well is 2 mete rand thickness of the well is 100mm, the water level must be a minimum of 2 meters in low tide, reinforcement of the well is 10mm bars 250X250mm B/W. The rate also must include a 150mm thick RC slab. |  | Item | 1
3.10.00 | BOUNDARY WALL 1.2METER HEIGHT.
3.10.1 |  |  | 150mm thick Solid block single wall 1.2m Height of boundary wall (from ground level ) surrounded by the land area with oil based paint system with textured finish, Footing: 600 x 600mm (T10 @150 BW) Foundation Beam: 300 x 200mm (4T12, R6@150) Columns (at 3.5M span): 200 x 200mm (4T12, R6@150) Foundation Depth: 750mm Capping Beam: 150 x 150mm (4T10, R6@150) |  | meter | 244
3.11.00 | FLAG POST
|  |  | Supply and Complete installation of 75mm dia Flag post, length of flag post is minimum 5.9 Meter, Flag post must install minimum 10mm thick SS flang with SS bolts. Flag post to be fabricated in Marine grade SS pipe with 350X350X600mm concrete footings. |  | Item | 1
3.12.00 |  |  |  | TOTAL OF BILL №: 03 - Carried Over To Summary
4.0.00 |  |  |  | Bill №: 04 - MASONRY
4.1.00 | GENERAL
|  |  | (a) | Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leavingholes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashing, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good.
|  |  | (b) | Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:5 i.e. cement: river sand) shall be of OPC & free form salt.
|  |  | (c) | Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance.
|  |  | (d) | Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance.
|  |  | (e) | All works complete as per drawing and specification
4.2.00 | BRICK WORK
150mm thk masonry solid block wall, bricks laid to form alternate courses of headers and stretchers, laid on and inc. mortar. (EXTERNAL WALLS)
4.2.01 |  |  |  | GROUND FLOOR | m2 | 1373.83
4.2.02 |  |  |  | FIRST FLOOR | m2 | 1089.22
4.2.03 |  |  |  | TERRACE FLOOR | m2 | 79.12
150mm thk 2000mm high masonry solid block wall, bricks laid to form alternate courses of headers and stretchers, laid on and inc. mortar. (EXTERNAL WALLS)
4.2.04 |  |  |  | GROUND FLOOR | m2 | 248.58
100mm thk 1200mm high masonry solid block wall, bricks laid to form alternate courses of headers and stretchers, laid on and inc. mortar. (EXTERNAL WALLS)
4.2.05 |  |  |  | TERRACE FLOOR | m2 | 336.64
150mm thk masonry solid block wall, bricks laid to form alternate courses of headers and stretchers, laid on and inc. mortar (INTERNAL WALLS).
4.2.06 |  |  |  | GROUND FLOOR | m2 | 957.58
4.2.07 |  |  |  | FIRST FLOOR | m2 | 1029.5
4.3.00 | PLASTERING
20mm thk cement plaster on external surface as specified on the drawing. Waterproofed with Sika product or equivalent.
4.3.01 |  |  |  | GROUND FLOOR | m2 | 1870.99
4.3.02 |  |  |  | FIRST FLOOR | m2 | 1089.22
4.3.03 |  |  |  | TERRACE FLOOR | m2 | 752.4
16mm thk cement plaster on internal surface as specified on the drawing
4.3.04 |  |  |  | GROUND FLOOR | m2 | 3288.99
4.3.05 |  |  |  | FIRST FLOOR | m2 | 3148.22
4.3.06 |  |  |  | TERRACE FLOOR | m2 | 79.12
4.4.00 | CEMENT SCREED
50mm thk cement screed waterproofed with SIKA product or equivalent
4.4.01 |  |  |  | GROUND FLOOR | m2 | 2643.58
4.4.02 |  |  |  | FIRST FLOOR | m2 | 1937.98
4.4.03 |  |  |  | TERRACE FLOOR | m2 | 1790.3
4.5.00 |  |  |  | TOTAL OF BILL №: 04 - Carried Over To Summary
5.0.00 |  |  |  | Bill №: 05 - STRUCTURAL METAL WORKS
5.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all fabrication work, welding, marking, drilling for bolts incl. those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
|  |  | (b) | Rates shall include for fabrication and erection and temporary supports and fixing into position.
|  |  | (c) | “Welding” is deemed to be in accordance with the specification and for the material to which it is to be used. Gusset plates, shoe plates, ends, caps, cleats, brackets, stiffeners, bolts, etc.,are required to be included to the rate of the associated steel work in which they occur.
|  |  | (d) | For the description of materials and workmanship refer to the Specification of works, pricing Preambles and Drawings.
|  |  | (e) | Contractor shall submit shop drawings for approval prior to fabrication.
|  |  | (f) | Unless specified otherwise, rate shall include for: All shop fabrication work, marking, delivery, unloading, hoisting, erecting and fixing as per detail drawings, All welds & allowance for rolling margin, the weight of weld metal in welded constructions, members of any length, cutting to size and shape and joints in the running length, grinding to a smooth finish, unless otherwise required, Machine drilled bolt, holes, bolts, nuts and washers, cleats, shoe and gusset plates and all other connections, Wire brushing to clean all the steel surfaces (except stainless steel) after fabrication and spray painting with two coats of quick drying metal primer zinc phosphate & two coats of matt anti corrosive paint with final paint, all necessary accessories and preparation and submission of Shop Drawings and As Built Drawings as specified.
5.2.00 | TRUSS
Steel truss with 50mm dia x 2.5mm thick CHS top and bottom chord and 35mm dia. x 2.5mm thick CHS web members
5.2.01 |  |  |  | Truss TR1 | m | 29.95
5.2.02 |  |  |  | Truss TR2 | m | 83.7
5.2.03 |  |  |  | Truss TR3 | m | 18
5.2.04 |  |  |  | Truss TR4 | m | 71.8
5.3.00 | PURLINS
5.3.01 | 50 | x | 100 | x 2.5mm thick C section purlins | m | 587.1
5.4.00 |  |  |  | TOTAL OF BILL №: 05 - Carried Over To Summary
6.0.00 |  |  |  | Bill №: 06 - CARPENTRY
6.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
6.2.00 | DRYWALL
100mm thick drywall panels on steel frame
6.2.01 |  |  |  | GROUND FLOOR | m2 | 1840.4
6.2.02 |  |  |  | FIRST FLOOR | m2 | 1397.38
35mm thick 2400mm high plywood partition with high pressure laminated finish with edging
6.2.03 |  |  |  | GROUND FLOOR | m2 | 16.31
6.2.04 |  |  |  | FIRST FLOOR | m2 | 15.83
Supplying and installation of Furniture for Health Center
6.2.05 |  |  |  | Office Table, 1200mm ( table should be solid wood) with drawer. | No | 20
6.2.06 |  |  |  | Office Table 1500mm ( table should be solid wood) with drawer. | No | 4
6.2.07 |  |  |  | Executive chair, high back | No | 10
6.2.08 |  |  |  | Secretary chair , high back. | No | 15
6.2.09 |  |  |  | Secretary chair , Low back. | No | 20
6.2.10 |  |  |  | Meeting room chair Material: Iron/Aluminum Surface treatment: Spray painting finished. Seat and back: Hight-density sponge, minimum 2.5" thick seat cushion | No | 50
6.2.11 |  |  |  | Folding Meeting Table, 1400X600mm, Specifications: Lockable castorsm Aluminum components Feature: Chrome with polished aluminum feet, Easy tilt mechanism for compact storage, Table surface: Scratch resistant, Natural Ash. | NO | 15
6.2.12 |  |  |  | Supply and installation of 4 seater Airport Bench set, Armrest/Leg/bracket: Die-casting molding of high strength aluminum alloy. Seat: Numerical control hydraulic molding of high quality cold rolling steel plate. Sponge: Cold consolidation and foam-forming of high density and super soft PU. Beam: metal tube with a diamond shape. Coating: Electrostatic coating after Rust-proof treatment, electroplated polishing. | no | 20
6.2.13 |  |  |  | Design and Fabrication of Wooden shelves at Medical Store room, length of Shelf is 1.2M, Width is 0.4m and heigh is 2M, 18mm thick Plywood with both side paint to be used. Frame with 4 shelf, | No | 20
FIXED FURNITURE
Fixed counter/furniture as per drawing
GROUND FLOOR
6.2.14 |  |  |  | Main Reception counter | no | 1
6.2.15 |  |  |  | Nurse station counter - isolation ward | no | 1
6.2.16 |  |  |  | Nurse station counter - suspected ward | no | 1
6.2.17 |  |  |  | Nurse station counter - emergency department | no | 1
6.2.18 |  |  |  | Triage counter | no | 1
6.2.19 |  |  |  | Xray room cubical with counter with LED glass | no | 1
6.2.20 |  |  |  | Pharmacy counter | no | 1
FIRST FLOOR
6.2.21 |  |  |  | Laboratory working area | no | 1
6.2.22 |  |  |  | Centeral reception counter | no | 1
6.2.23 |  |  |  | Nurse station counter - labour | no | 1
6.2.24 |  |  |  | Nurse station counter - NICU | no | 1
6.2.25 |  |  |  | Nurse station counter - Ward area | no | 1
6.2.26 |  |  |  | Wardrobe - private rooms | no | 1
Supplying and installation of Furniture for Accomodation Area
6.2.27 |  |  |  | Double bed, | Item | 2
6.2.28 |  |  |  | Single bed, | Item | 8
6.2.29 |  |  |  | Wordrobe 2 door panel, | Item | 8
6.2.30 |  |  |  | Dressing table, | Item | 8
6.2.31 |  |  |  | Double mattress, 6 inch thick. | Item | 2
6.2.32 |  |  |  | Single mattress, 6 inch thick. | Item | 8
6.2.33 |  |  |  | Dining table, for 4 people with chairs | Item | 4
6.2.34 |  |  |  | Sofa set, 1 sofa for 2 person and 1 sofa for 1 person with coffee table. | Item | 4
6.2.35 |  |  |  | Sofa set, 1 sofar for 2 person and 2 sofa for 1 person with coffee table. | Item | 4
6.2.36 |  |  |  | Display TV 65" with TV reck | Item | 8
6.2.37 |  |  |  | Electric stove, No of burners 3. | Item | 8
6.2.38 |  |  |  | Automatic washing machine, minimum 8KG | Item | 8
Kitchen cupbord
6.2.39 |  |  |  | Design and fabrication of kichen cupboard with over hed cupbord. Rates includes to sink and hood, length of kitchen cupboard is same as floor plan. | Item | 4
6.3.00 |  |  |  | TOTAL OF BILL №: 06 - Carried Over To Summary
7.0.00 |  |  |  | Bill №: 07 - RAILINGS
7.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all fabrication work, welding, marking, drilling for bolts incl. those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
|  |  | (b) | Rates shall include for fabrication and erection and temporary supports and fixing into position.
|  |  | (c) | All SS popes and accessories must be marine-grade SS pipes and accessories.
7.2.00 |  |  |  | Main Staircase Handrailing
50x50mm SS SHS hailine finish railing with 12mm thick tempered glass railing, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
7.2.01 |  |  |  | Ground to First Floor | m | 6.33
7.2.02 |  |  |  | First to Terrace Floor | m | 6.33
7.3.00 |  |  |  | Staircase 01 Handrailing
50 mm dia SS CHS hairline finish railing with 25mm dia SS CHS hairline finish railing, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
7.3.01 |  |  |  | Ground to First Floor | m | 6.7
7.4.00 |  |  |  | Staircase 02 Handrailing
50 mm dia SS CHS hairline finish railing with 25mm dia SS CHS hairline finish railing, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
7.4.01 |  |  |  | Ground to First Floor | m | 6.7
7.5.00 |  |  |  | Balcony Handrailing
50 mm dia SS CHS hairline finish hand railing fixed to wall and welded to 25mm dia SS CHS hairline finish railing, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
7.5.01 |  |  |  | Balcony hand rail | m | 3
50x50mm SS SHS hailine finish railing with 12mm thick tempered glass railing, including bolts, washers and fixing to reinforced concrete as shown in the drawing.
7.5.02 |  |  |  | Balcony railing | m | 54.3
7.6.00 |  |  |  | TOTAL OF BILL №: 07 - Carried Over To Summary
8.0.00 |  |  |  | Bill №: 08 - CEILING
8.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
8.2.00 |  |  |  | BORAL CEILING
USG BORAL suspended ceiling tiles 600x600mm, 16mm thick with aluminium framing
8.2.01 |  |  |  | Ground floor | m2 | 1162.5
8.2.02 |  |  |  | First floor | m2 | 1175.38
8.3.00 |  |  |  | GYPSUM BOARD CEILING
False flat ceiling with 12mm thick Gypsum Board under 50x50mm ceiling joist with emulsion paint finish
8.3.01 |  |  |  | Ground floor | m2 | 824.98
8.3.02 |  |  |  | First floor | m2 | 589.58
8.3.03 |  |  |  | Terrace floor | m2 | 11.96
8.4.00 |  |  |  | TOTAL OF BILL №: 08 - Carried Over To Summary
8.0.00 |  |  |  | Bill №: 09 - WINDOWS, SCREENS & LIGHTS
9.1.00 | GENERAL
|  |  | (a) | Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
|  |  | (b) | Rates shall include for door frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings.
|  |  | (c) | Sizes are given overall outside dimensions of actual doors and windows.
|  |  | (d) | Thickness and sizes of glass panels are shown on the Drawings and doors and windows schedule
|  |  | (e) | Rates shall include for all painting as specified
|  |  | (f) | Rates shall include all items specified in the door schedule and specification.
|  |  | (g) | Frames and sashes to be 25-60 micron black powder coated aluminium other wise specified.
9.2.00 | WINDOWS
9.2.01 | 750 | x | 1000 | V01 - Top hung window | nr | 13
9.2.02 | 750 | x | 550 | W01 - Top hung window | nr | 4
9.2.03 | 1000 | x | 1500 | W02 - Top hung window | nr | 4
9.2.04 | 1650 | x | 1000 | W03 - Top hung window | nr | 21
9.2.05 | 1000 | x | 1000 | W04 - Top hung window | nr | 12
9.2.06 | 3000 | x | 1300 | W05 - Top hung window | nr | 1
9.2.07 | 2400 | x | 3600 | W06a - Fixed window | nr | 1
9.2.08 | 3200 | x | 3405 | W06b - Fixed window | nr | 1
9.2.09 | 3200 | x | 2985 | W06c - Fixed window | nr | 1
9.2.10 | 3200 | x | 2565 | W06d - Fixed window | nr | 1
9.2.11 | 900 | x | 2700 | W07 - Top hung window and fixed window panel | nr | 9
9.2.12 | 1950 | x | 1800 | W08 - Top hung window | nr | 2
9.2.13 | 2350 | x | 1800 | W09 - Top hung window | nr | 8
9.2.14 | 1800 | x | 1500 | SW01 - Sliding window | nr | 10
9.2.15 | 3000 | x | 1500 | SW02 - Sliding window | nr | 5
9.2.16 | 1100 | x | 1100 | SW04 - Sliding window | nr | 1
9.2.17 |  |  |  | Supply and complete installation of top quality Hospital grade bed side curtain including railing/Track. Length of rail/track is 6870mm, | Item | 43
9.2.18 |  |  |  | Supply and complete installation of window curtains and vertical bliends | Item | 1
9.3.00 |  |  |  | TOTAL OF BILL №: 09 - Carried Over To Summary
10.0.00 |  |  |  | Bill №: 10 - DOORS, SHUTTERS & HATCHES
10.1.00 | GENERAL
|  |  | (a) | Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
|  |  | (b) | Rates shall include for door frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings.
|  |  | (c) | Sizes are given overall outside dimensions of actual doors and windows.
|  |  | (d) | Thickness and sizes of glass panels are shown on the Drawings and doors and windows schedule.
|  |  | (e) | Rates shall include for all painting as specified
|  |  | (f) | Rates shall include all items specified in the door schedule and specification.
|  |  | (g) | Frames and sashes to be 25-60 micron black powder coated aluminium other wise specified.
|  |  | (g) | All solid timber doors are teak timber or equivalent.
10.2.00 | DOORS
10.2.01 | 1500 | x | 2100 | TD01 - Solid timber door with view panel (double swing) | nr | 6
10.2.02 | 1500 | x | 2100 | TD02 - Solid timber door (double swing) | nr | 1
10.2.03 | 1500 | x | 2100 | TD03 - Solid timber door with view panel (double swing) | nr | 8
10.2.04 | 1500 | x | 2100 | TD04 - Solid timber door (double swing) | nr | 2
10.2.05 | 1000 | x | 2100 | TD05 - Solid timber door with view panel (single swing) | nr | 53
10.2.06 | 1000 | x | 2100 | TD06 - Solid timber door with view panel (single swing) | nr | 2
10.2.07 | 1000 | x | 2100 | TD07 - Solid timber door with view panel (single swing) | nr | 9
10.2.08 | 1000 | x | 2100 | TD08 - Solid timber door (single swing) | nr | 34
10.2.09 | 1000 | x | 2100 | TD09 - Solid timber door (single swing) | nr | 19
10.2.10 | 1000 | x | 2500 | TD10 - Solid timber door (single swing) with top hung window | nr | 6
10.2.11 | 900 | x | 2100 | TD11 - Solid timber door (single swing) | nr | 9
10.2.12 | 850 | x | 2100 | TD12 - Solid timber door (single swing) | nr | 10
10.2.13 | 1000 | x | 2100 | PD01 - Marine Plywood door (single swing) | nr | 11
10.2.14 | 750 | x | 2100 | PD02 - Marine Plywood door (single swing) | nr | 21
10.2.15 | 750 | x | 2100 | PD03 - Marine Plywood door (single swing) | nr | 4
10.2.16 | 1500 | x | 2100 | THD01 - Prefabricated Theatre door with view panel (Double Swing) by specialized theatre door supplier | nr | 1
10.2.17 | 1500 | x | 2100 | LD01 - Lead-lined solid timber door with view panel (Double Swing) | nr | 1
10.2.18 | 1000 | x | 2100 | LD02 - Lead-lined solid timber door with view panel (Single Swing) | nr | 1
10.2.19 | 1500 | x | 2100 | FD01 - Fire-rated door (Double Swing) | nr | 2
10.2.20 | 1000 | x | 2100 | FD02 - Fire-rated door (Single Swing) | nr | 3
10.2.21 | 1500 | x | 2100 | AD01 - Aluminium door with fixed glass panel (Double Swing) | nr | 11
10.2.22 | 1000 | x | 2100 | AD02 - Aluminium door (Single Swing) | nr | 12
10.2.23 | 1000 | x | 2100 | AD03 - Aluminium door (Single Swing) | nr | 1
10.2.24 | 2000 | x | 2100 | TG01 - Sliding door | nr | 1
10.2.25 | 3500 | x | 2100 | TG02 - Sliding door and fixed window panel | nr | 2
10.2.26 | 2000 | x | 2100 | SD01 - Sliding door | nr | 7
10.2.27 | 1800 | x | 2100 | SD02 - Sliding door | nr | 3
10.2.28 | 3000 | x | 2600 | RS01 - Roller Shutter Door | nr | 2
10.3.00 |  |  |  | TOTAL OF BILL №: 10 - Carried Over To Summary
11.0.00 |  |  |  | Bill №: 11 - DECORATIONS
11.1.00 | GENERAL
|  |  | (a) | Rates shall include for: the provision, erection and removal of scaffolding, preparation, wall putty application, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door & window furniture.
|  |  | (b) | All painting work shall be carried in accordance with the Specifications.
11.2.00 |  |  |  | WALL PAINTING
EXTERNAL SURFACES: Textured weatherbound paint finish as specified.
11.2.01 |  |  |  | GROUND FLOOR | m2 | 1870.99
11.2.02 |  |  |  | FIRST FLOOR | m2 | 1089.22
11.2.03 |  |  |  | TERRACE FLOOR | m2 | 752.4
INTERNAL SURFACES: Emulsion paint finish including putty application on brick walls as specified.
11.2.04 |  |  |  | GROUND FLOOR | m2 | 3288.99
11.2.05 |  |  |  | FIRST FLOOR | m2 | 3148.22
11.2.06 |  |  |  | TERRACE FLOOR | m2 | 79.12
11.3.00 |  |  |  | CEILING PAINTING
Matt emulsion paint finish ground smoothing as specified in specification and finishing schedule.
11.3.01 |  |  |  | GROUND FLOOR | m2 | 755.88
11.3.02 |  |  |  | FIRST FLOOR | m2 | 589.58
11.3.03 |  |  |  | TERRACE FLOOR | m2 | 11.96
11.4.00 |  |  |  | SLAB SOFFIT PAINTING
Matt emulsion paint finish ground smoothing as specified in specification and finishing schedule.
11.4.01 |  |  |  | GROUND FLOOR | m2 | 19.6
11.4.02 |  |  |  | FIRST FLOOR | m2 | 25.34
11.4.03 |  |  |  | TERRACE FLOOR | m2 | 41.34
11.5.00 |  |  |  | TOTAL OF BILL №: 11 - Carried Over To Summary
12.0.00 |  |  |  | Bill №: 12 - FINISHES
12.1.00 | GENERAL
|  |  | (a) | Rates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing.
12.2.00 |  |  |  | PAVING
Paver block
12.2.01 |  |  |  | Ground | m2 | 989.24
12.3.00 |  |  |  | FLOOR PAINTING
Gray Epoxy paint over leveling screed
12.3.01 |  |  |  | Ground Floor | m2 | 182.37
12.3.02 |  |  |  | First Floor | m2 | 12.56
12.3.03 |  |  |  | Terrace Floor | m2 | 1710
12.4.00 |  |  |  | FLOOR TILING
1200 x 1200 Semi-polished fullbody Homogeneous floor tile
12.4.01 |  |  |  | Ground Floor | m2 | 417.38
12.4.02 |  |  |  | First Floor | m2 | 550.7
12.4.03 |  |  |  | Terrace Floor | m2 | 12.5
1200 x 1200 Polished fullbody Homogeneous floor tile
12.4.04 |  |  |  | First Floor | m2 | 103.82
600 x 600 Semi-polished fullbody Homogeneous floor tile
12.4.05 |  |  |  | Ground Floor | m2 | 645.32
12.4.06 |  |  |  | First Floor | m2 | 476.64
600 x 600 Matt full body Homogeneous Non-slip outdoor floor Tiles
12.4.07 |  |  |  | Ground Floor | m2 | 292.29
12.4.08 |  |  |  | First Floor | m2 | 145.29
600 x 600 Matt fullbody Homogeneous Non-slip floor Tiles
12.4.09 |  |  |  | Ground Floor | m2 | 215.39
12.4.10 |  |  |  | First Floor | m2 | 247.17
300 x 300 Matt fullbody Homogeneous Non-slip floor Tiles
12.4.11 |  |  |  | Ground Floor | m2 | 118.28
12.4.12 |  |  |  | First Floor | m2 | 147.91
12.5.00 |  |  |  | Vinyle flooring
Homogenous Vinyl flooring
12.5.01 |  |  |  | Ground Floor | m2 | 275.39
12.5.02 |  |  |  | First Floor | m2 | 42.35
Permanently static dissipative pressed Homogenous Vinyl flooring
12.5.03 |  |  |  | First Floor | m2 | 28.44
12.6.00 |  |  |  | WALL TILING
300 x 600 Ceramic Tiles
12.6.01 |  |  |  | Ground Floor | m2 | 900.2
12.6.02 |  |  |  | Second Floor | m2 | 984.36
12.7.00 |  |  |  | Vinyle wall covering
Vinyl wall covering to 2100mm height
12.7.01 |  |  |  | Ground Floor | m2 | 1055.7
12.7.02 |  |  |  | First Floor | m2 | 899.96
12.8.00 |  |  |  | Cladding
PVC Hygenic Cladding
12.8.01 |  |  |  | Ground Floor | m2 | 2376.73
12.8.02 |  |  |  | First Floor | m2 | 1749.2
12.9.00 |  |  |  | TOTAL OF BILL №: 12 - Carried Over To Summary
13.0.00 |  |  |  | Bill №: 13 - ROOFING
13.1.00 | GENERAL
|  |  | (a) | Rates shall include for: fair edges, dressing over angel fillets, roof sealant, turning into grooves, all other labours, circular edges, nails, screws and other fixings and laps.
13.2.00 |  |  |  | ROOF COVERING
13.2.01 |  |  |  | BHP Lysaght Trimdek Hi-Ten or equivalent roofing sheet, over C purlin frame including all fixings, fixed in accordance with manufacturer's instructions. | m² | 494.1
13.2.02 |  |  |  | 50mm mineral wool insulation with both side foil backing on one side. | m² | 494.1
13.3.00 |  |  |  | CAPPING
13.3.01 |  |  |  | Lysaght ridge Flashing as per drawing | m | 50.63
13.4.00 |  |  |  | GUTTER
13.4.01 |  |  |  | Zinc gutter 200 x200mm | m | 80.55
13.5.00 |  |  |  | FASCIA BOARD
13.5.01 | 50 | x | 200 | mm Fascia Board ( fiber cement board). | m | 80.55
13.5.00 |  |  |  | TOTAL OF BILL №: 13 - Carried Over To Summary
14.0.00 |  |  |  | Bill №: 14 - HYDRAULICS AND DRAINAGE
14.1.00 | HYDRAULICS
14.2.00 | GENERAL
|  |  | (a) | All plumbing works included herein shall be executed according to the provisions of the plumbing code of the Maldives. In the absence thereof, shall be in accordance with acceptable international code and standards.
|  |  | (b) | Coordinate the drawing with other related drawings and specification. The engineer shall be notified immediately of any discrepancy found therein.
|  |  | (c) | All pipes shall be installed as indicated on plans. Any relocations required for proper execution of other trade shall be with prior approval of the Architect or Engineer.
|  |  | (d) | Proposed sanitary utilities shall confirm to the actual location. Depth and invert elevation of all existing pipes and structures as verified by the contractor.
|  |  | (e) | All slopes for horizontal drainage shall maintain 1% unless otherwise specified.
|  |  | (f) | Size of water supply pipes to fixtures shall be in accordance with the manufacturer's instructions.
|  |  | (g) | The contractor shall verify all existing utilities at site, coordinate the works with the sewer line effluent disposal point and water line service connecting point.
|  |  | (h) | All pipe sizes are in millimeters and all dimensions are in meters unless otherwise specified
|  |  | (i) | The proposed utilities shall be made to conform to the actual location, tapping point, depth and invert levels of all existing pipes and structures as verified by the contractor.
|  |  | (j) | All pipe diameter indicated on plans are nominal pipe sizes.
|  |  | (k) | Vent and waste stack to connect to soil pipe. Soil pipe stack as main soil and waste vent through roof
14.3.00 |  |  |  | MWSC WATER SUPPLY NETWORK
14.3.01 |  |  |  | Connection to main network | item | 1
14.3.02 |  |  |  | GROUND FLOOR | item | 1
14.3.03 |  |  |  | FIRST FLOOR | item | 1
14.4.00 |  |  |  | SANITARY FITTINGS
Sanitary fittings including installations as per drawings
14.4.01 |  |  |  | Water closet (Anti bacterial type), dual top flush | nr | 46
14.4.02 |  |  |  | Muslim Shower | nr | 46
14.4.03 |  |  |  | Bidet | nr | 2
14.4.04 |  |  |  | Wash basin | nr | 46
14.4.05 |  |  |  | Wash basin tap | nr | 46
14.4.06 |  |  |  | Grab rails at WC | nr | 16
14.4.07 |  |  |  | ceramic laboratory sink 620x480x255mm with sink cupboard | nr | 62
14.4.08 |  |  |  | Sink tap | nr | 62
14.4.09 |  |  |  | Sink (pantry) | nr | 8
14.4.10 |  |  |  | Sink tap (pantry) | nr | 8
14.4.11 |  |  |  | Toilet paper holder | nr | 46
14.4.12 |  |  |  | Soap holder | nr | 116
14.4.13 |  |  |  | Mirror set | nr | 46
14.4.14 |  |  |  | Shower | nr | 10
14.4.15 |  |  |  | Shower H&C | nr | 6
14.4.16 |  |  |  | Bed pan Wash | nr | 14
14.4.17 |  |  |  | Floor drain (FD) | nr | 40
14.4.18 |  |  |  | Vent stack through roof | item | 2
14.4.19 |  |  |  | Supply and Complete instalaation of Scrub sink, Inspital SK90.02 dual sink or equivalent at OT. | item | 1
14.5.00 |  |  |  | DRAINAGE PIPEWORKS
14.5.01 |  |  |  | Connection to main network | item | 1
14.5.02 |  |  |  | GROUND FLOOR | item | 1
14.5.03 |  |  |  | FIRST FLOOR | item | 1
14.6.00 |  |  |  | WATER PUMP
14.5.01 |  |  |  | Designg supply and installation of Ground water pump, Deavy or equivalent. | item | 2
14.5.02 |  |  |  | Designg supply and installation of Fresh water pump, Deavy or equivalent. | item | 2
14.6.00 |  |  |  | TOTAL OF BILL №: 14 - Carried Over To Summary
15.0.00 |  |  |  | Bill №: 15 - ELECTRICAL INSTALLATIONS
15.1.00 | GENERAL
|  |  | (a) | All lights to be connected to their respective DB
|  |  | (b) | All corridor lights and outdoor lights are timmered
|  |  | (c) | The AC unit shall be suitable for operation under tropical condition with ambient temperature and relative humidity
|  |  | (d) | Proper access for easy maintenance to be provided as recommended by the manufacturer of AC equipment above false ceiling
|  |  | (e) | All ceiling suspended unit to be provided with anti vibration hangers spring type
|  |  | (f) | GI Ducting/Pre insulated dcut for common areas and AL Ducting for OTs ,CSSD and sterile areas
|  |  | (g) | Acoustic insulation to be provided for duct with minimum 3Sqm from each AHU unit except OT and CSSD areas AHUs Canvas connection to be provided between indoor unit and duct
|  |  | (h) | Canvas connection to be provided between indoor unit and duct
|  |  | (i) | Aluminum cladding to be provided over the insulation for the exposed duct and pipe works
|  |  | (j) | Air outlet shall be completely factory aluminum extruded with powder coated and the colour shall be the approval of the interior design
|  |  | (k) | Air outlet location and size shall be adjusted to suit reflected ceiling drawing,or site condition
|  |  | (l) | Louver with bird screen to be provided for all the fresh air and exhaust air duct
|  |  | (m) | Kitchen hood exhaust should be provided in the kitchen areas
|  |  | (n) | Contractor shall be responsible to provide electrical power requirements to electrical contractor
|  |  | (o) | Contractor shall be responsible for coordination of all other services
|  |  | (p) | Contractor shall be responsible to modify,change,reroute,re locate as per the site condition and submit shop drawing for approval
|  |  | (q) | Contractor to be provided detailed shop drawings before starting works
15.2.00 | MAINS CONNECTION & BOARD
15.2.01 |  |  |  | Completion of 3 phase electrical main. | item | 1
15.2.02 |  |  |  | Main Panel Board | nr | 1
15.3.00 | ELECTRICAL BOARDS
Complete installation, including for all cabling, wiring, connections, earthing, painting, testing and similar of:
15.3.01 |  |  |  | Distribution Board | nr | 55
15.4.00 | LIGHTING
15.4.01 |  |  |  | LED recessed light type 1 (18W) | nr | 11
15.4.02 |  |  |  | LED Strip Cover light IP65(8W) | nr | 56
15.4.03 |  |  |  | LED recessed light type 2 12W) | nr | 117
15.4.04 |  |  |  | 600x600 LED Square diffuser with T5 Fittings(12W) | nr | 281
15.4.05 |  |  |  | LED recessed light type 3 12W) | nr | 77
15.4.06 |  |  |  | LED Outdoor Wall light 8W weatherproof | nr | 32
15.4.07 |  |  |  | LED Dustproof (32W) | nr | 1
15.4.08 |  |  |  | Troffer 28W LED with T5 fitting | nr | 35
15.4.09 |  |  |  | LED SPKE Light 3W | nr | 7
15.4.10 |  |  |  | Outdoor Wall light Weatherproof 12W | nr | 47
15.4.11 |  |  |  | LED Indoor Wall light up/down 8W | nr | 30
15.4.12 |  |  |  | Supply and complete installation of OT light. Inspital OT light, model LD20.53, Double Head with Arm Mounted 24” Medical Monitor (With Camera) | Item | 1
1.5.00 | SWITCHES
15.5.01 |  |  |  | Light switch 2gang | nr | 99
15.5.02 |  |  |  | Light switch 3gang | nr | 12
15.5.03 |  |  |  | Light switch 4gang | nr | 8
15.5.04 |  |  |  | Ceiling Switch | nr | 14
15.6.00 | SOCKETS
15.6.01 |  |  |  | 13A power outlet (300mm from FFL) | nr | 260
15.6.02 |  |  |  | 13A Twin socket outlet (300mm from FFL) | nr | 361
15.6.03 |  |  |  | 13A UPS socket outlet (300mm from FFL) | nr | 75
15.6.04 |  |  |  | Power over ethernet outlet | nr | 16
15.6.05 |  |  |  | Flex Power Outlet with Cover plate(Ehxhaust fan) | nr | 11
15.6.06 |  |  |  | 15A Power Outlet | nr | 14
15.6.07 |  |  |  | VGA Cable for projector | nr | 2
15.6.08 |  |  |  | Proximity Card reader | nr | 27
15.6.09 |  |  |  | Automatic Door motion detector sensor | nr | 6
15.6.10 |  |  |  | Access controller | nr | 3
15.6.11 |  |  |  | Exit switch | nr | 27
15.6.12 |  |  |  | 13A sockets for toilets | nr | 8
15.6.13 |  |  |  | Weatherproof polycarbonate enclosure | nr | 69
15.6.14 |  |  |  | Paging mic | nr | 13
15.6.15 |  |  |  | Volume controller | nr | 13
15.6.16 |  |  |  | Wall speakers at ceiling level | nr | 9
15.6.17 |  |  |  | Emergency door release | nr | 30
15.6.18 |  |  |  | Nurse station panel room indicator | nr | 12
15.6.19 |  |  |  | Electromagnetic lock | nr | 30
15.6.20 |  |  |  | Door bell button | nr | 7
15.6.21 |  |  |  | Home speaker | nr | 13
15.6.22 |  |  |  | Ceiling speaker | nr | 74
15.6.23 |  |  |  | Doorbell Receiver | nr | 7
15.6.24 |  |  |  | Power points on Envirom Verticalheadwalls call point to nurses station integrated in Envirom bedhead trunk | nr | 84
15.6.25 |  |  |  | Theater control panel(Includes telephone unit, fire alarm strobe, medical gas indicator unit) | nr | 1
15.6.26 |  |  |  | Table integrated or FFL Outlets | nr | 45
15.6.27 |  |  |  | Design supply and installation of IP PABX with IP telephone. | Item | 1
15.6.28 |  |  |  | Supply and complete installation of Computer system as per specifications | Item | 15
15.6.29 |  |  |  | Supply and complete installation of 65" QLED TV, LG or Equivalent at meting room. Any cast or chrome cast must support. | Item | 4
15.6.30 |  |  |  | Supplying of Canon Monochrome Multi-Functional Device, Image runner iR 2630i, (A4 & A3 sze) 3 in 1 printer or equivalent. | Item | 3
15.6.31 |  |  |  | Design supply and complete installation on 50KW Solar PV system. Rates includes to complete the system and connect to the grid with net metering as per specification. ( junction box specs, Solar AC&DC cable specs, solar bracket specs, inverter specs & solar panel specs). | Item | 1
15.7.00 | AIR CONDITION AND VENTILATION
General
(a) Rates shall include for supplying and complete installation of air-conditioning systems; including all pipework, electrical wiring, insulation, stands for outdoor units etc.
(b)All AC Equipments must be VRV/VRF or Central systems which have the capacity to control & operate multiple indoor units
(c) Contractor shall provide Shop Drawings for Consultants' Approval for all electrical units including lighting, power, ACMV systems.
(d) The Brand of AC Equipment specified or to be proposed should demonstrate that it is adequate to cater for highly corrosive environment of Maldives.
(e)The brand or AC Equipment specified should demonstrate all specs below from manufacturer's catalogue /spec sheet.
(d) Proposed system brand and models shall be detailed in Contractor's quotation. Contractor shall propose design and manufacturer's specification sheets of models/units proposed, detailing minimum of below information.
Outdoor Specifications
(a)The Outdoor Unit Shall be factory assembled with Weather Proof casing, constructed from Heavy Gauge Mild Steel Panels and coated with Anti Corrosive Epoxy resin finish. The unit should be completely factory wired and tested and shall be fitted with all necessary controls and switch gear.
(b) All outdoor units need to be VRV or Central systems which have the capacity to control & operate multiple indoor units
(c) All outdoor units needs to have aluminium fins with 105+2 μm thickness, with special Anti corrosive coating of 1.3 ± 0. 35 μm thickness and an outside Hydrophilic layer coating of 0.35 ± 0. 07 μm thickness.
(d) The proposed outdoor or outdoor set specifications should detail Energy Efficiency Ratio (EER) kw/kwh not less than 4.5kw
(e) The brand of AC Equipment proposed should have Outdoor Environment sensor for Compressor Control and adjustment
(f) The Brand of AC Equipment proposed should have an outdoor or outdoor sets of Sound Pressure Level below 60dB (A)
(g)All Outdoor units shall be with inverter compressors and be able to operate even in the event of failure of one compressor.
(H) All outdoor units shall be equipped with high efficiency optimized heat exchangers with variable heat exchanger circuits
(i)The outdoor units shall be provided with its own microprocessor control panels
(j) Service and Parts Replacement Warranty of minimum 12 months for the proposed system should be proposed by the AC Manufacturer
(k) The Outdoot should have a high external static pressure (75Pa or higher)
(l) The Scroll Compressor should have Back Pressure control mechanism to minimize refrigerant load and operational loss.
(m) Outdoor refrigerant type shall be R410A or R32
Indoor Specifications
(a) The address of the indoor unit shall be set automatically in case of individual and group control
(b) Wired centralized control shall be set by liquid crystal remote controller
(c) The fan shall be a dual suction, aerodynamically designed turbo, multi blade centrifugal type fan which shall be statically & dynamically balanced to ensure low noise and vibration free operation. The fan shall be direct driven, mounted directly on motor shaft having support from the unit housing.
(d) The cooling coil shall be made out of seamless copper tubes and have continuous aluminum fins. The tubes shall be staggered in the direction of airflow and shall be hydraulically/ mechanically expanded to bond to the fins. Each coil shall be factory tested at 21kg/sqm air pressure under water.
(e) Each unit shall have a cleanable type filter fixed to an integrally moulded plastic frame. The filter shall be a slide out type and shall be neatly inserted.
(f) Automatic Sensors to control airflow and direction of the airflow by detecting human presence
(i) Each unit shall be provided with a hand held multi-function remote controller. The controller shall be able to change fan speed and angle of swing, temperature and mode (Optional).
(J) Each Unit shall have service Ball valves for After sale service and future Isolation of FCU
(h) The proposed indoor unit should have an indoor Sound Pressure Level below 30dB (A)
(f) All AC Fresh air duct systems must have an H14 Hepa filters attached with 99.99% efficiency on Supply & Return Duct as well
Refrigerant Piping
(a) All refrigerant piping for the air conditioning system shall be constructed from Hard seamless copper up to outer diameter of 41.3 mm and hard drawn copper above outer diameter of41.3 mm. Fittings shall have silver-soldered joints and connections to equipment shall us compression fittings.
(b) All joints in copper piping shall be swag joints using low temperature brazing and or silver solder. Before joining any copper pipe or fittings, its interiors shall be thoroughly cleaned by passing a clean cloth via wire or cable through its entire length. The piping shall be continuously kept clean of dirt etc. while constructing the joints. Subsequently, it shall be thoroughly blown out using nitrogen.
(c) After the refrigerant piping installation has been completed, the refrigerant piping system shall be pressure tested using nitrogen at pressure of 580 PSIG. Pressure shall be maintained in the system for 24 hours. The system shall then be evacuated to minimum vacuum of 700mm hg and held for 24 hours.
(d) The thickness of copper piping shall as per Standard ASTM B280-03
Refrigerant Pipe Insulation
(a) The whole of the liquid and suction refrigerant lines including all fittings, valves etc. shall be insulated with 25mm thick insulation for all copper sizes. Insulation shall be closed cell elastomeric nitrile rubber.
(b) To protect nitrile rubber of exposed piping from degrading due ultra violet rays & atmospheric conditons, it shall be covered polyshield coating with at least two coats of resin and hardener (Make-Polybond /Paramount Polytreat). Fiberglass tape shall be helically wound & painted with two coats of resin with hardener to give smooth & plain finish.
(c) All insulation has to be wrapped in Aluminium Fiber Foil Tape or sheet
Ducting & Ventilation System
(a) All Conceal Duct Indoor System shall be connected to a Duct Ventilation system which shall be designed to provide the most appropriate air flow for designed Air-condition areas
(b) The Duct System shall be made with Pre-Insulated Panels with the below specs - Panel Thickness: 20 – 30mm - Foam Density: 45-48kg/m3 - Aluminium thickness: 80/80m - Alimunium Type: Embossed - The Boards should be Anti-Bacterial, Anti Fungus & Fire Restiant
(c) All supplier & Return Diffusers shall be - The Supply and return air diffusers/grills shall be made of extruded aluminum section with flush fixed pattern - White Powder Coated RAL9010 or 9016 standard - Supply Diffusers shall be with opposed Blade Volume dampers - Thickness of frame should not be less than 1.2mm. The core of the diffuser is 0.9mm thick pressed aluminum.
(d) All ducts shall be installed generally as per the drawings and in strict accordance with approved shop drawings to be prepared by the Contractor.
Rates shall include for outdoor units
15.7.01 |  |  |  | Air Handling Unit | nr | 20
15.7.02 |  |  |  | Wall mounted AC unit | nr | 48
15.7.03 |  |  |  | 4 way cassette units | nr | 68
15.7.04 |  |  |  | Outdoor unit top discharge | nr | 8
15.7.05 |  |  |  | Outdoor unit side discharge | nr | 5
15.7.06 |  |  |  | Ceiling mounted exhaust fan | nr | 11
15.7.07 |  |  |  | Fresh air/ exhaust air fan (Duct in line) | nr | 11
15.7.08 |  |  |  | Ceiling fan (52"-54") | nr | 18
15.7.09 |  |  |  | Exhaust air grill | nr | 89
15.8.00 | IT / SECURTIY SYSTEM
15.8.01 |  |  |  | Close circuit television | nr | 17
15.8.02 |  |  |  | Close circuit television pullbox | nr | 1
15.8.03 |  |  |  | Centralization module | nr | 5
15.8.04 |  |  |  | Nurse call | nr | 21
15.8.05 |  |  |  | Pilot light | nr | 16
15.8.06 |  |  |  | Tel/ Data terminal cabinet | nr | 1
15.8.07 |  |  |  | Main distribution frame - TTC | nr | 1
15.8.08 |  |  |  | Tel/ Data outlet | nr | 91
15.8.09 |  |  |  | Private automated branch exchange | nr | 1
15.9.00 | LIGHTENING PROTECTION SYSTEM
15.9.01 |  |  |  | Lightning protection system complete | item | 1
15.10.00 |  |  |  | TOTAL OF BILL №: 15 - Carried Over To Summary
16.0.00 |  |  |  | Bill №: 16 - INSULATION, FIRE STOPPING & FIRE PROTECTION
16.1.00 | GENERAL
|  |  | (a) | Contractor may modify the system to suit the supplied equipment.
|  |  | (b) | For actual number of detectors/ anunciator manual pull station and horn, refer to lay-out plan.
|  |  | (c) | Firemans telephone jacks at respective floors shall be treated as one zone per floor.
|  |  | (d) | j mean fire rated cable gauge #16.
|  |  | (e) | Size, type and number of wires may be modified by the contractor to suit the supplied equipment and as per manufacturers standard requirement.
|  |  | (f) | Wiring between TB's/ PB's and FACP are multiplex signal wiring.
|  |  | (g) | Circuit connection between detectors , MCP, annunciator etc… shall be conform via loop interface modules (addressable).
|  |  | (h) | Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
|  |  | (i) | Rates for cable conduits, fittings, equipment and similar items shall include for: all fixings to various building surfaces
|  |  | (j) | Rates shall include for all necessary electrical wiring and accessories required for completion
|  |  | (k) | All items shall be supply and complete installation
16.2.00 | FIRE FIGHTING SYSTEM
16.2.01 |  |  |  | Smoke detectors -Addressable/ Analog | nr | 286
16.2.02 |  |  |  | Heat detectors - Addressable/ Analog | nr | 11
16.2.03 |  |  |  | Fire alarm control panel | nr | 1
16.2.04 |  |  |  | Fire alarm manual call point | nr | 14
16.2.05 |  |  |  | Fire alarm sounder with strobe light 950B | nr | 14
16.2.06 |  |  |  | Fire resistant cable 1.5mm2 x 2 core | item | 1
16.2.07 |  |  |  | Fire blanket | nr | 11
16.2.08 |  |  |  | Fire extinguishers - 9 liters H2O &2 KG Co2 | nr | 55
16.2.09 |  |  |  | Fire hose reel with 25mm hose and 30 meters | nr | 8
16.2.10 |  |  |  | Emergency light | nr | 14
16.2.11 |  |  |  | Exit signs light with back up batteries | nr | 24
16.2.12 |  |  |  | MWSC Water meter | nr | 1
16.2.13 |  |  |  | 25mm air release valve | nr | 1
16.2.14 |  |  |  | PVC Pipe- 40mm connection to fill fire tank | item | 1
16.2.15 |  |  |  | Pipe riser- GI pipe 100mm, schedule 40 | nr | 9
16.2.16 |  |  |  | Pipe riser- GI pipe 25mm, schedule 40 | nr | 9
16.2.17 |  |  |  | Pipe riser- GI pipe 50mm, schedule 40 | item | 1
16.2.18 |  |  |  | Pipe riser- GI pipe 25mm, schedule 40 | item | 1
16.2.19 |  |  |  | Pipe HDPE 100mm , PE 100, PN16, SDR11 | item | 1
16.2.20 |  |  |  | Fire pump system consist of electrical duty pump and diesel stand by pump- pumps capacity is 466 liters @70mm head | nr | 1
16.2.21 |  |  |  | Fire rated door 90 mins | nr | 2
16.3.00 |  |  |  | TOTAL OF BILL №: 16 - Carried Over To Summary
17.0.00 |  |  |  | Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS
OXYGEN & MEDICAL AIR FOR ALL BEDS
17.01.00 | GENERAL
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rates shall include for: Design, supply and install according to hospital operators’ demand/specifications. screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
17.02.00 | OXYGEN DELIVERY SYSTEM
Design supply and complete installation of Piped and tested oxygen delivery system from the Oxygen bank as per Specifications and manufactures guidelines, instructions. Oxygen bank, capacity to connect minimum 6 jumbo cylinder. System to be insttaled as per manufactures standards.
17.02.1 |  |  |  | ER area | Item | 9
17.02.2 |  |  |  | SUSPECTED ISOLATION ROOM | Item | 4
17.02.3 |  |  |  | GYNY WARD | Item | 4
17.02.4 |  |  |  | NICU WARD | Item | 2
17.02.5 |  |  |  | PEDI WARD | Item | 4
17.02.6 |  |  |  | PRIVATE ROOM | Item | 2
17.02.7 |  |  |  | LABOUR ROOM | Item | 3
17.02.8 |  |  |  | MEDICAL WARD (MALE) | Item | 4
17.02.9 |  |  |  | MEDICAL WARD (FEMALE) | Item | 4
17.02.10 |  |  |  | TREATMENT ROOM | Item | 1
MEDICAL AIR SYSTEM
Design supply and complete installation of Piped and tested Medical air system from medical air plant as per Specifications and manufactures guidelines, instructions.. Oxygen bank, capacity to connect minimum 12 jumbo cylinder. System to be insttaled as per manufactures standards.
17.02.11 |  |  |  | ER area | Item | 9
17.02.12 |  |  |  | SUSPECTED ISOLATION ROOM | Item | 4
17.02.13 |  |  |  | GYNY WARD | Item | 4
17.02.14 |  |  |  | NICU WARD | Item | 2
17.02.15 |  |  |  | PEDI WARD | Item | 4
17.02.16 |  |  |  | PRIVATE ROOM | Item | 2
17.02.17 |  |  |  | LABOUR ROOM | Item | 3
17.02.18 |  |  |  | MEDICAL WARD (MALE) | Item | 4
17.02.19 |  |  |  | MEDICAL WARD (FEMALE) | Item | 4
17.02.20 |  |  |  | TREATMENT ROOM | Item | 1
VACUME SYTEM
Design supply and complete installation of Piped and tested vacuum system from a central vacuum system as per Specifications and manufactures guidelines, instructions..
17.02.21 |  |  |  | ER area | Item | 9
17.02.22 |  |  |  | SUSPECTED ISOLATION ROOM | Item | 4
17.02.23 |  |  |  | GYNY WARD | Item | 4
17.02.24 |  |  |  | NICU WARD | Item | 2
17.02.25 |  |  |  | PEDI WARD | Item | 4
17.02.26 |  |  |  | PRIVATE ROOM | Item | 2
17.02.27 |  |  |  | LABOUR ROOM | Item | 3
17.02.28 |  |  |  | MEDICAL WARD (MALE) | Item | 4
17.02.29 |  |  |  | MEDICAL WARD (FEMALE) | Item | 4
17.02.30 |  |  |  | TREATMENT ROOM | Item | 1
BED HEAD UNITS
17.02.31 |  |  |  | Supply and complete installation of Bed head units, with control panels , each unit must includes 13amp 4 single sockets, 15amp 1 single socket with 2 USB port, 1 network point, Obsevatuion light and other necessary accessories. | Item | 37
17.3.00 |  |  |  | TOTAL OF BILL №: 16 - Carried Over To Summary
18.0.00 |  |  |  | Bill №: 18 - ADDITIONS AND OMMISIONS
18.1.00 | ADDITIONS
18.1.01 |  |  |  | Bill №: 01 - PRELIMINARIES
18.1.02 |  |  |  | Bill №: 02 - GROUND WORKS
18.1.03 |  |  |  | Bill №: 03 - CONCRETE WORKS
18.1.04 |  |  |  | Bill №: 04 - MASONRY & PLASTERING
18.1.05 |  |  |  | Bill №: 05 - STRUCTURAL METAL WORKS
18.1.06 |  |  |  | Bill №: 06 - CARPENTRY
18.1.07 |  |  |  | Bill №: 07 - RAILINGS
18.1.08 |  |  |  | Bill №: 08 - CEILING
18.1.09 |  |  |  | Bill №: 09 - WINDOWS, SCREENS & LIGHTS
18.1.10 |  |  |  | Bill №: 10 - DOORS, SHUTTERS & HATCHES
18.1.11 |  |  |  | Bill №: 11 - DECORATIONS
18.1.12 |  |  |  | Bill №: 12 - FINISHES
18.1.13 |  |  |  | Bill №: 13 - ROOFING
18.1.14 |  |  |  | Bill №: 14 - HYDRAULICS AND DRAINAGE
18.1.15 |  |  |  | Bill №: 15 - ELECTRICAL INSTALLATIONS
18.1.16 |  |  |  | Bill №: 16 - INSULATION, FIRE STOPPING & FIRE PROTECTION
18.1.17 |  |  |  | Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS
18.1.18 |  |  |  | Bill №: 18 - ADDITIONS AND OMMISIONS
TOTAL
18.2.00 | OMISSIONS
18.2.01 |  |  |  | Bill №: 01 - PRELIMINARIES
18.2.02 |  |  |  | Bill №: 02 - GROUND WORKS
18.2.03 |  |  |  | Bill №: 03 - CONCRETE WORKS
18.2.04 |  |  |  | Bill №: 04 - MASONRY & PLASTERING
18.2.05 |  |  |  | Bill №: 05 - STRUCTURAL METAL WORKS
18.2.06 |  |  |  | Bill №: 06 - CARPENTRY
18.2.07 |  |  |  | Bill №: 07 - RAILINGS
18.2.08 |  |  |  | Bill №: 08 - CEILING
18.2.09 |  |  |  | Bill №: 09 - WINDOWS, SCREENS & LIGHTS
18.2.10 |  |  |  | Bill №: 10 - DOORS, SHUTTERS & HATCHES
18.2.11 |  |  |  | Bill №: 11 - DECORATIONS
18.2.12 |  |  |  | Bill №: 12 - FINISHES
18.2.13 |  |  |  | Bill №: 13 - ROOFING
18.2.14 |  |  |  | Bill №: 14 - HYDRAULICS AND DRAINAGE
18.2.15 |  |  |  | Bill №: 15 - ELECTRICAL INSTALLATIONS
18.2.16 |  |  |  | Bill №: 16 - INSULATION, FIRE STOPPING & FIRE PROTECTION
18.2.17 |  |  |  | Bill №: 17 - OXYGEN & MEDICAL AIR FOR ALL BEDS
18.2.18 |  |  |  | Bill №: 18 - ADDITIONS AND OMMISIONS
TOTAL
18.3.00 |  |  |  | TOTAL OF BILL №: 18 - Carried Over To Summary