Section 6 - Purchaser’s Requirements

Table of Contents

1	Scope of Supply of Plant and Services	6-2

2.	Specifications	6-3

3.  	Drawings	6-4

4.  	Supplementary Information	6-5

5.  	Certificates	6-6

5.1  Form of Completion Certificate	6-7

5.2  Form of Operational Acceptance Certificate	6-8

6. 	Change Orders	6-9

6.1. 	Change Order Procedure	6-10

6.1.1	General	6-10

6.1.2 	Change Order Log	6-10

6.1.3	References for Changes	6-10

6.2	Change Order Forms	6-11

6.2.1	Request for Change Proposal Form	6-11

6.2.2  Estimate for Change Proposal Form	6-12

6.2.3  Acceptance of Estimate Form	6-13

6.2.4  Change Proposal Form	6-14

6.2.5  Change Order Form	6-16

6.2.6  Pending Agreement Change Order Form	6-17

6.2.7  Application for Change Proposal Form	6-18

7. 	Personnel Requirements	6-19

8. 	Equipment Requirements	6-20

### 1. Scope of Supply of Plant and Services

This section contains the Scope, the Specifications, the Drawings, and Supplementary Information that describe the Facilities and Forms to be used during the implementation of the contract, as well as Personnel and Equipment Requirements.

The scope of supply of plant and services consists of:

- The Design, supply, erection and commissioning of a new and fully functional Construction and Demolition waste processing plant including all steel structures, ladders, stairs, platforms, electrical and control installations, health and safety features according to the general and particular technical specifications and requirements

- The design of a roof/shed for protection against harsh weather conditions

- The coordination and work supervision of all works and interfaces

- The procurement of a set of spare and wear parts for two years of operation

- The training of Employers or Employers representative staff responsible for the operation of the plant

### 2. Specifications

The specifications contained in this section shall apply to all constructions and construction related works of the plant.

| 1. | SECTION 1 GENERAL |  |
| --- | --- | --- |
| 1.1 | INTERPRETATION OF DOCUMENTS |  |
| 1.1.1 | Application of the General Specification for Civil Engineering Works | (1) The provisions contained in the Particular Specification and the Drawings shall prevail over the provisions contained in this General Specification |
|  |  | (2) The provisions contained in this General Specification shall prevail over the provisions contained in British Standards, British Standard Codes of Practice and similar standard documents stated in the Contract. |
| 1.1.2 | Abbreviations | (1) The following list shows the meaning of the abbreviations for the common terms used in this GS but is not intended to be exhaustive: |
|  |  | ANSI: American National Standards Institute BS: British Standards BS EN:European Standard adopted as British Standards BS EN ISO : European Standards (EN) & International/Organization for Standardization for (ISO) ’s Standards adopted as British Standards CD: Chart Datum C & D: Construction and demolition CI: Cast iron CP: British Standard Code of Practice DDF: Disposal Delivery Form DFT: Dry film thickness DRS: Daily Record Summary EM&A: Environmental Monitoring and Audit EPA : Environmental Protection Agency FGL: Finished ground level, or finished level of the permanent works GCC: General Conditions of Contract GS: General Specification ISO: International Organisation for Standardization PC: Portland cement PD: Principal Datum PS: Particular Specification QPME: Quality Powered Mechanical Equipment SCC: Special Conditions of Contract SMM: Standard Method of Measurement for Civil Engineering |
|  |  | (2) The following list shows the meaning of the abbreviations for the units used in this GS but is not intended to be exhaustive: |
|  |  | °C: degrees Celsius dB: decibels g: gram g/mL: gram(s) per millilitre g/m2:gram(s) per square metre ha: hectare hr: hour kV: kiloVolt kW: kiloWatt m2 m3 m/s: square metre cubic metre metre(s) per second Mg : megagram Mg/m3 min: megagram(s) per cubic metre minute mL: millilitre mm: millimetre mm2 mm3 mm/s: square millimetre cubic millimeter millimetre(s) per second MPa: megaPascal N: Newton N/mm N/m2: Newton(s) per millimeter Newton(s) per square metre No. : number T: tonne µm: micrometer(micron) %: percentage |
| 1.1.3 | Glossary of terms | (1) Words and expressions to which meanings are assigned in any section of the GS shall have the same meanings in other sections of the GS except when the context otherwise requires. (2) Utilities are the installations (including cables, ducts and pipes) used to supply or provide electricity, lighting, traffic control, telecommunications, cable television, gas, water, drainage, sewerage and tramway, including all associated protection, supports, ancillary structures, fittings and equipment. |
| 1.1.4 | Trials and approval | (1) Reference in this GS to the approval of the Engineer shall mean approval given by the Engineer in writing. Materials, methods of construction and any other matters, which have been approved by the Engineer, shall not be changed without the approval of the Engineer to the proposed changes. (2) Trials shall be carried out as stated in the Contract to demonstrate that proposed materials and methods of construction will produce work which complies with the specified requirements. (3) Trials shall be carried out before the relevant permanent work starts so as to allow the Engineer a sufficient period to determine if the trial complies with the specified requirements. The Contractor shall inform the Engineer 24 hours, or such shorter period agreed by the Engineer, before the trial starts. (4) Trials shall be carried out using materials and methods of construction of the types submitted to the Engineer, and at locations agreed by the Engineer. (5) If in the opinion of the Engineer, the work that complies with the specified requirements has not been produced in the trial, particulars of proposed changes to the materials or methods of construction shall be submitted to the Engineer. Further trials shall be carried out until the work that complies with the specified requirements has been produced in the trial unless otherwise agreed by the Engineer. Works for which trials are required shall not commence, until in the opinion of the Engineer, the work that complies with the specified requirements has been produced in the trial. (6) Unless permitted by the Engineer, the materials and methods of construction used to produce the work that complies with the specified requirements in a trial, shall not be changed unless further trials have been carried out to demonstrate that the proposed changes are satisfactory. |
| 1.1.5 | British Standards, Codes of Practice and other standards | (1) Unless otherwise stated in the Contract, reference in this GS to British Standards, British Standard Codes of Practice and similar standards shall be to the latest edition (2) Later editions of British Standards, British Standard Codes of Practice and other similar standards, or standards which are considered to be equivalent, shall not apply unless approved by the Engineer. The Engineer shall not be bound to give or withhold his approval until the Contractor has provided him with a legal copy of the relevant standard for information. If approval is obtained, the Contractor shall provide two legal copies of the document for use by the Engineer. |
| 1.1.7 | Dimensions from Drawings | Dimensions shall not be obtained by scaling from the Drawings. Dimensions that are not shown on the Drawings or calculable from dimensions shown on the Drawings shall be obtained from the Engineer. |
| 1.3 | CONTRACTOR'S SUPERINTENDENCE |  |
| 1.3.1 | Foreman for concrete works | If structural concrete works are included in the Contract, the Contractor shall employ on the Site a Foreman who is suitably experienced in concrete works. The Foreman shall be on the Site at all times when concreting is in progress. |
| 1.4 | SAFETY |  |
| 1.4.1 | Safety | (1) The Contractor shall keep on the Site a set of the current Construction Site Safety Manual. Attention of the Contractor is drawn about the need to keep one set of the legislation, regulations and/or codes pf practice on the Site. (2) Safety precautions for working in sewers, drains and other confined spaces shall comply with the Factories and Industrial Undertakings (Confined Spaces) Regulations. (3) Divers shall undergo regular medical checks and obtain certificates of fitness. (4) Adequate safety equipment including, as appropriate, safety helmets, goggles, ear protectors, safety belts, safety equipment for working in sewers, drains and confined spaces, equipment for rescue from drowning, fire extinguishers, first aid equipment and other necessary safety equipment shall be available on the Site at all times. (5) Safety equipment, scaffolds, working platforms, ladders and other means of access, and lighting, signing and guarding equipment shall be inspected and maintained regularly. Lights and signs shall be kept clean and easy to read. Equipment that are damaged, dirty, incorrectly positioned or not in working order shall be repaired or replaced immediately. (6) Posters in both English and Dhivehi to draw attention to safety shall be obtained from the Labour Department and displayed at prominent locations around the Site including site offices, workshops and canteens. |
| 1.6 | CARE OF THE WORKS |  |
| 1.6.1 | Protection from water | (1) Unless otherwise permitted by the Engineer, all work shall be carried out, as near as may be practicable in the circumstances, in dry conditions, except where the work is required to be carried out in or with water or other fluids. (2) Where necessary and as far as practicable, the Works including materials for use in the Works shall be kept free of water and protected from damage due to water. Temporary drainage, pumping systems or other effective measures approved by the Engineer shall be used. Silt and debris shall be intercepted with traps before water is discharged from the Site. (3) The discharge points of the temporary drainage and pumping systems shall be approved by the Engineer. The Contractor shall make all arrangements with and obtain the necessary approvals and inspections from the relevant authorities for discharging water to drains, watercourses or the sea. The relevant work shall not start until the approved arrangements for disposal of the water have been implemented. (4) Measures shall be taken to prevent flotation of new and existing structures. |
| 1.6.2 | Protection from weather | (1) Works shall not be carried out in weather conditions that may adversely affect the works unless protection by methods agreed by the Engineer is provided. (2) Permanent works, including materials for permanent works, shall be protected by methods agreed by the Engineer from exposure to weather conditions that may adversely affect the work or materials. |
| 1.6.3 | Protection of works | Finished works shall be protected with methods agreed by the Engineer from damage that could arise from the execution of adjacent works. Works shall be carried out in such a manner that works carried out by others, including Government departments, utility undertakings and other contractors, is not damaged. |
| 1.7 | DAMAGE AND INTERFERENCE |  |
| 1.7.1 | Damage and interference | (1) Works shall be carried out in such a manner that, as far as is reasonable and practicable, there is no damage to or interference with the following, other than such damage as is required to enable the execution of the Works: - Utilities; - Structures, roads including street furniture, or other property; - Public or private vehicular or pedestrian accesses; and (2) The Contractor shall inform the Engineer as soon as practicable of any item, utility or thing which is not stated in the Contract as requiring diversion, removal or relocation but which the Contractor considers as requiring diversion, removal or relocation to enable the Works to be executed. The Contractor shall not divert, remove or relocate any such item, utility or thing without the prior approval of the Engineer. (3) Items which are damaged or interfered with as a result of the works being carried out and items which are diverted, removed or relocated to enable the works to be carried out, shall be reinstated to the same condition as was existing before the works started or to such other condition as may be agreed or instructed by the Engineer. |
| 1.7.2 | Utilities | (1) The details of existing utilities are given for information only and the accuracy of the details is not guaranteed. The Contractor shall make his own enquiries and shall carefully excavate inspection pits to locate accurately the utilities indicated to him by the utility undertakings. (2) Temporary supports and protection to utilities shall be provided by methods agreed by the Engineer. Permanent supports and protection shall be provided if instructed by the Engineer. (3) The Contractor shall inform the Engineer and the utility undertakings without delay of the following: Damage to utilities, Leakage of utilities, Discovery of utilities not shown on the Drawings, and Diversion, removal, repositioning or re-erection of utilities, which is required to enable the execution of the Works. (4) The Contractor shall take all steps necessary to enable the utility undertakings to proceed in accordance with the programme agreed between the Contractor and the utility undertakings. The Contractor shall maintain close liaison with the utility undertakings and shall inform the Engineer of any delays in works by the utility undertakings. (5) Records of existing utilities encountered shall be kept by the Contractor on the Site with a copy provided for the Engineer. The records shall be agreed by the Engineer and shall contain the following details: Location of utility, Date on which utility was encountered, Nature and size of utility, Condition of utility, and Temporary or permanent supports provided. (6) The Contractor shall provide adequate and experienced site personnel to control the operation of heavy mechanical plant in the proximity of utilities. (7) The Contractor shall make arrangements to avoid any heavy mechanical plant or vehicles standing or passing over buried pipe-work in particular those at shallow depths with less than 1 metre overburden cover, especially when the road surface is removed. Unless agreed by the Engineer, the Contractor shall not stockpile any material immediately over or in the vicinity of any pipe-work. (8) The Contractor shall carry out the Works in such a manner to avoid any damage or interference with any concrete blocks or structures attached to the utilities. The Contractor shall ensure that all cable draw-pits, valve-pits and the like are not covered up or removed as a result of his works and are accessible by utility undertakings at any time during the course of the Works for emergency repair. (9) Where utility installations are exposed, the Contractor shall liaise with the utility undertakers about the necessary protection for the exposed utilities and provide temporary protective measures and warning signs to prevent damaging the utility installations. |
| 1.7.3 | Structures, roads and other property | The Contractor shall immediately inform the Engineer of any damage to structures, roads or other property not required for the execution of the Works. |
| 1.7.4 | Access | Alternative access shall be provided if interference with existing public or private vehicular or pedestrian access is necessary to enable the execution of the Works. The arrangements for the alternative access shall be as agreed by the Engineer. The permanent access shall be reinstated as soon as practicable after the works are complete and the alternative access shall be removed as soon as practicable after it is no longer required. |
| 1.8 | RECORDS |  |
| 1.8.1 | Records of correspondence | Copies of correspondence relevant to execution of the Works (and not of a confidential nature) received from or despatched to Government departments, utility undertakings and other contractors employed by the Employer shall be submitted to the Engineer for information as soon as possible, but in any case not later than 7 days after receipt or despatch. |
| 1.8.2 | Records and reports | Reports and records, which are to be submitted to the Engineer, shall be in a format agreed by the Engineer. Reports and records shall be signed by the Contractor's agent or by another representative authorised by the Contractor. |
| 1.9 | LIAISON WITH OTHERS |  |
| 1.9.1 | Liaison with others | (1) The Contractor shall make all necessary arrangements with and obtain the necessary approvals from Government departments, utility undertakings and other duly constituted authorities for carrying out the Works. (2) The Contractor shall maintain close liaison with other contractors employed by the Employer, and utility undertakings or other authorities who are carrying out works on or adjacent to the Site. The Contractor shall ensure as far as possible that the progress of the Works is not adversely affected by the activities of such other contractors. |
| 1.10 | SITE CLEANLINESS |  |
| 1.10.1 | Site cleanliness | (1) The Site shall be maintained in a clean and tidy condition. Materials, including materials required for Temporary Works, shall be stored in an orderly manner. The measures to be taken shall include but not limited to the following: Promptly remove all debris and litter on the site including those dumped into the site from outside by the public. Promptly remove debris and litter not within the site if the debris and litter are in connection with the Works or disposal of by the persons working on the site. Keep traffic cones, temporary traffic lights and signs clean, secure and in an orderly manner and refurbish, repaint and/or repair hoardings and/or steel barriers half yearly. Keep passageways clear and free of greasy dirt, waste and timber. (2) The Contractor shall assign a designated person, with adequate knowledge, experience and authority, for the overall co-ordination, monitoring and overseeing of the performance of the site on cleanliness and control of mosquito breeding. Thereafter, the Contractor shall notify the Engineer of the name and contact telephone number of the assigned person and any subsequent change. |
| 1.10.2 | Prevention of mosquito breeding | (1) Measures shall be taken to prevent mosquito breeding on the Site. The measures to be taken shall include the following: Empty cans, oil drums, packings and other receptacles that may retain water shall be deposited at a central collection point and those not required for future use shall be removed from the Site regularly. Standing water shall be treated at least once every week with an oil which will prevent mosquito breeding. Construction plant and other items on the Site which may retain water shall be stored, covered or treated in such a manner that water will not be retained. Properly cover all water storage tanks, remove unnecessary stagnant water and disused containers, or use non-hazardous larvicide to prevent mosquito breeding as the last resort. The Contractor shall submit the characteristics, mixing formulation and method of application of the proposed larvicide to the Engineer for approval before its use; (2) Posters in both English and Dhivehi drawing attention to the dangers of permitting mosquito breeding shall be obtained from the relevant authority and displayed prominently on the Site. |
| 1.10.3 | Prevention of dust | Works shall be carried out in such a manner that avoidable dust is not generated. |
| 1.11 | MATERIALS AND EQUIPMENT |  |
| 1.11.1 | Materials | (1) Materials for inclusion in the permanent works shall be new or other material as stated in the Contract or approved by the Engineer. (2) Certificates of tests by manufacturers that are submitted to the Engineer shall relate to the material delivered to the Site. Certified true copies of certificates may be submitted if the original certificates cannot be obtained from the manufacturer. A letter from the supplier stating that the certificates relate to the material delivered to the Site shall be submitted with the certificates. (3) Samples of materials submitted to the Engineer for information or approval shall be kept on the Site and shall not be returned to the Contractor or used in the permanent works unless permitted by the Engineer. |
| 1.12 | TESTING |  |
| 1.12.1 | Quality assurance schemes | Tests stated in the Contract may be omitted or reduced in number as agreed by the Engineer if materials or articles delivered to the Site: Tests are covered by a manufacturer's quality assurance scheme stated in the Contract or approved by the Engineer. |
| 1.12.2 | Batches, samples and specimens | (1) A batch of material is a specified quantity of the material, which satisfies specified conditions such that it may be assumed that all of the material in the batch is of consistent type and quality. If one of the specified conditions is that the material is delivered to the Site at the same time, material delivered to the Site over a period not exceeding 7 days may be considered as part of the same batch if in the opinion of the Engineer there is sufficient evidence that the other specified conditions applying to the batch apply to all of the material delivered over the period. (2) A sample is a specified amount, or a specified number of pieces or units, taken from a batch for testing, such that the result of tests on the sample can be taken as representing the quality of the batch as a whole. (3) A specimen is a portion of a sample that is to be tested. |
| 1.13 | WORKMANSHIP AND TOLERANCES |  |
| 1.13.1 | Workmanship | Workmanship shall comply with best trade practice and with relevant British Standard. |
| 1.13.2 | Tolerances | (1) Tolerances stated in the Contract shall be measured perpendicular to the specified lines unless otherwise stated in the Contract. (2) If adjacent parts of the Works are subject to different dimensional tolerances then the most critical tolerance shall apply to all such works that relate to each other in respect of dimension, line and level. |
| 1.14 | SITE ESTABLISHMENT |  |
| 1.14.1 | Use of the Site | (1) The Site shall not be used by the Contractor for any purpose other than for executing the Works or carrying out other works associated with the Works and approved by the Engineer. (2) Entry to and exit from the Site shall be only gained at the locations stated in the Contract or agreed by the Engineer. |
| 1.14.2 | Submission of particulars | (1) The following particulars shall be submitted to the Engineer for approval not more than 14 days of the commencement of the Works: Drawings showing the layout within the Site of the Contractor's accommodation, project signboards, access roads and major facilities required early in the Contract, Drawings showing the details to be included on project signboards. (2) Drawings showing the location of stores, storage areas, concrete materials batching and mixing plants if needed , and other major facilities not required early in the Contract shall be submitted to the Engineer for approval as early as possible, but in any case not later than 28 days before such facilities are constructed on the Site. |
| 1.14.3 | Survey of the Site | A survey of the Site to establish the precise boundaries of the Site and the levels within the Site will be carried out by the Engineer after site clearance, and before other works start in each area to be surveyed. The Contractor shall carry out the survey jointly with the Engineer and agree the result as soon as practicable after completion of site clearance, before commencing other works in the area surveyed. |
| 1.14.4 | Fences and signs on the Site | (1) Hoardings, fences, gates and signs on the Site shall be maintained in a clean, presentable, stable and secure condition. Logos, pictures and text shall be legible and not visually obstructed at all times. (2) Project signboards stated in the Contract shall be erected not more than 4 weeks, or such other period agreed by the Engineer, after the date for commencement of the Works. Other advertising signs shall not be erected on the Site unless permitted by the Engineer. (3) The Engineer’s permission shall be obtained before hoardings, fences, gates or signs are removed. Hoardings, fences, gates and signs that are to be left in position after completion of the Works shall be repaired and repainted as instructed by the Engineer. (4) All components of site hoardings and signboards shall be metallic and not be made of timber. Bolts and nuts shall be used to join the panels of hoardings and signboards unless otherwise approved by the Engineer. |
| 1.14.6 | The Contractor's Site accommodation | The Contractor's offices, sheds, stores, mess rooms, latrines and other accommodation on the Site shall be maintained in a clean, stable and secure condition. Living accommodation shall not be provided on the Site unless stated in the Contract or approved by the Engineer. |
| 1.14.7 | Site utilities and access | (1) Temporary water, electricity, telephone, sewerage and drainage facilities shall be provided for the Contractor's use in carrying out the Works by the Employer. The Contractor shall make all arrangements with and obtain the necessary approvals from the relevant authorities for the facilities. (2) Access roads and parking areas shall be provided within the Site as required and shall be maintained in a clean, passable and stable condition with regular suppression of dust |
| 1.14.9 | Clearance of the Site | Temporary Works that are not to remain on the Site after completion of the Works shall be removed on completion of the Works or at other times instructed by the Engineer. The Site shall be cleared and reinstated to the lines and levels and to the condition existing before the Works started except as otherwise stated in the Contract. |
| 1.15 | MEETINGS |  |
| 1.15.1 | Meetings | The Contractor's agent shall attend, and shall arrange for the representatives of Sub-contractors, Government departments, transport companies, utility undertakings and other Contractors to attend, meetings when required by the Engineer. The Contractor shall inform the Engineer in 48 hours (or such a shorter period as agreed by the Engineer) before conducting meetings with Government departments, transport companies, utility undertakings and/or other Contractors and shall give the Engineer an opportunity to attend such meetings. |
| 2. | SECTION 2 SITE CLEARANCE | N/A |
| 3. | SECTION 3 LANDSCAPE SOFTWORKS AND ESTABLISHMENT WORKS | N/A |
| 4. | SECTION 4 FENCING | N/A |
| 5. | SECTION 5 DRAINAGE WORKS | N/A |
| 6. | SECTION 6 EARTHWORKS | N/A |
| 7. | SECTION 7 GEOTECHNICAL WORKS | N/A |
| 8. | SECTION 8 CARRIAGEWAYS: SUB-BASE MATERIAL AND BITUMINOUS MATERIALS | N/A |
| 9. | SECTION 9 CONCRETE CARRIAGEWAYS | N/A |
| 10. | SECTION 10 MISCELLANEOUS ROADWORKS | N/A |
| 11. | SECTION 11 TRAFFIC SIGNS, ROAD MARKINGS AND ROAD STUDS | N/A |
| 12. | SECTION 12 WORK FOR ELECTRICAL AND MECHANICAL INSTALLATIONS |  |
| 12.1 | GENERAL |  |
| 12.1.1 | General requirements | The works and materials specified below shall comply with the sections stated, unless otherwise stated in this Section. |
| 12.1.2 | Galvanization | Galvanization in this Section shall be hot dip galvanization to BS EN ISO 1461: 1999 |
| 12.2 | GLOSSARY OF TERMS |  |
| 12.2.1 | Concealed electrical conduit system | Concealed electrical conduit system is an electrical conduit system, including all bends, couplers, bushes, saddles, boxes, covers, plugs, draw wires and other conduit fittings, which is cast into concrete or fixed in chases in brickwork with a minimum cover of 20 mm or which is laid directly in the ground. |
| 12.3 | MATERIALS |  |
| 12.3.1 | Electrical conduits and fittings | (1) Electrical conduits and fittings shall comply with BS 4568: Parts 1 and 2 and shall have Class 4 heavy protection inside and outside. Conduits shall be heavy gauge with screw-end construction in steel and shall have an external diameter of at least 20 mm. Conduits shall be longitudinally welded. (2) Metal boxes for enclosing electrical accessories shall comply with BS 4662 and shall have heavy protection inside and outside. The boxes shall be of preferred sizes and shall be 35 mm or 47 mm deep as appropriate. Circular ceiling boxes of deep pattern shall comply with BS 4568: Part 2 and shall have Class 4 heavy protection inside and outside. The boxes shall be at least 60 mm deep internally. (3) Circular boxes, dome covers and hook covers shall be cast iron. Bushes and plugs shall be brass. |
| 12.3.2 | Cable ducts and fittings | (1) uPVC cable ducts for installation above ground or for casting into concrete shall be Class 0 uPVC pipes complying with BS 3506. Cable ducts for installation below ground shall be Class B uPVC pipes complying with BS 3506. (2) Joints and fittings for use with uPVC cable ducts shall comply with BS 4346: Part 1 and BS 4346: Part 2. Solvent cement for uPVC pipes and fittings shall comply with BS 4346: Part 3. (3) Steel cable ducts shall be steel tubes complying with BS 1387, medium series, screwed and socketted tubes and shall have screwed sockets suitable for screwing to BS 21, Table 2 pipe threads. The tubes, sockets, clamps and saddles for ducts shall be hot dip galvanized in accordance with BS EN ISO 1461:1999. |
| 12.3.3 | Paint for conduit and duct systems | (1) Bituminous paint for steel conduits and steel cable ducts shall comply with BS 3416, type 1. (2) Anti-rust paint for concealed electrical conduit systems shall be of a proprietary type approved by the Engineer. (3) Zinc chromate primer for cable duct systems shall comply with BS 4652. (4) Galvanizing paint for cable duct systems shall be of a proprietary type approved by the Engineer. |
| 12.3.4 | Fire barriers | Internal fire barriers shall be a type offering adequate fire resistance for the application. The material shall be approved by the Engineer in compliance with Fire Services Department’s requirements and shall be resistant to fire, smoke, gas and water. |
| 12.3.5 | Cement grout for electrical and mechanical installations | The different types of cement grout for electrical and mechanical installations shall consist of Portland cement, sand in the proportions by mass stated in Table 12.1 together with the minimum amount of water necessary to achieve a consistency suitable for completely filling the voids. The mix shall contain a non-shrink admixture of a proprietary type approved by the Engineer. |

Table 12.1: Mix proportions of cement grout

| Type | Mix proportions by mass |  |
| --- | --- | --- |
|  | Cement | Sand |
| G1 | 1 | - |
| G2 | 1 | 3 |
| G3 | 1 | 10 |
| G4 | 1 | - |

| 12.4 | STORAGE OF MATERIALS |  |
| --- | --- | --- |
| 12.4.1 | Storage of materials for conduit and cable duct systems | Materials for concealed electrical conduit systems and for cable duct systems shall be stored in accordance with the manufacturers' recommendations in a dry and weatherproof store. |
| 12.5 | HOLES AND RECESSES FOR ELECTRICAL AND MECHANICAL INSTALLATIONS |  |
| 12.5.1 | Holes and recesses for electrical and mechanical installations | (1) Holes and recesses shall be left in structures for electrical and mechanical installations. If instructed by the Engineer, holes and recesses shall be cut in structures for electrical and mechanical installations. (2) Holes and recesses in internal floors, stairways and platforms shall be protected with temporary covers or by other methods agreed by the Engineer until the electrical and mechanical installation starts. Holes and recesses in roofs, external walls and external floors shall be sealed with watertight temporary covers until the electrical and mechanical installation starts. (3) Holes in structures shall be filled and made good after electrical and mechanical installations are complete. Holes left in structural elements designated as fire barriers shall be sealed to at least the same degree of fire resistance as the structural element. |
| 12.6 | FIRE BARRIERS |  |
| 12.6.1 | Fire barriers | Internal fire barriers shall be constructed in service channels, service shafts and service ducts for electrical and mechanical installations at the following locations: At points of intersection with structural elements designated as fire barriers, At 5 m centres in vertical and inclined shafts, and at intersections with floor slabs, and At termination points and open ends. |
| 12.7 | CONCEALED ELECTRICAL CONDUIT SYSTEMS |  |
| 12.7.1 | Construction of conduit systems | (1) Concealed electrical conduit systems shall be mechanically and electrically continuous and shall be effectively earthed. (2) Principal conduit runs shall be either vertical or horizontal. Tee pieces and elbows, including those with provision for inspection, shall not be used unless approved by the Engineer. (3) Joints shall be made using coupler units into which the ends of the conduits shall be inserted and tightened. Running couplings shall not be used unless permitted by the Engineer. If permitted, the couplings shall be made by screwing each of the conduits half way into the coupler with a hexagonal lock nut against each end of the coupler. (4) Adaptable boxes shall be provided at: - Every second bend, - After a bend and a straight run of 10 m or less, and - Every 15 m in straight runs. (6) Adaptable boxes for conduits installed in floor screeds shall have the lids set flush with the adjacent floor. The boxes shall be covered with the same material as the remainder of the floor and shall remain accessible at all times. (7) The clearance between conduits entering adaptable boxes and between adjacent or parallel conduits shall be at least the nominal maximum coarse aggregate size of the concrete plus 5 mm. |
| 12.7.2 | Installation of conduit systems | (1) Concealed electrical conduit systems shall be arranged and installed in accordance with best trade practice and in such a manner that all cables can be drawn with ease and without damage. (2) Bends in concealed electrical conduit systems shall be formed by using proprietary bending equipment of a type agreed by the Engineer. Connections and other work shall be carried out using purpose made equipment. (3) Conduits shall not be bent by more than 900 and the internal radius at bends shall be at least 2.5 times the external diameter of the conduit. Conduits shall not be flattened at bends. (4) Burrs and sharp edges shall be removed from the ends of conduits before installation. (5) Concealed electrical conduit systems that are to be cast into concrete shall be fastened to the reinforcement with tying wire of the same type used for the reinforcement. The conduit systems shall not be positioned between the reinforcement and the outside face of the concrete unless permitted by the Engineer. (6) Conduit boxes shall be of a compatible size and shall have a single extension ring of the required depth if the plaster finish exceeds 13 mm thick. Multiple extension rings shall not be used. |
| 12.7.3 | Terminations of conduit systems | Screw fitting couplers shall be provided at each end of conduits which terminate in distribution boards, busbar chambers, motor starters, cable ducts, boxes or similar termination points. The item at which the conduit terminates shall be drilled with an unthreaded clearance hole to receive a brass male bush. The bush shall be screwed into the coupler from the inside of the item in such a manner that the surface of the item is gripped between the coupler and the bush. The threads shall be at least half the length of the coupler. |
| 12.7.4 | Protection of conduit systems | (1) Concealed electrical conduit systems shall have special arrangements designed by the Contractor to permit movement of conduits to take place on each side of movement joints in structures. A separate circuit protective conductor shall be installed to maintain effective electrical continuity across the joint. The protective conductor shall have a cross-sectional area rated to suit the largest live conductor to be drawn into the conduit. (2) Steel conduit systems laid in contact with or adjacent to other metal work shall have efficient and permanent metallic connection made between the conduit and the metal work. (3) Underground steel conduits and conduits in contact with soil shall be painted with two coats of bituminous paint before installation. (4) Exposed threads and damage to protective coatings of conduit systems shall be painted with two coats of anti-rust paint. (5) Conduits shall be laid in such a manner that accumulation of condensed moisture in the conduit system is prevented. Measures shall be taken to prevent water from entering the system. (6) Water, moisture and deleterious material shall be prevented from entering permanent and temporary terminations in concealed electrical conduit systems, including conduit boxes, by using conduit-stopping plugs of a type approved by the Engineer. Paper or rags shall not be used. |
| 12.7.5 | Cleaning of conduit systems | After installation, concealed electrical conduit systems shall be swabbed out with draw-in tapes and absorbent cloth of a type agreed by the Engineer. All obstructions shall be removed and draw wires shall be installed. After cleaning, exposed conduit ends shall be sealed. |
| 12.8 | CABLE DUCT SYSTEMS |  |
| 12.8.1 | Installation of cable duct system | (1) Changes in direction in cable duct systems shall be constructed in such a manner that the cables in the duct will have radii of curvature of at least 800 mm. Ducts entering draw-in pits shall be on the same horizontal plane as the draw-in pit. (2) uPVC cable ducts shall be jointed in accordance with the manufacturer's recommendations. (3) Steel cable ducts shall be jointed using screwed hot dip galvanized sockets and spun yarn or by an equivalent method approved by the Engineer such that the jointed pipes abut. The threads shall be painted with two coats of bituminous paint. Internal rags and burrs shall be removed to provide a smooth bore through joints in the cable duct system. (4) Surface mounted cable ducts shall be secured by hot dip galvanized steel clamps or saddles at spacings not exceeding 3 m. |
| 12.8.2 | Protection of cable duct systems | (1) After jointing, exposed bare metal in cable duct systems shall be cleaned and painted with two coats of zinc chromate primer and two coats of galvanizing paint. (2) Surface-mounted hot dip galvanized steel cable ducts shall be cleaned and painted after fittings and jointing have been completed. |
| 12.8.3 | Cleaning of cable duct systems | After jointing, cable duct systems shall be cleaned internally by scrubbing with a cylindrical brush of a type agreed by the Engineer. The ends of ducts, including ends of ducts in draw-in pits and spare ducts, shall be fitted with tapered hardwood plugs to prevent water, moisture and deleterious material from entering the system and a 6 mm diameter nylon draw line shall be installed. The plugs shall be centrally drilled for the draw line and the draw line shall be secured by a knot tied on the outer face of the plug to leave at least 1500 mm of surplus line at each plug. |
| 12.9 | ELECTRICAL EARTHING SYSTEMS |  |
| 12.9.1 | Electrical earthing systems | (1) Pits and trenches for electrical earthing systems shall be excavated at positions and at the times instructed by the Engineer. (2) After the electrical earthing systems have been installed fill material shall be deposited and compacted in the pits and trenches to a depth of 300 mm above the electrical earthing system. Fill material shall be sand or fine fill material which has been selected from the excavated material, and which is free of stones retained on a 20 mm BS test sieve. Fill material shall be compacted by handrammers in a manner approved by the Engineer. |
| 12.10 | GROUTING FOR ELECTRICAL AND MECHANICAL INSTALLATIONS |  |
| 12.10.1 | Grouting for electrical and mechanical installations | (1) Grouting shall be carried out at the times instructed by the Engineer and shall be completed within 7 days of the instruction unless otherwise permitted by the Engineer. (2) The permission of the Engineer shall be obtained before items or equipment are grouted. The Contractor shall inform the Engineer within 3 days, or a shorter period agreed by the Engineer, before grouting starts and shall allow the Engineer sufficient time to inspect the work that is to be grouted. (3) Concrete surfaces shall be scabbled to remove laitance and loose material and to expose the aggregate before the item or equipment is installed in position. (4) The voids to be grouted shall be cleaned and thoroughly wetted immediately before grouting. Excess water shall be removed by using a compressed air jet or by other methods agreed by the Engineer. (5) Grout shall be mixed and placed by methods agreed by the Engineer. (6) If grouting is to be carried out in two operations, holding down bolts shall be grouted into preformed pockets and sufficient time shall be allowed for the grout to cure and for the bolts to be tensioned before the remaining voids are grouted. (7) Exposed grout surfaces shall have a uniform, dense and smooth surface free of trowel marks and which is produced by steel trowelling the surface under firm pressure. The exposed surfaces shall be cured by either: Using a liquid curing compound applied to the surface by a low-pressure spray until a continuous visible covering is achieved, or covering the surface with hessian or sacking. The hessian or sacking shall be lapped and securely held in position and shall be kept damp for at least 4 days. |
| 12.11 | COMPLETION AND PROTECTION OF WORK FOR ELECTRICAL AND MECHANICAL INSTALLATIONS |  |
| 12.11.1 | Completion of work for electrical and mechanical installations | (1) Work shall be completed before structures are made available to others for electrical and mechanical installations. (2) The structure shall be clean, dry and free of dust. Work that in the opinion of the Engineer will produce large quantities of dust shall be complete. (3) Holes and recesses, concealed electrical conduit systems and cable duct systems required for the installation shall be complete. Concrete surfaces on which items and equipment are to be installed shall be scabbled. (4) Plinths, trenches, louvres, openings and similar work shall be complete and shall have hardened sufficiently to allow the installation to proceed. (5) Temporary power supplies and connections required for the installation shall be complete. The supply shall be metered and shall be a 346V, 3-phase supply of 20A maximum rating. Temporary power supplies shall be provided for the periods stated in the Contract. |
| 12.11.2 | Protection of work for electrical and mechanical installations | (1) Structures in which electrical and mechanical installations are being carried out shall be maintained in a clean, dry condition, free of dust, during the installation. (2) The dust level in plant rooms shall be kept to a minimum by using industrial dust extractors of a type agreed by the Engineer during and after the installation. Temporary screens shall be installed to separate dust-affected areas from the installations or temporary covers shall be installed around the installation. |
| 12.12 | TOLERANCES |  |
| 12.12.1 | Tolerances: floors of switchgear rooms | The tolerance in floor levels for switchgear rooms shall be as follows: ± 2 mm in 1000 mm for high voltage switchgear rooms, ± 4 mm in 1000 mm for medium voltage switchgear rooms. |
| 12.12.2 | Tolerances: lamp standards | Lamp standards shall be within 0.1 degrees of the vertical. |
| 12.13 | INSPECTION OF WORK FOR ELECTRICAL AND MECHANICAL INSTALLATIONS |  |
| 12.13.1 | Inspection of work for electrical and mechanical installations | (1) The Contractor shall allow the Engineer to inspect the following work for electrical and mechanical installations: Completed concealed electrical conduit systems, cable duct systems, electrical earthing systems and items and equipment which are to be grouted or covered up, Items and equipment which are to be tested, and Structures that are to be made available for electrical and mechanical installations. (2) The Contractor shall inform the Engineer three days, or such shorter period agreed by the Engineer, before work is covered up, tested or made available. |
| 12.14 | TESTING: EARTHING CONTINUITY |  |
| 12.14.1 | Testing: earthing continuity | (1) Concealed electrical conduit systems shall be tested to determine the earthing continuity. The system shall be tested: - Before the system is cast in concrete or covered up, - After the system is cast in concrete or covered up, and - After electrical wiring that is installed by the Contractor is complete. (2) Unless otherwise approved by the Engineer the method of testing shall be in accordance with Appendix 15 to the IEE Wiring Regulations, 15th Edition, 1981 issued by the Institution of Electrical Engineers. |
| 12.14.2 | Compliance criteria: earthing continuity | The results of tests for earthing continuity shall comply with the IEE Wiring Regulations, 15th Edition, 1981 issued by the Institution of Electrical Engineers. |
| 12.15 | TESTING: LOAD TESTS ON BEAMS AND JOISTS |  |
| 12.15.1 | Testing: load tests on beams and joists | (1) Load tests shall be carried out on lifting beams, rolled steel joists and lifting hooks that are installed by the Contractor. (2) Testing shall be carried out by an independent testing consultant approved by the Engineer and by using methods approved by the Engineer. (3) A certificate showing the results of the load tests and signed by the testing agent shall be submitted to the Engineer within 14 days of the test. |
| 12.15.2 | Compliance criteria: load tests on beams and joists | The results of tests on lifting beams, rolled steel joists and lifting hooks shall comply with the Factories and Industrial Undertakings. |
| 13. | SECTION 13 FORMWORK AND FINISHES TO CONCRETE | N/A |
| 14. | SECTION 14 STEEL REINFORCEMENT | N/A |
| 15. | SECTION 15 CONCRETE AND JOINTS IN CONCRETE | N/A |
| 16. | SECTION 16 STEELWORK |  |
| 16.1 | GENERAL |  |
| 16.1.1 | Steelwork | (1) Steelwork shall comply with BS 5950: Part 2 unless it is stated in the Contract that the steelwork shall comply with BS 5400: Part 6. (2) Allowances shall be made for the deformation due to permanent loads and the process and sequence of fabrication, erection and construction such that steelwork is completed to within the specified tolerances. (3) The compatibility of the dimensions and setting-out data of steelwork shall be verified by the Contractor before the materials for steelwork are ordered. |
| 16.1.2 | Protection of steelwork | Protection of steelwork against corrosion shall comply with BS 5493. Amendments to BS 5400: Part 6. |
| 16.1.3 | Amendments to BS 5400: Part 6 | The Contractor shall determine the dead load camber of beams required. The camber of plate girders shall be formed by either of the following alternative : Type A cambering camber introduced by welding the flanges pressed against a web plate cut to a smooth cambered profile, |
| 16.2 | MATERIALS |  |
| 16.2.1 | Structural steel | (1) Structural steel shall comply with BS 4360, including Clause B7 at Appendix B, and with BS 5950: Part 2, Section 2.1 or BS 5400: Part 6, Section 3.1 as appropriate. (2) Hot rolled sections complying with BS 4: Part 1, BS 4848: Part 2, BS 4848: Part 4 or BS 4848: Part 5 shall not be replaced with sections complying with other standards unless approved by the Engineer. If approved, the sections shall have equivalent properties to, and the dimensional tolerances shall comply with, the relevant British Standard. |
| 16.2.2 | Rivet steel | Steel rivet bars for the manufacture of steel rivets shall comply with BS 5400: Part 6, Appendix A. |
| 16.2.3 | Steel for shear connectors | Steel for headed-stud-type shear connectors shall have a yield stress of at least 385 N/mm2 and a tensile strength of at least 495 N/mm2. Steel for other types of shear connectors shall comply with BS 4360. |
| 16.2.4 | Bolts, screws, nuts and washers | (1) Bolts, screws and nuts shall comply with the British Standards strength grades stated in Table 16.1 unless other strength grades or British Standards are stated in the Contract. (2) Washers for high strength friction grip bolts and nuts shall comply with the following: High strength friction grip bolts and associated nuts and washers for structural engineering: - General grade : BS 4395: Part 1 - Higher-grade bolts and nuts and general-grade washers : BS 4395: Part 2 - Higher-grade bolts (waisted shank), nuts and general-grade washers : BS 4395: Part 3 Plain washers for other bolts, screws and nuts shall comply with BS 4320. Tapered washers for other bolts, screws and nuts shall comply with BS 3410. |
| 16.2.5 | Welding consumables | (1) Welding consumables used in metal-arc welding of grades of steel complying with BS 4360 shall comply with BS 5135. Welding consumables used in the fusion welding of steel castings shall comply with BS 4570. Welding consumables used in metal-arc welding of austenitic stainless steels shall comply with BS 4677. (2) Welding consumables and the procedures used shall be such that the mechanical properties of the deposited weld metal shall not be less than the respective minimum values of the parent metal being welded. (3) Welding consumables used with grades of steel other than those complying with BS 4360 shall be such that the performance requirements stated in BS 5400: Part 6, Table 1 or BS 5950: Part 2, Table 1 as appropriate are achieved. |
| 16.2.6 | Rolled steel pins | Rolled steel pins, including those made from slabs, shall comply with BS 970: Part 1 or BS 4360, Grades 43, 50 or 55. |

Table 16.1: British Standards and strength grades for bolts, screws and nuts

| Type of bolts, screws and nuts | British Standard | Strength grade of bolt | Strength grade of nut |
| --- | --- | --- | --- |
| High strength friction grip (HSFG) bolts and nuts | BS 4395: Part 1 | General grade | as specified in BS 4395: Part 1 |
| Precision bolts, screws and nuts | BS 3692 | 4.6 | 4.0 |
| Cup head and countersunk head bolts, screws and nuts | BS 4933 | 4.6 | 4.0 |
| Black bolts, screws and nuts | BS 4190 | 4.6 | 4.0 |
| Other types of bolts, screws and nuts | BS 4190 | 4.6 | 4.0 |
| Hexagon socket screws | BS 4168: Part 1 | 12.9 | 12.0 |

| 16.2.7 | Steel castings and cast steel pins | Carbon manganese steel castings shall comply with BS 3100. |
| --- | --- | --- |
| 16.2.8 | Steel forgings and forged steel pins | Steel forgings and forged steel pins shall comply with BS 29. |
| 16.2.9 | Stainless steel | (1) Wrought stainless steel shall comply with BS 970: Part 1, Grade 316 S 16. (2) Flat rolled stainless steel shall comply with BS 1449: Part 2, Grade 316 S 16 in the softened condition. (3) Stainless steel tubes shall comply with BS 6323: Part 1 and BS 6323: Part 8, designation LW 23 GZF(S). (4) Stainless steel bolts and nuts shall comply with BS 6105, steel Grade A4 and property class 80. Stainless steel washers shall comply with BS 1449: Part 2, Grade 316 S 31 in the softened condition. The dimensions and tolerances of bolts and nuts shall comply with BS 3692. The dimensions and tolerances of tapered washers shall comply with BS 3410 and the dimensions and tolerances of flat washers shall comply with BS 4320, Form C. |
| 16.2.10 | Cast iron | (1) Grey cast iron shall comply with BS 1452, Grade 10. (2) Malleable cast iron shall comply with BS 6681. (3) Spheroidal or nodular cast iron shall comply with BS 2789. |
| 16.2.11 | Grout for column bases | (1) Grout for bedding steel bases and for filling bolt pockets and pocket bases shall be based on OPC and shall have the same grade strength as the surrounding foundation concrete. The grout shall contain a non-metallic expanding admixture and shall have a total chloride content of not more than 0.1% by mass of cement. (2) Grout for bedding steel bases and for filling bolt pockets shall be of a proprietary type approved by the Engineer and shall be suitable for filling the space by pouring under a suitable head. The proportions of the grout shall be in accordance with the manufacturer’s recommendations. (3) A dry packed mortar may be used for bedding steel bases that exceed 75 mm thick. The mortar shall consist of 1 part by weight of cement to 2 parts by weight of fine aggregate together with the minimum amount of water necessary to achieve a consistency suitable for thorough ramming against supports such that the space is completely filled. (4) Grout for filling pocket bases shall be a mix approved by the Engineer with a nominal maximum aggregate size of 10 mm. |
| 16.2.12 | Lubricant for nut threads of HSFG bolts | Lubricant for lubricating nut threads of high strengthen friction grip (HSFG) bolts shall be of a wax-based type approved by the Engineer. Machine oil and other free-flowing lubricants shall not be used. |
| 16.2.13 | Paint for steelwork | (1) Paint for steelwork shall comply with BS 5493, Section 2, Table 4. Organic zinc-rich paint shall comply with BS 4652. Lead-based paint shall not be used for finishing coats. (2) Paint shall be supplied in sealed containers of not more than 5 litres capacity. Each container shall be marked on the side to show the following: - The name of the manufacturer, - The paint manufacturer’s reference number, - Intended purposes, type of pigment and binder, - Batch number, date of manufacture, expiry date and pot life, and - Colour, gloss, drying times and flash point. (3) The Volatile Organic Compound (VOC) content, in grams per litre, of all paint applied on surfaces of steelwork shall not exceed: Water-based Paint: 100 g/litre Solvent-based Paint: 450 g/litre The VOC content of paint shall be determined either by recognized method of calculation or laboratory testing. |
| 16.3 | SUBMISSIONS |  |
| 16.3.1 | Particulars of steel | (1) The manufacturer’s certificates for steel shall be submitted to the Engineer in accordance with BS 4360, Clause 12 and Appendix B 6. (2) The certificates shall be submitted to the Engineer not more than 2 days after the steel has been delivered to the place of fabrication. |
| 16.3.2 | Particulars of workshop drawings | (1) Two sets of drawings of the steelwork shall be submitted to the Engineer. The drawings shall show details of the following: Steelwork and welds, including any stud welds, marked with the relevant welding procedures, Joints or non-standard welds proposed by the Contractor, Locations and method of removal of any temporary welded attachments proposed by the Contractor, Edges of steelwork complying with BS 5400: Part 6 to be formed by flame cutting or shearing procedures complying with BS 5400: Part 6, Clause 4.3.3(a), (d) or (e) with the edges marked with the procedures to be used, and Parts of steelwork complying with BS 5400: Part 6 to be worked by hot processes complying with BS 5400: Part 6, Clause 4.8, 4.9 or 4.10 with the parts marked with the processes to be used. (2) The drawings shall be submitted to the Engineer for approval at least 6 weeks before fabrication of the steelwork starts. Drawings shall not be approved until all procedures and details shown on the drawing have been approved by the Engineer. (3) A print and a diazo film of the approved drawings shall be submitted to the Engineer at least 7 days before fabrication of the steelwork starts. |
| 16.3.3 | Particulars of delivery of steelwork | (1) The following particulars of steelwork fabricated off the Site shall be submitted to the Engineer: - Expected and actual arrival dates, - Name of carrier, - Duplicate copies of bill of lading and packing list for steelwork transported by sea, and - Duplicate copies of delivery note and a list showing the marking and weight of each component for steelwork transported by land. (2) The particulars of expected arrival date and name of carrier shall be submitted to the Engineer at least 14 days before the due date. Other particulars shall be submitted to the Engineer within 3 days after delivery of the steelwork to the Site. |
| 16.3.4 | Particulars of method of erecting steelwork | (1) The following particulars of the proposed method of erecting steelwork shall be submitted to the Engineer: - Sequence and method of erection of steelwork, - Method of lifting and handling the components, - Method of preventing damage to protective coatings on steelwork during handling, - Procedure for aligning, levelling and plumbing steelwork, including temporary supports and method of making beddings for column bases, and - Sequence of casting concrete bonded to the steelwork. (2) The particulars shall be submitted to the Engineer at least 6 weeks before erection of the steelwork starts. |
| 16.3.5 | Welder certificates | (1) Certificates endorsed by an inspecting authority approved by the Engineer shall be submitted to the Engineer to show that each welder has been approved in accordance with BS 4570, BS EN 287: Part 1 or BS 4872: Part 1 as appropriate. The extent of approval of the welder shall be appropriate to the categories of welds that he will carry out. (2) The welder certificates shall be submitted at least 4 weeks before fabrication of the steelwork starts. |
| 16.3.6 | Particulars of welding procedures | (1) The following particulars of the proposed welding procedures shall be submitted to the Engineer: Welding procedures in accordance with BS 5135, Clause 20 for each type and size of weld other than welds stated in Table 16.2, Documentation endorsed by an inspecting authority approved by the Engineer to show that the welding procedure has complied with the procedure trial requirements stated in the Contract in previous tests, or that the welding procedure for steel castings complies with the exemption criteria stated in BS 4570, Clause 20.1.1, and Records of approval tests as stated in Clause 16.4.7 if procedure trials are required under Clause 16.4.1 (2) The welding procedures for permanent welds shall be submitted to the Engineer at the same time as welder certificates are submitted. The welding procedures for temporary welds shall be submitted to the Engineer at the same time as welder certificates are submitted. |

Table 16.2: Welds for which submission of welding procedures is not required

| Weld Type | Weld Size |
| --- | --- |
| Fillet weld | Leg length not exceeding 4 mm |
| Butt weld | Thickness of the parts or, if the parts are of different thicknesses, the thickness of the thinner part to be joined not exceeding 4 mm |

| 16.3.7 | Particulars of stud welding, flame cutting and shearing procedures | (1) The following particulars of the proposed stud welding, flame cutting and shearing procedures for steelwork complying with BS 5400: Part 6 shall be submitted to the Engineer: Procedures for stud welding, flame cutting and shearing processes complying with BS 5400: Part 6, Clause 4.3.3(a),(d) or (c), Documentation endorsed by an inspecting authority approved by the Engineer to show that the stud welding, flame cutting or shearing procedure has complied with the procedure trial requirements stated in the Contract in previous tests, and Report of procedure trials as stated in Clause 16.4.7 if procedure trials are required under Clause 16.4.1 (2) The particulars shall be submitted to the Engineer at least 6 weeks before fabrication of the steelwork starts. |
| --- | --- | --- |
| 16.3.8 | Particulars of vent holes for galvanizing | Particulars of the method of plugging vent holes required for hot-dip galvanizing hollow or box sections shall be submitted to the Engineer at least 3 weeks before fabrication of the steelwork starts. |
| 16.3.9 | Particulars of method of non-destructive testing | Particulars of the proposed method for carrying out non-destructive testing on welds shall be submitted to the Engineer at least 4 weeks before the tests start. |
| 16.3.10 | Particulars of paint | (1) The following particulars of the proposed paints and associated products shall be submitted to the Engineer: - Name of manufacturer, - Duplicate copies of the manufacturer’s data sheets including temperature, humidity and other conditions at the workshop or on the Site under which the paint is to be applied, and - Manufacturer’s product specifications, product range and technical information, (2) The particulars shall be submitted to the Engineer at least 6 weeks before the painting starts. |
| 16.3.11 | Samples of materials | (1) A sample of blast cleaned steel plate shall be submitted to the Engineer for approval at least 14 days before blast cleaning starts. The sample shall be 150 mm x 150 mm x 6 mm and shall be enclosed in a sealed, colourless, transparent wrapping. The grade of steel and the method of blasting shall be representative of those that will be used in the permanent work. (2) Two samples of painted tin plates for each painting system shall be submitted to the Engineer at least 14 days before painting starts. Each plate shall be 150 mm x 75 mm x 1 mm and shall have smooth edges and 10 mm corner radii. The plates shall be brush cleaned and painted on one face with the painting system in such a manner that each coat is stepped back from the underlying coat in equal strips. The degree of gloss of the finishing coat shall be as agreed by the Engineer. (3) Samples of each type of nut, bolt, washer, stud and rivet shall be provided within 3 days after the material is delivered to the Site. |
| 16.4 | TRIALS |  |
| 16.4.1 | Procedure trials for welding, flame cutting and shearing | (1) If in the opinion of the Engineer the proposed welding procedure submitted or the proposed stud welding, flame cutting or shearing procedure for steelwork complying with BS 5400: Part 6 has not complied with the procedure trial requirements for the procedure in previous tests (2) Procedure trials for welding for structural steel shall comply with BS 5400: Part 6, Clauses 4.7.3, 5.4.1.1 and 5.4.1.2. (3) Procedure trials for welding for steel castings shall comply with BS 5400: Part 6, Clauses 4.7.3 and 5.4.2. (4) Procedure trials for welding of studs shall comply with BS 5400: Part 6, Clauses 4.7.4 and 5.4.4. (5) Procedure trials for flame cutting and shearing shall comply with BS 5400: Part 6, Clauses 4.7.3 and 5.4.3. (6) Welds for grade A steels complying with BS 4360 are not required to comply with the requirements for Charpy V-notch impact tests. The temperature of -20°C stated in BS 5400: Part 6, Clause 5.4.1.2(a)(3) shall be amended to 0°C. (7) If in a welding procedure one or more of the parts to be welded is coated with a prefabrication primer or metal coating before welding, the same primer or coating shall be applied to the sample before the procedure trial for the welding procedure is carried out. (8) The thickness of the sample of material to be used in procedure trials for flame cutting shall be: 20 mm for material not exceeding 20 mm thick, 40 mm for material exceeding 20 mm and not exceeding 40 mm thick, and T mm for material exceeding (T-10) mm and not exceeding T mm thick, where T is any multiple of 10 from 50 up. |
| 16.4.2 | Inspection of procedure trials for welding, flame cutting and shearing | Procedure trials for welding, flame cutting and shearing shall be carried out in the presence of an inspecting authority approved by the Engineer. |
| 16.4.3 | Results of procedure trials for welding, flame cutting and shearing | If a procedure trial for welding, flame cutting or shearing does not comply with the specified requirements for the procedure trial, the cause of failure shall be established by the Contractor and particulars of proposed changes shall be submitted to the Engineer. Further procedure trials shall be carried out to establish the amended procedure unless otherwise permitted by the Engineer. |
| 16.4.4 | Approved procedures for welding, flame cutting and shearing | (1) A welding, flame cutting or shearing procedure that complies with the specified requirements for the procedure trial shall become an approved procedure. (2) If a procedure trial is not required, the procedure for welding, flame cutting or shearing shall become an approved procedure. |
| 16.4.5 | Commencement of welding, flame cutting and shearing | Welding, flame cutting or shearing shall not commence until the procedure has been approved by the Engineer. |
| 16.4.6 | Changes in procedures for welding, flame cutting and shearing | Unless permitted by the Engineer, approved procedures for welding, flame cutting or shearing shall not be changed. Further procedure trials shall be carried out to demonstrate proposed changes to the procedure unless otherwise permitted by the Engineer. |
| 16.4.7 | Records of procedure trials for welding, flame cutting and shearing | (1) A record of the approval test for welding procedures shall be submitted to the Engineer for approval at least 3 weeks before fabrication of the steelwork starts. The record shall be in the form stated in BS 4870: Part 1, Appendix B or BS 4570, Appendix A as appropriate and shall be endorsed by the inspecting authority approved by the Engineer. (2) Reports of procedure trials for stud welding, flame cutting and shearing shall be submitted to the Engineer at least 3 weeks before fabrication of the steelwork starts. |
| 16.4.8 | Painting trials | (1) A painting trial shall be carried out for each painting system that will be applied to areas exceeding 100 m2 to demonstrate that the proposed materials and methods of application will produce a painted surface that complies with the specified requirements. (2) Painting trials shall be carried out at the place where painting to the permanent work will be carried out and using the employees and equipment which will be used to carry out painting to the permanent work. (3) Painting trials shall be carried out on blast cleaned steel. |
| 16.4.9 | Results of painting trials | If the painted surface produced in a painting trial does not comply with the specified requirements for the paintwork, the cause of failure shall be established by the Contractor and particulars of proposed changes shall be submitted to the Engineer. Proposed changes to the paint formulation, other than an adjustment in the amount of thinners, shall be carried out at the paint manufacturer’s works before the final painting trial and before the first batch of paint is delivered. |
| 16.4.10 | Commencement of painting | Painting shall not commence until the painted surface produced in painting trials complies with the specified requirements for paintwork. |
| 16.4.11 | Changes in materials and methods of application for painting | Unless permitted by the Engineer, the materials and methods of application used in a painting trial that complies with the specified requirements shall not be changed. |
| 16.5 | HANDLING, STORAGE AND TRANSPORT OF MATERIALS |  |
| 16.5.1 | Handling and transport of steelwork | (1) Steelwork shall not be subject to rough handling, shock loading or dropping from a height. (2) During handling and transport of coated steelwork, the steelwork shall be separated from wires and lashings by rubber padding in such a manner that the coatings are not damaged or discoloured. Free ends shall be stiffened, measures shall be taken to prevent permanent distortion and machined surfaces and faying surfaces shall be protected. (3) Steelwork shall not be lifted from the painting bed until the last applied coating is sufficiently dry or cured for handling. (4) Rivets, bolts, nuts, washers, screws and small plates and articles shall be packed in containers marked to identify the contents. |
| 16.5.2 | Storage of steelwork | (1) Steelwork shall be stored off the ground on level supports in well drained areas in a manner which will not result in damage or deformation to the steelwork or coatings or in contamination of the steelwork or coatings. Packings shall be placed between steelwork that is stacked. (2) Covered places in which steelwork is stacked shall be ventilated. (3) Different types and sizes of steelwork shall be stored separately. (4) Steelwork shall not be stored on or adjacent to concrete surfaces that form part of the permanent work. (5) Steelwork shall be protected from exposure to conditions that may affect the steelwork or coatings. (6) Wet paint films, steelwork surfaces that are to be primed or overcoated and joint surfaces that are to be assembled shall be protected from exposure to conditions which may affect the film or surface. Undercoats which contain anatase titanium dioxide shall be protected from exposure to direct sunlight. (7) Steelwork shall be stored in an enclosed workshop and protected from conditions which may affect the steelwork after the steelwork has been cleaned until the following times: - When the second undercoat to painted steelwork has hard dried, - When the coating process to hot dip galvanized, electroplated or metal sprayed steelwork has been completed, - When the sealer to metal sprayed and sealed steelwork has been completely absorbed, and - When the first undercoat to metal sprayed and painted steelwork has hard dried. (8) Primed steelwork surfaces may be exposed outside the enclosed workshop for a period not exceeding two weeks. (9) Micaceous iron oxide undercoats to steelwork may be exposed outside the enclosed workshop for the minimum period necessary to move the steelwork from one part of the workshop to the other. The undercoat surfaces shall be covered when the steelwork is being moved. |
| 16.5.3 | Storage of paint | Paint and associated materials shall be stored in containers and protected from exposure to conditions that may affect the material. The materials shall be stored in accordance with the manufacturers’ recommendations and shall not be used after the recommended expiry date has been exceeded. The materials shall be stored in a locked store. |
| 16.6 | FABRICATION OF STEELWORK |  |
| 16.6.1 | Fabrication of steelwork | Fabrication of steelwork shall comply with BS 5400: Part 6, Clauses 4.1 to 4.16 or BS 5950: Part 2, Sections 3 and 4 as appropriate except as stated in Clauses 16.6.3 to 16.6.11. |
| 16.6.2 | Reinstatement on zinc coating with post-galvanising welding | (1) Where post-galvanising welding is necessary, the zinc coating shall be ground off the mating surfaces directly before welding. Immediately after welding, the surface of the weld area shall be prepared by removal of slag with the chipping hammer followed by vigorous wire brushing. The zinc coating shall then be restored by either: Application of the two coats of an organic zinc rich paint (zinc content at least 95%) to an overall dry film thickness greater than 100 µm. (ref. BS EN ISO 12944), or Pre-heating to 315oC and application of proprietary metallic repair stick or powder to a thickness greater than 100 µm. (2) If re-coating does not take place within 4 hours of welding, the weld areas shall be vacuum-grit blasted to BS EN ISO 8501 “first quality” and hot-zinc spray coated. Work shall be in accordance with BS EN 22063(1994) and to a minimum coating thickness of 100 µm.” (3) After reinstatement of the zinc coating, a complete paint system as specified in Clause 16.7.10 shall be applied to the repaired area in such a manner that the new paint overlaps the existing coats by at least 50 mm all around the affected part. |
| 16.6.3 | Welding, heating and cutting | (1) Welding shall be carried out by welders who possess a valid welding certificate for the appropriate category of welding. A welder shall cease to carry out welding if any of the circumstances stated in BS 4570, Clause 21.1 or BS 4872: Part 1, Clause 6 as appropriate occurs, or the requirements stated in BS EN 287: Part 1, Clause 10.1 are not satisfied. (2) Pre-setting, pre-bending, skip welding, back-step techniques and other measures shall be taken as necessary to counteract shrinkage or distortion due to welding, gouging, thermal cutting or heat treatment. (3) Butt welds shall be complete penetration butt welds made between fusion faces. (4) Butt welds in each component part shall be completed before the final assembly of built-up assemblies. (5) Welding of austenitic stainless steel shall be carried out in accordance with BS 4677. (6) Temporary welded attachments shall not be used unless permitted by the Engineer. Temporary welded attachments, when permitted, shall be removed by cutting with a flame torch 3 mm above the surface of the steel member when not required any longer. The excess metal protruding above the parent plate surface shall be removed by grinding and finished flush. (7) Welding, heating or thermal cutting processes which give off toxic or irritant gases shall not be used unless permitted by the Engineer. If permitted, precautions, including the provision of exhaust ventilation, breathing apparatus and display of warning signs, shall be taken to enable the work to be carried out in safe conditions. Welding, heating or thermal cutting shall not be carried out within 2 m of lead-based, cadmium or carbonaceous coatings. |
| 16.6.4 | Length of bolts | The length of HSFG bolts shall comply with BS 4604: Part 1 or BS 4604: Part 2 as appropriate. The length of bolts complying with BS 3692, BS 4190 and BS 4933 shall be such that the end of the bolt will project above the nut by at least one thread, but by not more than one nominal bolt diameter, after tightening. |
| 16.6.5 | Length of threads | The length of threads on bolts shall be determined in accordance with BS 3692, BS 4190, BS 4395: Part 1, BS 4395: Part 2, BS 4395: Part 3 or BS 4933 as appropriate. If additional locknuts or other nuts are specified, the thread length shall be increased by one nominal bolt diameter for each additional nut. |
| 16.6.6 | Use of nuts | Nuts shall not be used with bolts or screws that comply with a different standard. |
| 16.6.7 | Use of washer | Washers for HSFG bolts shall be provided in accordance with BS 4604: Part 1 or BS 4604: Part 2 as appropriate. Washers shall be provided for bolts complying with BS 3692, BS 4190 and BS 4933 under the nut or bolt head, whichever is rotated during tightening, if the parts to be connected are to be coated with protective coatings before assembly. Washers shall be provided under the nuts and heads of bolts in oversized and slotted holes. |
| 16.6.8 | Tightening of bolts | Bolts shall be tightened in such a manner that the contact surfaces of permanent bolted joints are drawn into close contact. |
| 16.6.9 | Tightening of HSFG bolts | (1) The degree of preliminary tightening of bolts and nuts complying with BS 4395: Part 1, which is tightened by the part turn method, shall be torque controlled. The tightening equipment for preliminary tightening shall be calibrated with a bolt load meter. The value of bedding torque for the preliminary tightening shall be within 10% of the values stated in Table 16.3. (2) Bolts and nuts at each joint with bolts or washers with load indicating devices shall be initially tightened to bring the faying surfaces into close contact over the full area. The range of the average gap after initial tightening shall be as agreed by the Engineer. The bolts and nuts shall be re-tightened if necessary to close the average gap back to the agreed range. After all bolts and nuts at the joint have been initially tightened, the bolts and nuts shall be finally tightened to attain the shank tension stated in BS 4604: Part 1 or BS 4604: Part 2 as appropriate. The range of average gap corresponding to the required shank tension shall be established for each batch as defined in BS 4395: Part 1, BS 4395: Part 2 or BS 4395: Part 3 as appropriate by testing at least three bolt, nut and washer assemblies in a bolt load meter and shall be as agreed by the Engineer. The average gap after final tightening shall be within the established range. (3) The threads of nuts for HSFG bolts that are to be tightened by the part turn method or the load indicating method shall not be lubricated unless approved by the Engineer. If the use of lubricant is approved in the part turn method, the bedding torque shall be established by a bolt load meter and shall be as agreed by the Engineer. The lubricant shall be applied at the place of manufacture and shall only be applied to the nut threads. The bearing surfaces of the nuts and the faying surfaces shall not be contaminated with the lubricant. (4) The bolt load meter for measuring bolt shank tension in the part turn, torque control or load indicating methods of tightening shall be calibrated by a laboratory approved by the Engineer before tightening of bolts and nuts starts and at regular intervals agreed by the Engineer. During re-calibration, a replacement calibrated bolt load meter shall be provided on the Site. Calibration results shall be submitted to the Engineer at least one week before the bolt load meter is used. |

Table 16.3: Bedding torque for HSFG bolts

| Nominal diameter of bolt (mm) | Bedding torque (N.m) |
| --- | --- |
| 16 | 80 |
| 20 | 160 |
| 22 | 210 |
| 24 | 270 |
| 27 | 340 |
| 30 | 460 |

| 16.6.10 | Defects in steelwork | Defective components for steelwork shall not be used in the permanent work unless repair of the defects is permitted by the Engineer If permitted, defective components shall be repaired by methods agreed by the Engineer. |
| --- | --- | --- |
| 16.6.11 | Approval of fabricated steelwork | Fabricated steelwork shall not be: Covered with protective coatings, concrete or other materials, Erected, or Despatched from the place of fabrication if fabricated off the Site until the steelwork, including any repaired areas, complies with the specified test and inspection requirements and has been approved by the Engineer. |
| 16.7 | PREPARATION OF STEELWORK SURFACES |  |
| 16.7.1 | Cleaning of steelwork and coated surfaces | (1) Soil, concrete and other adherent matter shall be removed immediately from steelwork or coated surfaces and the surfaces shall be made good by methods agreed by the Engineer. (2) Dust, soot, grit, detritus, metallic or other loose particles shall be removed by vacuuming after steelwork surfaces have been blast cleaned or before coated surfaces are washed or steam cleaned. (3) Oil and grease shall be removed by emulsion cleaners, by steam cleaning or by high pressure water jets before removing rust and mill scale or overcoating. Oil and grease shall not be removed with turpentine or other solvents. If steam cleaning is used, steam cleaning shall be carried out after the greasy deposits have been removed by scraping and a detergent shall be added to the feed water of the steam generator. (4) Salts, chemicals, corrosion or paint degradation products, including rust-spotting on blast cleaned surfaces and zinc salts on zinc coatings or zinc-rich paints, shall be removed by washing with detergent solution before coating steelwork surfaces or overcoating. (5) The final shop coats on external surfaces shall be thoroughly washed with a detergent solution at the Site before being overcoated. (6) Unless otherwise permitted by the Engineer finished coated surfaces shall be cleaned not more than 14 days before handover of the steelwork. (7) Cleaning agents to be used shall be as agreed by the Engineer. Surfaces that have been cleaned using cleaning agents shall be rinsed with fresh water to remove all traces of the cleaning agent. (8) Cleaning tools shall be of a type that will not result in damage to the surfaces being cleaned. Wire brushes and brooms shall not be used for cleaning coated surfaces. |
| 16.7.2 | Preparation of steelwork surfaces |  |
| 16.7.3 | Blast cleaning of steelwork | (1) Bare metal surfaces of steelwork which are to be painted or metal coated shall be treated before rust and mill scale are removed in accordance with the following requirements: - Burrs, arrises and serrations shall be smoothed by grinding or filing. - Weld spatter, weld slag and raised metal laminations shall be removed by grinding or chipping and the surface shall be made good. (2) Rust and mill scale shall be removed from steelwork which is to be metal coated in factories by a pickling process which is compatible with the metal coating process. (3) Rust and mill scale shall be removed from steelwork which is to be metal sprayed by blast cleaning carried out in accordance with BS 2569: Part 1, Clause 3. (4) Rust and mill scale shall be removed from steelwork which is to be painted by blast cleaning unless the use of acid-pickling, mechanical cleaning or flame cleaning has been approved by the Engineer. (5) Excess acid or other chemicals used in the pickling process shall be removed from steelwork that has been prepared by pickling before the application of the metal coating. Pickling shall not be carried out for longer than is necessary to remove the rust and mill scale. |
| 16.7.4 | Blast cleaning of steelwork | (1) Blast cleaning of steelwork shall be carried out to second quality of surface finish using chilled iron abrasive. (2) Chilled iron grit shall be graded in accordance with BS 2451. The maximum size of grit shall be G17 for use in automatic-impeller-type equipment and shall be G12 for manual or compressed air equipment. The difference in level between a peak and the adjacent trough of the blasted surface profile shall not exceed 0.1 mm. (3) Non-metallic abrasives with a maximum particle size not exceeding 1 mm shall not be used other than with portable equipment. (4) Abrasives shall not contain materials that may contaminate the steel surfaces. Sand containing salt or excessive amounts of silt shall not be used. Contaminants shall be removed from recovered abrasives before re-use. (5) Blast cleaning shall be carried out in a fully enclosed space separated from the place of painting. The enclosed space shall be fitted with dust extractors and filters to prevent the dispersal of dust outside the enclosed space. |
| 16.7.5 | Acid-pickling of steelwork | Acid-picking of steelwork shall be carried out in accordance with BS 5493, Clause 14.3.2. The first priming coat of paint shall be applied as soon as the steel has dried and is still warm. |
| 16.7.6 | Mechanical cleaning of steelwork | Mechanical cleaning of steelwork shall be carried out using grinding discs or other power-driven tools followed by steel wire brushing and dusting to remove all loosened material which is not firmly bonded to the metal surface. Excessive burnishing of the metal through prolonged application of rotary wire brushes shall not be carried out. Visible peaks and ridges shall be removed. Pneumatic chipping hammers shall not be used. |
| 16.7.7 | Flame cleaning of steelwork | (1) Flame cleaning of steelwork shall not be carried out at the following locations: - Within 2 m of HSFG bolts, cold worked high tensile steel and surfaces already coated with paint or cadmium, lead-based or carbonaceous materials, and - On sections thinner than 0.5 mm. (2) Flame cleaning shall be carried out without distorting the steelwork and without adversely affecting the properties of the steel. The temperature of the steel surface being flame cleaned shall not exceed 200°C. (3) Loose materials shall be removed from the flame-cleaned surface by wire brushing followed by blowing dry air or vacuuming. The priming coat shall be applied when the surface temperature of the steel is between 35°C and 40°C. Surfaces with temperatures of less than 35°C shall be reheated. |
| 16.7.8 | Cleaning of bolts, nuts and washers | Bolts, nuts and washers for steelwork shall be kept free of dirt and deleterious material. Oil and grease on bolts, nuts and washers, other than approved lubricants for nuts of HSFG bolts, shall be removed before assembling and coating the exposed parts of assembled bolts, nuts and washers. |
| 16.7.9 | Approval of surface preparation | Surfaces shall not be coated until the cleaning and preparation of the surfaces have been approved by the Engineer. |
| 16.7.10 | Metal coatings to steelwork | (1) Metal coatings to steelwork shall be as stated in Clause 16.7.10 (2) Galvanized coatings shall be applied by hot-dip galvanizing in accordance with BS EN ISO 1461:1999. The coating thickness shall comply with BS EN ISO 1461:1999. (3) Sherardized zinc coatings shall comply with BS 4921, Table 1, Class 1. (4) Sprayed zinc and aluminium coatings shall comply with BS 2569: Part 1. The nominal coating thickness shall be 100 m. The sprayed metal shall be pre-treated with product CP1 and sealed with product CP3C in accordance with BS 5493. (5) Electroplated zinc and cadmium coatings on threaded components with a diameter not exceeding 36 mm shall comply with BS 3382: Parts 1 and 2. The coating thickness shall be at least 5 µm. (6) Metal coatings that will be overcoated with paint shall not be passivated. (7) Allowance for the thickness of the metal coating shall be made in the sizes of the threads of metal coated threaded components. Nuts shall not be tapped oversize by more than 0.4 mm. Metal-coated HSFG bolts and nuts shall not be tapped oversize unless approved by the Engineer. (8) Damaged areas of metal coatings shall be rubbed down to remove excessive roughness, cleaned and made good with a compatible coating of a type approved by the Engineer. (9) Metal coatings required on part of a component shall be completed before the rest of the component is painted. |
| 16.8 | PAINTING STEELWORK |  |
| 16.8.1 | Painting systems for steelwork | (1) The painting system to be used for steelwork shall be one or more of the following systems as stated in the Contract, where DFT is the dry film thickness: System A: - primer: 1 coat of high build zinc phosphate paint, - undercoat: 2 coats of oil based with micaceous iron oxide phenolic paint - finish : 1 coat of alkyd resin paint, - minimum total DFT : 250 µm System B: - primer : 1 coat of epoxy resin with aluminium mastic paint, - undercoat : 1 coat of epoxy resin paint, - finish : 1 coat of epoxy resin paint, - minimum total DFT : 280 µm System C: - primer : 1 coat of inorganic zinc silicate paint, DFT 75 µm, - undercoat : 2 coats of high build micaceous iron oxide epoxy paint, - finish : 1 coat of high build amine adduct cure epoxy paint, - minimum total DFT : 320 µm System D: - primer : 1 coat of two pack wash primer, DFT 5 µm, - undercoat : 1 coat of epoxy resin paint, - finish : 1 coat of epoxy resin paint or 2 coats of polyurethane paint, - minimum total DFT : 180 µm System E: - Inhibitor : Rustoleum or other rust inhibitor paint approved by the Engineer, - primer : zinc phosphate or, for hot-dip galvanized or GI surface, ‘T’ wash as specified in BS 5493, Section 2, Clause 11.3.2, - undercoat : 2 coats of micaceous iron oxide paint, - finish : 1 coat of oil based paint or 1 coat of micaceous iron oxide paint, - DFT of each coat : as recommended by the manufacturer (2) The different types of paints within each painting system shall be compatible with each other and shall be manufactured by the same manufacturer. Successive coats in a painting system, including stripe coats, shall be in contrasting colours to aid identification. |
| 16.8.2 | Application of paint to steelwork | (1) Surfaces that are to be painted shall be dry immediately before paint is applied. (2) Paint shall be taken from the paint store ready for application. Thinning, if necessary, shall be carried out in the paint store in the presence of the Engineer and using the type of thinner in the ratio stated in the manufacturer’s data sheets. (3) Paint shall be applied by brush, by air pressure spray or by airless spray. Sealer and primers shall be applied by continuous spraying. (4) Each coat in the paintwork system shall be sufficiently dry or cured before the next coat is applied. The time between the applications of successive coats shall be within the limits recommended by the manufacturer (5) Paints having a pot life specified by the manufacturer, including two pack paints and moisture cured paints, shall be discarded on expiry of the pot life or at the end of each working day, whichever comes first. Other paints in opened containers shall be kept in sealed containers with not more than 10% ullage in store after each day’s work and shall not be thinned or mixed with fresh paint when re-issued for another day’s work. |
| 16.8.3 | Working conditions for painting | (1) Paint shall not be applied to steelwork under the following conditions: When the ambient temperature falls below 4°C or the relative humidity rises above 90%, For outdoor work, during periods of inclement weather including fog, frost, mist and rain or when condensation has occurred or is likely to occur on the metal, When the surface temperature of the metal to be painted is less than 3°C above the dew point of the ambient air, and When the amount of dust in the air or on the surface to be painted is in the opinion of the Engineer excessive. (2) Two pack paints of the epoxide-resin type shall not be applied and cured when the temperature is below that recommended by the paint manufacturer. |
| 16.8.4 | Priming and overcoating time limits | (1) Blast cleaned steel shall be primed or metal coated within 4 hours after blast cleaning. (2) Primed steel surfaces shall be overcoated within 8 weeks after priming. (3) Second undercoats shall be applied within 72 hours after application of the first undercoat. (4) Sealer or etch primer to sprayed metal shall be applied within 4 hours after spraying. The etch primed surfaces shall be overcoated within 72 hours after priming. (5) Etch primer to galvanized steelwork shall be applied within 14 days after delivery of the steelwork to the Site. The etch primed surfaces shall be overcoated within 48 hours after priming. (6) Overcoats to two pack paints of the epoxide- or polyurethane-type shall be applied within 48 hours after application of the two-pack paint. If it is not possible to overcoat within 48 hours, the two pack paint shall be abraded to produce a roughened surface and shall be given a flash coat of primer of a type approved by the Engineer. The primer shall be allowed to dry for at least 4 hours before application of the next coat of the system. |
| 16.8.5 | Stripe coats to steelwork | Immediately after the first undercoat of the painting system to steelwork has dried, a stripe coat of undercoat paint shall be applied by brush to edges, corners, crevices, exposed parts of bolts, nuts, rivets and welds. Another stripe coat of finishing paint shall be applied in the same manner after the last undercoat has dried. |
| 16.8.6 | Paint coats to steelwork | (1) The dry film thickness of the paint coats to steelwork shall be measured using a magnetic dry film thickness gauge or other apparatus approved by the Engineer. The total dry film thickness shall be measured at spacings of approximately 1.0 m. If the measured dry film thickness is less than 75% of the specified nominal dry film thicknesses or if more than 10% of the measured dry film thickness are less than 95% of the specified nominal dry film thickness, repair work shall be carried out as stated in Clause 16.8.8 (2) Wet film thickness gauges shall not be used as a means of determining whether the dry film thickness of the painting system complies with the specification. (3) Each coat of paint shall be free of embedded foreign matter, mechanical damage and surface defects, including bittiness, blistering, brush marks, bubbling, cissing, cracking, cratering, dry spray, floating, pinholing, rivelling, runs, sagging, spotting and spray mottle as stated in BS 2015. The finished paintwork system shall have an even and uniform appearance. (4) Each coat of paint shall adhere firmly to the substrate without blistering, chipping, flaking or peeling. |
| 16.8.7 | Etch primers and blast primers | Etch primers and blast primers shall not be applied on phosphated steel and shall not be overcoated with zinc-rich primers. |
| 16.8.8 | Repairs to damaged areas of paint | (1) Areas of paint to steelwork that have been damaged shall be cleaned to bare metal or to the metal coating. The edges of the undamaged paint shall be bevelled. (2) The full specified painting system shall be restored in such a manner that each new paint coat overlaps the existing paint by at least 50 mm all round the affected part. |
| 16.9 | PROTECTION OF JOINTS IN STEELWORK |  |
| 16.9.1 | Protection of HSFG bolted joints | (1) The faying surfaces of HSFG bolted joints in steelwork that is metal sprayed overall and sealed or metal sprayed and painted overall shall be coated with the sprayed metal. The sealer on the parent material shall extend for a distance of between 10 mm and 20 mm inside the perimeter of the faying surfaces. Free surfaces and edges of the joint material shall be coated with the same sealer. (2) The joint material and the faying surfaces on the parent material of steelwork which is metal sprayed only at joints and painted overall shall be metal sprayed. The sprayed metal on the parent material shall extend for a distance of between 10 mm and 20 mm outside the perimeter of the faying surfaces. The primer on the parent material shall extend for a distance of between 10 mm and 20 mm inside the perimeter of the faying surfaces. Sprayed metal on the free surfaces and edges of the joint material shall be coated with a sealer which is compatible with the painting system. (3) The primer on the parent material of steelwork which is painted overall and uncoated at faying surfaces of HSFG bolted joints shall extend for a distance of between 10 mm and 20 mm inside the perimeter of the faying surfaces. |
| 16.9.2 | Protection of other shop-bolted joints | Blast primer for painted steelwork or sprayed metal plus sealer for metal sprayed steelwork shall be applied to the joint and parent material of shop-bolted joints other than HSFG bolted joints. Joints for painted steelwork shall be assembled after the first undercoat of the painting system has been applied to the contact surfaces and while the undercoat is still wet. |
| 16.9.3 | Protection of other site-bolted joints | Surfaces of the parent and joint material of site-bolted joints other than HSFG bolted joints shall be coated with the same protective system as the parent material. |
| 16.9.4 | Protection of welded joints | Welds and steelwork surfaces that have been affected by welding shall be coated with the same protective system as the parent material. |
| 16.9.5 | Joints made after coating the parent material | (1) Hot-dip galvanizing and electroplating to steelwork shall not be carried out until all welds for the steelwork that is to be galvanized or electroplated have been completed. (2) Sprayed metal on the parent material shall be kept at least 15 mm, but not more than 300 mm, clear of areas that are to be welded. The restricted area shall be masked during metal spraying. (3) Successive coats of paint on the parent material shall be stepped back at 30 mm intervals commencing at 100 mm from welded joints and at 10 mm from the perimeter of HSFG bolted joints. (4) If the parent metal in the approved welding procedure is coated with the pre-fabrication primer or sprayed metal such coatings are permitted to cover the area to be welded. After welding the pre-fabrication primer or sprayed metal adjacent to the weld shall be made good. (5) The parent material, joint material, exposed parts of bolts, nuts and washers, welds and weld affected areas shall be cleaned, prepared and brought up to the same protective system as the adjoining surfaces not more than 14 days after the joints have been made. |
| 16.9.6 | Sealing of joints in steelwork | (1) The different parts of joints in steelwork shall be dry immediately before the joints are assembled. (2) Gaps around the perimeter of bolted joints and load indicator gaps of HSFG bolts in steelwork painted overall shall be sealed by brush application of the same painting system as the parent material. Gaps shall be plugged if necessary with soft solder wire without flux core as a backing before sealing with paint. |
| 16.10 | PROTECTION OF SPECIAL SURFACES OFSTEELWORK |  |
| 16.10.1 | Protection of hollow steel sections | The ends of hollow steel sections shall be sealed by welding mild-steel plates over the open ends. The plates shall be at least 5 mm thick. Immediately before hollow steel sections are sealed, bags of anhydrous silica gel shall be inserted in each void at the rate of 0.25 kg/m3 of void. |
| 16.10.2 | Protection of bearing surfaces for bridge bearings | Dirt, oil, grease, rust and mill scale shall be removed from the metal bearing surfaces for bridge bearings. The surfaces shall be masked with tape or other methods agreed by the Engineer and shall not be primed or painted until the bonding agent has been applied. |
| 16.10.3 | Protection of uncoated steelwork surfaces | The coated surfaces of steelwork coated over part of the surface shall be protected from rust that may form on the uncoated surfaces. Temporary coatings that may affect the bond between concrete and uncoated surfaces against which the concrete is to be placed shall be removed and the uncoated surfaces shall be cleaned before the concrete is placed. The full coating system shall extend 25 mm, or 75 mm for steel piles, into areas against which concrete is to be placed. |
| 16.11 | ERECTION OF STEELWORK |  |
| 16.11.1 | Temporary supports and fastenings to steelwork | (1) Steelwork shall be secured in position by temporary supports and fastenings until sufficient permanent connections are complete to withstand the loadings liable to be encountered during erection. The temporary supports and fastenings shall be capable of withstanding loadings that may be encountered during erection and shall not damage the steelwork or the protective coatings. (2) Riveted and bolted connections shall be aligned using drifts complying with BS 5400: Part 6, Clause 4.12 and shall be temporarily fastened using service bolts. |
| 16.11.2 | Alignment of steelwork | (1) Measures shall be taken to ensure that the steelwork will remain stable before temporary supports and fastenings are slackened or removed for lining, levelling, plumbing or other purposes. The temporary supports and fastenings shall be re-tightened or replaced as soon as the adjustments are complete and at the end of each continuous period of working. (2) Permanent connections shall be made as soon as a sufficient portion of the steelwork has been lined, levelled and plumbed. Temporary supports and fastenings shall be replaced by permanent connections progressively and in such a manner that the parts connected are securely restrained in the aligned position at all times. (3) Permanent connections for each portion of steelwork shall be completed not more than 14 days after the portion has been erected. |
| 16.11.3 | Foundation bolts for steelwork | 1) Foundation bolts for steelwork shall be held firmly in the set position during fixing. Measures shall be taken to ensure that the full movement tolerances are achieved and the bolts are not displaced during concreting. Bolts and nuts, including the threads, shall be protected against damage, corrosion and contamination. (2) Bolt pockets shall be kept dry and clean. Tubes that are cast in concrete for grouting bolt pockets shall be securely fixed and sealed to prevent ingress of grout during concreting. (3) Bolts in bolt pockets shall be installed in such a manner that the bolt can be moved inside the pocket as designed without hindrance. |
| 16.11.4 | Supporting devices for steelwork | The material, size, position and cover of packs, shims and other supporting devices for steelwork which are to be embedded shall be as approved by the Engineer. |
| 16.11.5 | Bedding and grouting of column bases | (1) Column bases for each portion of steelwork shall not be bedded or grouted until the portion has been lined, levelled, plumbed and permanently connected. Spaces below the steel shall be dry, clean and free of rust immediately before bedding or grouting. (2) Proprietary types of grout shall be used in accordance with the manufacturer’s recommendations. (3) Temporary timber wedges holding steel columns in position shall not project into pocket bases by more than one-third of the embedded length of the steel column. The pocket shall be initially concreted up to the underside of the wedges and the steel column shall be left undisturbed until 48 hours after concreting. The wedges shall then be removed and the remainder of the pocket shall be concreted. |
| 16.12 | TOLERANCES |  |
| 16.12.1 | Tolerances fabrication of steelwork | Fabrication tolerances for steelwork shall comply with BS 5400: Part 6, Clause 4.2 or BS 5950: Part 2, sub-section 7.2 as appropriate. |
| 16.12.2 | Tolerances: foundation bolts | The position of cast-in foundation bolts at the top of base plates shall be within 3 mm of the specified position. The position of foundation bolts in bolt pockets at the top of base plates shall be within 5 mm of the specified position. The line of bolts shall not be tilted from the specified line by more than 1 in 40. |
| 16.12.3 | Tolerances: erection of steelwork | (1) The position in plan of vertical components at the base shall be within 10 mm of the specified position. (2) The level of the top of base plates and the level of the lower end of vertical or raking components in a pocket base shall be within 10 mm of the specified level. (3) The thickness of bedding shall be within one-third of the nominal thickness or 10 mm, whichever is less, of the specified nominal thickness. (4) The line of vertical or raking components other than in portal frames shall be within 1 in 600 and within 10 mm of the specified line in every direction. (5) The line of vertical or raking components in portal frames shall be within 1 in 600 and within 10 mm of the specified line normal to the plane of the frame. (6) The position and level of components connected with other components shall be within 5 mm of the specified position and level relative to the other components at the point of connection. (7) The position of components supported on a bearing shall be within 5 mm of the specified position relative to the bearing along both principal axes of the bearing. (8) The difference in level between adjacent sloping or horizontal components connected by a deck slab shall be within 10 mm of the specified difference in level. |
| 16.14 | TESTS ON STEELWORK AT MANUFACTURER’S WORKS |  |
| 16.14.1 | Tests on steelwork at manufacturer’s works | (1) Tests shall be carried out on structural steel in accordance with BS 5400: Part 6, Clauses 5.2.1, 5.2.2 and 5.3. (2) Tests shall be carried out on bolts, nuts and washers in accordance with BS 3692, BS 4190, BS 4395: Part 1, BS 4395: Part 2, BS 4395: Part 3 or BS 4933 as appropriate. The tests shall be carried out on full size bolts. The rates of sampling and testing shall be in accordance with BS 4395: Part 1. (3) The tests shall be carried out by the manufacturer at the manufacturer’s works on samples selected by the manufacturer. |
| 16.15 | TESTING: STEELWORK |  |
| 16.15.1 | Batch: steelwork | (1) A batch of steelwork is the amount of steelwork stated in the Contract and which is completed or delivered to the Site at any one time. (2) The Contractor shall submit to the Engineer a list of the parts included in each batch at least 7 days before testing starts. |
| 16.15.2 | Samples: steelwork | (1) Samples to be tested shall be selected by the Engineer if testing is to be carried out in the Maldives (2) Samples shall be selected from positions that in the opinion of the Engineer or approved testing consultant are representative of the batch as a whole. (3) The Engineer shall inform the Contractor of the samples selected for testing at least 3 days before testing starts. |
| 16.15.3 | Testing: steelwork | (1) The relevant tests shall be carried out on each batch of steelwork. (2) The Contractor shall inform the Engineer at least 7 days before tests are carried out. |
| 16.15.4 | Reports of tests on steelwork | (1) Records of tests on steelwork carried out by the Contractor or the approved testing consultant shall be kept by the Contractor and a report shall be submitted to the Engineer at least 7 days before approval of the batch of steelwork tested is required. The report shall contain the following details: - Procedure tested and exact test location in the steelwork, - Results of tests compared to the required values, with any non-complying results highlighted, - Any tearing, cracking or other defects, and - Conclusion as to the overall acceptability of the parts of steelwork examined by the approved testing consultant. (2) Reports shall be certified by the Contractor’s authorised representative or by the approved testing consultant who carried out the tests. |
| 16.15.5 | Non-compliance: steelwork | (1) If the result of any test on steelwork does not comply with the specified requirements for the test, the test shall be carried out on additional samples from the batch. The number of additional tests shall be twice the number of original tests. (2) The batch shall be considered as not complying with the specified requirements for the test if the result of any additional test does not comply with the s (3) If the result of every additional test complies with the specified requirements for the test, only those parts the samples from which have failed in the original tests shall be considered as not complying with the specified requirements of the test. |
| 16.15.6 | Samples: steel | Samples of steel shall be provided from each batch of steel within 3 days after delivery of the batch to the fabricator’s works or to the Site. The rate of sampling and the position and direction of the samples shall be in accordance with BS 4360. |
| 16.15.7 | Testing: steel | (1) The tensile test and the impact test shall be carried out on each sample of steel. The method of testing shall be in accordance with BS 4360. (2) Quality grading of structural steel shall be carried out on steel that has not been tested for quality grades by the manufacturer. Quality grading shall be carried out in accordance with BS 5400: Part 6, Clause 3.1.4 or BS 5950: Part 2, Clause 2.1.6 as appropriate. (3) Testing and quality grading shall be carried out by the approved testing consultant. |
| 16.15.8 | Testing: welds | (1) Examination and testing of welds shall be carried out after post-weld heat treatment and before the application of corrosion protective coatings. De-burring, dressing, grinding, machining and peening shall be carried out after the visual inspection for cracks, surface pores and joint fit-up and before other inspections and tests are carried out. (2) Destructive testing of welds for steelwork complying with BS 5400: Part 6 shall be carried out in accordance with BS 5400: Part 6, Clauses 5.5.1.1, 5.5.1.2 and 5.5.1.3. (3) Welds for structural steel and steel castings shall be visually inspected in accordance with BS 5289. No-destructive testing shall be carried out on a proportion of welds after visual inspection. The compliance criteria and the proportion of welds to be tested are denoted by quality categories as stated in BS 5135, Table 18 for butt welds and in BS 5135, Table 19 for fillet welds. The quality categories of welds shall be as stated in Table 16.4. (4) No-destructive testing of butt welds shall be carried out by ultrasonic examination in accordance with BS 3923: Part 1 or BS 3923: Part 2 or by radiographic examination in accordance with BS 2600: Part 1, BS 2600: Part 2 or BS 2910. No-destructive testing of fillet welds shall be carried out by either the liquid penetrant method in accordance with BS 6443 or the magnetic particle flaw detection method in accordance with BS 6072. The particular standard or part of standard to be used shall be appropriate for the joint geometry, material and production requirements and shall be as agreed by the Engineer. Welds shall be dressed to facilitate ultrasonic examinations. (5) If the parent metal adjacent to a length of weld subject to non-destructive testing has been tested for laminations in accordance with BS 5996, the same areas on the parent metal shall be tested by ultrasonic examination in accordance with BS 3923: Part 1 or BS 3923: Part 2 as appropriate when no-destructive testing is carried out on that length of weld. (6) Welds for steelwork that has been fabricated and tested by no-destructive testing at the fabricator’s works shall be visually inspected for cracks when the steelwork is delivered to the Site. 5% of the welds other than welds stated in Table 16.2 shall be examined for cracks by the magnetic particle flaw detection method in accordance with BS 6072. (7) Inspection of welds will be carried out by the Engineer for welds stated in Table 16.2. |

Table 16.4: Quality categories of welds

| Type of welds | Steelwork Complying with BS 5400: Part 6 |  | Steelwork Complying with BS 5950: Part 2 |  |
| --- | --- | --- | --- | --- |
|  | Butt Welds | Fillet Welds | Butt welds | Fillet welds |
| Welds stated in the Contract for 100% non-destructive testing | A | A | A | A |
| Welds stated in Table 16.2 | D | D | D | D |
| Other welds | B | B | C | C |

| 16.15.9 | Testing: stud shear connectors and rivets | (1) Tests shall be carried out on 5% of welded stud shear connectors in accordance with BS 5400: Part 6, Clause 5.5.4. (2) Tests shall be carried out on 5% of driven rivets in accordance with BS 5400: Part 6, Clause 5.8. (3) Testing shall be carried out by the Contractor in the presence of the Engineer. |
| --- | --- | --- |
| 16.15.10 | Testing: fabrication tolerance | (1) Rolled and built-up sections of steelwork complying with BS 5400: Part 6 shall be tested to determine compliance with fabrication tolerances in accordance with BS 5400: Part 6, Clauses 5.6.1 to 5.6.6. (2) Testing shall be carried out by the Contractor in the presence of the Engineer. |
| 16.15.11 | Testing: repairs | Defects that have been repaired and adjoining areas that in the opinion of the Engineer may have been affected by the repair shall be retested as instructed by the Engineer. |
| 17. | SECTION 17 HANDRAILING, LADDERS, STAIRS AND FLOORING |  |
| 17.1 | GENERAL |  |
| 17.1.1 | General requirements | The works and materials specified below shall comply with the sections stated, unless otherwise stated in this Section. Hot dip galvanization shall comply with BS EN ISO 1461:1999. |
| 17.1.2 | Materials for grout | Materials for grout shall comply with Section 15. |
| 17.1.3 | Steelwork | Steelwork, including protective treatment, shall comply with Section 16. |
| 17.2 | MATERIALS |  |
| 17.2.1 | Steel | Steel for handrailing, ladders, stairs and flooring shall comply with the following: Steel tubes and tubulars suitable for screwing to BS 21 pipe threads : BS 1387 Hot rolled sections : BS 4: Part 1 Hot rolled structural steel sections Equal and unequal angles : BS 4848: Part 4 Hollow sections : BS 4848: Part 2 Weldable structural steels : BS 4360. |
| 17.2.2 | Stainless steel | Stainless steel for handrailing, ladders, stairs and flooring shall be Grade 304 S 15 complying with BS 970: Part 1. Stainless steel tubes shall be longitudinally welded tubes complying with BS 6323: Part 8, designation LW 21 GZF(S). Tubes for handrails shall be polished. |
| 17.2.3 | Aluminium | (1) Aluminium for handrailing, ladders, stairs and flooring shall be of type H 30 TF and shall comply with the following: Wrought aluminium and aluminium alloys for general engineering purposes Plate, sheet and strip BS 1470 Drawn tube BS 1471 Bars, extruded round BS 1474 tubes and sections (2) Aluminium shall be anodised to Grade AA 25 in accordance with BS 1615. |
| 17.2.4 | Bolts, nuts, screws, washers and rivets | (1) Bolts, nuts, screws, washers and rivets shall comply with the following: ISO metric black hexagon bolts, screws and nuts : BS 4190 ISO metric black cup and countersunk headbolts and screws with hexagon nuts : BS 4933 Metal washers for general engineering purposes : BS 4320 Rivets for general engineering purposes : BS 4620 Wrought aluminium and aluminium alloys for general engineering purposes : BS 1473 rivet, bolt and screw stock Stainless steel fasteners : BS 6105 (2) The length of bolts shall be such that the threaded portion of each bolt projects through the nut by at least one thread and by not more than four threads. (3) Rag, indented bolts, expansion bolts and resin bonded bolts shall be of a proprietary type approved by the Engineer and shall be capable of withstanding the design working load. (4) Hot dip galvanized bolts, nuts, screws, washers and rivets shall be used with hot dip galvanized handrailing, ladders, stairs and flooring. Aluminium bolts, nuts, screws, washers and rivets shall be used with aluminium handrailing, ladders, stairs and flooring. Stainless steel bolts, nuts, screws, washers and rivets shall be used with other types of handrailing, ladders, stairs and flooring. Bolts, nuts, screws and washers shall be insulated from aluminium by non-metallic washers and sleeves. |
| 17.2.5 | Cement mortar | (1) Mortar for grouting fixing bolts shall consist of 1 part of Portland cement to 3 parts of sand together with the minimum amount of water necessary to achieve a consistency suitable for completely filling the bolt holes. The mix shall contain a non-shrink admixture. (2) Resin grout shall be of a proprietary type approved by the Engineer and shall contain a non-shrink admixture. (3) Mortar for building in curbs for metal flooring shall consist of 1 part of cement to 3 parts of sand together with the minimum amount of water necessary to achieve a consistency suitable for the work. The mix shall contain a non-shrink admixture. |
| 17.3 | DESIGNED BY CONTRACTOR |  |
| 17.3.1 | Designed by Contractor | Handrailing, ladders, stairs and flooring which are to be designed by the Contractor shall comply with the following requirements: Handrailing shall be capable of withstanding a horizontal loading of 740 N/m. The deflection of handrailing shall not exceed 1 in 200 at mid-span. Stairs shall be designed for a live loading of 5 kPa. Flooring shall be designed for a live loading of 5 kPa. deflection of flooring shall not exceed 1/200 of the span. |
| 17.4 | FABRICATION OF HANDRAILING, LADDERS, STAIRS AND FLOORING |  |
| 17.4.1 | Fabrication of steelwork | Steelwork for handrailing, ladders, stairs and flooring shall be fabricated in accordance with BS 5950: Part 2. |
| 17.4.2 | Galvanizing to steel | (1) All steel that is to be galvanized shall be hot dip galvanized in accordance with BS EN ISO 1461:1999. (2) Galvanizing to steel shall be applied after welding, drilling and cutting are complete. |
| 17.4.3 | Welding steel | (1) Welds to steel for handrailing, ladders, stairs and flooring shall be full depth fillet welds. The welded surface shall be clean and flush before application of the protective coating. (2) Steel shall not be welded after hot dip galvanizing unless permitted by the Engineer and if permitted, the welded areas shall be free from scale and slag and shall be treated with appropriate coating system approved by the Engineer, which is compatible with the protective system of the parent material. |
| 17.4.4 | Fabrication of handrailing | Handrailing shall be discontinued at movement joints in structures. The spacing between standards shall be regular and shall not exceed 1.6 m. Curved handrailing shall not be made up of a series of straights. |
| 17.4.5 | Fabrication of ladders | (1) Ladders shall comply with BS 4211 or similar (2) Steel ladders shall be hot-dip galvanized. (3) Aluminium ladders shall be Grade 6082 aluminium. (4) Rungs, extended stringers, safety cages and brackets shall be welded to the stringers of ladders. (5) Rungs on aluminium ladders shall have longitudinal grooves and pressed aluminium alloy caps shall be fixed to open ends. |
| 17.4.6 | Fabrication of stairs | Stairs shall comply with BS 5395: Part 1 or similar |
| 17.4.7 | Fabrication of flooring | (1) The shape of each panel of flooring shall be such that the panel can be easily removed. The mass of each panel shall not exceed 40 kg. Where intermediate supports are provided to support flooring they shall be capable of being removed to provide the specified clear opening. (2) Curbs shall be provided in concrete surfaces for flooring. (3) Cut-outs in flooring shall be neatly shaped and shall be provided with toe plates. Cut-outs in open mesh flooring shall be trimmed with edge bars welded to the bearing bars. The clearance between the edge of cut-outs and the component passing through the cut-out shall not exceed 30 mm. (4) The bearing bars in open mesh flooring shall be welded to the nosing bars. The transverse bars shall be rivetted or welded to the bearing bars. Panels of open mesh flooring shall be secured with adjustable fixing clips. (5) Chequer plate flooring shall have a non-slip pattern of a type approved by the Engineer and shall be provided with lifting holes. The flooring shall be secured to curbs by countersunk screws. |
| 17.4.8 | Fabrication of toe plates | Toe plates shall be fixed to handrail standards by brackets and shall be bolted or welded to stairs and flooring. |
| 17.4.9 | Fabrication of safety chains | (1) Safety chains shall comply with BS 4942 and shall be capable of withstanding a breaking force of 30 kN and a proof force of 15 kN. (2) Steel safety chains shall be 8 mm nominal size, Grade M4 non-calibrated chain Type 1 and shall be hot-dip galvanized. (3) The links of stainless steel safety chains shall be welded and shall have an internal length exceeding 45 mm and an internal width of between 12 mm and 18 mm. Fins caused by welding shall be removed. (4) Hot dip galvanized hooks on chains shall be fitted with a sprung securing device. |
| 17.5 | SUBMISSIONS |  |
| 17.5.1 | Particulars of handrailing, stairs, ladders and flooring | (1) The following particulars of the proposed handrailing, ladders, stairs and flooring shall be submitted to the Engineer: - Details of manufacturer's name and place of manufacture, - An original certificate bearing the chop of the manufacturer showing that the materials comply with the requirements - Drawings showing layout and details of handrailing, including positions of the different types of standards, - Drawings showing details of ladders, stairs, toe plates and safety chains, - Drawing showing layout and details of flooring, including positions and sizes of panels and supports, - Details of methods of fixing and of rag, indented, expansion and resin bonded bolts, including manufacturer's literature, and (2) The particulars shall be submitted to the Engineer at least 14 days before fabrication starts. |
| 17.5.2 | Samples of materials | (1) The following samples of the proposed handrailing, ladders, stairs and flooring shall be submitted to the Engineer at least 14 days before the relevant work starts: - Handrails, - Standards, - Ladders, including rungs, - Toe plates, - Flooring and curbs, - Safety chains, and - Rag, indented, expansion and resin bonded bolts. (2) The details of samples shall be as instructed by the Engineer. |
| 17.6 | STORAGE OF MATERIALS |  |
| 17.6.1 | Storage of handrailing, ladders, stairs and flooring | Handrailing and flooring shall be stored on level supports in a dry weatherproof store and in a manner that will not result in damage or deformation to the materials or in contamination of the materials. Handrailing, ladders, stairs and flooring shall be protected from damage and damaged handrailing, ladders, stairs and flooring shall not be used in the permanent work unless permitted by the Engineer. |
| 17.7 | INSTALLATION OF HANDRAILING, LADDERS, STAIRS, AND FLOORING |  |
| 17.7.1 | Installation of handrailing, ladders and stairs | (1) Handrailing shall be installed to a smooth alignment to the Engineer’s satisfaction. (2) Handrail standards, flanges, ladders and stairs shall be bolted to metalwork and shall be fixed to concrete using rag, indented, expansion or resin bonded bolts. The bolts shall be fitted into pockets left in the concrete and the pockets shall be filled with cement mortar or resin grout. |
| 17.7.2 | Installation of flooring | (1) Flooring and curbs shall be flush with the adjoining surfaces. (2) Curbs shall be fitted into rebates left in the concrete and the rebates shall be filled with cement mortar. (3) Flooring shall be closely butted and the gap between panels and curbs, adjacent panels and other surfaces shall not exceed 10 mm. |
| 17.8 | TOLERANCES |  |
| 17.8.1 | Tolerances: handrailing, ladders, stairs and flooring | Handrailing, ladders, stairs and flooring shall comply with the following requirements: The position and height of handrailing shall be within 10 mm of the specified position and height. The level of the top rung of ladders and the top tread of stairs shall be within 75 mm of the specified level. The level of flooring and curbs shall be within 3 mm of the specified level. |
| 18. | SECTION 18 BRIDGEWORKS | N/A |
| 19. | SECTION 19 MARINE WORKS | N/A |
| 20. | SECTION 20 WATER SUPPLY PIPEWORKS | N/A |
| 21. | SECTION 21 WATER RETAINING STRUCTURES | N/A |
| 22. | SECTION 22 BUILDING WORKS | N/A |
| 23. | SECTION 23 ENVIRONMENTAL PROTECTION |  |
| 23.1 | GENERAL |  |
| 23.1.1 | General requirements | (1) The Contractor shall undertake environmental protection measures to reduce the environmental impacts arising from execution of the Works. In particular, he shall arrange his method of working to minimize the effects on the air, noise, water quality as well as nuisance of waste within and outside the Site, on transport routes and at the stockpiling, loading, dredging and dumping areas. (2) The Contractor shall observe and comply with all the current enactments, relevant environmental protection and pollution control regulations, and any additions or amendments thereto coming into effect before completion of the Works. The Contractor shall provide his staff and the Engineer on site at all times with on-line access through the Internet to such regulations. If on-line access is not possible and when required by the Engineer, the Contractor shall maintain on site legal copies of the relevant regulations, and provide one legal copy for the Engineer. (3) The Contractor shall design, construct, operate and maintain pollution control measures to ensure compliance with the contract provisions as well as the relevant regulations. (4) Where the activities on Site are found not in compliance with the requirements as specified or cause unacceptable environmental impacts, the Contractor shall immediately carry out appropriate environmental mitigation measures to rectify the situation to the Engineer’s satisfaction. |
| 23.2 | WATER POLLUTION CONTROL |  |
| 23.2.1 | Water pollution control |  |
| 23.2.2 | general requirements | (1) The Contractor shall observe and comply with the Water Pollution Control regulations and the Standards for Effluents Discharged into Drainage and Sewerage Systems and any additions or amendments thereto coming into effect before completion of the Works. (2) The Contractor shall follow the practices and be responsible for the design, construction, operation and maintenance of all the necessary mitigation measures, as specified in the relevant regulations |
| 23.2.3 | Protection of water quality at water intakes and storage | When dredging mud or placing fill in the vicinity of a water intake, the Contractor shall protect the water intake by surrounding it with a suitable silt curtain to prevent excessive suspended solids from entering the intake. The silt curtain shall be designed to ensure that the concentration of suspended solids entering the intake meets the intake user requirements. |
| 23.2.5 | Discharge into sewers, drains and water bodies | (1) In accordance with the Water Pollution Control regulation requirements, the Contractor shall apply for the respective licence before discharging any effluent, including but not limited to any trade effluent or foul or contaminated water or cooling or hot water, from the Site into any public sewer, stormwater drain, channel, stream-course or sea. The Contractor shall provide a copy of the application and licence to the Engineer. The content of effluent to be discharged into the waters from the Site shall strictly comply with the limits set in the respective regulations and discharge licence. (2) The discharge licence may include conditions to require the Contractor to provide, operate and maintain at the Contractor's own expense to the satisfaction of the Engineer suitable works for the treatment and disposal of such trade effluent or foul or contaminated or cooling or hot water. The design of such treatment works, if required, shall be submitted to the Engineer for approval not less than one month before commencement of the relevant works. (3) If any toilet or shower facilities are erected, foul water effluent from these facilities shall be discharged to a foul sewer either directly or indirectly by means of pumping or other means approved by the Engineer. Wastewater collected from a kitchen or canteen, including that from basins, sinks and floor drains, shall be discharged into four sewers via grease traps of adequate retention capacities as appropriate. If no sewer connection is available, the Contractor shall arrange for a licensed sub-contractor to collect the sewage generated from the Site or implement an on-site packaged sewage treatment system approved by the Engineer. |
| 23.2.6 | Wastewater from construction activities | (1) The following mitigation measures shall be carried out to mitigate environmental impacts from wastewater due to construction activities: Water used for water testing, boring, piling, drilling works, concrete batching, washing of concrete trucks, and precast concrete casting and the like shall be re-circulated and re-used for such beneficial uses as dust suppression, wheel washing and general cleaning. The discharge of wastewater shall be kept to a minimum. Online standby sump pumps of adequate capacity and with automatic alternating devices shall be provided to prevent overflow of wastewater from any water recycling system. Wastewater from concrete batching, bored piling and precast concrete casting activities shall be treated for pH adjustment and silt removal before discharge. Sand, silt or other materials present in the wash-water resulting from wheel washing facilities shall be removed before discharge of the wastewater. That section of access road between any site exit and the public road shall be paved with concrete or bituminous surfacing and provided with a suitable backfall to prevent the site run-off from entering the public road. All fuel tanks and fuel storage areas shall be provided with locks and sited on bunded sealed areas of a capacity equal to 110% of the storage capacity of the largest tank. Site compounds and plant/vehicle service areas shall be, unless it is practically impossible, located within roofed areas. The drainage in these areas shall be discharged to a proper wastewater system (e.g. foul sewer, septic tank or storage tank) via a properly maintained oil interceptor to prevent release of oil into the surface water drainage system after accidental spillages. The interceptor shall have a bypass to prevent flushing during periods of heavy rain. Waste-oil shall be collected and stored for recycling or disposal in accordance with the Waste Disposal regulation. (2) The drainage system for stormwater run-off shall be designed as segregated from the system for wastewater discharge arising from construction activities, unless it is practically impossible to reduce the risk of cross contamination. |
| 23.2.7 | Surface runoff | (1) Surface run-off from the Site shall be discharged into stormwater drains via adequately designed silt-removal facilities such as sand traps, silt traps, silt retention pond, sediment basins and mechanical water treatment plant. Channels or earth bunds or sand bag barriers shall be provided on the Site to properly direct stormwater to such silt-removal facilities. Perimeter channels at the Site boundaries shall be provided where necessary to intercept storm run-off from outside the Site so that it will not wash across the Site. Catchpits and perimeter channels shall be constructed in advance of site formation works and earthworks. Manholes shall be adequately covered or temporarily sealed. (2) Silt-removal facilities shall be designed with adequate capacity and constructed within the surface-water drainage systems at appropriate locations. (3) The Contractor shall be responsible for adequately maintaining any existing Site drainage system at all times including removal of solids from sand traps, manholes and stream beds. (4) Silt-removal facilities, channels and manholes shall be maintained and the deposited silt and grit shall be removed regularly, and after each rainstorm, to ensure that these facilities are functioning properly at all times. Disposal of material shall be carried out properly subject to the knowledge and approval of the Engineer. These facilities shall be regularly inspected as required by the Engineer. (5) Temporary access roads shall be protected with crushed stone or gravel, particularly during the rainy seasons. Intercepting channels shall be provided to prevent storm runoff from washing across exposed soil surfaces. |
| 23.3 | NOISE CONTROL |  |
| 23.3.1 | Noise control - general requirements | (1) The Contractor shall observe and comply with the Noise Control regulation including their subsidiary regulations and technical memoranda and any additions or amendments thereto coming into effect before completion of the Works if existing (2) Where a QPME is used, the plant shall be registered with EPA, and the label issued by EPA from such registration shall be affixed on the plant at all times and kept legible. The Engineer shall deem a constructional plant or equipment as non-compliant for the purpose of this sub-clause if it does not have its registration label so affixed. (3) To facilitate monitoring and control, the Contractor shall establish a register to record all QPME referred to in sub-clause (2) used on the Site. (4) The Contractor shall devise, arrange methods of working and carry out the Works in such a manner so as to minimize noise impacts on the surrounding environment, and shall provide experienced personnel with suitable training to ensure that these methods are implemented. (5) The Contractor shall submit for the Engineer’s prior approval, at least 2 weeks before commencement of any work, method statements, the plant and equipment to be used, and the sound-reducing measures to be adopted on the Site for the work. Noise reduction methods shall include but not be limited to scheduling of the work, locating of facilities, selection of plant and equipment and use of purpose-built acoustic panels and enclosures. The Contractor’s submission shall also include a statement explaining why his proposed methods of working, plant and equipment are able to minimize the noise impacts arising from the work. The method statements shall be updated and resubmitted for agreement from time to time as required by the Engineer. (6) In considering the submissions made under sub-clause (5) above, the Engineer may require the Contractor to demonstrate the proposed methods of working, plant equipment and sound-reducing measures to be used on the Site in trials or make them available for inspection, to ensure that they are suitable for execution of the Works. |
| 23.3.2 | Allowable noise limits | (1) For carrying out any construction work other than percussive piling during the time period from 0700 to 1900 hours on any day not being a general holiday (including Fridays), the Contractor shall comply with the following requirements The noise level at 1m from the most affected external facade of the nearby noise sensitive receivers from the construction works alone during any 30-minute period shall not exceed an equivalent sound level (Leq) of 75 dB(A). If the limits are exceeded, the construction activities shall stop and shall not re-commence until appropriate measures acceptable to the Engineer that are necessary for compliance have been implemented. The Engineer may, upon application in writing by the Contractor, allow the use of equipment and carrying out of any construction activities for any duration, provided that he is satisfied with the application and in his opinion, such application is considered to be of absolute necessity and adequate noise insulation has been provided to the noise sensitive receivers affected, or is of emergency nature, and is not in contravention with the Noise Control regulation in any respect. |
| 23.3.3 | Noise mitigation measures | (1) All hoods, cover panels and inspection hatches of powered mechanical plant such as generators, air compressors etc. shall be closed during operation. (2) The Contractor shall provide damping materials inside and outside refuse chutes during breaking construction. |
| 23.4 | AIR POLLUTION CONTROL |  |
| 23.4.1 | Air pollution control - general requirements | (1) The Contractor shall observe and comply with the Air Pollution Control and its subsidiary regulations, and any additions or amendments thereto coming into effect before completion of the Works. (2) The Contractor shall submit for the Engineer’s prior approval, at least 2 weeks before commencement of any work, method statements identifying operations and plant likely to cause air pollution or dust emissions from the Site, together with measures to be implemented to mitigate and control such pollution and emissions. (3) In considering the submissions the Engineer may require the methods of working, plant, equipment and air pollution control system to be used on the site to be demonstrated or made available for inspection to ensure that they are suitable for the project. (4) If during the course of construction, the equipment or work methods are in the opinion of the Engineer not effective in controlling air quality impacts to meet the Contract requirements, the Contractor shall update and resubmit the proposals for agreement promptly. (5) The Contractor shall undertake at all times to prevent dust nuisance and smoke as a result of his activities. |
| 23.4.2 | Dust suppression | (1) The Contractor shall devise, arrange methods of working and carrying out the works in such a manner as to minimize dust impact on the surrounding environment, and shall provide experienced personnel with suitable training to ensure that these methods are implemented. (2) Material storage and handling areas shall be located on a hard-core surface or the like to facilitate cleaning and minimise dust generation. Screens, dust-sheets, tarpaulins or other methods agreed by the Engineer shall be used to prevent generation of dust. (3) In the process of material handling, any material that has the potential to create dust shall be treated with water or sprayed with a wetting agent unless this would have a detrimental affect on the material. (4) All conveyors carrying materials that have the potential to create dust shall be totally enclosed and fitted with belt cleaners. Conveyor transfer points and hopper discharge areas shall be housed in three-sided roofed enclosures with a flexible curtain on the fourth side to minimize emission dust. Exhaust ventilation shall be provided for this enclosure and vented to a fabric filter system. (5) Cement and other fine-graded materials delivered in bulk shall be stored in closed silos. All air vents on cement silos shall be fitted with suitable fabric filters provided with either shaking or pulse-air cleaning mechanisms. The filter must be thoroughly cleaned after cement is blown into the silo to ensure adequate dust collection capacity for subsequent loads. (6) The Contractor shall restrict the speed of all vehicles moving within the Site to minimize fugitive dust emission. Haulage and delivery vehicles shall be confined to designated roadways inside the Site. Unpaved roads shall be regularly compacted and the road surface shall be kept clear of loose material. The Contractor shall ensure that areas within the Site where there is regular traffic of vehicles are paved with either concrete or bituminous material and kept clear of any loose surface material. (7)The Contractor shall undertake regular cleaning and watering of the Site, including access roads, construction areas and material stockpiles, after starting work each day to minimize fugitive dust emission as follows: The frequencies, extent and amount of watering shall be adequate for the respective areas of the Site during the operational day to attain the invisible dust emission level. The Contractor shall ensure that there is adequate water supply/storage for dust suppression at all times. The Contractor shall, from commencement to completion of the Contract, ensure that the watering facilities are available on the Site in good working conditions at all times. The Contractor shall ensure that the watering facilities are properly maintained and operating efficiently at all times and replacement facilities are deployed in full operating conditions immediately in the event of down time owing to mechanical repairs or any other reasons. (8) Earth, or debris including any deposits arising from the movement of plant or vehicles shall not be deposited on public roads or private rights of way as a result of the Contractor's activities. Wheel-washing and vehicle-cleaning facilities shall be provided if needed. Cement and concrete trucks in particular shall be thoroughly cleaned before leaving the site. (9) Any vehicle with an open load compartment used for transferring dusty materials off site shall have properly fitted side-boards and tail-boards. Dusty materials shall not be loaded to a level higher than the side-boards and tail-boards, and shall be covered with a suitable tarpaulin (or any other impervious covering material approved by the Engineer) in good conditions before leaving the Site. The tarpaulin shall be properly secured and extended at least 300 mm over the edges of the side-board and tail boards and be properly secured and maintained throughout the journey to the off-loading destination. For the purpose of this sub-clause, “dusty materials” include cement, earth, pulverized fuel ash, excavated and crushed rock, aggregates, silt, stone fines, sand, debris, saw dust and wooden chips, etc. (10) The location of dust-producing plant or facilities, either fixed or temporary, shall be subject to the agreement of the Engineer. (11) For activities that are likely to generate a substantial amount of dust and where there are no effective measures or it is not possible to adequately control the dust level, vacuum cleaners should be used where practicable to suppress such dust. |
| 23.4.3 | Smoke and exhaust control | (1) The Contractor shall not light bonfires on the Site for burning of debris or other materials. |
| 23.4.4 | Prior consent for pollutant emitting equipment | The Contractor shall not, upon the Site or any part thereof, install or use any machinery, furnace boiler or other equipment, or use any fuel that may result in the discharge or emission of any pollutant or any noxious, harmful or corrosive matter, whether it be in the form of gas, smoke, liquid, solid or otherwise, without the prior written consent of the Engineer in consultation with the EPA |
| 23.4.5 | Odour Mitigation | (1) The Contractor shall take necessary measures, including but not limited to masking sprays and suitable covering, to minimize odour problems arising from the construction activities and the temporary stockpile of odorous material. (2) Temporary stockpiling of odorous material and the mitigation measures shall be subject to the prior approval of the Engineer. Approved odorous stockpiles shall be placed as far away from air sensitive receivers as possible. |
| 23.5 | WASTE MANAGEMENT |  |
| 23.5.1 | Waste management - general requirement | (1) The Contractor shall observe and comply with the Waste Disposal regulation and its subsidiary regulations and any additions or amendments thereto coming into effect before completion of the Works. (2) The Contractor shall be responsible for the control of waste within the Site, removal of the waste material arising from the Site and implementation of any mitigation measures to minimize waste or reduce problems arising from the waste produced on the Site. |
| 23.5.2 | Measures to reduce/minimize generation of C&D materials | (1) The Contractor shall identify and list out the work processes or activities that will generate Construction and Demolition (C&D) materials during construction activities, and the proposed measures to reduce/minimize such generation in particular metallic waste, timber, paper/cardboard packaging and chemical waste. The Contractor shall submit the list of work processes/activities and the proposed measures to the Engineer for approval within 45 days of the date of the Employer’s letter of acceptance of the Tender. The submission should also include the Contractor’s proposed organizational structure and lines of responsibilities for implementation of the waste management measures on the Site. (2) The proposed measures shall include proper planning of works, good site management, minimizing over-ordering, avoiding cross contamination to reusable and/or recyclable materials collected, optimizing the use of metal formwork or other work processes to reduce or minimize the use of timber in temporary works construction, maximizing the reuse of excavated inert C&D materials within the Site, etc. |
| 23.5.3 | Sorting of C&D materials | (1) All C&D materials (which mean both the inert and non-inert materials generated from construction activities) arising from or in connection with the Works shall be sorted on site to recover the inert portion of these materials, and reusable and/or recyclable materials before disposal of the waste portion off site. The inert portion of the C&D materials includes soil, building debris, broken rock, concrete, etc. and the non-inert portion comprises timber, paper, plastics, general refuse, etc. (2) The Contractor shall devise a system for on-site sorting of C&D materials. The system shall include the identification of the source of generation, estimated quantity, arrangement for on-site sorting and/or collection, temporary storage areas, frequency of collection by recycling contractors or frequency of removal off the Site, etc. The Contractor shall submit details of the proposed system for sorting of C&D materials to the Engineer for approval within 45 days of the date of the Employer’s letter of acceptance of the Tender. (3) The Contractor shall ensure that different types of C&D materials are sorted on site and stored in different containers, skips or stockpiles to facilitate reuse/recycling and disposal at different outlets as appropriate. (4) The Contractor shall identify the inert portion of C&D materials that are suitable for recycling into aggregates, in particular broken concrete generated from demolition or road improvement works, and recover the materials for delivery to recycling facilities or a location as notified by the Engineer. (5) For other C&D materials, the Contractor shall be required to check and ensure that the general refuse, as far as reasonably practicable, contains no observable inert or reusable/recyclable C&D materials (e.g. metal, and paper/cardboard packaging) before disposal. If it is found that the Contractor cannot meet this requirement, the Engineer shall request the Contractor to review the system for retrieval of reusable or recyclable materials that are observed. In addition, sorted inserted C&D materials for disposal to public filling outlets shall contain no observable non-inert materials, such as general refuse, timber etc. (6) Equipment and material packaging (i.e. paper and cardboard) shall be recovered, properly stockpiled in a dry and covered condition to prevent cross-contamination by other C&D materials before disposal by recycling sub-contractors. The Contractor shall pay particular attention to avoiding cross-contamination in the course of collecting paper for recycling. (7) The Contractor shall identify and provide sufficient space for temporary storage of C&D materials to facilitate collection and/or sorting on the Site. The space provided shall be commensurate with the estimated quantity for each type of C&D materials generated from the Site. (8) Except for those inert C&D materials to be reused on the Site, the Contractor shall remove all other C&D materials off the Site as soon as practicable in order to optimize the use of the on-site storage space. (9) The Contractor shall make arrangements with the potential recycling contractors to facilitate the collection of recyclable materials sorted from the Site with reasonable care. (10) The Contractor shall establish a system for proper handling and storage of chemical wastes generated from the Site, and arrange collection and disposal of such chemical wastes by specialist contractors. The Contractor shall record the details about the nature of the chemical wastes, method of storage (e.g. type, size and materials of the container), the collection and disposal arrangements, etc. |
| 23.5.4 | Handling and disposal of waste | (1) General refuse shall be stored in enclosed bins separate from inert C&D material and chemical wastes and shall be removed from the Site on a regular basis in order to minimize odour, pest and litter impacts. Burning of refuse on site is not permitted. (2) The Contractor shall take the following general measures to minimize adverse impacts while handling waste: - Handle and store waste in a manner which ensures that it is held securely without loss or leakage, thereby minimizing the potential for pollution; - Remove waste in a timely manner; - Maintain and clean waste storage areas regularly; - Use reputable and authorized waste collectors to collect specific categories of waste for recycling or disposal; - Minimize windblown litter and dust during transportation by either fitting trucks with mechanical covers or transporting waste in enclosed containers; |

Particular Technical Specifications (PTS)

| - General | This section applies to the particular technical specifications and requirements which applies to the design, supply, erection, commissioning of the waste processing plant including the provision of auxiliary services. Notwithstanding the Contractor’s obligation to deliver a functional plant, the Contractor is requested to advise the Employer of any missing requirement stipulated hereinafter. |  |
| --- | --- | --- |
| - Site description | The C&D waste processing plant will be erected on the rehabilitated harbour and waste acceptance area at Thilafushi (see drawing 01 and 02). The final location shall be defined with the Engineer. The C&D plant shall be fixed on a new concrete carriageway (provided by the Employer). The thickness of this concrete slab is 300 mm. The contractor shall plug the plant to the existing electrical connection point (provided by the Employer). A water supply line is also provided by the Employer. The contractor shall provide the design for a shed construction over the plant according to the weather conditions at Thilafushi. |  |
| - Climate and rainfall | The climate of the Maldives is influenced by the Asian monsoon as the country lies on the equator in the Indian Ocean. It is warm and humid throughout the year with temperature ranging between 25.5°C and 30.4°C and average relative humidity of 80%. The average annual rainfall is approx. 2000 mm and is expected to rise showing atypical patterns of intense rainfall during the rainy season and extended dry seasons. The two monsoons that govern the climate are Iruvai, the Northeast monsoon (dry season) that extends from January to March and the Hulhangu, Southwest monsoon (wet season) that extends from mid-May to November. The month of December and April are considered as monsoon transitional periods. Surface currents and winds, humidity, rainfall, temperature and salinity are strongly affected by the monsoons. Daily rainfall data supplied by the Employer for Hulhule Male for the period starting from Jan 1975 to Dec 2016 (42 years) were used to identify maximum annual daily rainfalls and they were subjected to extreme value analysis. Figure 1 shows annual daily maximum rainfall and Figure 2 shows distribution extreme rainfall over return period. Figure 1 : Daily rainfall data (1975-2015) Figure 2: Rainfall return period |  |
| - Input | The construction and demolition waste processing plant shall be designed for processing commingled C&D waste of a composition that is typical for construction and demolition activities. It has to be noted that Hulhumale Island and a significant number of holiday resorts are being developed generating a significant amount of commingled construction waste while in Male both construction and demolition waste is produced. An estimate of the exact amount of each cannot be provided. It has to be noted, that at the construction sites no systematic pre-segregation of C&D wastes is conducted. The images below show a typical range of the C&D waste delivered to one of the transfer sites and also a heap of C&D waste delivered. A significant portion of the waste is delivered in woven bags since this is the currently applied packaging method at the construction sites. No containers are used. To what extent the input will be commingled with other waste materials and components cannot be anticipated (see also section 5 of this PTS). Figure 3: Images taken during a C&D waste survey 3 m 0.5x0.5x2m Figure 4: C&D waste mound accumulated prior to transfer The above indicated dimensions of the concrete blocks shall not be understood as the maximum dimensions occurring. |  |
| - Waste Delivery (not within the scope of the supplier) | It is expected that at least two (potentially three) containers for different C&D waste will be provided at transfer stations and will facilitate the delivery of waste separated into two (or three), categories - Concrete and brick material; - Earth, sand and bagged material; - Mixed C&D waste that can contain any kind of contraries and non-mineral material. Waste containers will be emptied at a pre-sorting area next to the C&D waste processing plant and will be pre-sorted as far as possible into bulky flammable items such as wooden pallets, furniture, etc and also water pipes as well as large coarse (i.e. larger than the aperture of the crusher) concrete blocks etc. It cannot be expected that the pre-segregation will yield fully separated material streams. |  |
| - Objective and Process Description | Notwithstanding the description given below, it shall be the suppliers responsibility to deliver a fully functional plant that can meet the output specification as defined in section 7 of this PTS. Objective of the C&D waste processing shall be to recover valuable mineral fractions for their use as recycled C&D material and to sort out any material which can limit or preclude the application as recycled C&D waste. The processed mineral fraction will be used as concrete aggregate for non structural applications. In general, the processing of C&D waste shall consist of the following components: - Grizzly screen; - Pre-crusher; - Magnetic separator; - Eddy current separator (optional); - Bag opener; - Screen; - Heavy part (or density) separation; - Sorting station; - Impact crusher/hammer mill (optional); - 2nd magnet separator (optional) - Light weight item separation (optional); - Classifier; and - Containers for intermediate storage. All necessary components and equipment such as, but not limited to, feeders and conveyors, electrical installations, steel work, ladders and stairs, platforms, safety features and installations, dust and noise suppression systems as required, shall be supplied and installed. Any item not mentioned in section 8 of this PTS which yet is required shall be provided and installed to guarantee a fully functional facility. Each component and conveying equipment shall be designed and dimensioned to avoid any manual interventions or downtimes of the system due to material flow stoppage, overflow of hoppers and feeding chutes, unsuitable aperture sizes etc. Conveying speed, width of conveyors and dimensions of receiving hoppers shall be designed to match the above requirement. The components shall be arranged to allow a versatile use of the system or parts thereof for processing the envisaged input categories as given above. It shall be the suppliers’ responsibility to suggest a solution with either fully mobile, semi-mobile or stationary equipment or a combination thereof. In any case, all components shall be accessible to allow an easy access for maintenance or replacement. Process Description C&D input material will be handled with either a wheel loader or a waste handler to be provided by the Employer. Irrespective of the reference design as depicted in Figure 5 of this PTS, the Contractor shall use its knowledge and experience to design the plant as it deems appropriate. A grizzly screen with an appropriate bar distance may be used to separate larger objects than the pre-crusher’s aperture. The coarse (i.e. larger than the pre-crushers aperture) fraction may be stored for further pre-crushing while the through fraction may be crushed in a pre-crusher equipped with a magnet separator. If a magnet separator is chosen at that stage, appropriate countermeasures shall be foreseen to avoid reinforcing steel to straightening up and to damage the conveyor underneath. The pre-crusher shall be of a jaw-crusher type. Large objects after the grizzly screen or pre will be chiselled down to size that fits into the pre-crusher (out of the supplier’s scope). Owing to a significant amount of bagged waste, a bag opener is required that operates in parallel. A suitable feeder system (vibrating feeder or similar with screen) be used to supply an inclined conveyor towards the sorting station. The coarse fraction of the screen may be forwarded to a sorting station to sort out wood, paper, plastics and larger metal objects etc. manually. The sorted materials may be collected in containers via sorting chutes. Wood, paper and plastics will be transported to a waste incineration plant or temporarily shredded and baled (incinerator, shredder and baler not subject of this tender). Fines of the screening may be mechanically separated (e.g. via wind sifter) into a heavy (i.e. minerals, metals etc.) and light fraction (plastic, paper etc.). Optionally, the following may be considered: The fines after mechanical separation of the non-mineral fraction and any mineral residue from the sorting may be crushed in a secondary impact crusher. After the crusher, a magnetic separation may be arranged. After the magnetic separator, any remaining light weight fraction may be sorted via an appropriate mechanical separation technology (e.g. vibro or flip-flop screen, wind sifter etc.). The screening deck to classify the material according to section 7 shall allow to replace the screens to obtain a different grading if needed. The individual fractions shall be stored in the corresponding production compartments for further use close to the facility. Transport shall be arranged with a wheel loader (not part of the scope). Subject to the final location of the C&D waste plant, screened materials may be either stored in bays or heaped up beneath discharge belts. |  |
| Figure 5: Possible flow chart of a C&D waste treatment which shall not be regarded as binding (except output specification). |  |  |
| - Output specification | Given that recycled C&D waste will be mainly used as fine aggregate for masonry concrete blocks and as sub-base layer for foundations and roads, the material shall be classified into the following fractions: - < 3.35 mm - 3.35 to 20 mm - 20 to 37.5 mm The content of non mineral contraries in the fraction smaller than 3.35 mm shall be less than 1% by weight. |  |
| - Main components and their technical requirements | It shall be within the Contractor’s discretion to decide about the design and the specification unless explicitly mentioned in this section. |  |
|  | Item | Minimum requirement |
|  | Grizzly screen | Bar width according to selected crusher aperture Heavy duty model May be incorporated into the jaw crusher |
|  | Mobile or skid mounted jaw crusher including discharge belt | Capacity not less than 100 t/h (at smallest jaw width) Crusher Aperture > 900 x 500 mm Jaw width adjustable Hopper size to be defined by Contractor |
|  | Magnet separator | Either integrated in the jaw crusher or separated as over belt or over pulley magnet Equipped with enforced cooling Band width to be defined by the Contractor Field strength: to be defined by the Contractor |
|  | Optional: Eddy current separator |  |
|  | Vibrating feeder with screen | Capacity not less than 100 t/h Cut off size: to be defined by the supplier |
|  | Inclined conveyor | Capacity not less than 100 t/h Speed and width: to be defined by Contractor |
|  | Bag opener | Capacity not less than 50 t/h Bag opening efficiency > 99% |
|  | Sorting station for metals and flammable fraction (at least sorting 6 chutes, 3 on each side) | Capacity not less than 30 t/h (input) Speed: to be defined by the supplier Sorting belt width: to be defined by the supplier |
|  | Wind sifter including vibrating feeding conveyor | Capacity not less than 50 t/h (input material) with integrated dedusting system and adjustable air flow rate |
|  | Screening deck with discharge belts | Capacity not less than 100 t/h Material grain size: see output parameters above Exchangeable screening decks Including loading hopper and oversize grain discharger Cut-off sizes according to section 7 |
|  | Set of containers | Container for sorted flammables and metals (one redundant set, number subject to the Contractor’s design) Dimension: To be defined by the supplier Compatible with the proposed plant Mandatory requirements: - Compatible with hook lift trucks, hook height 1500 mm - Maximum container volume: 25 m³ |
|  | Optional: Secondary impact crusher with magnet separator and discharge belt | Capacity not less than 100 t/h Aperture > 900 x 600 mm |
|  | Optional: Second wind sifter/flip flop screen with discharge belt | Capacity not less than 50 t/h (input material) with integrated dedusting system and adjustable air flow rate if a wind sifter is used) |
| - Roof / shed | The machinery shall be protected by a roof construction of steel or concrete or a mixture of both. A wooden construction is not acceptable due to fire protection The roof has to fulfil the following requirements: - The roof construction shall have the extension to protect all machinery from rainfall. - Height of the roof shall allow operation of the facilities especially of the feeder and the distribution belts. - Placement of piles of the roof construction must allow undisturbed operation of the plant. - The roof has to be equipped with rain gutters and pipes for rainwater collection and deviation. - All elements of the roof have to be protected against erosion by painting or zinc-coating. - Rainwater from the roof shall be collected in a closed water tank with a capacity of 10m³ minimum. The tank shall be placed over ground due to high ground/sea water level. Water from the tank shall be used for sprinkling the waste during the treatment process to reduce pollution by dust. The tank has to be equipped with an overflow and a connection to the next stormwater drain. - The water tank shall be equipped with pump and flexible tube for sprinkling the waste. - The structural calculations for the roof construction have to be in line with all local regulations. Calculations have to be prepared by an accredited structural engineer. The Contractor is responsible for obtaining all approvals according to local regulations |  |
| - Electrical installation | This item includes delivery and laying of the electrical cables in plastic conduits and the connection to the Main Distribution Panel board (LMO) and the placement of the earthing system according to GTS. All required internal cabling, switches, MCCs, control boards, emergency stop buttons, rope switches etc. shall be installed according to the functionality of the entire plant and according to a corresponding single line diagram to be provided in the bidding documents. Any electrical drive shall be classified as high efficiency drives. The supply voltage is 0.4 kV. |  |
| - Control installation | The Contractor shall install a suitable control of the entire plant either via a PLC or any other suitable control equipment to allow at least for a sequenced starting of the individual components and an immediate emergency response to shut down all electrically or diesel driven components. |  |
| - Environmental, health and safety features | Besides the requirements, to meet the standards mentioned in the general section, the plant shall be operated based on internationally practiced environmental, health and safety standards with respect to noise and dust emissions, safety at work and prevention of accidents. The plant shall be, but not limited to, equipped with noise and dust suppression systems as required, rope switches along conveying equipment (particularly inclining conveyors and conveyors discharging in conveying equipment), emergency stop buttons, light barrier control where needed. For dust suppression water spray systems or dust filters may be used. The plant’s environmental, health and safety features shall be comprehensively described and potential interfaces to supplies by the Employer to be addressed. |  |
| - Design and documentation | Provision of all detailed design and shop drawings (as built) including the technical documentation and description of the equipment, operation & maintenance manuals, wear and spare parts list To allow for continuous operation of the facility even under harsh and rainy weather conditions, the Contractor shall suggest a shed construction that would be constructed by the Contractor. |  |
| - Spare and wear parts | The Contractor shall provide a set of spare and wear parts for an operation time of the plant of 2 years or 2,800 operation hrs. |  |
| - Interfaces | The C&D waste processing plant should be fixed on the concrete carriageway (30 cm reinforced concrete slab) provided by the employer and connected to the Main distribution panel nearest the foreseen area. The Contractor has to supervise and to coordinate all his works with operation works of the employer on this site as well as the construction of the protective shed according to his design drawings. Interfaces to the required utilities (power, water etc.) shall be clearly mentioned in the bidding documents. |  |
| - Training | • Technician training shall be performed by factory trained personnel with at least three years repair/service experience with proposed plant • Technician training shall include two x six hours sessions covering two thousand (2000) hour preventative maintenance, diagnostics and fault detection • All training sessions shall be scheduled during or right after commissioning and trial test period • Operator training shall be performed by factory trained personnel with at least three years of training experience • Operation training includes two x six hour sessions on separate days to familiarize the Employer’s personnel or delegated third parties with the equipment to yield the desired output quality. • Technician and operator training to be carried out separately. |  |

### 3. Drawings

Layout drawings are only for information purposes

Drawings are provided in Annex

### 4. Supplementary Information

### 5. Certificates

5.1  Form of Completion Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Dear Ladies and/or Gentlemen,

Pursuant to GCC Clause 24 (Completion of the Facilities) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . . . .insert date. . . . . ], relating to the [. . . .brief description of the Facilities . . . .], we hereby notify you that the following part(s) of the Facilities was (were) complete on the date specified below, and that, in accordance with the terms of the Contract, the Employer hereby takes over the said part(s) of the Facilities, together with the responsibility for care and custody and the risk of loss thereof on the date mentioned below.

1.	Description of the Facilities or part thereof:  [. . . .description . . . .]

2.	Date of Completion:  [. . . .date . . . .]

However, you are required to complete the outstanding items listed in the attachment hereto as soon as practicable.

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

5.2  Form of Operational Acceptance Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Pursuant to GCC Subclause 25.3 (Operational Acceptance) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . .date. . .], relating to the [. . .brief description of the facilities. . .], we hereby notify you that the Functional Guarantees of the following part(s) of the Facilities were satisfactorily attained on the date specified below.

1.	Description of the Facilities or part thereof:  [. . . description . . .]

2.	Date of Operational Acceptance:  [. . . date . . .]

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

### 6.  Change Orders

6.1	Change Order Procedure

6.1.1	General

6.1.2	Change Order Log

6.1.3	References for Changes

6.2.	Change Order Forms

6.2.1	Request for Change Proposal

6.2.2	Estimate for Change Proposal

6.2.3	Acceptance of Estimate

6.2.4	Change Proposal

6.2.5	Change Order

6.2.6	Pending Agreement Change Order

6.2.7	Application for Change Proposal

### 6.1. 	Change Order Procedure

### 6.1.1  General

This section provides samples of procedures and forms for implementing changes in the Facilities during the performance of the Contract in accordance with GCC Clause 39 (Change in the Facilities) of the General Conditions.

### 6.1.2 	Change Order Log

The Contractor shall keep an up-to-date Change Order Log to show the current status of Requests for Change and Changes authorized or pending. Entries of the Changes in the Change Order Log shall be made to ensure that the log is up-to-date. The Contractor shall attach a copy of the current Change Order Log in the monthly progress report to be submitted to the Employer.

### 6.1.3	References for Changes

(1)	Request for Change as referred to in GCC Clause 39 shall be serially numbered CR-X-nnn.

(2)	Estimate for Change Proposal as referred to in GCC Clause 39 shall be serially numbered CN-X-nnn.

(3)	Acceptance of Estimate as referred to in GCC Clause 39 shall be serially numbered CA-X-nnn.

(4)	Change Proposal as referred to in GCC Clause 39 shall be serially numbered CP-X-nnn.

(5)	Change Order as referred to in GCC Clause 39 shall be serially numbered CO-X-nnn.

Note:

(a)	Requests for Change issued from the Employer’s Home Office and the Site representatives of the Employer shall have the following respective references:

Home Office	CR-H-nnn

Site		CR-S-nnn

(b)	The above number “nnn” is the same for Request for Change, Estimate for Change Proposal, Acceptance of Estimate, Change Proposal and Change Order.

### 6.2	Change Order Forms

### 6.2.1  Request for Change Proposal Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to the captioned Contract, you are requested to prepare and submit a Change Proposal for the Change noted below in accordance with the following instructions within [  number  ] days of the date of this letter [or on or before (  date  )].

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Originator of Change:

Employer:  [Name]

Contractor (by Application for Change Proposal No. [Number Refer to Annex 6.2.7])

4.	Brief Description of Change:  [  Description  ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [  Description  ]

6.	Reference drawings and/or technical documents for the request of Change:

Drawing No./Document No.		Description

7.	Detailed conditions or special requirements on the requested Change:  [  Description  ]

8.	General Terms and Conditions:

(a)	Please submit your estimate showing what effect the requested Change will have on the Contract Price.

(b)	Your estimate shall include your claim for the additional time, if any, for completing the requested Change.

(c)	If you have any opinion that is critical to the adoption of the requested Change in connection with the conformability to the other provisions of the Contract or the safety of the Plant or Facilities, please inform us in your proposal of revised provisions.

(d)	Any increase or decrease in the work of the Contractor relating to the services of its personnel shall be calculated.

(e)	You shall not proceed with the execution of the work for the requested Change until we have accepted and confirmed the amount and nature in writing.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.2   Estimate for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to your Request for Change Proposal, we are pleased to notify you of the approximate cost to prepare the below-referenced Change Proposal in accordance with GCC Subclause 39.2.1 of the General Conditions.  We acknowledge that your agreement to the cost of preparing the Change Proposal, in accordance with GCC Subclause 39.2.2, is required before estimating the cost for change work.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Brief Description of Change:  [  Description  ]

4.	Scheduled Impact of Change:  [  Description  ]

5.	Cost for Preparation of Change Proposal:  [  insert costs, which shall be in the currencies of the contract  ]

(a)	Engineering	(Amount)

(i)	Engineer		 hours (hrs) x 	 rate/hr =

(ii)	Draftsperson		 hrs x 	 rate/hr =

Sub-total		 hrs

Total Engineering Cost

(b)	Other Cost

Total Cost (a) + (b)

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.3  Acceptance of Estimate Form

[ Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [ Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby accept your Estimate for Change Proposal and agree that you should proceed with the preparation of the Change Proposal.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Request number/revision  ]

3.	Estimate for Change Proposal No./Rev.:  [  Proposal number/revision  ]

4.	Acceptance of Estimate No./Rev.:  [  Estimate number/revision  ]

5.	Brief Description of Change:  [  Description  ]

6.	Other Terms and Conditions:  In the event that we decide not to order the Change accepted, you shall be entitled to compensation for the cost of preparing the Change Proposal described in your Estimate for Change Proposal mentioned in para. 3 above in accordance with GCC Clause 39 of the General Conditions.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.4  Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

In response to your Request for Change Proposal No. [Number], we hereby submit our proposal as follows:

1.	Title of Change:  [  Name  ]

2.	Change Proposal No./Rev.:  [  Proposal number / revision ]

3.	Originator of Change:	Employer:  [ Name  ] / Contractor:  [  Name  ]

4.	Brief Description of Change:  [  Description  ]

5.	Reasons for Change:  [  Reason  ]

6.	Facilities and/or Item No. of Equipment related to the requested Change:  [  Facilities  ]

7.	Reference drawings and/or technical documents for the requested Change:

[  Drawing/Document No./Description  ]

8.	Estimate of increase/decrease to the Contract Price resulting from the Change Proposal:

Amount

[ insert  amounts in the currencies of the Contract ]

(a)	Direct material

(b)	Major construction equipment

(c)	Direct field labor (Total 	 hrs)

(d)	Subcontracts

(e)	Indirect material and labor

(f)	Site supervision

(g)	Head office technical staff salaries

Process engineer		 hrs @ 	 rate/hr

Project engineer		 hrs @ 	 rate/hr

Equipment engineer		 hrs @ 	 rate/hr

Procurement		 hrs @ 	 rate/hr

Draftsperson		 hrs @ 	  rate/hr

Total			hrs

(h)	Extraordinary costs (computer, travel, etc.)

(i)	Fee for general administration, 	 % of Items

(j)	Taxes and customs duties

Total lump sum cost of Change Proposal		[  Sum of items (a) to (j)  ]

Cost to prepare Estimate for Change Proposal	 	[  Amount payable if Change is not accepted  ]

9.	Additional time for Completion required due to Change Proposal

10.	Effect on the Functional Guarantees

11.	Effect on the other terms and conditions of the Contract

12.	Validity of this Proposal:  within [Number] days after receipt of this Proposal by the Employer

13.	Other terms and conditions of this Change Proposal:

(a)	You are requested to notify us of your acceptance, comments or rejection of this detailed Change Proposal within [Number] days from your receipt of this Proposal.

(b)	The amount of any increase and/or decrease shall be taken into account in the adjustment of the Contract Price.

(c)	Contractor’s cost for preparation of this Change Proposal: [ . . . .insert amount. This cost shall be reimbursed by the employer in case of employer’s withdrawal or rejection of this Change Proposal without default of the contractor in accordance with GCC Clause 39 of the General Conditions . . . . ]

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.5  Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We approve the Change Order for the work specified in the Change Proposal (No. [  number  ]), and agree to adjust the Contract Price, Time for Completion, and/or other conditions of the Contract in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Change Request No./Rev.:  [  Request number / revision  ]

3.	Change Order No./Rev.:  [  Order number / revision  ]

4.	Originator of Change:	Employer:  [Name] / Contractor:  [  Name  ]

5.	Authorized Price:

Ref. No.:  [  Number  ]	Date:  [  Date  ]

Foreign currency portion [  Amount  ]  plus Local currency portion [  Amount  ]

6.	Adjustment of Time for Completion

None		Increase [  Number  ] days	 	Decrease [  Number  ] days

7.	Other effects, if any

Authorized by:  		Date:

Employer

Accepted by:  		Date:

Contractor

6.2.6  Pending Agreement Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We instruct you to carry out the work in the Change Order detailed below in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Employer’s Request for Change Proposal No./Rev.:  [  number/revision  ]	dated:  [ date  ]

3.	Contractor’s Change Proposal No./Rev.:  [  number / revision  ]	dated:  [ date ]

4.	Brief Description of Change:  [ Description ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [ Facilities ]

6.	Reference Drawings and/or technical documents for the requested Change:

[  Drawing / Document No. / Description  ]

7.	Adjustment of Time for Completion:

8.	Other change in the Contract terms:

9.	Other terms and conditions:

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

6.2.7  Application for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby propose that the work mentioned below be treated as a Change in the Facilities.

1.	Title of Change:  [  Name  ]

2.	Application for Change Proposal No./Rev.:  [  Number / revision  ]	dated:  [  Date  ]

3.	Brief Description of Change:  [  Description  ]

4.	Reasons for Change:

5.	Order of Magnitude Estimation (amount in the currencies of the Contract): [  Amount  ]

6.	Scheduled Impact of Change:

7.	Effect on Functional Guarantees, if any:

8.	Appendix:

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### 7.  Personnel Requirements

Using Form PER - 1 and PER - 2 in Section 4 (Bidding Forms), the Contractor must demonstrate that it has personnel who meet the following requirements:

| No. | Position | Total Work Experience [years] | Experience In Similar Work [years] |
| --- | --- | --- | --- |
|  | Head Engineer | Min 15 | Min. 5 |
|  | Site Engineer | Min 10 | Min. 5 |
|  | Design Engineer | Min 10 | Min. 5 |
| 1 | International work supervisor for the specific supply and erection works of plants – 1 No. | Min 10 | Min. 5 |
| 2 | National or international crane driver – 1 No. | Min 10 | Min 5 |
| 3 | National or international wheel loader driver – 1 No. | Min 10 | Min 5 |
| 4 | Safeguard and Construction Safety compliance officer – 1 No. | Min 10 | Min 5 |

### 8.  Equipment Requirements

Using Form EQU in Section 4 (Bidding Forms), the Contractor must demonstrate that it has the key equipment listed below:

| No. | Equipment Type and Characteristics | Minimum Number Required |
| --- | --- | --- |
| 1 | Transport, unload and upload crane | 01 |
| 2 | Wheel loader | 01 |
| 3 | Heavy duty Fork lift | 01 |
| 4 | Steel Welding equipment | 01 set |