PART 1 - GENERAL

## 1.01	RELATED DOCUMENTS

- Submitted electrical drawings

1.02	SUMMARY

- This section includes the following

- PV modules

- Mounting structures

- Automatic change over

- Charge controllers

- Multimode Hybrid Inverters / Chargers with possibility for grid – tie for feed – in tariff.

- Batteries

- Battery monitoring system.

- The PV modules specified herein are based on the concept design. Contractor shall use this document for guidance in preparation of procurement strategy and costing purpose only. Revised IFC specifications, drawings and schedules shall be issued prior to start of construction

- Mock-up: shall be required to be installed on a location determined by the client. The purpose is to demonstrate the system capability and performance prior to final installation.

- Install mock-up and obtain Engineer’s approval prior to proceeding to the main installation.

- Schedule: mock-up shall be arranged before the scheduled final installation without affecting the project schedule. Allow enough time for installation, inspection by Engineer and providing comments / approval.

- An array of 12 panels minimum shall be used.

- This specification is performance based and might not necessarily list all required components, ancillaries and accessories. It shall be the contractor responsibility to develop the solution and provide a complete operational solution to the satisfaction of the engineer, where all required components/ancillaries are deemed to be included for a good operation as intended.

1.03	SYSTEM SELECTION REQUIRMENTS

- PV modules to be submitted shall be based on a complete system design solution, supported by detailed calculations to substantiate the selection made. The proposed solution shall include PV modules, appropriate selection of charge controller, the required automatic change over, inverters, battery chargers, batteries, wires and wire ways, etc.

- All necessary protection equipment shall be provided as per code requirements. This includes fuses, breakers, surge protection and the like for safety purpose.

1.04	DEFINITIONS

- IP code: Required ingress protection to comply with IEC 60529

- MPPT: Maximum power point tracking

- PV: Photovoltaic.

- STC: Standard Test conditions defined in IEC 61215

- NOCT: Normal operating cell temperature

- Cnom: Battery nominal capacity at 10 hours discharge at 20 deg C according to DIN 40742

- Cj˳, C5, C3 and Cj: Battery capacity at 1 Oh,5h,3h and 1 hour discharge at 20 deg C.

1.05	ACTION SUBMITTALS

- Product Data: For each type of product based on complete and approved system solution.

- Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for PV panels.

- Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

- Shop Drawings: For PV modules.

- Include plans, elevations, sections, and mounting details

- Include details of equipment assemblies

- Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

- Penetration plan and details

- Details fabrication and assembly

- Include diagrams for power, signal, and control wiring.

- Detailed system calculation and requirements/design, as specified under article 1.3”system selection requirements” above

1.06	INFORMATIONAL SUBMITTALS

- General: submit listed submittals in accordance with contract conditions and section submittal procedures.

- Test and Evaluation Report:

- Certified test reports showing compliance with specified performance characteristics and physical properties

- Manufacturer’s instruction: submit manufacturer’s storage and installation instructions.

- Source Quality Control: Submit documentation verifying that components and materials specified in this section are from a single manufacturer.

- Qualification statements:

- Submit letter of verification for manufacturer’s qualifications.

- Submit letter of verification for installer’s qualifications.

- Field quality-control reports

- Sample Warranty: For manufacturer’s special materials and workmanship warranty and minimum power output warranty.

1.07	CLOSEOUT SUBMITTALS

- Operation and maintenance data: For PV modules to include in operation and maintenance manuals. Include as a minimum:

- Manufacturer’s instructions detailing maintenance requirements.

1.08	QUALITY ASSURANCE

- Qualifications:

- Manufacturer:

- having minimum of 10 years experience manufacturing components similar to or exceeding requirements of project.

- Having sufficient capacity to produce and deliver required materials without causing delay in work

- Capable of providing field service representation during construction.

- Manufacturing facility certified to ISO 9001 and to ISO 14001.

- Installer:

- Experienced installer who is an authorized representative of PV manufacturer for both installation and maintenance of units required for this project. Minimum 5 years of experience for similar installations.

- Local representative: provide evidence that proposed equipment manufacturer has a locally established and authorized organization which can be called upon for professional advice and maintenance as may be required, and which can immediately supply spare parts to support day to day and emergency maintenance requirements. Failure to satisfy engineer may disqualify a manufacturer.

- Mock-Up: Construct mock-up as follows:

- Purpose: Construct showing solar electric module to judge quality of work, substrate preparation, and operation of equipment and material application.

- Dimensions and Process: Construct the required dimensions as directed by the Engineer, using proposed procedures, colors, textures, finishes and quality of work.

- Locate where directed by the Engineer

- Do not proceed with work prior to receipt of written acceptance of mock-up.

- When accepted, mock-up will demonstrate minimum standard of quality required for this work. Approved mock-up may, or may not, remain part of finished work, as directed by the Engineer.

- Reference Standards:

- American National Standards Institute (ANSI):

- ANSI/UL 1703 Standard for Flat-Plate Photovoltaic Modules and Panels (Or approved equal European Standard).

- International Electrical Commission (IEC):

- IEC 61215 International Standard (Extended Version) - Crystalline silicon terrestrial photovoltaic (PV) modules - Design qualification and type approval.

- IEC 61646 International Standard - Thin-film terrestrial Photovoltaic (PV) modules - Design qualifications and type approval.

- IEC 61730-1 International Standard - Photovoltaic (PV) module safety qualification - Part 1 - Requirements for construction

- IEC 61730-2 International Standard - Photovoltaic (PV) module safety qualification - Part 2 - Requirements for testing.

- International Organization for Standardization (ISO):

- ISO 9001 Quality Management Systems.

- ISO 14001 Environmental Management Systems.

- Underwriters Laboratories,Inc.(UL):

- Underwriters Laboratories, Inc. (UL):

- UL 790 Standard Test Methods for Fire Tests of Roof Coverings (Or approved equal European Standard).

- UL 1703 Standard for Flat-Plate Photovoltaic Modules and Panels (Or approved equal European standard.

- PV installation shall comply with NEC Article 690 Solar Photovoltaic Systems, or approved equal European Standard.

- Products shall be sourced either directly from manufacturer, or from authorized agent/representative.

1.09	DELIVERY, STORAGE & HANDLING

- Delivery and Acceptance Requirements:

- Deliver material in accordance with the related sections of this specification, and in accordance with manufacturer's written instructions

- Deliver materials in manufacturer's original packaging with identification labels intact and in sizes to suit project.

- Storage and Handling Requirements:

- Store materials protected from exposure to harmful weather conditions and at temperature conditions recommended by manufacturer.

1.10	COORDINATION

- Coordinate layout and installation of PV modules components with roof skin and other construction and electrical work, including conduit, piping, equipment, adjacent surfaces, raceways, electrical boxes and fittings, and cabling/wiring work. Maintain required workspace clearances and required clearances for equipment access

- Coordinate size and location of mounting structures.

1.11	CLIMATIC CONDITIONS

- Equipment is to be designed and derated for continuous and trouble free service under the following climatic conditions of Maldives:

- Altitude: Coastal sea level.

- Maximum ambient temperature: 50 deg C (in the shade).

- Minimum ambient temperature: 10 deg C .

- Maximum relative humidity: 100 percent.

- Atmospheric conditions: Sandy, heavy condensation air blown salinity, and sand storms also prevail.

- Equipment, apparatus, material accessories outdoors is to be corrosion and salinity proof. UV stabilized requirement shall be applied for outdoor installations and their surface finish and due certification be provided by manufacturer as necessary.

- Manufacturer to calculate how much module power will be lost or gained due to temperature shifts. In hot climates, cell temperatures can reach an excess of 70 deg C.

1.12	WARRANTY

- Manufacturer's Special Materials and Workmanship Warranty: Manufacturer agrees to repair or replace components of PV modules that fail in materials or workmanship within specified warranty period.

- Manufacturer's materials and workmanship warranties include, but are not limited to, the following:

- Faulty operation of PV modules.

- Defects in materials and workmanship and hot spots.

- Warranty Period: Five years from date of Substantial Completion

- Manufacturer's Special Minimum Power Output Warranty: Manufacturer agrees to repair or replace components of PV modules that fail to exhibit the minimum power output within specified warranty period. Special warranty, applying to modules only, applies to materials only, on a prorated basis, for period specified.

- Manufacturer's minimum power output warranties include, but are not limited to, the following warranty periods, from date of Substantial Completion:

- Specified minimum power output to 90 percent or more, for a period of 12 years.

- Specified minimum power output to 80 percent or more, for a period of 25 years.

1.13	EXTRA MATERIALS

- Spare Parts List:

- Provide spare parts as per manufacturer recommendation

- Tools and Instruments: Provide tools and instruments required for normal routine inspection, testing, operation and general maintenance, as recommended by the manufacturer.

- For PV modules, furnish extra materials described below that match products installed, are packaged with protective covering for storage, and are identified with labels describing contents. Deliver extra materials to the Project site.

- PV modules: 2 for every 100 of each type and rating, but not less than 2 of each

PART 2 -  PRODUCTS

2.01	STANDARD COMMERICAL PRODUCTS

2.02	SYSTEM DESCRIPTION

- Connected to a battery bank to provide electricity to Project.

- The off-grid PV system has a utility back-up

- System shall generate a total nominal rating of 300 kWp minimum

- System Components:

- Cell materials

- PV modules.

- Array frame.

- Mounting structure.

- Charge Controller.

- Multimode Hybrid Inverter/Charger.

Other system components including hybrid inverter/chargers, batteries, over current protection/combiner boxes, etc. are specified in a different section, and are part of contractor’s scope

2.03	MANUFACTURED UNITS

- Cell Materials: Polycrystalline

- Module Construction:

- Nominal Size: 1999 mm x 981 mm x 40 mm.

- Weight: 27.8 Kg approximately.

- Material Composition: 60-cell polycrystalline photovoltaic modules incorporating anti- reflective coated (ARC) glass with an aluminum frame, integrated bypass diodes and MC4 connectors.

- Performance/Design Criteria:

- Certified according IEC 61215 (Design qualification and type approval).

- Certified according to IEC 61646.

- Certified according to the IEC 61730-1.

- Certified according to the IEC 61730-2.

- Complies with UL 790, Class C.

- Listed to ANSI/UL 1703 (Or Approved European Equal).

- Loading:

- Frames capable of withstanding loads of not less than 50 psi (2400Pa) in a variety of mounting methods, and suitable for the specified project climatic conditions. Module shall also withstand extreme wind loads anticipated in the project location.

- Front Panel: Fully tempered glass with antireflective coating

- Bypass Diode Protection: Internal.

- Junction Box

- Size: 39.6 by 100.6 by 13.2 mm.

- Fully potted, vandal resistant.

- IP Code: minimum IP66

- Flammability Test: UL 1703

- Output Cabling:

- Quick, multiconnect, polarized connectors.

- Two-Conductor Harness: No traditional return wire is needed from the end of a row back to the source combiner.

2.04	CAPACITIES AND CHARACTERISTICS

- Minimum Electrical Characteristics (STC):

- Rated Open Circuit Voltage (Voc): 37Vdc.

- Rated Operating Voltage (Vmp): 29.8 Vdc

- Rated Short-Circuit Current (Isc): 8.5 A

- Rated Operating Current (Imp): 8.1 A.

- Maximum Power at STC (Pmax): 240 Wp

- Minimum Electrical Characteristics (NOCT):

- Rated Open Circuit Voltage (Voc): 34 Vdc.

- Rated Operating Voltage (Vmp): 27 Vdc.

- Rated Short-Circuit Current (Isc): 6.8 A.

- Rated Operating Current (Imp): 6.5 A.

- Maximum Power at NOCT (P^): 175 Wp.

- Other Additional Electrical Characteristics:

- Tolerance of Pmax: 0 to+5 percent.

- Series Fuse Rating: 20A.

- Minimum Module Effiency: 14.7 percent at least.

- Wind Loading or Surface Pressure: per Maldives Condition.

- Maximum System Voltage: 1000V dc (IEC)

- Thermal Characteristics:

- Operating Module Temperature: -40 deg C to + 85 deg C.

- Temperature at Nominal Operating Cell Temperature (NOCT): 47  ± 2 deg C.

- Temperature Coefficient (Pmax): -0.44 %/ deg C.

- Temperature Coefficient (Voc): -0.33%/degC.

- Temperature Coefficient (lsc): +0.05 %/deg C.

- PV controller,ATS,Battery are installed inside each group inverter located at roof.

2.05	MODULE FRAMING

- PV laminates mounted in anodized extruded-aluminum frames.

- Entire assembly UL listed for electrical and fire safety, Class C, according to UL 1703, complying with IEC 61215

- Frame strength: exceeding code requirements.

- Finish: Anodized aluminum.

- Alloy and temper recommended by framing manufacturer for strength, corrosion resistance, and application of required finish

- Color: As indicated by manufacturer's designations.

2.06	ARRAY CONSTRUCTION

- Framing:

- Material: Extruded aluminum.

- Maximum System Weight: Less than 19.53 kg/sq. m.

- Minimum Distance to Connectors to be used

- Raceway Cover Plates: Galvanized steel

- Flat-Roof Mounting:

- No roof penetrations

- Self-ballasting

- Wind-tunnel tested to 160-km/h wind

- Service Life: 25 years

- Freestanding system.

2.07	MOUNTINGSTRUCTURES

- Roof Mount: Extruded aluminum, with rails, tilt legs, and roof standoffs, unless otherwise shown on the drawings.

2.08	HYBRID INVERTER/CHARGER

- Control Type: Multi-stage process.

- Inverter Electrical Characteristics:

- Continuous Output Power: 7500 W – 15000W.

- DC input Voltage range: 41 to 64 Vdc.

- Nominal AC Input Voltage: 230 Vac.

- Nominal AC Input frequency: 50 Hz.

- Nominal AC Output Voltage: 230 Vac +/- 3 percent.

- Maximum AC pass through current: 56 A.

- Minimal Continuous AC Output current: 26 A.

- Maximum Total Harmonic Distorsion: 5percent at rated power.

- Continuous Battery Charging current: 100 A.

- Power Factor corrected charging: 0.98.

- Minimum Peak Efficiency: 95 percent.

- Ingress Protection: IP20.

- Operating Conditions:

- Operating Ambient Temperatures: Minus 25 deg C to plus 50 deg C.

- Battery Bank Size: 100 to 15000 Ah.

- Hybrid Inverters/Chargers shall have the following:

- Overcurrent protection.

- Automatic transfer relay.

- DC to AC Inverter.

- Battery Charger.

- Battery Temperature Sensor.

- Integrated battery monitoring system.

- Multiple-units configuration.

- Grid-interactivity option.

- Non-volatile memory.

- Enclosure:

- Enclosure type: NEMA 1 indoor enclosure.

- Enclosure Material: Die-cast Aluminum.

- Cooling Methods:

- Active cooling system

- Protective Functions:

- AC over/under voltage.

- AC over/under frequency.

- Ground over current.

- Over temperature.

- AC and DC over current.

- DC over voltage

- Protective Functions:

Standard liquid crystal display, with user display and on/off toggle switch.

- Disconnects:

- Low-voltage disconnect.

- Low-voltage reconnect.

- High-temperature disconnect.

- High-temperature reconnect.

- Regulatory Approvals:

- IEEE 1547.1.

- IEEE 1547.3.

- UL 1741.

- Or approved equal European Standard.

- Warranty:

- At least 5 years.

2.09	BATTERIES

- Type: 24 OPzV 3000 (according to DIN regulations).

- Construction:

- Sealed valve regulated lead-acid, Gel cell type.

- Maintenance free.

- Shippable.

- Recyclable.

- Performance:

- Capable of over 1200 discharge at 80 percent Depth of Discharge.

- Self-Discharge at 20 deg C: less than 2 percent a month.

- Necessary recharge at least once every 6 months.

- Deep-Cyling technology.

- Design life of at least 15 years

- Electrical Charasteristics:

- Nominal Voltage: 2V.

- Nominal Capacity Cnom, at 1.80V/Cell: 3000Ah.

- C10, at 1.80V/Cell: 3100Ah.

- C5, at 1.77V/Cell: 2600Ah.

- C3, at 1.75V/Cell: 2260Ah.

- Cj, at 1.67V/Cell: 1540Ah.

- Final Discharge Voltage: 1.80V/Cell.

- Float Voltage at 20 deg C: 2.23 V/Cell.

- Boost Recharge, with the maximum current of 0.25 x C10: 2.4V/Cell maximum.

- Short circuit current: 18000 A

- Internal Resistance: 0.108 mfl.

- Operating Conditions:

- Nominal Temperature: plus 20 deg C +/- 5 deg C.

- Operating Ambient Temperatures: Minus 20 deg C to plus 40 deg C.

- Battery bank consists of 2 strings of 12 batteries in series.

- Battery Bank Size: 6000 Ah, 48 Vdc.

- Batteries shall have the following:

- Tubular positive plates.

- Pasted negative plates.

- Dilute sulphuric acid Electrolyte.

- High porosity, low internal resistance Separators.

- Plastic (ABS) Containers and Lids.

- One-way relief valve.

- Female treated terminals M10.

- High integrity post seals.

- Flexible, fully insulated Connectors.

- Applicable Standards:

- IEC 60896-21

- IEC 60896-227

- DIN 40742

PART 3 - EXECUTION

3.01	EXAMINATION

- Examine substrate areas and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

- Do not begin installation until mounting surfaces have been properly prepared.

- If preparation of mounting surfaces is the responsibility of another installer, notify Engineer of unsatisfactory preparation before proceeding.

- Examine modules and array frame before installation. Reject modules and arrays that are wet, moisture damaged, or mold damaged.

- Examine roofs, supports, and supporting structures for suitable conditions where PV system will be installed.

- Proceed with installation only after unsatisfactory conditions have been corrected.

3.02	PREPARATION

- Ensure structure or substrate is adequate to support solar electric module(s).

- Surface Preparation: Prepare surface in accordance with manufacturer's written recommendations and coordinate with relevant Sections of the specification.

3.03	INSTALLATION

- Coordinate installation of components in accordance with manufacturer's installation instructions.

- Coordinate solar electric module work with work of other trades for proper time and sequence to avoid construction delays.

- Accurately fit, align, securely fasten and install free from distortion or defects.

3.04	FIELD QUALITY CONTROL

- Manufacturer Services: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

- Coordinate manufacturer's services. Have manufacturer review work involved in handling, installation/application, protection and cleaning of produces, and submit written reports in acceptable format to verify compliance of work with Contract.

- Manufacturer's Field Services: Provide manufacturer's field services, consisting of product use recommendations and periodic site visits, for product installation inspection in accordance with manufacturer's instructions.

- Perform tests and inspections with the assistance of a factory-authorized service representative.

- Schedule site visits to review work at stages listed:

- After delivery and storage of products, and when preparatory work on which work of this Section depends is complete, but before installation begins.

- Twice during progress of work at 25% and 60% complete.

- Upon completion of work, after cleaning is carried out.

- Obtain reports within three days of review and submit immediately to Engineer.

- PV module will be considered defective if it does not pass tests and inspections.

- Prepare test and inspection reports.

3.05	SYSTEM STARTUP

- List actions applicable to operational systems and equipment startup.

- Commission the system to ensure that it complies with applicable code requirements and manufacturer's requirements.

3.06	ADJUSTING

- Adjust components and systems for correct function and operation in accordance with manufacturer's written instructions. Coordinate with Section Starting and Adjusting.

3.07	CLEANING

- Perform cleanup in accordance with the relevant Section of the specification.

- Upon completion, remove surplus materials, rubbish, tools and equipment in accordance with the relevant Section of the specification.

3.08	CLOSEOUT ACTIVITIES

- Demonstration:

- Coordinate requirements for solar electric module demonstration in accordance with Section Demonstration and Training.

- Training: Coordinate training in accordance with Section Demonstration and Training.

- Instruct Owner's designated maintenance personnel in care, adjustment and operation of solar electric module system.

- Provide competent instructor for not less than 8 hours training session(s) after completion and acceptance of work.

- Forward statement to Owner and Engineer countersigned by maintenance personnel confirming that these instructions have been provided.

3.09	PROTECTION

- Protect installed product from damage during construction in accordance with the relevant section of the specification.

- Repair damage to adjacent materials caused by solar electric module installation.

3.10	MAINTENANCE

- Coordinate maintenance requirements with Section Closeout Submittals and Section Operation and Maintenance Data.

END OF SECTION