Section 011300

COMPACT WASTE WATER TREATMENT PLANT

1.0	GENERAL

1.1	Scope of Work

Design, Supply, Install, Test and commission of a Compact Waste Water Treatment Plant (CWWTP) with all related accessories, Civil, Electrical and Mechanical works required for the full and safe operation of the plant and as per Drawings within the site boundaries established.

1.2	Extent of Works

- The Compact Waste Water Treatment Plant [CWWTP] shall be a modular and compact unit having all the required equipment fitted in the Compact Unit. The operation shall be designed on a continuous twenty four hour basis. All the mechanical equipment supplied with the CWWTP shall be of reputed make acceptable to Engineer and are tested and designed for running twenty four hours on a continuous basis.

- The CWWTP shall be designed on a modular concept that it should occupy the minimum of space, at no case the overall size exceed the identified site boundaries. The equipment layout shall be done in such a manner that the CWWTP provides savings on land area. The CWWTP shall be designed and constructed to satisfy the requirements of Ministry OF Environment and Energy [MEE], Government of Maldives and the Engineer and shall be suitable and fully functional to be taken over by the Ministry OF Environment and Energy .

- It is intended that the effluent from the plant will be disposed off in outer sea/ocean.

- The CWWTP is to be designed employing the biological treatment process of Activated Sludge Process.

- All materials used/supplied and all machinery used/supplied shall be completely new and of the highest quality and superior standards. They shall comply with the British Standards.

- It is intended that the completed CWWTP works will be taken over by Ministry OF Environment and Energy of Government of Maldives. All designs, materials, machinery, processes and layouts are subject to the approval of the Ministry OF Environment and Energy, Government of Maldives. At the time of hand over to Ministry, CWWTP and all its ancillaries shall be in full and correct operational order.

- The contractor shall be responsible for constructing the works accurately in accordance with the approved design so that the structural, hydraulic, mechanical, electrical and aesthetic functions are not impaired and to the complete approval and satisfaction of MEE, Govt. of Maldives.

- Any materials that may react adversely with the prevailing conditions in which they are in contact shall be avoided or shall be suitably protected.

1.3	Design Criteria

A.        Organic Loading Rates

The table provided below indicates the organic loading rates Known for the treatment unit; Contractor may verify the results further

| LOADING RATES |  |
| --- | --- |
| Parameter | Value |
| Bio-chemical Oxygen Demand (SS) | 220 MG/L |
| Suspended Solids (SS) | 60 gms /person/ day |
| Ammonia cal (NH3) | 5 mg/L |

B.	Treatment Process Selection

The selection of a particular process for sewage treatment is affected by diurnal and seasonal flow variations, sewerage strength (variability of wastewater constituents) infiltration / inflow, ambient temperature and its induced septicity, degree of treatment required, magnitude and direction of wind etc.

The treatment works shall consist of:

| Process stage | Purpose |
| --- | --- |
| Preliminary Treatment | Screening and grit removal flow measurement |
| Secondary Treatment by Bio-Remediation | Oxygenations by means of Aerations followed by clarification-separations of effluent and sludge. |
| Effluent Treatment (Optional) | Effluent subjected to disinfection by chlorination |
| Sludge Removal | Sludge disposal |

C.	Required Effluent Standards

- The minimum required standards for effluent are as shown below.

| EFFLUENT STANDARD |  |
| --- | --- |
| Parameter | Value |
| Bio-chemical oxygen demand (BOD) | 70 MG/L |

1.4	Submittal

- Contractor shall submit the following minimum documents for approval before placing order with the manufacturer

  - Sectional Hydraulic Profile

  - Treatment Process Employed

  - Controls Employed

  - Materials specification of each items involved in the CWWTP

  - Layout Plan with each component, vendor and other items, marked with sections, method of construction/installation etc complete.

1.5	Training of MEE Staff:

Before handing over the fully operational plant over to the MEE, the supplier/contractor shall train the MEE staff in all aspects of the operation and maintenance of the plant. Training shall be complete and include all the aspects of:

1, Process employed

2, Controls employed

3, Complete Plant Maintenance

4, Testing

5, Safety

Two sets of Documents/Manual of the above mentioned aspects (from one to five as above) of CWWTP shall be handed over to MEE and receive acknowledgement before release of final payment.

2.0	PRODUCTS

- The CWWTP shall include the following

- Collection Well with one duty & one standby pump (optional as per manufacturers selection)

- Splitter Box

- Compact Waste Water Treatment Unit containing aeration & settlement

- Sludge tank of capacity 6 months, and having a sludge pump with line connected to sea outfall

- Effluent manhole with one duty and standby pumps

- Sea outfall line

2.1	Inlet Lift Well (Optional)

A.	Inlet lift station will use submersible type grinder to transfer the raw incoming sewage to the flow splitter box.

Quantity Required 		: One

Dimension	: 5m x3 m x 3m (Depth) [indicative, final sizes as per Manufacturers design calculations]

Material of Construction	: Concrete or GRP with full water proofing. Provide       epoxy coating inside. Concrete/GRP shall be able to resist the saline ground water conditions.

A protective membrane/coating shall be applied to the outside of concrete in contact with the ground. This protection shall be fully able to prevent the adverse effects of highly saline ground water. Internal surfaces of concrete in contact with the sewage shall be provided with anti-corrosive type epoxy painting.

B	Provide two numbers-[one duty + one standby] raw sewage grinder pumps in the inlet lift well.

Type	: Submersible, Non Clog, Centrifugal with required capacity grinder provided shall be integral with pump and pump inlet.

Mode of Control	: By float switches.

Casing/Impeller	: Cast Iron.

Shaft	: Stainless Steel Material.

C.	This item is optional, should the pumped main from lifting station be directly received by the splitter box of the manufacturer, this may be avoided and necessary adjustment be made in the splitter box

2.2	Splitter Box

A	The splitter boxes will direct the flow to the CWWTP to receive the flow. Provide Galvanized Steel splitter box with access platform.

2.3	Compact Waste Water Treatment Plant [CWWTP]

The CWWTP shall employ the biological remediation process of activated sludge process.

A	Air Blowers.

Three numbers of air blowers per unit shall be provided [Two on alternating duty + one stand by]. Air blowers shall be of rotary type, positive displacement, and oil free, Vee belt coupled. Filter shall be provided at air inlet and silencer shall be provided at air outlet. Isolating valve, non-return valve and pressure relief valve shall be provided. Belt tensioner, required flexible connections of superior quality shall also be provided. Air Blowers shall only be of very good quality and shall be of only German made or Japanese made. Manufacturer/ Supplier shall obtain clearance endorsement from MEE regarding proof that specified air blower is German made OR Japanese made.

Air Blowers shall be provided with excess capacity to provide aeration to Sludge Stabilization and Storage Tank.

B	Air Diffusers in Aeration Tank

Type of air diffusers in aeration tank shall be medium bubble diffuser with plastic body and superior quality rubber diaphragm. Sufficient valve controls per down comer pipes shall be provided.

2.4	Effluent Pump & Tank.

A	Two numbers effluent pumps of submersible type, float control shall be provided. One on duty and one standby. Capacity of each effluent pump shall be as indicative, final capacities as per Manufacturers design calculations]

B.	3m x 3m x 2m effluent tank to house the pumps above grade or under grade shall be constructed by concrete or GRP, sizes are indicative and shall be modified to suit the manufacturers design work

2.5	Sludge Stabilization and Holding Tank

A	Sufficient storage space shall be provided for sludge stabilization before being disposed. Sludge storage chamber shall be aerated using the excess capacity of air blowers which are used for aeration tanks.

B	One number sludge pump shall be used. Stabilized and digested sludge can be disposed off to sea using the same effluent disposal pipe line over one month interval period.

3 	EXCECUTION

3.1	 Operation & Maintenance

- The CWWTP shall be a fully automatic operated installation. Only few hours weekly of regular inspection & maintenance must be expected. Vital function of the CWWTP must have an optional remote supervision facility.

- The CWWTP shall be supplied with minimum 2 copies of Operational & maintenance manuals. These manuals shall include manufacturer manual for pumps, blowers, filters etc., electrical wiring diagram, drawings and a recommended maintenance schedule.

- The tank must be easy to transport on a trailer and/or in a sea container. The tank must be suitable for installation both under and above ground level.

END OF SECTION