## Project Cover sheet
BILL OF QUANTITIES
Construction of Sewerage Facilities on the Island of HDh.Nolhivaranfaru, K.Himmafushi & K.Thulusdhoo
CLIENT : MINISTRY OF ENVIRONMENT AND ENERGY

## Grand Summary
PROJECT GRAND SUMMARY OF BILLS OF QUANTITIES
Construction of Sewerage Facilities on the Island of HDh.Nolhivaranfaru, K.Himmafushi & K.Thulusdhoo
| DESCRIPTION | AMOUNT (MRF) | %
1 SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
2 SEWERAGE SYSTEM IN K.HIMMAFUSHI
3 SEWERAGE SYSTEM IN K.THULUSDHOO
| TOTAL AMOUNT | 0

## cover page
BILL OF QUANTITIES
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
CLIENT : MINISTRY OF ENVIRONMENT AND ENERGY

## main summary
SUMMARY OF BILLS OF QUANTITIES
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
| DESCRIPTION | AMOUNT (MRF) | %
Bill №: 01 - GENERAL WORKS
Bill №: 02 - GRAVITY SEWERAGE SYSTEM
Bill №: 03 - ADMIN BUILDING
Subtotal of Bills
Total for DAYWORK
Total for PROVISIONAL SUMS
| TOTAL AMOUNT | 0
Note: Client reserves the right to remove items listed as (optional) in which case the price of the items will be deducted from the bill

## 01 General BoQ summary
SUMMARY OF BILLS OF QUANTITIES
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
01 GENERAL WORKS
| DESCRIPTION | AMOUNT (MRF) | %
BILL NO. 01 - GENERAL AND PRELIMINARIES
BILL NO. 02 - SITE PREPARATION
BILL NO. 03 - DECOMISSIONING
| TOTAL AMOUNT | 0

## 01 general BoQ
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
01 GENERAL WORKS
Male', Republic of Maldives
BILL OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
BILL NO. 01 - GENERAL AND PRELIMINARIES
1.1.00 | Project Management cost
1.1.01 | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings & similar. | 1 | Item
1.2.00 | Contractual Requirements
1.2.01 | Provide & Maintain all necessary Insurances, Guarantees and Securities. | 1 | Item
1.3.00 | Specified Requirements
1.3.01 | Provision and Erection of Notice Boards 3m x 4m size as per drawing and specification, including complete cost and conveyanceof materials, labour charges, & etc. | 1 | Item
1.3.02 | Provision of photographs of important activities of the work during the progress of work as directed by the Engineer. | 1 | Item
1.3.03 | Provision of videograph of the progress of works, one video tape not more than 30 minutes duration showing the progress during evey month. | 1 | Item
1.3.04 | Submission of detailed drawings for approval by the Engineer prior to commencement of work | 1 | Item
1.3.05 | Detailed survey of each plot and prepare site layout and identify household catchpit and water supply connection meter location and obtain Homeowner & Contractor agreement for each house | 1 | Item
1.3.06 | Provision and maintaining of adequately equipped Laboratory services as required for site control on the quality of materials and the works as required by the engineer; | 1 | Item
1.3.07 | Consultant Engineer's office | 1 | Item
1.4.00 | Temporary Works
1.4.01 | Arrange during dewatering of trenches, for pumping ground water of salinity greater than 2500 microsiemens to be pumped out to sea. | 1 | Item
1.5.00 | Dewatering
1.5.01 | Dewatering as required as per EPA regulation 2013/R-1697 | 1 | Item
1.4.00 | TOTAL OF BILL №: 01 - Carried Over To Summary
BILL NO. 02 - SITE PREPARATION
2.1.00 | Clearing grass, bushes, shrubs, saplings, uprooting rank vegetation all along the pipeline route and removal & disposal of rubbish to approved tips anywhere in the island as directed by the Engineer-in-charge | 1 | Item
2.2.00 | Cutting of trees, including trunks, branching and removal of stumps, roots, stacking of serviceable materials with all lifts and up to all lead within project area and earthfilling in the depression/pit, including excavation & backfilling
2.2.01 | Girth size up to 300mm | 1 | item
2.2.02 | Girth size from 300mm to 600mm | 1 | item
2.2.03 | Girth size from 600mm to above | 1 | item
2.3.00 | Dismantling of existig structures like pillars, walls, slabs and any other structureconstructed of Brick or coral stone masonry, cement concrete, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material | 1 | item
2.5.0 | TOTAL OF BILL №: 02 - Carried Over To Summary
BILL NO. 03 - DECOMISSIONING
3.1.00 | Decomissioning of existing septic tanks and small bore gravity sewers upon completion and testing and comissioning of new system. Rates shall include for removal of all the existing sludge from the septic tanks and soak wells using proper equiment such as sucker truck; and transfer the contents to STP. Once all the content has been thoroughly removed the septic tanks should be backfilled with adequate material and compacted | 1 | item
3.2.00 | TOTAL OF BILL №: 03 - Carried Over To Summary

## 02 Sewerage System summary
SUMMARY OF BILLS OF QUANTITIES
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
02 GRAVITY SEWARAGE SYSTEM
| DESCRIPTION | AMOUNT (MRF) | %
BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (4 nos.)
BILL NO. 02 - SUPPLY AND INSTALLATION OF PUMPS
BILL NO. 03 - MECHANICAL AND ELECTRICAL WORKS
BILL NO. 04 - GRAVITY SEWER MAINS
BILL NO. 05 - STP
BILL NO. 06 - SEA OUTFALL
BILL NO. 07 - SUPPLY OF O&M EQUIPMENT AND SPARES
BILL NO. 08 - TESTING AND COMMISSIONING
| TOTAL AMOUNT | 0

## 02 sewarage system
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
02 GRAVITY SEWARAGE SYSTEM
Male', Republic of Maldives
BILL OF QUANTITIES
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
BILL NO. 01 - CIVIL WORK FOR PUMP STATIONS (4 nos.)
1.1.00 | General Notes
(a) Cement for all structural works shall be Sulphate resistant portland cement to BS4027:1996 unless specified otherwise
(b) All structural reinforcement steel shall be epoxy coated reinforcement to ASTM A775 / A775M
(c) The required soil bearing pressure for the foundation is 150kn/m². The contractor shall carryout geotechnical testing to ensure that this is achieved and necessary ground improvements and piling shall be done if required
d) Rates shall include the pump sump, valve chamber, control panel cabinet and valves, fittings inside the valve chamber and vent structures
(e) All internal concrete surfaces shall be protected with epoxy coating of thickness 500 microns
(f) Bituminous coating shall be provided to all external surfaces of concrete works below ground
(g) Rates shall include for formwork, reinforcement, cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
1.2.00 | Excavation Works
1.2.01 | Excavation for PS1 | 33.6 | m3
1.2.02 | Excavation for PS2 | 33.6 | m3
1.2.03 | Excavation for PS3 | 34.35 | m3
1.2.04 | Excavation for PS4 | 33.6 | m3
1.3.00 | Concrete Works
1.3.01 | Lean concrete for PS1 | 2.74 | m3
1.3.02 | Lean concrete for PS2 | 2.74 | m3
1.3.03 | Lean concrete for PS3 | 2.74 | m3
1.3.04 | Lean concrete for PS4 | 2.74 | m3
1.3.05 | Reinforced concrete for PS1 | 19.8 | m3
1.3.06 | Reinforced concrete for PS2 | 19.8 | m3
1.3.07 | Reinforced concrete for PS3 | 20.09 | m3
1.3.08 | Reinforced concrete for PS4 | 19.8 | m3
1.4.00 | Plastering works
1.4.01 | Plastering works for PS1 | 75.35 | m2
1.4.02 | Plastering works for PS2 | 75.35 | m2
1.4.03 | Plastering works for PS3 | 76.32 | m2
1.4.04 | Plastering works for PS4 | 75.35 | m2
1.5.00 | Internal coating (500 Micron Epoxy coating )
1.5.01 | Coating for PS1 | 50.5 | m2
1.5.02 | Coating for PS2 | 50.5 | m2
1.5.03 | Coating for PS3 | 51.3 | m2
1.5.04 | Coating for PS4 | 50.5 | m2
1.6.00 | Bituminous External coating
1.6.01 | External coating for PS1 | 75.35 | m2
1.6.02 | External coating for PS2 | 75.35 | m2
1.6.03 | External coating for PS3 | 76.32 | m2
1.6.04 | External coating for PS4 | 75.35 | m2
1.7.00 | Covers and Ancillaries
1.7.01 | Access Cover for PS1 | 2 | nos
1.7.02 | Access Cover for PS2 | 2 | nos
1.7.03 | Access Cover for PS3 | 2 | nos
1.7.04 | Access Cover for PS4 | 2 | nos
1.8.00 | TOTAL OF BILL №: 01 - Carried Over To Summary
BILL NO. 02 - SUPPLY AND INSTALLATION OF PUMPS
2.1.00 | General Notes
(a) Rates shall include for supply and installation as per approved drawings and manufacturers details
b) rates shall include costs for Power cable, duckfoot bend, dischage connection, guide bars and 6m of stainless steel lifting chain, level control switches as per drawing and specifications.
(C) Rates shall include for all internal piping and connections as per detail
2.2.00 | Pumps
2.2.01 | Submersible Pumps 8.9kW (Pump Station 01) - Pump Capacity,Pump Capacity, Qdp=10.5 l/s, Head=21.4m each | 2 | nos.
2.2.02 | Submersible Pumps 7.1kW (Pump Station 02) - Pump Capacity,Pump Capacity, Qdp=8.6 l/s, Head=23.2m each | 2 | nos.
2.2.03 | Submersible Pumps 7.1kW (Pump Station 03) - Pump Capacity,Pump Capacity, Qdp=5.6 l/s, Head=19.4m each | 2 | nos.
2.2.04 | Submersible Pumps 8.9kW (Pump Station 04) - Pump Capacity,Pump Capacity, Qdp=11.3 l/s, Head=23.9m each | 2 | nos.
2.3.00 | Vent structures
| Supply and installation of vent structure with carbon filter as per the drawing | 4 | nos.
2.4.00 | Monitoring system
2.4.01 | Monitoring system for Pump stations including all necessary cabling and wiring or GSM modules. | 1 | Item
2.5.00 | Pumping Main
2.5.01 | Pumping main 110mm dia. HDPE PE100 SDR11 PN16 pipe | 1313 | m
2.5.02 | Pumping main 160mm dia. HDPE PE100 SDR11 PN16 pipe | 78 | m
2.5.03 | Pumping main 200mm dia. HDPE PE100 SDR11 PN16 pipe | 290 | m
2.6.00 | TOTAL OF BILL №: 02 - Carried Over To Summary
BILL NO. 03 - MECHANICAL AND ELECTRICAL WORKS
3.1.00 | General Notes
(a) The rate shall include for any necessary excavation of trenches, backfilling after laying and testing, jointing, installing house connection wyes on the main line, dewatering if absolutely necessarry, and any other required accessories, including dismantling of road layers and reinstatement after works
(b) The rate shall include for making good any areas affected by below works
3.2.00 | Main feeder cable from island grid to control panels (4 pump stations and admin building/STP) including , materials and accessories required for complete works | 1 | Item
3.2.01 | 25 mm2 4-Core armoured cable (feeder to PS) | 240 | m
3.2.02 | 50 mm2 4-Core armoured cable ( Power House to STP) | 70 | m
3.3.00 | Control Panels with necessary cabling and control wiring as per approved details (4 Pump stations and admin building/STP) | 1 | Item
3.4.00 | Monitoring system for STP including all necessary cabling and wiring. | 1 | Item
3.5.00 | Preparation of electrical drawings and obtaining approval from MEA | 1 | Item
3.6.00 | Testing and Commissioning of the complete electrical system. | 1
3.7.00 | TOTAL OF BILL №: 03 - Carried Over To Summary
BILL NO. 04 - GRAVITY SEWER MAINS
4.1.00 | General Notes
(a) The rate for pipe laying shall comprise excavation of trenches, backfilling after laying and testing, jointing pipes, installing house connection wyes on the main line, dewatering if absolutely necessarry, providing granular bedding for pipe laying, including dismantling of road layers and reinstatement after works
(b) all gravity sewer pipes shall be UPVC to BS EN1401-1:2009.
(c) All gravity sewer mains shall be 160mm dia UPVC of wall thickness & stiffness rated to SN4 & SDR41.
(d) All gravity house laterals shall be 110mm dia UPVC of wall thickness & stiffness rated to SN4 & SDR41.
(e) All gravity sewer mains shall have minimum 0.4% slope.
(f) All gravity sewer pipes shall be jointed using rubber ring push fit jointing method & rubber rings comply with BS 2494 (type2).
(h) All sewer pipes shall be buried under earth cover of minimum 0.6 meters.
4.2.00 | Pipe laying
All pipes are measured in linear meters on plan veiw. Contractor shall adjust for slopes
4.2.01 | 160mm dia, uPVC gravity sewer main (SN4, SDR41) | 12286 | m
4.3.00 | Maintenance shaft
(a) Rates shall include for all connections, concrete protections and necessary ancillary items, as per drawing and technical specifications
4.3.01 | 600mm dia. PE/PP Maintenance shaft with concrete protection | 163 | nos.
4.4.00 | House Connection
4.4.01 | Lateral house connection to main network, not exceeding maximum distance of 6m, including provision and installation of 315mm dia. uPVC House inspection chamber as per detail drawing | 629 | nos.
4.5.00 | Clean out
(a) Rates shall include for all connections, concrete protections and necessary ancillary items, as per drawing and technical specifications
4.5.01 | 160mm dia. uPVC clean out | 121 | nos.
4.6.00 | TOTAL OF BILL №: 04 - Carried Over To Summary
BILL NO. 05 - STP
5.1.00 | General Notes
(a) Lean concrete shall be GRADE C15 and all structural concrete shall be GRADE C35A
(a) Cement for all structural works shall be Sulphate resistant portland cement to BS4027:1996 unless specified otherwise
(b) All structural reinforcement steel shall be epoxy coated reinforcement to ASTM A775 / A775M
(a) The required soil bearing pressure for the foundation is 150kn/m². The contractor shall carryout geotechnical testing to ensure that this is achieved and necessary ground improvements shall be done if required
(b) All internal concrete surfaces shall be protected with epoxy coating of thickness 500 microns
(c) Bituminous coating shall be provided to all external surfaces of concrete works below ground
(b) All GI / steel members shall be protected with universal primer and 2 coats of anti-corrosive
5.2.00 | Civil works
Construction of complete STP system as per detailed drawing. Rates shall include for all piping and accessories as needed.
5.2.01 | 10mm Bar screen and Grit channel - including 1800x1800 foundation pads, 400x400 columns, 400x600 beam, stainless steel gate, bar screen, walkway (25 SQ GI grating), ladder, etc
| Excavation for Grit channel | 7.78 | m3
| Reinforced Concrete for Grit chanel | 15.45 | m3
5.2.02 | 4900x5600 oil and grease trap - including 300mm RC base and walls, 150mm RC top, SS checkered plates, etc
| Excavation for Oil and Grease trap | 21.95 | m3
| Reinforced Concrete for Oil and Grease trap | 29.04 | m3
5.2.03 | 7900x6600x3100mm depth equalization tank - including 400mm thick RC base, 300mm thick RC walls, etc
| Excavation for Equalization Tank | 61.21 | m3
| Reinforced Concrete for Equalization Tank | 49.21 | m3
5.2.04 | 10750x6750x5325mm depth Aeration tank (2nos) - including 475mm thick RC base, 375mm thick RC walls, 450x600mm RC bottom beams, 350x600 RC top beams, ladder, floor grating, GI pipe railing, diffusers with EPDM membrane system
| Excavation for Aeration Tank | 271.62 | m3
| Reinforced Concrete for Aeration Tank | 208.13 | m3
5.2.05 | 4300mm dia. x 4200mm depth clarifier (2nos) - including 450mm thick RC base, 300mm thick RC walls, 50mm dia. GI hand rail
| Excavation for Clarifier | 109.44 | m3
| Reinforced Concrete for Clarifier | 65.79 | m3
5.2.06 | 2500mm dia. x2500mm depth Sludge Holding Tank (2nos) - 350mm thick RC base, 300mm thick RC walls, 200mm thick RC top, 800x800 SS chequered plate, etc
| Excavation for Sludge Holding Tank | 40.4 | m3
| Reinforced Concrete for Sludge Holding Tank | 36.9 | m3
5.2.07 | 2600x5600x3900mm depth clear water tank - including 400mm thick RC base, 300mm thick RC walls, etc
| Excavation for Clear Water Tank | 19.76 | m3
| Reinforced Concrete for Clear Water Tank | 30.41 | m3
5.2.08 | 17500x6100mm sludge drying beds - includiung 1000x350x50mm thick concrete slabs, 100mm dia. GI pipe columns, 100x150 GI RFS support beam, 50x50 GI SHS purlins, 50x100 GI RHS, translucent sheet roof covering
| Excavation for Sludge Drying Beds | 106.8 | m3
| Reinforced Concrete for Sludge Holding Beds | 76.3 | m3
5.2.09 | 2950mm dia. x 2500mm depth Effuluent Tank (1nos) - 350mm thick RC base, 225mm thick RC walls, 150mm thick RC top, 800x800 SS chequered plate, etc
| Excavation for Effuluent Tank | 19.63 | m3
| Reinforced Concrete for Effuluent Tank | 6.08 | m3
5.2.10 | Complete electrical works required for pumps, connections, and accessories as needed | 1 | item
5.2.11 | External painting on all exposed external surfaces including primer and minimum two coats of emulsion paint | 1 | item
5.3.00 | Pumps and blowers
(a) Rates shall include for supply and installation as per approved manufacturers details
(b) Rates shall include for all internal piping and connections as per detail
(b) Rates shall include for float switches, gate valves, and all other necessary fittings and ancillieries, etc
5.3.01 | O/G Trap - EQT Pump - 2.5kw Submersible pump controlled By manual operation (Q=1.63l/s , H=5m) | 2 | no.
5.3.02 | EQT - Aerator pump - 5kw Submersible Pump controlled By Level sensors (float switch) (Q=5 l/s , H=15m) | 2 | no.
5.3.03 | Sludge Holding Tank Pump - 2.5kw Submersible pump controlled By Level sensors (float switch) (Q=2 l/s , H=7m) | 4 | no.
5.3.04 | Aeration Blowers - 11kw Twin lobe design controlled By manual operation (580m3/hr @ .6kg/cm2) | 3 | no.
5.3.05 | Effluent Tank Pump - 1.5kw Submersible pump controlled By Level sensors (float switch) (Q=1 l/s , H=6m) | 2 | no.
5.3.06 | Sea Outfall pump - 10.5kw pump controlled By Level sensors (float switch) (Q=16.3 l/s , H=16.6m) | 2 | no.
5.4.00 | Flow meter
5.4.01 | Flow meter between EQT tank and Aeration tank to specifications | 2 | no.
5.4.02 | Flow meter at outfall pipe | 1 | no.
5.5.00 | TOTAL OF BILL №: 05 - Carried Over To Summary
BILL NO. 06 - SEA OUTFALL
6.1.00 | Installation of outfall pipeline with concrete ballast block, anchoring and necessary concrete protection as per drawing
| 200mm dia, HDPE sea outfall pipe (PE 100, PN16, SDR11). The minimum depth of diffuser head from MSL is 15m and away from reef edge. | 350 | m
6.2.00 | TOTAL OF BILL №: 06 - Carried Over To Summary
BILL NO. 07 - SUPPLY OF O&M EQUIPMENT AND SPARES
Spares for Admin Building and STP:
7.1.00 | Safety Tools
Supply and Delivery of the following safety equipments and tools:
7.1.01 | Wooden First Aid Box | 3 | Nr.
7.1.02 | Fire Bucket sand with 3 nos. of round bottom buckets. | 3 | Nr.
7.1.03 | Rubber mat of 1.1kV grade of size 6mm thick. | 3 | Nr.
7.1.04 | Fire Safety Rules chart. | 3 | Nr.
7.1.05 | Shock Treatment Chart | 3 | Nr.
7.2.00 | Maintenance Tools
| Supply and Delivery of standard maintenance tools / equipments to Engineer's approval. | 3 | sets
7.3.00 | Laboratory Equipment ( Optional)
| Supply and Delivery of laboratory equipments and related consumables for a duration of one year to Engineer's approval. | 1 | item
7.4.00 | Sewer jetting and Suction Machine/Vehicle ( 1500 litre tank) (Optional) | 1 | item
7.5.00 | TOTAL OF BILL №: 07 - Carried Over To Summary
BILL NO. 08 - TESTING AND COMMISSIONING
8.1.00 | Preparation ofall O&M manuals, training documents and as-built drawings | 1 | item
8.2.00 | Provision of one year warranty of system including all required maintenance and provision of spare parts (including pump spares) during this period | 1 | item
8.3.00 | Training of employeer's nominnes in operation and maintainance as per employer's requirement | 1 | Item
8.4.00 | Testing and comissioning of system | 1 | item
8.5.00 | TOTAL OF BILL №: 08 - Carried Over To Summary

## 03-Admin Summary
SUMMARY OF BILLS OF QUANTITIES
SEWARAGE SYSTEM IN HDH.NOLHIVARANFARU
03-ADMIN BUILDING
| DESCRIPTION | AMOUNT | %
Bill №: 01 - PRELIMINARIES
Bill №: 02 - EXCAVATION AND FILLING
Bill №: 03 - INSITU CONCRETE WORKS
Bill №: 04 - MASONRY
Bill №: 05 - CEILINGS
Bill №: 06 - WINDOWS
Bill №: 07 - STAIRS AND BALCONY
Bill №: 08 - FINISHING
Bill №: 09 -PAINT AND DECORATION
Bill №: 10 - HYDRAULICS AND DRAINAGE
Bill №: 11 - MECHANICAL AND ELECTRICAL SERVICES
Bill №: 12- ROOFING
TOTAL AMOUNT

## 03-Admin Building
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
03 ADMINISTRATION BUILDING
Male', Republic of Maldives
BILL OF QUANTITIES
ITEM |  |  |  | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1.0.00 |  |  |  | Bill №: 01 - PRELIMINARIES
1.1.00 | GENERAL NOTES
Abbreviations
|  |  | m | - metre
|  |  | nr | - numbers
|  |  | m3 | - cubic metres
|  |  | m2 | - square metres
|  |  | m | - linear metre
|  |  | t | - tons
|  |  | inc. | - including
|  |  | mm | - millimetre
|  |  | SS | - stainless steel
|  |  | GI | - galvanized iron
1.2.00 | PAVING
|  |  |  | Rates shall include for subgrade preperation and Paving of the Pathways sourrounding the STP and admin buiilding Site | m2 | 359
1.3.00 | TOTAL OF BILL №: 01 - Carried Over To Summary
2.0.00 |  |  |  | Bill №: 02 - EXCAVATION AND FILLING
2.1.00 | GENERAL
|  |  | (a) | Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating, and disposing surplus soil.
2.2.00 | SITE CLEARING
2.2.01 |  |  |  | Clear the area of site from rubbish and vegetable matters, stumps, roots. Rates shall include for removal of trees and tree stumps | m2 | 130
2.3.00 | EXCAVATION
Excavation quantities are measured to the faces of concrete members. Rates shall include for all the additional excavation required to place the formwork. Rates shall include for backfilling.
2.3.01 |  |  |  | Excavation for Foundation beams and tie beams | m3 | 31.82
2.3.02 |  |  |  | Excavation for Foundation Pads | m3 | 4.46
2.4.00 | DAMP-PROOF MEMBRANE
Rate shall include for: dressing around and sealing to all penetrations.
2.4.01 |  |  |  | Bituminous waterproofing membrane | m2 | 108
2.5.00 | DE-WATERING
2.5.01 |  |  |  | De-watering the excavation until completion of concrete work as required | item | 1
2.6.00 | TOTAL OF BILL №: 02 - Carried Over To Summary
3.0.00 |  |  |  | Bill №: 03 - INSITU CONCRETE WORKS
3.1.00 | GENERAL
|  |  | (a) | Rates shall include for: placing in position, making good after removal of formwork, mortar touch up to all concrete and casting in all required items; additional concrete required to conform to structural and excavated tolerances
|  |  | (b) | Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6.
|  |  | (d) | Rates shall include for: concrete, formwork, reinforcement, cleaning, fabrication, placing, the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
|  |  | (e) | Rates shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork.
|  |  | (f) | Rates shall include for: cleaning, fabrication, placing the provision for all necessary temporary fixings and supports including tie wires and chair supports, laps, distribution bars and wastage.
|  |  | (g) | All reinforcing bars shall be high strength bars.
|  |  | (h) | Slab soffits to be finished fairfaced, use plasteciser and formwork with reducing agent.
|  |  | (i) | Waterproofing shall be added to all areas specified.
3.1.01 |  |  |  | Allow for Concrete Testing. | item | 1
3.2.00 | MASS CONCRETE
Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
3.2.01 |  |  | 75 | mm Lean Concrete (Foundations and bases) | m3 | 2.72
3.3.00 | REINFORCED INSITU CONCRETE
SUB-STRUCTURE
FOUNDATION BEAMS
3.3.01 | 300 | x | 250 | mm Foundation beam, FB1 | m3 | 6.6094
3.3.02 | 225 | x | 225 | mm Foundation beam (Boundary Wall) | m3 | 7.4925
FOUNDATION PADS-250MM
3.3.03 | 600 | x | 600 | mm Foundation Pad F1/C1 | m3 | 1.35
3.4.00 | GROUND FLOOR
Ground Floor Slab
3.4.01 |  | 100 | mm Thick slab |  | m3 | 8.2
| 200 | mm Concrete slab
3.4.02 |  |  | Pump Blower Room |  | m3 | 2.912
3.4.03 |  |  | Generator Room |  | m3 | 2.782
Generator & Pumps Concrete Base
3.4.05 | 400 | Concrete base |  |  | m3 | 3.532
COLUMNS
3.4.06 | 200 | x | 200 | mm Concrete columns C1 | m3 | 1.83
3.4.07 | 200 | x | 200 | mm Concrete columns (Boundary Wall) | m3 | 2.639
ROOF BEAM
3.4.08 | 300 | x | 200 | mm Roof beam | m3 | 5.2875
3.4.09 | 125 | x | 125 | mm Beam (Boundary Wall) | m3 | 2.2656
3.5.09 |  |  | RAMP |  | m2 | 8.1
3.6.00 |  |  |  | TOTAL OF BILL №: 03 - Carried Over To Summary
4.0.00 |  |  |  | Bill №: 04 - MASONRY
4.1.00 | GENERAL
|  |  | (a) | Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leavingholes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashing, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good.
4.2.00 | BLOCK WORK
Cement block wall, bricks laid to form alternate courses of headers and stretchers, laid on and inc. mortar. (INTERNAL & EXTERNAL WALLS)
|  |  | 150 | mm thk full height
4.2.01 |  |  |  | GROUND FLOOR | m2 | 237.4204
4.2.02 |  |  |  | GROUND FLOOR (BOUNDARY WALL) | m2 | 294.9585
4.2.03 |  |  |  | ABOVE ROOF BEAM LEVEL | m2 | 36.4865
4.3.00 |  |  |  | TOTAL OF BILL №: 04 - Carried Over To Summary
5.0.00 |  |  |  | Bill №: 05 - CEILING
5.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
5.2.00 | CEILING
False Flat Ceiling with 9mm Thick Gypsum Board under 50x38mm Timber framing with Emulsion Paint Finish
5.2.01 |  |  |  | Ground Floor | m2 | 50.36
Exposed Wooden Roof Members Covered with PVC net
5.2.02 |  |  |  | Ground Floor | m2 | 63.09
6mm Cement Board Eave Ceiling with Exterior Paint
5.2.03 |  |  |  | Ground Floor | m2 | 26.06
5.3.00 |  |  |  | TOTAL OF BILL №: 05 - Carried Over To Summary
6.0.00 |  |  |  | Bill №: 06 - DOORS AND WINDOWS
6.1.00 | GENERAL
|  |  | (a) | Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
|  |  | (b) | Rates shall include for door frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings.
|  |  | (c) | Sizes are given overall outside dimensions of actual doors and windows.
|  |  | (d) | Thickness and sizes of glass panels are shown on the Drawings and doors and windows schedule
|  |  | (e) | Rates shall include for all painting as specified
|  |  | (f) | Rates shall include all items specified in the door schedule and specification.
|  |  | (g) | Frames and sashes to be 25-60 micron black powder coated aluminium other wise specified.
6.2.00 | DOOR & WINDOWS
GROUND FLOOR
6.2.01 | 5010 | x | 1700 | 50x50mm GI Box Bar Frame Gate Finished With Anti-corossive 2 coats and selected paint finished | nr | 1
6.2.02 | 1400 | x | 2100 | D1-Aluminum Framed Doors With Aluminium Panels | nr | 1
6.2.03 | 1200 | x | 2100 | D2-Aluminum Framed Doors With Aluminium Panels | nr | 1
6.2.04 | 900 | x | 2100 | D3-Aluminum Framed Doors With Aluminium Panels | nr | 4
6.2.05 | 900 | x | 2100 | D3a-Aluminum Framed Doors With Aluminium Panels | nr | 1
6.2.06 | 900 | x | 2100 | D3b-Aluminum Framed Doors With Aluminium Panels and Louvers | nr | 2
6.2.07 | 2400 | x | 1200 | W1-White Powder Coated Aluminium Door With Reflective Double Glazed Glass Panels | nr | 1
6.2.08 | 1200 | x | 1200 | W2-White Powder Coated Aluminium Door With Reflective Double Glazed Glass Panels | nr | 3
6.2.09 | 1800 | x | 1200 | W3-White Powder Coated Aluminium Door With Reflective Double Glazed Glass Panels | nr | 1
6.2.10 | 1200 | x | 1200 | W4-White Powder Coated Aluminium Door With Reflective Double Glazed Glass Panels | nr | 1
6.2.11 | 600 | x | 700 | V1-White Powder Coated Aluminium Door With Reflective Double Glazed Glass Panels | nr | 2
6.3.00 |  |  |  | TOTAL OF BILL №: 06 - Carried Over To Summary
7.0.00 |  |  |  | Bill №: 07 - RAILINGS
7.1.00 | GENERAL
|  |  | (a) | Rates shall include for: all fabrication work, welding, marking, drilling for bolts incl. those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
|  |  | (b) | Rates shall include for fabrication and erection and temporary supports and fixing into position.
7.2.00 | Boundary wall's barb wire
3 Rows Barb wire
7.2.01 |  |  |  | GROUND FLOOR (BOUNDARY WALL) | m | 142.2
7.3.00 |  |  |  | TOTAL OF BILL №: 07 - Carried Over To Summary
8.0.00 |  |  |  | Bill №: 08 - FINISHING
8.1.00 | GENERAL
|  |  | (a) | Rates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing.
8.2.00 | PLASTERING
EXTERNAL PLASTERING 16MM
|  |  | 20 | mm thk cement plaster on internal surface as specified on the drawing
8.2.01 |  |  |  | GROUND FLOOR | m2 | 703.152
INTERNAL PLASTERING 16MM
|  |  | 16 | mm thk cement plaster on internal surface as specified on the drawing
8.2.02 |  |  |  | GROUND FLOOR | m2 | 355.585
8.3.00 | CEMENT SCREED
|  |  | 35 | mm thick cement screed
8.3.01 |  |  |  | GROUND FLOOR | m2 | 117.56
8.4.00 | FLOOR TILING
| 300 | x | 300 | Ceramic tiles
8.4.01 |  |  |  | GROUND FLOOR | m2 | 42.52
Toilets floor
| 300 | x | 300 | Ceramic Non-Slip tiles
8.4.02 |  |  |  | GROUND FLOOR | m2 | 6.24
toilet wall
| 300 | x | 300 | Ceramic Non-Slip tiles
8.4.03 |  |  |  | GROUND FLOOR | m2 | 38.1105
8.5.00 |  |  |  | TOTAL OF BILL №: 08 - Carried Over To Summary
9.0.00 |  |  |  | Bill №: 09 - PAINTING & DECORATIONS
9.1.00 | GENERAL
|  |  | (a) | Rates shall include for: the provision, erection and removal of scaffolding, preparation, wall putty application, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door & window furniture.
|  |  | (b) | All painting work shall be carried in accordance with the Specifications.
9.2.00 | PAINTING
WALL PAINTING
Emulsion paint finish including putty application on brick walls as specified (EXTERNAL SURFACES)
9.2.01 |  |  |  | GROUND FLOOR | m2 | 703.152
Emulsion paint finish including putty application on brick walls as specified (INTERNAL SURFACES)
9.2.03 |  |  |  | GROUND FLOOR | m2 | 355.585
CEILING PAINTING
Emulsion paint finish including putty application on brick walls as specified (INTERNAL & EXTERNAL SURFACES)
9.2.04 |  |  |  | GROUND FLOOR | m2 | 76.42
9.3.00 |  |  |  | TOTAL OF BILL №: 09 - Carried Over To Summary
10.0.00 |  |  |  | Bill №: 10 - HYDRAULICS AND DRAINAGE
10.1.00 | GENERAL
|  |  | (a) | Rates shall include for: sockets, running joints, connectors, elbows, junctions, valves, reducers, expansion joints; backnuts and similar; incidental fittings, clips, saddles, brackets, straps, hangers, screws, nails and fixing complete including cutting and forming holes; excavating, laying pipes and backfilling trenches.
|  |  | (b) | All pipe work and fittings shall be uPVC.
10.2.00 | COLD WATER SUPPLY
GROUND FLOOR
Rain Water Supply
10.2.01 |  |  | 25 | mm Dia Cold water supply PVC pipe | m | 34.118
10.2.02 |  |  | 16 | mm CWS to Basin Faucet | nr | 5
10.2.03 |  |  | 16 | mm CWS to Cistern | nr | 2
10.3.00 | SANITARY FITTINGS
GROUND FLOOR
10.3.01 |  |  |  | No. of toilets | nr | 2
10.3.02 |  |  |  | Water Closet | nr | 2
10.3.03 |  |  |  | Wash basin | nr | 2
10.3.04 |  |  |  | Wash basin tap | nr | 2
10.3.05 |  |  |  | Mirror | nr | 2
10.3.06 |  |  |  | Toilet paper holder | nr | 2
10.3.07 |  |  |  | Soap holder | nr | 2
10.3.08 |  |  |  | Muslim Shower | nr | 2
10.3.09 |  |  |  | Gate Valve | nr | 3
10.4.00 | SEWER AND WASTE WATER DRAINAGE SYSTEM
GROUND FLOOR
WASTE PIPE
10.4.01 |  |  | 40 | mm Dia. uPVC pipe | m | 18.145
10.4.02 |  |  | 82 | mm Dia. uPVC pipe | m | 10.02
SOIL PIPE
10.4.03 |  |  | 110 | mm Dia uPVC pipe | m | 11.911
RAIN WATER PIPE
10.4.04 |  |  | 82 | mm Dia.uPVC pipe | m | 32.36
10.5.00 |  |  |  | TOTAL OF BILL №: 10 - Carried Over To Summary
11.0.00 |  |  |  | Bill №: 11 - MECHANICAL & ELECTRICAL SERVICES
11.1.00 | GENERAL
|  |  | (a) | Design, provide and install electrical network for the entire building complete in accordance to standards set by the local governing authority.
|  |  | (b) | The cost shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
|  |  | (c) | Rates for electrical isolators, conduits, fittings, equipment and similar items shall include for: all fixings to various building surfaces.
|  |  | (d) | A light fixture is measured as one point; switch end of wire is not included in the quantity.
|  |  | (e) | A point wiring for power points is measured (regardless of 1 gang, 2 gang etc) as one point for each socket outlet; other end of wire is not included in the quantity.
|  |  | (f) | All under ground cables directly buried in ground/run in trenches to be properly laid and covered with cable tiles/trench covers. Rate for under ground cables shall include for all necessary excavation, sand layers, concrete tiles, warning strips and back filling with approved quality earth properly compacted, hot dipped galvenized brackets for trenches, accessories, etc as applicable.
|  |  | (g) | The contractor shall provide a schedule of all builder's work in connection with details of such items as necessary, along with the tender.
|  |  | (h) | Rates for materials/ plants/ equipments not approved for duty free facilities to be quoted on duty paid basis.
|  |  | (I) | All equipments shall be guaranteed for a period of 12 months from the date of commissioning or date of practical completion of the project which ever later
|  |  | (J) | The rate shall include for insurance during handling, rehandling, transport, storage until ready for installation, delivery of equipments up to the point of installation and until handing over.
|  |  | (K) | The rates shall include for comprehensive maintenance during defects liability period of 12 months from the date of handing over
|  |  | (L) | Rate shall include for supply, installation, maintaining, testing and commissioning of the system for power and lighting according to drawings and specifications to working order.
|  |  | (m) | All materials, equipment wiring shall confirm to local codes, specifications, standards/latest I.E.E. regulations ( BS 7671 ).
11.2.00 | ELECTRICAL BOARDS
DISTRIBUTION BOX
11.2.01 |  |  |  | GROUND FLOOR |  | 1
11.3.00 | POINT WIRING AND FITTINGS
Rate shall include for supply & installation of cable, conduits for point wiring in concealed installations including switches, power outlet, isolators, etc, all as specified
11.3.01 |  |  |  | Supply and Installation of 2 x 1C 1.5mm2 PVC/PVC/Cu + 2.5mm2 PVC/Cu earth cable c/w uPVC conduit, junction boxes etc. for light point wiring | nr | 57
11.3.02 |  |  |  | Supply and Installation of 2 x 1C 2.5mm2 PVC/PVC/Cu + 2.5mm2 PVC/Cu earth cable c/w uPVC conduit, junction boxes etc. for following Socket outlet/isolator point wiring | nr | 62
Wiring points
11.4.00 | SOCKETS
GROUND FLOOR
11.4.01 |  |  | 13 | A Twin socket Outlet 1200 | nr | 5
11.4.02 |  |  | 13 | A Twin socket Outlet 300 | nr | 26
11.4.03 |  |  | 15 | A SWITCHED/SPUR UNIT@H.L | nr | 5
11.4.04 |  |  |  | Computer Network Outlet (RJ 45 Connectors) | nr | 7
11.4.05 |  |  |  | Telephone Outlet (RJ11,Connector) | nr | 5
11.4.06 |  |  |  | TPN Isolator | nr | 10
11.4.07 |  |  |  | TV Points | nr | 4
11.5.00 | SWITCHES AND LIGHTING
GROUND FLOOR
11.5.01 |  |  |  | Gate Lamp | nr | 2
11.5.02 |  |  |  | Ceiling Down Light(18W) | nr | 16
11.5.03 |  |  |  | Recessed Down Light(13W) | nr | 4
11.5.04 |  |  |  | Ceiling Light | nr | 2
11.5.05 |  |  |  | 2 FT Tube Light | nr | 14
11.5.06 |  |  |  | Ceiling Fan | nr | 2
11.5.07 |  |  |  | Emergency Light | nr | 3
11.5.08 |  |  |  | Flex Power Outlet | nr | 3
11.5.09 |  |  |  | 1 Gang Light Switch | nr | 5
11.5.10 |  |  |  | 2 Gang Light Switch | nr | 2
11.5.11 |  |  |  | 3 Gang Light Switch | nr | 4
11.5.12 |  |  |  | Ceiling Fan switch with Dimmer | nr | 2
11.6.00 | AIR CONDITIONERS
GROUND FLOOR
11.6.01 |  |  |  | Single Split AC 9000BTU | nr | 2
|  |  |  | Single Split AC 14000BTU | nr | 3
11.7.00 | OTHERS
GROUND FLOOR
11.7.01 |  |  |  | Ceiling Mounted Exhaust Fan 90M3 | nr | 2
|  |  |  | Wall mounted Exhaust Fan | nr | 1
11.8.00 |  |  |  | TOTAL OF BILL №: 06 - Carried Over To Summary
12.0.00 |  |  |  | Bill №: 12 - ROOFING
12.1.00 | GENERAL
|  |  | (a) | Rates shall include for: fair edges, dressing over angel fillets, roof sealant, turning into grooves, all other labours, circular edges, nails, screws and other fixings and laps.
12.2.00 | MAIN ROOF COVERING
12.2.01 |  |  |  | Lysaght Roofing | m² | 146.4
12.2.02 |  |  |  | Mineral Wool Insulation in between Purlins | m² | 146.4
ROOF TRUSS
12.2.03 |  |  |  | 50x150mm Timber Rafters @900c/c | m² | 146.4
12.2.04 |  |  |  | 50x38mm Timber Purlins @ 600 c/c | m² | 146.4
12.2.05 |  |  |  | 25x250mm Timber Fascia Board | m | 28.35
Gutter
12.2.06 |  |  |  | 25x250mm Lysaght Gutter | m | 28.35
12.3.00 |  |  |  | TOTAL OF BILL №: 12 - Carried Over To Summary

## 04 Proviosional Sum
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
04 PROVISIONAL SUMS
Male', Republic of Maldives
BILL OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PROVISIONAL SUMS
A Maximum of MVR 1,000,000.00
1.2.00 | TOTAL OF PROVISIONAL SUMS - Carried Over To Summary

## Daywork Summary
SUMMARY OF BILLS OF QUANTITIES
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
DAYWORKS
| DESCRIPTION | AMOUNT (MRF) | %
DAYWORK 01 - LABOUR
DAYWORK 02 - MATERIALS
DAYWORK 03 - CONSTRUCTION PLANT AND EQUIPMENT
| TOTAL AMOUNT | 0

## Daywork
SEWERAGE SYSTEM IN HDH.NOLHIVARANFARU
DAYWORKS
Male', Republic of Maldives
BILL OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
DAYWORK 01 - LABOUR
1.1.00 | Labourer | Hr | 100
1.2.00 | Dresser | Hr | 100
1.3.00 | Mason | Hr | 100
1.4.00 | Carpenter | Hr | 100
1.5.00 | Plumber | Hr | 100
1.6.00 | Electrician | Hr | 100
1.7.00 | Plumber | Hr | 100
1.8.00 | Electrician | Hr | 100
1.9.00 | Steel reinforcement erector | Hr | 100
1.10.00 | Driver for vehicle up to 10 tons | Hr | 100
1.11.00 | Driver for 10 ton dump truck | Hr | 100
1.12.00 | Operator for excavator shovel | Hr | 100
1.13.00 | Operator for tractor, (tracked) with dozer blade or ripper | Hr | 100
1.14.00 | Operator for Mixer Machine/Lift Machine | Hr | 100
1.15.00 | Helper for heavy machinery | Hr | 100
1.16.00 | Skilled labour for the Engineer’s use | Hr | 100
1.17..00 | Unskilled labour for the Engineer’s use | Hr | 100
Subtotal
1.18.00 | Allow 10 percent of Subtotal for Contractor’s overhead, profit, etc
1.19.00 | TOTAL OF DAYWORK 01 LABOUR - Carried Over To Summary
DAYWORK 02 - MATERIALS
2.1.00 | Cement, Ordinary Portland in bags | Tonne | 1
2.2.00 | Cement, SRC Portland in bags | Tonne | 1
2.3.00 | Epoxy Coated Steel reinforcement Bars (High Yield) | Tonne | 1
2.4.00 | Steel reinforcement Bars (High Yield) | Tonne | 1
2.5.00 | Steel reinforcement Bars (Mild) | Tonne | 1
2.6.00 | Fine aggregate for concrete as specified. | Tonne | 1
2.7.00 | Coarse aggregate for concrete as specified | Tonne | 1
2.8.00 | TOTAL OF DAYWORK 02 MATERIALS - Carried Over To Summary
DAYWORK 03 - CONSTRUCTION PLANT AND EQUIPMENT
3.1.00 | Excavator, face shovel Up to and including 1 Cu. M. | Hr | 100
3.2.00 | Excavator, face shovel over 1 Cu. M. to 2 Cu. M. | Hr | 100
3.3.00 | Tractor (tracked) including bull or angle dozer: Up to and including 150 HP | Hr | 200
3.4.00 | Tractor (tracked) including bull or angle dozer: Up to and including 150 HP | Hr | 100
3.5.00 | Tractor (tracked) including bull or angle dozer: Over 150 150 HP to 200 HP | Hr | 50
3.6.00 | Tractor (tracked) with ripper up to and including 200 HP | Hr | 75
3.7.00 | Vibratory roller 10 tons. | Hr | 75
3.8.00 | Smooth drum roller 10-12 Tons | Hr | 200
3.9.00 | Motor grader | Hr | 200
3.10.00 | 10 Ton dump truck | Hr | 75
3.11.00 | Transit Mixer 4 Cu.M. | Hr | 50
3.12.00 | P.T.R. (9-Wheeler) 18 Tons | Hr | 50
3.13.00 | Paver 4m wide | Hr | 50
3.14.00 | Concrete Mixer/Concrete Lift Machine | Hr | 25
3.15.00 | Vibrator 1-1/2" Dia | Hr | 200
3.16.00 | Water Bowser | Hr | 150
3.17..00 | Plate Compactor | Hr | 100
3.18.00 | Compressor 300 cfm | Hr | 100
3.19.00 | TOTAL OF DAYWORK 03 - CONSTRUCTION PLANT AND EQUIPMENT Carried Over To Summary