## Summary_BOQ_WSP Nolhivaranfaru
Water Supply Facilities in Hdh. Nolhivaranfaru, Maldives
SUMMARY OF BOQ
Bill No. | INDEX | AMOUNT | REMARKS
I | GENERAL AND PRELIMINARIES | 0
II | WATER SUPPLY CONVEYANCE SYSTEM; LENGTH: 1548.00M | 0
III | WATER SUPPLY DISTRIBUTION NETWORK; LENGTH: 16792.00M | 0
IV | ULTRAFILTER; CAPACITY- 40 CUM/DAY/UNIT | 0
V | RAIN WATER COLLECTION / LIFT WELL; CAPACITY - 50 CUM; SIZE: 7.0m Dia x 2.00m Depth | 0
VI | RAW WATER TANK CAPACITY-700 CUM | 0
VII | CLEAR WATER TANK; CAPACITY - 300 CUM. | 0
VIII | BORE/TUBE WELL; 35.00M DEPTH & 200MM DIA; 1NO. | 0
VIII-A | RO (REVERSE OSMOSIS) UNIT; CAPACITY- 45.00 CUM/DAY | 0
VIII-B | BRINE DISPOSAL; Length: 300.00M; 110MM DIA | 0
IX | MECHANICAL WORK | 0
X | ELECTRICAL WORK | 0
XI | SOLAR ENERGY SYSTEM | 0
XII | FACILITY BUILDING | 0
XIII | SUPPLY OF O&M EQUIPMENT AND SPARES | 0
XIV | LABORATORY EQUIPMENT | 0
XV | TESTING AND COMMISSIONING | 0
XVI | ADDITIONS | 0
XVII | OMISSIONS | 0
| TOTAL | 0

## 1.1-Valve Specials (hidden)
Water Supply Facilities in Ha. Kelaa, Maldives
Details of All Valves with Dia, Nos., K12 Specials, DI Pipe Length
Sr. No. | Discription | Data | [14 empty] | Remarks
1 | SLUICE VALVE | [15 empty] | #REF!
| Valve Dia (mm) | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | #REF! | #REF! | #REF! | #REF! | #REF!
| K-12 (2 nos. Reducer) Specials Required for fixing the valve (QTL) | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wt. of 2 nos. Reducer Taken from Jindal Brousher-Engineering Data-Pipe Fittings
| Length of D/F DI Pipes (K-9) (m) | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Butterfly Valve | [15 empty] | 0
| Valve Dia (mm) | - | - | - | - | - | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| K-12 (2 nos. Reducer) Specials Required for fixing the valve (QTL) | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wt. of 2 nos. Reducer Taken from Jindal Brousher-Engineering Data-Pipe Fittings
| Length of D/F DI Pipes (K-9) (m) | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | SCOUR VALVE
| Valve Dia (mm) | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | 0 | 0 | 0 | 0 | 0
| K-12 (01 no.Tee+2 no. Tail Piece+01 no. Reducer) Specials Required for fixing the valve (QTL) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Length of D/F DI Pipes (K-9) (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | AIR VALVE | [15 empty] | #REF!
| Valve Dia (mm) | 50 | 50 | 80 | 100 | 150 | 200
| Main /Pipe Diameter (mm) | 63-100 | 110-150 | 160-200 | 225-250 | 280-300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | #REF! | #REF! | #REF! | #REF! | #REF! | 0
| K-12 (01 no.Tee+2 no. Tail Piece+01 no. Reducer) Specials Required for fixing the valve (QTL) | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | [9 empty] | Wt. of (01 no.Tee+2 no. Tail Piece+01 no. Reducer) Taken from Jindal Brousher-Engineering Data-Pipe Fittings
| Length of D/F DI Pipes (K-9) (m) | #REF! | #REF! | #REF! | #REF! | #REF! | 0
SUMMARY OF SPECIALS & PIPE/TAIL PIECE
Sr. No. | Discription |  |  | Dia | Unit | Qty.
A | Specials K - 12
1 | Specials K - 12 |  |  | Upto 300 mm | Qtl | #REF!
2 | Specials K - 12 |  |  | Above 300 mm | Qtl | 0
B | Double Flanged DI Pipe K-9
1 | DI Pipe K - 9 |  |  | 50 | m
2 | DI Pipe K - 9 |  |  | 80 | m
3 | DI Pipe K - 9 |  |  | 100 | m | #REF!
4 | DI Pipe K - 9 |  |  | 150 | m | #REF!
5 | DI Pipe K - 9 |  |  | 200 | m | #REF!
6 | DI Pipe K - 9 |  |  | 250 | m | #REF!
7 | DI Pipe K - 9 |  |  | 300 | m | #REF!
8 | DI Pipe K - 9 |  |  | 350 | m | 0
9 | DI Pipe K - 9 |  |  | 400 | m | 0
10 | DI Pipe K - 9 |  |  | 450 | m | 0
11 | DI Pipe K - 9 |  |  | 500 | m | 0
12 | DI Pipe K - 9 |  |  | 600 | m | 0
13 | DI Pipe K - 9 |  |  | 700 | m | 0
14 | DI Pipe K - 9 |  |  | 750 | m | 0
15 | DI Pipe K - 9 |  |  | 800 | m | 0
16 | DI Pipe K - 9 |  |  | 900 | m | 0
17 | DI Pipe K - 9 |  |  | 1000 | m | 0

## BOQ.-WSP Nolhivaranfaru
Water Supply Facilities in Hdh. Nolhivaranfaru, Maldives
BILL OF QUANTITIES
Item No. | Description | Unit | Quantity | Material Rate | Labor Rate | Amount
I | GENERAL AND PRELIMINARIES | LS | 1
Contractual Requirements
1.1.1 | Provide & Maintain all necessary Insurances, Guarantees and Securities.
SPECIFIED REQUIREMENTS
1.2.1 | Provision of Engineer's Office | Item | LS
1.2.2 | Maintaining Engineer's Office | Month | 18
1.2.3 | Provision of Contractor's Office | Item | LS
1.2.4 | Provision of Contractor's Staff Accommodation | Item | LS
1.2.5 | Maintaining Contractor's Office | Month | 18
1.2.6 | Maintaining Contractor's Staff Accommodation | Month | 18
1.2.7 | Provision of adequately equipped Laboratory services as required for site control on the quality of materials and the works as per special specification. | Item | LS
1.2.8 | Maintaining the Laboratory services as required for site control of materials and works as per specification including all costs. | Month | 18
1.2.9 | Provision and Erection of Notice Boards 3m x 4m size as per drawing and specification, including complete cost and conveyance of materials, labour charges, & etc. | No. | LS
1.2.10 | Provision of photographs of important activities of the work during the progress of work as directed by the Engineer , including all costs, etc. | No. | LS
1.2.11 | Provision of video graph of the progress of works, one video tape not more than 30 minutes duration showing the progress during every month. | No. | LS
1.2.12 | Training of employer's nominees in operation and maintenance as per Employer's Requirement. | Item | LS
TEMPORARY WORKS
1.3.1 | Mobilize to site and maintain water bowsers to meet the drinking water needs of the households affected by dewatering of trenches. | Item | LS
1.3.2 | Arrange during dewatering of trenches, for pumping ground water of salinity greater than 2500 microsiemens to be pumped out to sea. | Item | LS
SITE PREPARATION
| Clearing grass, bushes, shrubs, saplings, uprooting rank vegetation all along the pipeline route and removal & disposal of rubbish to approved tips anywhere in the island as directed by the Engineer-in-charge. | Item | LS
Cutting of trees, including trunks, branching and removal of stumps, roots, stacking of serviceable materials with all lifts and up to all lead within project area and earth filling in the depression/pit, including excavation & backfilling.
| Girth size up to 300mm | No. | 60
| Girth size from 300mm to 600mm | No. | 60
| Dismantling of existing structures like pillars, walls, slabs and any other structure constructed of Brick or coral stone masonry, cement concrete, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material. | Item | LS
Removing tree stumps up to 600mm girth from the route of pipeline.
| Removal and relocation of electrical poles. | Item | LS
| Removal and relocation of telephone cables. | Item | LS
II | WATER SUPPLY CONVEYANCE SYSTEM; LENGTH: 1548.00M | M | 1548
A | For Civil Works
1 | CLEARING & GRABBING LAND
1.1 | Clearing and grubbing road land including uprooting rank vegetation, grass, bushes, shrubs, saplings and trees girth up to 300 mm, removal of stumps of trees cut earlier and disposal of unserviceable materials and stacking of serviceable material to be used or auctioned, up to a lead of 1000 meters including removal and disposal of top organic soil not exceeding 150 mm in thickness. | hectare | 0.3096
2 | BARRICADING
2.1 | Providing and erecting 2.00 metre high temporary barricading at site as per drawing/ direction of Engineer-in-Charge which includes writing and painting, arrangement for traffic diversion such as traffic signals during construction at site for day and night, glow lamps, reflective signs, marking, flags, caution tape as directed by the Engineer-in- Charge. The barricading provided shall be retained in position at site continuously i/c shifting of barricading from one location to another location as many times as required during the execution of the entire work till its completion. Rate include its maintenance for damages, painting, all incidentals, labour materials, equipment and works required to execute the job. The barricading shall not be removed without prior approval of Engineer-in-Charge. | RM | 154.8
3 | EARTH WORK IN EXCAVATION
3.1 | EXCAVATION IN CORAL/ORDINARY SOIL
3.1.1 | Earthwork excavation including clearing vegetation, shoring, strutting, and ramming with selected earth for preparing the bed, as per specification and drawing, for pipeline trenches. In all kinds of soil.
3.1.2 | Refilling pipeline trenches with selected available earth from trench excavation using mechanical vibration including watering, compaction of layers of 30cms, With all leads and lifts as per Specification & drawing and as directed by the Engineer.
3.1.3 | Disposal of the remaining soil after the back filling from the available soil to the general garbage yard as approved by the engineer. Spreading the same uniformly as per Specification & drawing and as directed by the Engineer.
3.1.4 | Open timbering in trenches including strutting and shoring complete (Measurements to be taken of the face area timbered).
1 | 0 to 0.50 m | cum | 536.04
2 | From 0.50 m to 1.00 m | cum | 915.98
3 | From 1.00 m to 1.50 m | cum | 0
4 | SAND BEDDING WITH LOCAL SAND
4.1 | Providing and Placing of granular non plastic sand filling for the sides of the pipe line and up to 100mm above the crown of the pipe including 150 mm bedding below the pipe as per Specification & drawings and as directed by the Engineer. | cum | 431.3293
5 | SUPPLY & LAYING OF PIPES
5.1 | Providing, lowering, laying, aligning, fixing in position at and jointing at all level/ depths ISI marked HDPE pipes of PE-100 grade & PN-6 for potable water as per IS 4984 (amended up to date) in trenches in complete including all material, labour, testing and commissioning as per Technical Specifications and as directed by the Engineer in Charge; including jointing at all level/ depths HDPE pipe accessories/ fittings of PE-100 grade & PN-6 for potable water as per IS 8360 for fabricated (amended up to date) within pipe line including Disinfecting C.I. water mains by flushing with water containing bleaching powder @ 0.5 gms per litre of water and cleaning the same with fresh water, operation to be repeated three times including getting the sample of water from the disinfected main tested in the municipal laboratory.
5.1.1 | 110 mm | m | 648
5.1.2 | 140 mm | m | 0
5.1.3 | 160 mm | m | 320
5.1.4 | 180 mm | m | 0
5.1.5 | 200 mm | m | 60
5.1.6 | 250 mm | m | 40
5.1.7 | 280 mm | m | 0
5.1.8 | 315 mm | m | 480
6 | VALVES AND APPURTENANCES
6.1 | Supplying, delivering fixing and jointing at site flanged end Sluice / Gate valves as per Specification & drawings.
6.1.1 | 110 mm | No. | 6
6.1.2 | 160 mm | No. | 4
6.1.3 | 250 mm | No. | 1
6.1.4 | 315 mm | No. | 1
6.2 | Supplying, delivering fixing and jointing at site flanged end Wash out valve as per Specification & drawings.
6.2.1 | 63 mm | No. | 10
6.2.2 | 110 mm | No. | 0
6.2.3 | 140 mm | No. | 0
6.2.4 | 160 mm | No. | 0
6.2.5 | 180 mm | No. | 0
6.3 | Providing, lowering, laying, aligning, fixing in position and jointing in pipe line, dual plate Non Return / check valves of following dia (including jointing and jointing material), including all material, labour, testing and commissioning as per Technical Specifications and as per direction of Engineer.
6.3.1 | 110mm | No. | 12
6.3.2 | 160mm | No. | 8
6.3.3 | 63mm | No. | 10
6.4 | Supply and Installing Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
6.4.1 | 50 mm | No. | 0
6.4.2 | 63 mm | No. | 10
6.4.3 | 110 mm | No. | 28
6.4.4 | 140 mm | No. | 0
6.4.5 | 160 mm | No. | 12
6.4.6 | 180 mm | No. | 0
6.4.7 | 200 mm | No. | 0
6.4.8 | 250 mm | No. | 0
6.4.9 | 280 mm | No. | 1
6.4.10 | 315 mm | No. | 0
6.4.11 | 350 mm | No. | 1
6.5 | Providing, laying in position, jointing, hydraulic testing and commissioning of specials suitable for push on jointing including flanged special such as tees, bends, collars, tapers and caps etc. including cost of water required for testing etc. complete and as directed by the Engineer in Charge.
6.5.1 | Specials for Valves | MT | 0.55
7 | CONSTRUCTION OF CHAMBER FOR VALVES
7.1 | Construction of RCC Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum , including chamber cover & Frame
7.1.1 | Sluice Valve, Non Return Valve and Washout Valve Chamber
7.1.1.2 | 63 mm | No. | 10
7.1.1.3 | 110 mm | No. | 28
7.1.1.5 | 160 mm | No. | 12
7.1.1.9 | 280 mm | No. | 1
7.1.1.11 | 350 mm | No. | 1
8 | CONSTRUCTION OF THRUST BLOCKS
8.1 | Construction of RCC C25/20 grade thrust block for the bends and tees as specified below including earth wok to the required depth as per the drawing Back filling and disposal of the surplus soil after back filling with PCC of grade C20/20 as per Specification
8.1.1 | For Tee's
8.1.1.1 | 350x350 mm | cum | 1.1667
8.1.2 | For Bend's
8.1.2.1 | 350 mm-90degree | cum | 1.1667
9 | ROOF WATER HARVEST GUTTERS
9.1 | Providing and fixing on wall face un-plasticized-PVC (working pressure 4 kgf per sqm) rain water Gutters shape will be semi-circular or rectangular, V-shaped gutters as per specification including jointing with seal ring, leaving 10 mm gap for thermal expansion and as per direction of engineer in charge.
9.1.1 | Roof Catchment Area=0.3295*10000=329.6sqm and width 150 mm dia | m | 600
10 | ROOF WATER HARVEST DOWN PIPES
10.1 | Providing and fixing on wall face un-plasticized-PVC (working pressure 4 kgf per sqm) rain water pipes conforming to specification including jointing with seal ring, leaving 10 mm gap for thermal expansion and as per direction of engineer in charge.
10.1.1 | 90 mm @ 12 m for each Community Centre - 10 Nos. | m | 120
10.2 | Providing and fixing on wall face unplasticised -PVC molded fittings/accessories for unplasticised-PVC rain water pipes conforming to specification including jointing with seal ring, leaving 10 mm gap for thermal expansion.
10.2.1 | 90 mm Shoe, 2 Nos. for each house | No. | 40
10.2.2 | 90 mm 87.5 degree Bend, 2 Nos. for each house | No. | 40
10.2.3 | Automated first flush mechanism as per the detailed drawings. Including drainage and soil absorption or recharge pit / well recharge. - Considering 2 Nos. for each Community Centre | No. | 20
III | WATER SUPPLY DISTRIBUTION NETWORK; LENGTH: 16792.00M | M | 16792
A | For Civil Works
1 | CLEARING & GRABBING LAND
1.1 | Clearing and grubbing road land including uprooting rank vegetation, grass, bushes, shrubs, saplings and trees girth up to 300 mm, removal of stumps of trees cut earlier and disposal of unserviceable materials and stacking of serviceable material to be used or auctioned, up to a lead of 1000 meters including removal and disposal of top organic soil not exceeding 150 mm in thickness. | hectare | 3.36
2 | BARRICADING
2.1 | Providing and erecting 2.00 metre high temporary barricading at site as per drawing/ direction of Engineer-in-Charge which includes writing and painting, arrangement for traffic diversion such as traffic signals during construction at site for day and night, glow lamps, reflective signs, marking, flags, caution tape as directed by the Engineer-in- Charge. The barricading provided shall be retained in position at site continuously i/c shifting of barricading from one location to another location as many times as required during the execution of the entire work till its completion. Rate include its maintenance for damages, painting, all incidentals, labour materials, equipment and works required to execute the job. The barricading shall not be removed without prior approval of Engineer-in-Charge. | RM | 1679
3 | SUPPLY & LAYING OF PIPE LINE
Providing, lowering, laying & jointing of H.D.P.E. PIPES PE-100 GRADE; PN-6 pipes including fixing of complete components, such as bends, tees, tail pieces, reducers. Suitable for the pipeline etc., by fusion welding and giving satisfactory hydraulic test as per specification and drawing.
3.1 | EXCAVATION IN ORDINARY SOIL
3.1.1 | Earthwork excavation including clearing vegetation, shoring, strutting, and ramming with selected earth for preparing the bed level, as per the specification and drawing, for Pipeline trenches. In all kinds of soil.
3.1.2 | Refilling pipeline trenches with selected available earth from trench excavation using mechanical vibration including watering, compaction of layers of 30cms, With all leads and lifts as per Specification & drawing and as directed by the Engineer.
3.1.3 | Disposal of the remaining soil after the back filling from the available soil to the general garbage yard as approved by the engineer.
3.1.4 | Open timbering in trenches including strutting and shoring complete (Measurements to be taken of the face area timbered).
3.1.5 | Providing and Placing of granular non plastic sand filling for the sides of the pipe line and up to 100mm above the crown of the pipe including 150 mm bedding below the pipe as per Specification & drawings and as directed by the Engineer.
1 | 63 mm | m | 15110
2 | 75 mm | m | 275
3 | 90mm | m | 110
4 | 180mm | m | 1297
4 | VALVES AND APPURTENANCES
4.1 | Supply, delivery and fixing of brand new Tamper proof Kinetic Air Valves (Category 1) PN-1.6 with dimensions as per Specification & drawing conforming to BS 2494 and BS 4865 part I, as per Specification, drawings and as directed by the Engineer.
4.1.1 | 50 mm | No. | 2
4.2 | Supplying, delivering fixing and jointing at site flanged end Sluice / Gate valves as per Specification & drawings.
4.2.1 | 63 mm | No. | 13
4.2.2 | 180 mm | No. | 2
4.3 | Supplying, delivering fixing and jointing at site flanged end Wash out valve as per Specification & drawings.
4.3.1 | 63 mm | No. | 5
4.4 | Providing and fixing fire hydrant with all pipe connections, fittings and valves including construction of reinforced concrete fire hydrant chamber using C-30 grade concrete earth work to the required depth, back filling and disposal etc., complete as per the specification, drawing and as directed by the Engineer.
4.4.1 | 160 mm dia | No. | 2
4.5 | Supply and Installing Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
4.5.1 | 50 mm | No. | 2
4.5.2 | 80 mm | No. | 0
4.5.3 | 63 mm | No. | 18
4.5.4 | 180 mm | No. | 2
4.6 | Providing, laying in position, jointing, hydraulic testing and commissioning of specials suitable for push on jointing including flanged special such as tees, bends, collars, tapers and caps etc. including cost of water required for testing etc. complete and as directed by the Engineer in Charge. | MT | 0.502
5 | CONSTRUCTION OF CHAMBER FOR VALVES
5.1 | Construction of Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum
5.1.1 | Air Valve, Sluice valve and Washout Valve chamber
5.1.1.1 | 50 mm | No. | 2
5.1.1.2 | 63 mm | No. | 18
5.1.1.3 | 180 mm | No. | 2
6 | CONSTRUCTION OF THRUST BLOCKS
6.1 | Construction of RCC C25/20 grade Thrust block for the Ductile Iron bends as specified below including earth work to the required depth as per the drawing Back filling and disposal of the surplus soil after back filling with PCC of grade C20/20 as per Specification
6.1.1 | For Tee's -1No.
| 180 mm dia | cum | 0.5625
6.1.2 | For Bend's -2+2 No.
| 90º bend - 160 mm dia | cum | 1.05
7 | HOUSE SERVICE CONNECTIONS
7.1 | House Service Connection: Making House Service Connection from distribution main to property limit including (1) providing and fixing brass ferrule -1 No (2) Providing and fixing metal inserted compression female thread adapter (3) providing and fixing MDPE blue pipe PE-80 and 16 kg class confirming to ISO 4427 in required length -6 meter approx..(4) Providing and fixing compression elbow -2 Nos (5) Providing and fixing PVC ball valve with one side compression and another side female threaded -1 No .The work shall done as per detailed specifications and as per drawings complete with all lead and lift and as directed by the Engineer (6) Providing, installing and giving satisfactory field testing of AMR type water meter, horizontal inferential multijet type with magnetic drive and dry dial suitable for ambient 50º C temperature duly sealed against tampering complete with couplings at both ends and conforming to class B as per IS 779/1994 (VI Revision) with ISI mark along with manufacturer's test certificate and guarantee certificate, including cost of surface box for water meter and all other materials and labour including consumer survey.
7.1.1 | 18 mm | No. | 550
7.1.2 | 25 mm | No. | 20
IV | ULTRAFILTER; CAPACITY- 40 CUM/DAY/UNIT
| Supply, Transportation to site, lifting, installation, Testing, Commissioning of Ultrafiltration unit as per all relevant Codes, international practices and As per the Specification etc. complete and as per direction of Engineer In Charge including accessories such as water meters, pressure gauges all complete. | Job | 1
V | RAIN WATER COLLECTION / LIFT WELL; CAPACITY - 50 CUM; SIZE: 7.0m Dia x 2.00m Depth | No. | 1
1 | Providing a lift well pre-fabricated of size 50,000 litres, including one water meter, basket screen, etc all complete | No. | 1
1 | PUMPING MAIN from Collection well to RWT
Providing, lowering, laying & jointing of H.D.P.E. PIPES PE-100 GRADE; PN-6 pipes including fixing of complete components, such as bends, tees, tail pieces, reducers. Suitable for the pipeline etc., by fusion welding and giving satisfactory hydraulic test as per specification including Excavation, Refilling, Sand bedding etc. all complete.
The cost should include the cost of All earth works, including Barricading, Excavation, Bed Preparation, Pipe Welding, Back Filling, Disposal of Surplus Earth, Shoring & Strutting wherever necessary, Testing & Disinfection. Overflow drainage and recharge system Etc. all complete
| 180mm dia | RM | 25
VI | RAW WATER TANK CAPACITY-700 CUM | No. | 1
1 | Geotechnical Investigation, Providing, Transportation to site, lifting, installation and fixing to allocated places; Closed Top Vertical Flat Bottom Water Storage Tank; made of RTP (Rolled, Tapered Panel), LIQ Fusion 7000 FBE™ powder coated, bolted tank as manufactured by Tank Connection Affiliate Group. A) The cost shall be all inclusive of supply, erection and construction, all testing, disinfecting and commissioning of tank, Providing ladders with cage (Outside & Inside, as applicable), 600mm man way frame with cover, handrail, providing a mechanical float type water level indicator, Lift Lugs, Circular Cleanout, Skylight, Ventilation, Railings, Rungs etc. complete as per specification and relevant code and as per direction of engineer in charge. B) The Manufacturer shall follow all relevant Code and Specification etc. complete and produce all relevant information about the products before supply & Installation.
1.1 | 700,000 litres Capacity | No. | 1
A | Civil Works for Foundation
2 | REINFORCED CEMENT CONCRETE
2.1 | Providing and laying RCC of grade C35 including fabrication of high yield steel (fy = 415 MPa), as per Specification & drawing and as directed by the Engineer
| Foundation of Tank | cum | 171.0547
3 | Thermo-Mechanically Treated bars (FE-500)
3.1 | Foundation of Tank | MT | 17.1055
4 | VALVES AND APPURTENANCES
4.1 | Supplying, delivering fixing and jointing at site flanged end Wash out valve as per Specification & drawings.
| 80 mm | No. | 2
4.2 | Supplying, delivering fixing and jointing at site flanged end Sluice / Gate valves. as per Specification & drawings.
| 150 mm - Oulet | No. | 2
4.3 | Supply and Installing Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
| 150 mm | No. | 1
| 80 mm | No. | 1
4.4 | Providing, lowering, laying & jointing of H.D.P.E. PIPES PE-100 GRADE; PN-6 pipes including fixing of complete components, such as bends, tees, tail pieces, reducers. Suitable for the pipeline etc., by fusion welding and giving satisfactory hydraulic test as per specification and drawing.
The cost should include the cost of All earth works, including Barricading, Excavation, Bed Preparation, Pipe Welding, Back Filling, Disposal of Surplus Earth, Shoring & Strutting wherever necessary, Testing & Disinfection. Etc. all complete
4.4.1 | 80 mm (Washout Pipe) | m | 60
4.4.2 | 180 mm (Overflow Pipe) | m | 60
4.5 | CONSTRUCTION OF RCC CHAMBER
Construction of RCC Valve chamber C30 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum, Cover and frame.
| 80 mm | No. | 1
| 180 mm | No. | 1
5 | MISCELLANEOUS WORKS
5.1 | Lightening Arrester
| Providing and fixing in position lightening arrester set complete with 600mm x 600mm x 6mm thick G.I. earthing plate embedded below ground in earthling pit at 3.5 meter depth, G.I. strip of size 25mmx5mm thick from earthing plate to top of Over head tank, G.I. Finial made of GI bar 25mm dia and 2m long fixed on top of OH tank and connected to GI strip. The earthling set shall comply of IS:3043 complete in all respect as per specification and the direction of the Engineer. | set | 1
6 | FLOW MEASUREMENT
6.1 | Electromagnetic Flow Meter
Supply, installation, testing and commissioning of Electromagnetic Flow Meter etc. including all materials (excluding fittings) and making connection with existing pipeline required for Electromagnetic Flow Meter including cutting the existing pipe line etc. complete in all respect as per technical specification and as per direction of Engineer.
| 150 mm | No. | 2
6.2 | Ultrasonic level measuring sensor
| Providing, installing, testing and commission of Ultrasonic Level sensor with level window in the electrical panel for showing water level. | No. | 1
VII | CLEAR WATER TANK; CAPACITY - 300 CUM. | No. | 1
1 | Geotechnical Investigation, Providing, Transportation to site, lifting, installation and fixing to allocated places; Closed Top Vertical Flat Bottom Water Storage Tank; made of RTP (Rolled, Tapered Panel), LIQ Fusion 7000 FBE™ powder coated, bolted tank as manufactured by Tank Connection Affiliate Group. A) The cost shall be all inclusive of supply, erection and construction, all testing, disinfecting and commissioning of tank, Providing ladders with cage (Outside & Inside, as applicable), 600mm man way frame with cover, handrail, providing a mechanical float type water level indicator, Lift Lugs, Circular Cleanout, Skylight, Ventilation, Railings, Rungs etc. complete as per specification and relevant code and as per direction of engineer in charge. B) The Manufacturer shall follow all relevant Code and Specification etc. complete and produce all relevant information about the products before supply & Installation.
1.1 | 300,000 litres Capacity | No | 1
A | Civil Works for Tank Foundation
2 | REINFORCED CEMENT CONCRETE
2.1 | Providing and laying RCC of grade C 35/20 including fabrication of high yield steel (fy = 415 MPa), as per Specification & drawing and as directed by the Engineer
2.1.1 | Foundation of tank | cum | 69.2701
3 | THERMO-MECHANICALLY TREATED BARS (FE-500)
Reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete.
| Foundation of tank | MT | 6.927
4 | VALVES AND APPURTENANCES
4.1 | Supplying, delivering fixing and jointing at site flanged end Wash out valve as per Specification & drawings.
| 80 mm Washout | No. | 2
4.2 | Supplying, delivering fixing and jointing at site flanged end Sluice / Gate valves as per Specification & drawings.
| 225 mm (Pipe outlet) | No. | 2
4.3 | Supply and Installing Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
4.3.1 | 80 mm (Washout Pipe) | Nos. | 1
4.3.2 | 225 mm (Pipe outlet) | Nos. | 1
4.4 | Providing, lowering, laying & jointing of H.D.P.E. PIPES PE-100 GRADE; PN-6 pipes including fixing of complete components, such as bends, tees, tail pieces, reducers. Suitable for the pipeline etc., by fusion welding and giving satisfactory hydraulic test as per specification and drawing. |  | 0
The cost should include the cost of All earth works, including Barricading, Excavation, Bed Preparation, Pipe Welding, Back Filling, Disposal of Surplus Earth, Shoring & Strutting wherever necessary, Testing & Disinfection. Etc. all complete
4.4.1 | 80 mm (Washout Pipe) | m | 30
4.4.2 | 150 mm (Overflow Pipe) | m | 30
4.5 | Construction of Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum including chamber cover and frame
4.5.1 | 80 mm | Nos. | 1
4.5.2 | 225 mm | Nos. | 1
5 | MISCELLANEOUS WORKS
5.2 | LIGHTENING ARRESTER
| Providing and fixing in position lightening arrester set complete with 600mm x 600mm x 6mm thick G.I. earthing plate embedded below ground in earthling pit at 3.5 metre depth, G.I. strip of size 25mmx5mm thick from earthing plate to top of Over head tank, G.I. Finial made of GI bar 25mm dia and 2m long fixed on top of OH tank and connected to GI strip. The earthling set shall comply of IS:3043 complete in all respect as per specification and the direction of the Engineer. | Job | 1
6 | FLOW MEASUREMENT
6.1 | Electromagnetic Flow Meter
Supply, installation, testing and commissioning of Electromagnetic Flow Meter etc. including all materials (excluding CI/ fittings) and making connection with existing pipeline required for Electromagnetic Flow Meter including cutting the existing pipe line etc. complete in all respect as per technical specification and as per direction of Engineer.
6.1.1 | 110 mm (Inlet) | No. | 1
6.1.2 | 225 mm (Outlet) | No. | 1
6.2 | ULTRASONIC LEVEL SENSOR
6.2.1 | Providing, installing, testing and commission of Ultrasonic Level sensor with level window in the electrical panel for showing water level. | No. | 1
VIII | BORE/TUBE WELL; 35.00M DEPTH & 200MM DIA; 1NO. | No. | 1
1 | DRILLING OF BORE HOLE | LS
1.1 | Drilling of perfectly vertical bore hole of following diameters for construction of gravel packed tube well up to desired depth in all type of formation consisting of soils, sans, clays, gravels, moorum, boulders etc. and retaining the bore hole by using suitable drilling mud or foam or temporary housing pipe including all works pertaining to drilling such as transportation, installation and removal of drilling machine and arrangement of water etc. complete and as per direction of engineer in charge.
2 | CASING PIPE
2.1 | Supplying, assembling, lowering and fixing in vertical position in bore well, plain ended uPVC casing pipes of required dia, of reputed & approved make, including required hire & labour charges, fittings & accessories, cost of providing and fixing of centraliser, and transportation of casing assembly etc. all complete, for all depths, as per direction of Engineer-in-charge.
2.1.1 | 100 mm
2.2 | Supplying, assembling, lowering and fixing in vertical position in bore well, slotted / screened uPVC casing pipes (having slot of size 1.5/3.0 mm) of required dia, of reputed & approved make, including required hire & labour charges, fittings & accessories, cost of providing and fixing of centraliser, and transportation of casing assembly etc. all complete, for all depths, as per direction of Engineer-in-charge.
2.2.1 | 75 mm
3 | GRAVEL PACKING
3.1 | Gravel packing in tube well construction in accordance with IS : 4097, including providing gravel fine/ medium/ coarse, in required grading & sizes as per actual requirement, all complete as per direction of Engineer-in-charge.
4 | DEVELOPMENT OF TUBEWELLS
4.1 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor 250 PSI, running the compressor for required time till well is fully developed, measuring yield of well by “V” notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water samples & getting tested in approved laboratory, i/c disinfection of tube well, all complete, including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge.
5 | MISCELLANEOUS
5.1 | Providing and fixing uPVC Bail plug / Bottom plug of required dia to the bottom of pipe assembly of tube well as per standard specification etc. complete and as per direction of engineer in charge.
5.1.1 | 100 mm
5.2 | Providing and fixing M.S. clamp of required dia to the top of casing/housing pipe of tube well as per IS: 2800 (part I), including necessary bolts & nuts of required size as per standard specification etc. complete and as per direction of engineer in charge.
5.2.1 | 100 mm
5.3 | Providing and fixing suitable size threaded uPVC well cap to the top of bore well housing/ casing pipe, removable as per requirement, all complete as per standard specification etc. complete and as per direction of engineer in charge.
5.3.1 | 100 mm
6 | Water Sample Tests
6.1 | Water Quality Analysis– Collecting representative sample and Physical & Chemical testing of Parameter from NABL approved laboratory as per CPHEEO manual: PH, TDS, Taste & Odor, turbidity, magnesium, Total hardness, total alkalinity, chloride, sulphate, nitrate, fluoride, Calcium, Iron, Pesticide, Manganese, Cooper, Aluminum, Residual Chlorine, Zinc, phenolic compound, Arsenic, Cadmium, Chromium, cyanides, lead, selenium, Mercury.
VIII-A | RO (REVERSE OSMOSIS) UNIT; CAPACITY- 45.00 CUM/DAY
1 | Supply, Transportation to site, lifting, installation, Testing, Commissioning of Reserve Osmosis (RO) Plant as per all relevant Codes, international practices and As per the Specification etc. complete with Water Meters and as per direction of Engineer In Charge with the following capacity;
| 45 Cum/Day Capacity | No. | 2
VIII-B | BRINE DISPOSAL; Length: 300.00M; 110MM DIA | No. | 1
1 | SUPPLY & LAYING OF PIPE LINE
1.1 | Providing, lowering, laying fusion welded HDPE PIPE PE-100 GRADE; PN-16 pipe including all necessary excavation, bedding and trench filling from brine collection well to sea bed level | m | 50
1.2 | Providing, lowering, and installing in place brine collector chamber of 100mm dimeter including all necessary excavation, bedding and trench filling. | No. | 1
1.3 | Providing, lowering, laying fusion welded H.D.P.E. PIPE PE-100 GRADE; PN-16 pipe, in the sea including marine survey and methodology statement for approval and all necessary excavation, concrete surround, stainless steel straps and rock anchors to diffuser outlet. giving satisfactory hydraulic test as per specification and drawing. | m | 300
1.4 | Supply & installation of diffuser at end of outfall | No. | 1
IX | MECHANICAL WORK
1 | SUPPLY AND INSTALL CENTRIFUGAL SPLIT CASTING PUMP SETS WITH MOTOR
1.1 | Supply, delivery at site with necessary packing, receiving, unloading, shifting, storing, installation, testing and commissioning of Horizontal Centrifugal Split Casing pumps with motor, casing and delivery pipes and casing ring, SS 316 impeller, SS 410 Shaft and shaft sleeve, coupling guard, common base plate, foundation bolts etc. complete with all respect as per the specification.
1.1.1 | Disrtibution Pumps: 10 cum/hr, 20M Head; (1W +1 S) =2 Nos. | Nos. | 2
1.1.2 | For RWT to Ultra Filter: 40 cum/day, 10m Head; (1W +1 S) =2 Nos. | Nos. | 2
1.1.3 | For Brine Disposal: 17.5 cum/hr, 25m Head; (1W +1 S) = 2 Nos. | Nos. | 2
1.1.4 | Rain water Lifting Pumps 47.5 cum/hr, 20m Head; (3W +1 S) = 4 Nos. | Nos. | 4
1.1.5 | Ultra Filter to Treated water Tank: 40 cum/day, 10m Head; (1W +1 S) =2 Nos. | Nos. | 2
1.1.6 | RO Plant to Treated water Tank: 90 cum/day, 12m Head; (1W +1 S) =2 Nos. | Nos. | 2
1.1.7 | Fire Fighting Pumps: 72 Cu.m/hr, 20m head (1W +1S) = 2 Nos. | Nos. | 2
SUBMERSIBLE PUMP SETS WITH MOTOR
1.2 | Supply, Install, Testing and Commissioning of specification and relevent code, submersible Pumping Sets comprising of Submersible Motor of sufficient horse-power coupled to a Pump of required duty conditions with water cooling with 415V, 3000/1500 rpm and as per specification with following duty conditions; etc. complete with all electrical and other control mechanisms and accessaries as per the specification.
1.2.1 | For Bore Well (400 cum/day), 40m Head | Nos. | 1
2.0 | Supplying, delivering fixing and jointing at site flanged end Sluice / Gate valves. as per Specification & drawings.
2.1 | 65 mm | Nos. | 17
2.2 | 110 mm | Nos. | 4
2.3 | 180 mm | Nos. | 11
2.4 | 225 mm | No. | 7
3 | Providing, lowering, laying, aligning, fixing in position and jointing in pipe line, dual plate Non Return/check valves of following dia (including jointing and jointing material), including all material, labour, testing and commissioning as per Technical Specifications and as per direction of Engineer.
3.1 | 65 mm | Nos. | 8
3.2 | 110 mm | Nos. | 2
3.3 | 180 mm | Nos. | 4
3.4 | 225 mm | No. | 2
4.0 | Supply and Installing Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
4.1 | 65 mm | Nos. | 25
4.2 | 110 mm | Nos. | 6
4.3 | 180 mm | Nos. | 15
4.4 | 225 mm | No. | 9
5.0 | Construction of Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum including chamber cover & Frame
5.1 | For 65mm dia Sluice Valve & NRV | Nos. | 24
5.2 | For 110mm dia Sluice Valve & NRV | Nos. | 6
5.3 | For 180mm dia Sluice Valve & NRV | Nos. | 15
5.4 | For 225mm dia Sluice Valve & NRV | No. | 9
6.0 | Providing, installation, testing and commissioning of Electromagnetic Flow Meter etc. including all materials (excluding CI/ fittings) and making connection with existing pipeline required for Electromagnetic Flow Meter including cutting the existing pipe line etc. complete in all respect as per technical specification and as per direction of Engineer.
6.1 | 65 mm | Nos. | 2
6.2 | 110 mm | Nos. | 1
6.3 | 225 mm | Nos. | 1
7 | Providing, installing, testing and commission of Ultrasonic Level sensor with level window in the electrical panel for showing water tank etc. and as per direction of engineer in charge. | Nos. | 1
8 | Providing, installation, testing and commissioning of glycerin filled Pressure gauge (0-10 kg/cm2) of following ranges with isolation valve and tap off pipe complete in all respect as per technical specification and as per direction of Engineer. | Nos. | 1
9 | Providing, installing, testing and commissioning of Pressure transmitters (0 - 10 bar) in delivery pipes and as per direction of Engineer. | Nos. | 1
10 | ELECTRO-CHLORINATOR
10.1 | Providing, erecting, commissioning & giving test & trial for a period of one month including one year free maintenance after commissioning of Electro chlorinator capable of generating chlorine form common salt by electrolysis using electrodes in form of sodium hypo chlorite solution containing 6-8 gms/lit of available chlorine in batch or continuous process and capable of providing 8 hrs. storage of hypochlorite in case of power failure. The electro chlorinator shall comprise of following 1. Electrolytic cell consisting dimensionally stable electrodes made from Gr I Titanium sheet with multi metal Oxide coating. 2. Electolyzer tank made from PVC -FRP or Acrylic.3. Power pack consisting of transformer rectifier for generating suitable DC current from AC supply along with the control switch for dosing pumps, etc. through MCB's contacts, relays and wiring. 4. Control panel for the electro chlorinator consisting of DC voltage and current display income phase status unit on-off switches fuses etc. 5. Dosing tank of suitable capacity made from PVC/FRP. 6. Dosing pumps of special quality (1W+1S) suitable to handle hypo chlorite solution. 7. Entire chlorine solution pipeline shall be of PVC. Chlorine test kit suitable to measure residual chlorine up to 5PPM.
10.1.1 | 50 grams/hr (1+1 Spare) | Job | 2
X | ELECTRICAL WORK | Job | 1
1 | 11 KV SUB STATION
1.1 | 4- POLE STRUCTURE WITH 1 INCOMER & 2 OUTGOING | LS | 1
1.1.1 | Supply, Installation, Testing and Commissioning of 4.Pole. Structure With AIR BREAK SWITCH having following specifications: 1. 4P :Four pole structure on 4No. ISMB 125mm 10 mtr high pole or 4No. PCC pole 10 mtr high using 4 No. MS channel each of size 75mmx50mmx2500mm complete in all respect with nuts, springs washers, clamps as required.2. GO: Off load type gang operated 3-pole vertical flute type switch suitable for 11KV ; 400A ,3-ø, central post rotating double break isolator complete with MS hardware , copper moving & fixed contact ,assembly of insulator, GI pipe of suitable length for operation. 3. DO: Vertical / Horizontal mounted 11kv horn gap fuse set /drop out 11kv barrel fuses mounted on pin insulators. 4. LA:3 piece non linear resistor type. lighting arrestor of approved make suitable for 3 wire, 11kv oh line with rated voltage of 9kv rms & nominal discharge current rating of 5 ka & complete with galvanized clamping arrangement GI bolts, nuts, washer etc. as required. 5. JUMPERS: 11kv arcs conductors mounted on pin type insulators as required. 6. GENERAL: The go shall be operated by hand operated liver properly earthed with provision for locking mounted including getting approval from Electrical Inspector.
2 | H.T. PANEL
2.1 | OUTGOING PANEL
2.1.1 | Manufacture, supply, installation, testing and commissioning of 250 MVA, 11 KV indoor type, draw out, Vacuum circuit breaker Panel board fabricated out of minimum 2 mm thick CRCA sheet as per following specifications. The panel shall be complete work 1. 1 No. 11 KV, 630 A, 250 MVA Electrical draw out type vacuum circuit breaker (with ON/OFF/TRIP/Serve/Test position indication). 2. 2 sets of ammeter with 3 way ON and OFF selector switch and CT’s 30/5 A, CL-1, 15VA. 3. Two sets of IDMT & Instantaneous O/C and IDMT E/F relay complete with 4 No. ( 1 set) current transformers 630/1A, CL-5 P 10 for protection, 15 VA burden. | LS | 1
2.1.2 | Supply, Installation, Testing & Commissioning of HT metering cubical panel as approved By DISCOMs fabricated out of 14 SWG CRCA sheet steel in two compartment & MS angle of size 60mmX6mm having provision for Following: (i) Provision for fixing Trivector Meter (To be supplied by DISCOMs) (ii) Provision for fixing of combined CT PT Set (To be supplied by DISCOMs), (iii) TT Block, (iv) 6mm Bakelite sheet on all sides. | LS | 1
3 | TRANSFORMER (1W+1S)
3.1 | Supply, receiving, storing, inspection, handling , assembling ,installing in correct aligned position, effecting proper connections, testing and commissioning of out door type oil filled, off circuit tap changer (OCTC) transformer with the following specification and confirming to IS 2026( Part 1-5) No. of phases / frequency : 3 Phases/ 50 Hz - No Load Voltage ratio : 11/0.433 kV.
3.1.1 | 63 kVA | LS | 1
4 | SF of rubber matting with one side corrugated as per IS specification 15652/2006 | LS | 1
5 | BATTERY & BATTERY CHARGER FOR DC SUPPLY
5.1 | SITC of FCBC ( Float cum boost charger)suitable for 415V +/-10%, 50 Hz , 1-ǿ / 3 -ǿ Input & 24/ 48 /110 V DC Output Natural Cooled, free standing in Sheet Steel enclosure, SCR controlled, regulation +/-1% , Efficiency > 75% on FLAC/ DC Instruments, Selector Switch ,Built in DC Distribution Board (6 No MCB), indication, control as required of following rating: 20A+20A | LS | 1
5.2 | SITC of battery bank of min 150 AH capacity comprising SMF/VRLA batteries, MS / Teakwood battery stand, interconnect wiring etc. as required complete in all respect of rating: 48 V DC | LS | 1
5 | HT CABLE WITH ACCESSORIES
6.1 | Providing & Laying XLPE insulated IS:7098/II/85 of approved make H.T. cable for working voltage 11 K.V. Earthed direct in ground including excavation of 30cmx100cm size trench, 25cm layer of river sand, IInd class bricks covering, refilling earth, compaction of earth, making necessary connection testing etc.as required of size.
6.1.1 | 3C X 70 Sqm | LS | 1
6.1.2 | 3C X 35 Sqm | LS | 1
6.2 | Providing & making heat shrinkable type indoor/outdoor/straight through terminations/joint kit of approved make suitable for XLPE insulated 11 KV cable, with required components, preparation of cable ends, testing etc. as required
6.2.1 | 3x70 sq.mm cable I.D. termination
6.2.2 | 3x70 cable O.D. termination
6.2.3 | 3x70 cable Straight through
7 | EARTHING FOR SUBSTATION
7.1 | Plate Earthing as per IS:3043 with G.I. Earth plate of size 600mm x 600mm x 6.0mm by embodying 3 to 4 mtr. below the ground level with 20 mm dia. G.I. 'B' class watering Pipe including all accessories like nut, bolts, reducer, nipple, wire meshed funnel, and C.C. finished chamber covered with hinged type with locking arrangement C.I. Cover, C.I. Frame of size300mm x 300mm complete with alternate layers of salt and coke/charcoal, testing of earth resistance as required. | LS | 1
7.2 | S & Laying 25x6 mm size GI earth strip in horizontal or vertical run in ground/surface/recess including riveting, soldering, saddles, making connection etc. as required. | LS | 1
7.3 | S & Laying 6 SWG size GI earth wire in horizontal or vertical run in ground/surface/recess including riveting, soldering, saddles, making connection etc. as required. | LS | 1
8 | LT PANEL - PMCC
8.1 | Supply, Install, Testing and commissioning of wall/free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly painted by two coats of zinc/red oxide primer followed by Powder coated / epoxy / PU painted with phosphatisation in grey or required shade after rinsing. The panel having PU/Neoprene rubber gasket of not less than 3mm thickness, separate detachable, gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6mm up to 600mm length/width of any compartment and be of 2.0mm above 600mm. Load bearing structure shall be of 2.0mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with detachable extension type structure with 1). aluminum bus bar, 2). 3 nos of 4-pole air circuit breaker, 3). 100A MCCB for chlorinator, 4). 63A MCB, 5). 6 nos of 630A MCCB with CT, PT, ammeter, voltmeter, Phase indication lamp 6). Capacitor bank with required contactors, etc.. With 6 nos of 125KW Soft Starters for Clear Water Reservoir & with 3 nos of Star Delta Starter for Tube wells at ITI | LS | 1
8.2 | Supply, Install, Testing and commissioning of wall/free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly painted by two coats of zinc/red oxide primer followed by Powder coated / epoxy / PU painted with phosphatisation in grey or required shade after rinsing. The panel having PU/Neoprene rubber gasket of not less than 3mm thickness, separate detachable, gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6mm up to 600mm length/width of any compartment and be of 2.0mm above 600mm. Load bearing structure shall be of 2.0mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with detachable extension type structure with 1). aluminum bus bar, 2). 4-pole air circuit breaker for Lighting, 3). 100A MCCB for chlorinator, 4). 63A MCB for accessories, 5). MCCB of required capacity with CT, PT, ammeter, voltmeter, Phase indication lamp 6). Capacitor bank with required contactors, etc.. | LS | 1
9 | PANEL | LS | 1
9.1 | Supply, Install, Testing and commissioning of wall/free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly painted by two coats of zinc/red oxide primer followed by Powder coated / epoxy / PU painted with phosphatisation in grey or required shade after rinsing. The panel having PU/Neoprene rubber gasket of not less than 3mm thickness, separate detachable, gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6mm up to 600mm length/width of any compartment and be of 2.0mm above 600mm. Load bearing structure shall be of 2.0mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with detachable extension type structure with aluminum bus bar, 1.) 400 A MCCB Incomer with metering CTs, multi function meter compatible to scada ,Ampere meter with SS, Voltmeter with SS, Indicating Lamps, Control Fuse, wiring etc. 2.) 250A MCCB 3.) 100A MCCb for Chlorinator, 4.) 5 nos. of 32A MCB 5.) 25KVA of capacitor bank of different size with contactor, 6.) 2 nos. of Earth pit with required length of Earth flat, 7.) Star delta Starter with MCB, Main and Aux Contactor/L Relay, L/R Selector Switch, 3 Indicating lamps, Start-Stop Push Button ,Control MCB with panel with all accessories as per specification and employers requiremt with following rating
9.1.1 | 0 to 15kW | LS | 1
10 | LT FLAT FLEXIBLE CABLE
10.1 | P/Laying XLPE insulated / P.V.C. sheathed cable of 1.1 KV grade with aluminum conductor Un-armored of IS:7098-I/1554-1 approved make in ground as per IS:1255 including excavation of 30cmx75cm size trench, 25 cm thick under layer of sand, IInd class bricks covering, refilling earth, compaction of earth, making necessary connection, testing etc. as required of size
10.1.1 | 3C X 6 Sqm | LS | 1
10.1.2 | 3C X 10 Sqm | LS | 1
10.1.3 | 3C X 16 Sqm | LS | 1
10.1.4 | 3C X 25 Sqm | LS | 1
10.1.5 | 3C X 95 Sqm | LS | 1
11 | P/Laying XLPE insulated / P.V.C. sheathed cable of 1.1 KV grade with aluminum conductor Armored of IS:7098-I/1554-1 approved make in ground as per IS:1255 including excavation of 30cmx75cm size trench, 25 cm thick under layer of sand, IInd class bricks covering, refilling earth, compaction of earth, making necessary connection, testing etc. as required of size.
11.1 | 4C x 35 Sqm | LS | 1
11.2 | 4C x 70 Sqm | LS | 1
11.3 | 4C x 400 Sqm | LS | 1
12 | CASING PIPE FOR CABLE PROTECTION
12.1 | Providing, laying and fixing of following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep) and refilling etc. as required.
12.1.1 | 80 mm dia | LS | 1
13 | EARTHING
13.1 | Pipe Earthing as per IS:3043 with perforated 3.0 Mtr. Long, 40 mm dia. ' B ' class G.I. Pipe including all accessories like nut, bolts, reducer, nipple, wire meshed funnel, and C.C. finished chamber covered with hinged type with locking arrangement C.I. Cover, C.I. Frame of size 300mm x 300 mm and embodying the pipe complete with alternate layers salt and coke/ charcoal, testing of earth resistance as required. | LS | 1
13.2 | S & Laying 25x6 mm size GI earth strip in horizontal or vertical run in ground/surface/recess including riveting, soldering, saddles, making connection etc. as required. | LS | 1
13.3 | S & Laying 6 SWG size GI earth wire in horizontal or vertical run in ground/surface/recess including riveting, soldering, saddles, making connection etc. as required. | LS | 1
14 | Internal lighting for Pump Rooms with conduit wiring, required fittings as per specification and Engineers requirement. | LS | 1
14.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required.
14.1.1 | Light Point/Fan Points -
14.1.1.1 | Medium point -exceeding 3 m. but not exceeding 6 m. in length. | LS | 1
14.2 | Wiring of 3 pin 5 amp. light plug point with 1.5 sq. mm FR PVC insulated unsheathed flexible copper conductor 1.1 kV grade and 1.5 sq.mm FR PVC insulated unsheathed flexible copper earth conductor 1.1 kV grade(IS:694) of approved make in surface / recessed ISI marked medium duty PVC conduit & it's accessories, 18 SWG M.S. box with earth terminal, screw less cage connectors for neutral looping in switch board & false ceiling point, 6 A switch, 6 A socket, 3.0 mm thick phenolic laminated sheet, zinc plated / brass screws, cup washers, making connections, testing etc. as required.
14.2.1 | 3 Pin 6 Amp socket outlet on Separate Board
14.2.1.1 | Medium point -exceeding 3 m. but not exceeding 6 m. in length. | LS | 1
14.3 | Wiring of 6 pin 15 amp. Light power point with 6.0 sq.mm PVC insulated unsheathed solid / stranded copper conductor 1.1 kV grade of approved make in surface /recessed ISI marked pvc conduit & it's accessories, 18 SWG M.S. box with earth terminal, screw less cage connectors for neutral looping in switch board , 15 A switch, 15 A socket, 3.0 mm thick phenolic laminated sheet, zinc plated / brass screws, cup washers, bushes, check nuts, making connections, testing etc. as required.
14.3.1 | Medium point -exceeding 3 m. but not exceeding 6 m. in length. | LS | 1
14.4 | Circuit Wiring - Wiring for circuit wiring with PVC insulated cable FR with copper multi strand conductor ISI marked in Surface rigid P.V.C. conduit (MMS) of ISI marked suitable size including painting etc. as required as per specification 4x2.5 Sq.mm. | LS | 1
14.5 | METALLIC SWITCH BOXES - Supply and fixing of following size on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required MS Box size - 200 mm X 250 mm X 60 mm | LS | 1
14.6 | SUB MAINS IN SURFACE RIGID STEEL CONDUIT IN COPPER CONDUCTOR - Wiring for sub-mains with PVC insulated cable FR with copper multi strand conductor ISI marked in surface rigid steel ISI marked conduit of suitable size(conduit included) including connection painting etc., as required as per specification - 2 WIRE SUB MAIN - 4.0 sq mm cable | LS | 1
14.7 | Supplying of ISI Marked Switch Fuse Unit (rewirable type ) triple pole with neutral link ,415 Volt - 32 Amps. | LS | 1
14.8 | Supplying and fixing as per specification Caution / Danger Board as of approved make & design with necessary material complete. Large Size | LS | 1
14.9 | Supplying and fixing as per specification Switch of approved make ISI marked with necessary material complete. 6 Amp Flush type | LS | 1
14.10 | Supplying and fixing as per specification socket outlet of approved make & ISI marked with necessary material complete - 6 Amp 250 Volt 3 / 5 Pin Flush type | LS | 1
14.11 | Supplying, Fixing and Testing of Compact Fluorescent Lamp (CFL) with inbuilt electronic ballast ISI marked of approved make -36 W | LS | 1
14.12 | Supplying, fixing and testing of approved make bulk head luminaire consisting of pressure die aluminium housing lamp holder, prismatic glass cover, rubber gasket and wire guard, deluxe type, including fixing on wall as required, with necessary material complete Fitting(suitable for GLS w/o lamp up to 36 watt Retorted CFL | LS | 1
14.13 | Supplying, fixing & testing of approved make of low watt surface mounting luminaires, made of white powder coated CRCA sheet steel housing with aluminium mirror reflector complete with control gear, wired up to terminal block on a detachable tray including fixing on wall/ Ceiling on wooden round block including wiring & connection as required and suitable for CFL as following :- (without lamp) - 2 Nos 36 watt CFL | LS | 1
15 | P & F double ball bearing capacitor start ceiling fan of approved make complete with regulator as per required size and other accessories etc. complete and as per direction of engineer in charge | LS | 1
15.1 | I T C of ceiling fan and regulator including wiring the down rod up to 30 cm with 3 x 1.5 sq.mm pvc insulated flexible copper conductor making connection testing etc. as required. | LS | 1
15.2 | Providing and fixing circular/ Hexagonal cast iron or M.S. sheet box for ceiling fan clamp of internal dia 140mm, 73mm height, top lid of 1.5mm thick M.S. sheet with its top surface hacked for proper bonding, top lid shall be screwed into the cast iron/ M.S. sheet box by means of 3.3mm dia. round headed screws, one lock at the corners. Clamp shall be made of 12mm dia M.S. bar bent to shape as per standard drawing. | LS | 1
XI | SOLAR ENERGY SYSTEM
1 | Supply Installation, connection and commissioning of PV modules based on complete system design solution. System shall include PV modules, appropriate selection of charge controllers, the required auto change over, inverters, battery..etc. All necessary protection equipment shall be provided as per code requirement. This include fuses, breakers, surge protection.
1.1 | Hybrid Solar inverter (Capacity: 40 KVA), Make: Enertech, Series: Sun magic, Three Phase, Standard: IEC | Nos | 1
1.2 | Supply of Solar Panels (Capacity: 250 watt), Three Phase, Standard: IEC, | Nos | 160
1.3 | Supply of Finished solar Battery, 12 V 200 AH | Nos | 30
1.4 | Charge controllers | Item | 1
1.5 | Auto Changeover | Item | 1
1.6 | All necessary protection equipments | Item | 1
1.7 | Erection and commissioning including mounting structure | Item | 1
XII | FACILITY BUILDING | Job | 1
1 | CONCRETE WORKS
| Foundation, | Nos. | 4
| Concrete (1:2:3) | cu.m | 8.91
| Excavation | cu.m | 3.96
| Lean concrete (1:2:6) | cu.m | 0.2475
| Steel deformed bars, 10mm dia x6m | kg | 915.75
| Columns, | Nos. | 16
| Concrete (1:2:3) | cu.m | 6.9998
| Steel deformed bars, 10mm dia x6m | kg | 699.984
| Waterproofing compund | Ltrs | LS
| Beams, | Nos. | 3
| Concrete (1:2:3) | cu.m | 2.97
| Steel deformed bars, 10mm dia x6m | kg | 297
| Waterproofing compund | Ltrs | LS
| Ground Slab including plant foundations | Nos. | 1
| Concrete (1:2:3) | cu.m | 18.15
| Steel deformed bars, 10mm dia x6m | kg | 1815
| Waterproofing compund | Ltrs | LS
2 | MASONRY & PLASTERING
| Walls - Masonry - 150mm thick | cu.m | 56.1445
| External walls, 150mm thick (1:5) - 12mm thick | sq.m | 213.884
| Internal walls, 150mm thick (1:5) | sq.m
| Plastering external walls, 12mm thick (2-coats) (1:5) | sq.m | 213.884
| Plastering internal walls, 12mm thick (2-coats) (1:5) | sq.m
Floor screed 35mm thick (1:5)
4 | WOOD WORKS - Timber Battens, rafters, Facia board | Sq.m | LS
5 | CEILING, Aluminium framed ceiling system | sq.m | 181.5
6 | Door & windows | sq.m | 34.65
7 | PIPE WORK | m
8 | ELECTRICAL WORK
| Electrical works complete including all fixings and wiring inside conduit. | Item | LS
9 | FINISHES
| Painting on all Ceiling, interior & exterior surfaces of walls | sq.m | 213.884
Tiling on floor
| General area, 600 x 600 | sq.m | 172.5
| Wet area, 300 x 300 | sq.m | 9
10 | ROOFING
| Lysaght roofing | sq.m | 288
XIII | SUPPLY OF O&M EQUIPMENT AND SPARES | Item | LS
Spares for all pump stations:
1 | Safety Tools
Supply and Delivery of the following safety equipments and tools:
1.1 | 5 kg capacity dry chemical powder type Fire Extinguisher. | Nos | 4
1.2 | Wooden First Aid Box | Nos | 4
1.3 | Fire Bucket sand with 3 nos. of round bottom buckets. | Nos | 4
1.4 | Rubber mat of 1.1kV grade of size 6mm thick. | Nos | 4
1.5 | Fire Safety Rules chart. | Nos | 4
1.6 | Shock Treatment Chart | Nos | 4
2 | Maintenance Tools
Supply and Delivery of the following maintenance tools / equipments.
2.1 | Adjustable wrench made up of carbon steel with standard pattern of size 200mm. | Nos | 2
2.2 | Double ended open jaw spanner set of sizes (mm): 6x7, 8x9, 10x11, 12x13, 14x15, 16x17, 18x19, 20x21, 22x23, 24x25, 26x27, 28x29, 30x31, 32x33. | Nos | 2
2.3 | Screw driver set consisting of various sizes (6", 8", 12"). | Nos | 2
2.4 | Cutting Pliers 12" | Nos | 2
2.5 | Hacksaw frame with blade | Nos | 2
3 | Manuals and Catalogues.
| Supply of Three complete sets of pump catalogues and manuals. | Nos | 2
3.1 | Set of Pump Spare Parts of each pump. | Nos | 2
3.2 | All other items not covered above, including all materials, equipments and labour, for installation of equipment, drives, wiring, leakage, dewatering sump pump conduits, wire trays, lighting, breakers, switchgear, fixtures, access ladders, metal works, etc. |  | LS
4 | Operation and Maintenance Equipments
Provision of all operations and maintenance equipments.
4.4 | Set of cleaning rods. | Nos | 1
XIV | LABORATORY EQUIPMENT | Item | LS
XV | TESTING AND COMMISSIONING
| Testing and Commissioning of the overall water supply system | Item | LS
XVI | ADDITIONS | Item | LS
1 | GENERALS AND PRELIMINARIES | Item | LS
2 | WATER SUPPLY CONVEYANCE SYSTEM | Item | LS
3 | WATER SUPPLY DISTRIBUTION NETWORK | Item | LS
4 | ULTRA FILTER | Item | LS
5 | RAIN WATER COLLECTION / LIFT WELL | Item | LS
6 | RAW WATER TANK | Item | LS
7 | CLEAR WATER TANK | Item | LS
8 | BORE/TUBE WELL | Item | LS
9 | RO (REVERSE OSMOSIS) UNIT | Item | LS
10 | BRINE DISPOSAL | Item | LS
11 | MECHANICAL WORK | Item | LS
12 | ELECTRICAL WORK | Item | LS
13 | SOLAR ENERGY SYSTEM | Item | LS
14 | FACILITY BUILDING | Item | LS
15 | SUPPLY OF O&M EQUIPMENT AND SPARES | Item | LS
16 | LABORATORY EQUIPMENT | Item | LS
17 | TESTING AND COMMISSIONING | Item | LS
XVII | OMISSIONS | Item | LS
1 | GENERALS AND PRELIMINARIES | Item | LS
2 | WATER SUPPLY CONVEYANCE SYSTEM | Item | LS
3 | WATER SUPPLY DISTRIBUTION NETWORK | Item | LS
4 | ULTRA FILTER | Item | LS
5 | RAIN WATER COLLECTION / LIFT WELL | Item | LS
6 | RAW WATER TANK | Item | LS
7 | CLEAR WATER TANK | Item | LS
8 | BORE/TUBE WELL | Item | LS
9 | RO (REVERSE OSMOSIS) UNIT | Item | LS
10 | BRINE DISPOSAL | Item | LS
11 | MECHANICAL WORK | Item | LS
12 | ELECTRICAL WORK | Item | LS
13 | SOLAR ENERGY SYSTEM | Item | LS
14 | FACILITY BUILDING | Item | LS
15 | SUPPLY OF O&M EQUIPMENT AND SPARES | Item | LS
16 | LABORATORY EQUIPMENT | Item | LS
17 | TESTING AND COMMISSIONING | Item | LS

## 4.2-Abst.-RWR (hidden)
Water Supply Facilities in Ha. Kelaa, Maldives
RAW WATER RESERVOIR
ABSTRACT OF QUANTITY
S. No. | Particulars | Unit | Quantity | Reference
1 | EARTHWORK IN EXCAVATION
1.1 | Excavation in Coral/Ordinary Soil
Earthwork excavation including clearing vegetation, shoring, strutting, and ramming with selected earth for preparing the bed level, as per the specification and drawing, for Pipeline trenches.
| 0 to 0.50 m | cum | #REF!
| From 0.50 m to 1.00 m | cum
| From 1.00 m to 1.50 m | cum
1.2 | FILLING OF SOIL WITH APPROVED EXCAVATED SOIL
| Refilling pipeline trenches with selected available earth from trench excavation using mechanical vibration including watering, compaction of layers of 30cms, With all leads and lifts as per Specification & drawing and as directed by the Engineer. | cum | #REF!
1.3 | DISPOSAL OF SURPLUS EARTH
| Disposal of the remaining soil after the back filling from the available soil to the general garbage yard as approved by the engineer. | cum | #REF!
2 | PLANE CEMENT CCONCRETE; M-15
2.1 | Providing and laying of PCC 20/20 (20 N/mm2) grade using sulphate resistant cement for foundation as per Specification & drawing and as directed by the Engineer | cum | #REF!
3 | REINFORCED CEMENT CONCRETE- M30
Providing and laying RCC of grade C 35/20 including fabrication of high yield steel (fy = 415 MPa), as per Specification & drawing and as directed by the Engineer
3.1 | All work up to plinth level | cum | #REF!
3.2 | All works above plinth level upto floor fifth level. | cum | #REF!
4 | Thermo-Mechanically Treated bars (FE-500)
4.1 | All work up to plinth level | MT | #REF! | 2% taken for overall
4.2 | All works above plinth level upto floor fifth level. | MT | #REF!
5 | FORM WORK (CENTERING, SHUTTERING & SCAFFOLDING SYSTEM)
5.1 | Foundations, footings, bases of columns, etc. for mass concrete | sqm | #REF!
5.2 | Walls (any thickness) including attached plasters Butteresses, plinth and string courses etc. | sqm | #REF!
5.3 | Columns, Pillars, Piers, Abutments, Posts and Struts | sqm | #REF!
5.4 | Lintels, beams, plinth beams, girders, bressumers and cantilevers | sqm | #REF!
5.5 | Suspended floors, roofs, landings, balconies and access platform | sqm | #REF!
5.6 | Small surfaces such as cantilever ends, brackets and ends of steps, caps and bases to pilasters and columns. | sqm | #REF!
5.8 | SCAFFOLDING SYSTEM | sqm | #REF!
6 | CEMENT PLASTER
6.1 | Inner Side | sqm | #REF!
7 | PAINTING WORKS
7.1 | EPOXY PAINT
| Inner Side (Qty. taken as inner cement plaster) |  | #REF!
7.2 | EXTERIOR PAINTING OF REQUIRED SHADE
| Outer Side walls | sqm | #REF!
7 | DOUBLE FLANGED DI PIPES & SPECIALS
7.1 | DOUBLE FLANGED DI PIPES
7.1.1 | 200 mm (Washout Pipe) | m | #REF!
7.1.2 | 350 mm (Overflow Pipe+Inlet Pipe+Bypass Arrangement) | m | #REF!
7.1.3 | 500 mm (Pipe outlet) | m | #REF!
7.2 | DOUBLE FLANGED SPECIALS
7.2.1 | 350 mm (Overflow + Inlet + Bypass)
| Duckfoot bend | each | #REF!
| D/F Bend -90 degree | each | #REF!
| Tee 350x350 mm | each | #REF!
7.2.2 | 500 mm (Outlet)
| Duckfoot bend inlet | each | #REF!
| D/F Bend for over flow-90 degree | each | #REF!
| Tee 500x500 mm | each | #REF!
8 | VALVES AND APPURTENANCES
8.1 | SLUICE VALVES
| 200 mm | each | #REF!
8.2 | BUTTERFLY VALVES
| 350 mm dia | each | #REF!
| 500 mm dia | each | #REF!
8.3 | DOUBLE FLANGED DI PIPES
| 200 mm dia | m | #REF!
| 350 mm dia | m | #REF!
| 500 mm dia | m | #REF!
8.4 | DISMANTLING JOINTS
| 200 mm | each | #REF!
| 350 mm | each | #REF!
| 500 mm | each | #REF!
8.5 | CONSTRUCTION OF MASONRY CHAMBER
| 900x1000x1400 | each | #REF!
| 1550x1500x1750 | each | #REF!
| 1650x1700x1900 | each | #REF!
9 | FLOW MEASUREMENT
9.1 | Electromagnetic Flow Meter
| 500 mm | each | #REF!
9.2 | Ultrasonic level measuring sensor | each | #REF!
10 | Miscellaneous Works
10.1 | Weathering Protection for Roof Slab | Sqm | #REF!
10.2 | Cement Concrete tiles for plinth Protection | Sqm | #REF!
10.3 | Ventilation Pipe 100mm dia | each | #REF!
10.4 | CI Manhole Cover MH1 600x600mm | each | #REF!
10.5 | Sky Light 6mm glass; Rectangular shape 0.60*0.60 mm | each | #REF!
10.6 | Cage Ladder Stainess Steel (Ladder Type I) | m | #REF!
10.7 | Ladder Type II-1.00M Width | m | #REF!
10.8 | G.I. Steel Pipe Railing (RWR+Stair) | m | #REF!
10.9 | Lightening Arrester | set | #REF!
10.10 | Water Tightness Test | Job | #REF!
10.11 | Disinfection & washing | Job | #REF!