Addu Equatorial Hospital

Republic of Maldives

# Design and Build of Ambulance & Transport Service Complex for Addu Equatorial Hospital, Addu City.

Issued on: 28th February 2025

Issued By:
Addu Equatorial Hospital
Procurement Section
Republic of Maldives

Contents

SCOPE OF WORKS	4

BACKGROUND	4

PROJECT AREA	4

PROJECT BENEFICIARIES	4

1.1	WORKS TO BE PROVIDED BY THE CONTRACTOR	4

ICT & SECURITY SYSTEM REQUIREMENTS (BASE REQUIREMENT – MANDATORY)	5

FACILITY DESIGN MINIMUM REQUIREMENTS	8

1.2	Design Scope:	8

1.3	Materials Selection:	8

(d)	Plumbing Works:	8

(f)	Floor Finish:	9

(g)	Walls to be tiled:	9

(h)	Water closets: Standard commercial-grade sanitary ware	9

(m)	Air Condition and ventilation system :	9

1.4	CONTRACT DURATION	10

1.5	MATERIALS TO BE PROVIDED	11

1.6	FACILITIES TO BE PROVIDED	11

1.7	SECURITY AT WORK	11

1.8	GENERAL RESPONSEBILITIES / REQUIREMENTS	11

1.9	DRAWINGS	12

1.10	SITE OFFICES	13

1.11	SERVICES	13

1.12	SAMPLES, TESTING, INSPECTION & WELDING	13

1.13	CONCRETE	13

1.14	WORKING PRACTICES	13

1.15	HEALTH, SAFETY & ENVIRONMENTAL (HS&E) REQUIREMENTS	13

1.16	SITE SURVEY	14

1.17	SITE PREPARATION	14

1.18	MEASUREMENT OF QUANTITIES	14

1.19	TRANSPORTATION OF MATERIALS	14

1.20	REDUNDANT EQUIPMENT	14

1.21	PROGRAMME FOR THE WORKS	15

1.22	STANDARDIZATION OF CONSTRUCTION WORKS	15

1.23	STANDARDS	15

1.24	CONSTRUCTION AND MANUFACTURING STANDARDS	15

1.25	QUALITY STANDARDS	16

1.26	CONTRACT MANAGEMENT	16

1.27	QUALITY ASSURANCE REQUIREMENTS	16

1.28	TESTING UPON COMPLETION	17

1.29	HEALTH SAFETY AND ENVIRONMENTAL PROVISIONS	18

1.30	FIRST AID	19

1.31	FIRE PRECAUTIONS	19

1.32	WELFARE FACILITIES	19

1.33	CONTROL OF HAZARDS TO HEALTH	19

1.34	HS&E INCIDENCE REPORTING	19

1.35	INFRASTRUCTURE AND MINIMUM SPACE REQUIREMENT FOR THE AMBULANCE & TRANSPORT SERVICE COMPLEX	20

1.36	APPENDIX A: SITE INFORMATION & EXISTING SITE CONDITIONS	22

# SCOPE OF WORKS

## BACKGROUND

To strengthen emergency medical response services and enhance operational efficiency within Addu City, Addu Equatorial Hospital (AEH) is undertaking the development of a purpose-built Ambulance & Transport Service Complex.

Addu Equatorial Hospital operates a 24-hour emergency medical transport system serving Addu City and surrounding health facilities. With increasing service demand, expansion of fleet capacity, and the need for improved coordination and operational readiness, the establishment of a centralized ambulance operations facility has become necessary.

Currently, ambulance parking, dispatch coordination, and related operational functions are not housed within a dedicated infrastructure designed to support a modern emergency response system. In order to improve response time, asset protection, staff welfare, and long-term service sustainability, AEH is planning the design and construction of a new Ambulance & Transport Service Complex at Maarandhoo Magu, Addu City.

The proposed development will provide an integrated facility incorporating ambulance garage space, dispatch control room, administrative offices, maintenance areas and supporting infrastructure necessary to ensure efficient and sustainable emergency medical transport services.

## PROJECT AREA

The proposed Ambulance & Transport Service Complex shall be constructed at Maarandhoo Magu, Addu City, within the land allocated to Addu Equatorial Hospital.

The Site is located in an urban setting and shall be developed in compliance with applicable planning regulations, building codes, and relevant statutory requirements of the Republic of Maldives.

## PROJECT BENEFICIARIES

The primary beneficiaries of this project shall be the residents of Addu City and surrounding areas who require emergency medical transportation and pre-hospital care services.

The facility will directly support patients in need of urgent medical evacuation, inter-facility transfers, and emergency response services. Indirect beneficiaries include healthcare providers, emergency response personnel, and affiliated health centres served by Addu Equatorial Hospital.

The establishment of the Ambulance & Transport Service Complex will enhance the reliability, coordination, and efficiency of emergency medical services within the region.

# WORKS TO BE PROVIDED BY THE CONTRACTOR

    - Nature of Contract

This Contract comprises the Survey, Design and Construction of the Ambulance & Transport Service Complex, including installation, testing and commissioning of all civil, structural, architectural, electrical, mechanical, plumbing, ICT and associated systems required for the complete functioning of the facility.

The Contractor shall provide all labour, materials, plant, equipment, supervision and professional services necessary to execute and complete the “Works” as described in the Scope of Works, Technical Specifications and Price Schedule/Bill of Quantities.

The Works shall be delivered in fully operational condition, including commissioning and training of AEH personnel where required.

    - Description of Works

The scope of the required Works shall include, but shall not be limited to, the following:

• Survey and Design of the Ambulance & Transport Service Complex.
• Preliminaries and site establishment.
• Earthworks and in-situ reinforced concrete works.
• Masonry, plastering and structural metal works.
• Carpentry and roofing works.
• Windows, glazing and doors including shutters and ironmongery.
• Flooring, tiling, suspended ceilings and interior finishing works.
• Painting and decorative works.
• Plumbing, drainage and water supply systems.
• Mechanical and Electrical services including main incoming electrical connection, Main Distribution Board (MDB), Sub Distribution Boards (DBs), internal power distribution, lighting, air-conditioning works and Uninterruptible Power Supply (UPS) systems. The system shall include proper earthing, surge protection and segregation of critical operational loads.

• Fire detection, fire stopping, insulation and fire protection systems.
• Ramp access for universal accessibility compliance.
• External works including ambulance driveway paving, site drainage and minor landscaping works.
• Lightning protection system and earthing.
• Signage works (internal and external).
• Basic furnishing works as specified in the Bill of Quantities.
• Utility connections including water, sewerage and electricity.

• External security lighting shall be provided for driveway, garage and perimeter areas.

- Stormwater drainage system sized to prevent flooding of garage and driveway areas.

## ICT & SECURITY SYSTEM REQUIREMENTS (BASE REQUIREMENT – MANDATORY)

The Works shall include the supply, installation, testing and commissioning of all required materials and equipment’s including full operational testing of dispatch workstations, data connectivity and UPS backup functionality as detailed in the Price Schedule/Bill of Quantities and Technical Specifications, together with training of designated AEH personnel where required.

The Contractor shall provide all necessary manpower, machinery, materials and supervision to complete the Works in full compliance with the Contract Documents.

All ICT systems shall be integrated with the existing AEH central server and network infrastructure through a dedicated physical fiber link between AEH main building and the Ambulance & Transport Service Complex. No standalone server, no independent internet connection, and no separate PABX or PA system shall be installed at this facility. All such services shall be extended from AEH main building.

ICT & Security Systems – Minimum Quantities (for Tender)

| No. | Category | Item Description | Unit | Qty | Minimum Assumption / Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Core Network | Layer-3 Managed Core Switch (Fiber uplink, SFP+ capable) | No | 1 | Main distribution switch for the building |
| 2 | Core Network | 24-Port Managed PoE+ Switch | No | 1 | For CCTV, access control, Wi-Fi APs, future points |
| 3 | Core Network | 24-Port Managed Access Switch | No | 1 | For office/dispatch data points, printers, etc. |
| 4 | Wireless | Enterprise Wi-Fi 6 Access Points (Indoor) | No | 3 | Dispatch + admin + meeting + + garage/workshop coverage |
| 5 | Infrastructure | 42U Lockable Network Rack Cabinet (with PDU & cable management) | No | 1 | Adequate for switches, patch panels & UPS |
| 6 | Infrastructure | Fiber Termination Panel with SFP Modules (Single-mode) | Set | 1 | Termination for AEH fiber backbone + patching |
| 7 | Infrastructure | Structured Cabling System (Cat6A) incl. outlets, patch cords, labelling | Lot | 1 | Entire building as per final design |
| 8 | Infrastructure | Patch Panels + Cable Management Accessories | Lot | 1 | Within rack (size to suit final ports) |
| 9 | Control Room | 24/7 Dispatch Operator Workstations (PC/Workstation) | Set | 4 | Minimum 4 operator positions |
| 10 | Control Room | Supervisor Workstation | Set | 1 | Control room supervisor |
| 11 | Admin | Administrative Workstations | Set | 2 | Admin + records/logistics (minimum) |
| 12 | Displays | 24” LED Monitors | No | 08 | Dual screens for operators (8 total) |
| 13 | Displays | Large Display Panels (55” Commercial Grade) | No | 1 | Commercial-grade 55” LED panels suitable for 24/7 operation; wall-mounted in Dispatch/Control Room for , ambulance GPS tracking, call management dashboard and operational status monitoring |
| 14 | Dispatch | ( Call Centre Head Set ) Headset Communication Sets | Set | 6 | 4 operators + supervisor + spare |
| 15 | CCTV | IP Dome Cameras (Indoor, ≥4MP, PoE) | No | 6 | Dispatch, corridors, stores, workshop internal points |
| 16 | CCTV | IP Bullet Cameras (Outdoor, IP66, ≥4MP, PoE) | No | 6 | Building perimeter + ambulance bays + entry/exit |
| 17 | Access Control | Access-Controlled Door Sets (Reader + Lock + Exit button + PSU) | Door | 8 | Dispatch, IT rack room, admin, store, restricted areas, main entries |
| 18 | Power Backup | Online Double Conversion UPS (6–8 kVA) | No | 1 | For switches, NVR, controllers, video wall controller (critical loads) |
| 19 | Public Address System (Single Zone) | Complete single-zone Public Address & Paging System including central amplifier, ceiling and/or wall-mounted speakers covering all operational areas (Garage, Dispatch, Offices, Lounge, Outdoor), desktop paging microphone at Dispatch Room, cabling, rack integration, UPS backup connection, installation, testing and commissioning | Set | 1 | Single-zone system with announcements originating from Dispatch Room and broadcast simultaneously to all connected areas; system shall provide clear audibility in high-noise garage environment; no zone selection required |

The quantities listed above represent minimum requirements. Bidders shall comply with these minimum quantities. If the Contractor’s final design requires additional equipment to meet operational performance, such quantities shall be included within the Lump Sum Base Scope price without additional cost to the Employer. The Contractor’s detailed BOQ shall reflect all ICT quantities proposed.

## FACILITY DESIGN MINIMUM REQUIREMENTS

## Design Scope:

The Contractor shall undertake the complete survey and design of the Ambulance & Transport Service Complex in accordance with the allocated plot and approved development parameters.

The design shall include Architectural, Structural, Mechanical, Electrical, Plumbing, ICT and Interior design components necessary for the full functionality of the facility. The design shall also include site development works, ambulance circulation layout, driveway paving, minor landscaping and preparation of detailed Bill of Quantities for complete construction, installation and furnishing works.

Design works shall be carried out in consultation with Addu Equatorial Hospital (AEH). The Concept Design shall be submitted to AEH for review and approval prior to commencement of detailed design development. Detailed design drawings shall not proceed without written approval of the Concept Design.

All designs shall comply with applicable laws and regulations of the Republic of Maldives and shall follow relevant international standards and best practices applicable to emergency service facilities.

## Materials Selection:

All the materials selections shall comply to the technical specification and bill of quantities requirements and quantities.

        - Concrete works: Manufactured Sand, Aggregate and Cement to be used.

        - Masonry and plastering: As per the design and specification

        - Roofing Materials: Lysaght roofing sheet, Gutter, Ridge cap, end cap, flashing to be use 0.47mm thick

## Plumbing Works:

Appropriate sizes of uPVC pipes and fittings to be use all plumbing works, (Fresh water lines, Ground water lines, wastewater lines, sewer lines, Rainwater down pipes).

The ambulance washing bay drainage system shall be connected to an approved oil and grease trap prior to discharge into the sewer network. The system shall comply with applicable environmental and EPA requirements.

        - Tiles: Full body homogeneous tiles for all the buildings.

## Floor Finish:

- Skid-resistant tile finish shall be provided in general circulation areas, offices, toilets and common areas, complete with matching tile skirting.

- Heavy-duty, anti-slip and easy-to-clean flooring suitable for ambulance garage and wash areas shall be provided to withstand vehicular loads and operational wear.

- Heavy-duty commercial-grade vinyl flooring shall be provided in critical operational areas such as the dispatch/control room and first aid/paramedic preparation areas to ensure durability, hygiene and ease of maintenance.

- All floor finishes shall be non-slip, durable, and suitable for high-traffic emergency service use.

- The garage floor slab shall be reinforced concrete designed to withstand ambulance axle loads and frequent vehicular movement.

## Walls to be tiled:

- Garage and maintenance areas shall have durable, washable wall finish with protective coating suitable for oil exposure and frequent washing.

- Toilet and shower areas shall be tiled full height from finished floor level.

- Pantry and wash areas shall be tiled up to 1.8 m from finished floor level.

- Dispatch / Control Room walls shall receive smooth plastered finish with high-quality washable paint, with acoustic treatment where required.

- Driver lounge, meeting room and office areas shall receive plastered finish with washable paint.

- Staircase and circulation areas shall receive durable painted finish suitable for high traffic use.

- All wall finishes shall be moisture-resistant, easy to maintain, and suitable for an emergency service operational facility.

## Water closets: Standard commercial-grade sanitary ware

        - Handrail: Handrails shall be provided for all staircases and ramps in accordance with applicable building safety and accessibility regulations.

        - Windows curtains: Medium quality sun protected fabrics for all windows.

        - Interior Paint: Washable low-VOC paint suitable for operational facilities

        - Exterior Paint: Oil based textured paint.

## Air Condition and ventilation system :

        - Base Requirement (Mandatory): High-efficiency inverter split-type air-conditioning units shall be provided for all enclosed operational and occupied areas (dispatch/control room, offices, meeting rooms, lounges). Mechanical ventilation/exhaust shall be provided for toilets and service areas. Adequate ventilation shall be provided for garage and maintenance areas as per applicable standards.

        - Electricals: As per the design and specification

        - Lighting & fittings: As per the design and specification (LED lights to be use for lighting)

        - Internal Ceiling: As per the design and specification

        - External Ceiling: As per the design and specification

        - Sink Cupboards:

Concrete sink cupboards with tile finish shall be provided in pantry and maintenance areas.
Stainless steel sink (minimum 600 mm size) with elbow-operated tap shall be installed.
Granite or solid surface countertop shall be provided over sink cupboards.

        - Taps:

  - Elbow-operated taps shall be provided for sink cupboards and wash basins in operational areas, except in toilet areas where standard fittings may be used.

        - Dispatch Control Counter:

  - Fabrication of Dispatch / Control Room counters shall be provided using timber or metal frame with appropriate thickness plywood and laminated finish (PVC/Formica), complete with granite or solid surface countertop.

  - Counters shall allow provision for cable management and equipment installation.

        - Ambulance way paving:

  - Ambulance driveway and maneuvering areas shall be paved using heavy-duty interlocking concrete blocks or reinforced concrete pavement suitable for ambulance axle loads.

  - Paving shall be properly compacted and laid over approved sub-base to ensure durability.

        - Installation of Fire system:

  - As per Government regulations.

        - Pump systems:

  - Supply and complete the installation water pump for groundwater and/or domestic supply. (Appropriate size of Davey pump or Equivalent).

        - Lightning Protection System

  - Design, supply, and Complete installation of Erco, Eritech or equivalent lightning Protection System to cover the whole building as per local regulations (Rate shall include for all fixing of the system and down conductor to earthling) Coverage of lightning protection should be minimum 100 Meter Radius. Price also includes installing a Marine grade SS post.

    - Test and Commissioning

The scope of work includes testing and commissioning of all the equipment installed by the contractor.

# CONTRACT DURATION

All works shall be completed within Seven (7) calendar months of contract award.

# MATERIALS TO BE PROVIDED

    - Materials to be provided by the Contractor

The contractor shall be required to provide all equipment and materials as listed under the Bills of Quantities and Specifications” in accordance with the specifications provided to achieve the scope of work completely and in accordance with the instructions of the supervision engineer.

    - Materials to be Provided by Client

No materials will be supplied by Client.

# FACILITIES TO BE PROVIDED

    - Facilities Provided by Client

No site facilities shall be provided by Client.

    - Facilities Provided by the Contractor

All required facilities for proper development of all phases of the project shall be the contractor’s own responsibility. Unless otherwise explicitly called upon, any facilities shall be deemed included and/or surcharged in/to the contractor’s price.

# SECURITY AT WORK

It is the contractor’s responsibility to secure the Works against vandalism and interference during construction all the time till handing over the works officially.

# GENERAL RESPONSEBILITIES / REQUIREMENTS

The Services shall also include some duties normally performed by Client’s field staff, which includes the establishment and maintenance of contacts with counterparts and other stakeholders.

These shall include, yet not be limited to, liaising and maintaining strong working relations with all stakeholders and obtain all required letters, approvals, documentation…etc.

    - Reporting

One of project’s key management tools is through comprehensive progress reports supported by photographs, videos and similar materials from its implementation partners. The same also applies for illustrating project impacts.

    - Contents of Report

During implementation, the contractor shall provide Client with daily, and monthly progress reports including yet not limited to:

      - Meetings held with counterparts, contractors …..etc.

      - Progress reporting, delays….etc.

      - Staff employed by contractor, sub-contractors, counterparts.

      - Financial status, predicted cash flow, expected variations.

      - Technical Issues.

However, Client will supply the contractor with the format of the progress report. Photography & Video Material

The contractor shall provide adequate photographs and video materials as an integral part of any submitted report with the purpose of illustrating progress, impact, elements requiring particular attention and so forth. Photographs and videos shall also be captured and submitted as frequent as requested by Client.

While in certain instances the photographs/videos shall be required to portray the status of technical elements, which necessitates that these be of technical nature portraying an engineering view of the photographed element (i.e. defective bearing, leaking pipeline, broken cable, defective concrete,

etc.), in other instances the photographs/videos are rather required for general illustrative purposes and should convey a general inclusive overview for non-engineering purposes. It should be noted that these should have an artistic essence to them.

Photographs and videos must be accompanied by basic caption information linked to each image file name identifying the date, location, subject and (if relevant) activity. The name and contact of the staff photographer should also be provided for follow-up queries.

The contractors cost shall be deemed included and/or surcharged in/to the rates for each activity.

    - Close Out Report

Upon completion of all activities of the project the contractor shall submit a collective Close-Out Report which reflects all aspects encountered during implementation inclusive of all original documentation, photographs…etc. The contractor shall, at least, submit two (2) hard copies to Addu Equatorial Hospital, One (1) soft copy in editable digital format (USB drive or secure electronic submission).

Translation of Documents

The contractor shall only convey all official correspondences with the counterparts and other relevant material shall be translated to the English language by a certified translator. The contractor shall always submit the any language version together with the English translated version including due stamping and sealing of the translated version with sufficient proof that the utilized translator is certified the Government.

The contractors cost shall be deemed included and/or surcharged in/to the rates for each activity.

# DRAWINGS

The drawings are to be read together with the Scope of Works, Technical Specifications and the Price Schedule/Bills of Quantities.

GENERAL REQUIREMENTS

# SITE OFFICES

Within one (1) week of the “Commencement Date”, the contractor shall establish a temporary site office as per the description (but not limited to) in clause ‘Preliminary and General Works’.

# SERVICES

The Contractor shall be responsible for the provision of services such as electricity, water, sewerage, telecommunications and roads and other facilities required to execute works.

# SAMPLES, TESTING, INSPECTION & WELDING

Cost of all samples and all laboratory testing in accordance with the instructions of the supervision engineer shall be borne by the Contractor and deemed to be included in the Contract price.

All welding works must be inspected by the supervision engineer and all required tests must be applied according to the latest international standards. All welding works must be done by certified welders.

# CONCRETE

The contractor must supply ready mix / in-situ mix concrete for all types of concrete works to achieve the scope of work without any additional cost and as per the instructions of the supervision engineer.

# WORKING PRACTICES

The contractor shall at all times comply with the restrictions and conditions stipulated by the responsible authorities. Before any work is undertaken, the contractor shall give due notice to the engineer and all utilities where services may be in conflict with the works.

The contractor shall provide and erect work signs, bollards, lighting, safety barriers, and such like where necessary or required to ensure safety of the public and workers.

All care shall be taken to minimize damage to property in the execution of these works, by means of route planning, design, and prior consultation with owners, occupiers, and responsible authorities. It shall be the contractor's responsibility to make good any damage, which is caused, to lands, crops, trees, walls, fences, gates, drains, pipelines, buildings, roads, or other property, caused directly or indirectly by the execution of the works.

# HEALTH, SAFETY & ENVIRONMENTAL (HS&E) REQUIREMENTS

    - General

The Contractor throughout the execution and completion of the works shall fully comply with international recognized safety regulations specified under the Technical Specifications i.e.:

Take care for the safety of all persons engaged at site works,

Use reasonable efforts to keep the site and works clear of unnecessary obstruction so as to avoid danger

to these persons,

Provide and maintain temporary electrical supply and necessary safety measures for the Works until completion and taking over

Take all reasonable steps to protect the environment on and off site and to avoid damage or nuisance to persons or to property of the public or others resulting from pollution, noise or other cause arising as a consequence of his method of operation.

Provide to all site workers personal protective equipment, safety clothes, equipment, materials, etc., to perform ongoing activity such as portable earths, safety helmets, working and insulated gloves and safety shoes.

# SITE SURVEY

Bidders shall be deemed to have inspected and examined the site and its surroundings, and to have satisfied themselves with site conditions before submitting the Bid.

# SITE PREPARATION

The Contractor shall be responsible for all site preparation works.

The Site is currently vacant and no demolition works are required under this Contract.

# MEASUREMENT OF QUANTITIES

Addu Equatorial Hospital reserves right to increase, decrease quantities or cancel any items in the bill of quantities as per actual requirements.

Bidders shall familiarize themselves with the conditions on site and actual quantities required as the prices submitted in the bid shall be inclusive of everything required for successful completion of the project.

# TRANSPORTATION OF MATERIALS

The Contractor shall be responsible for transport of all equipment to the site including loading, off-loading, etc. and all costs and expenses involved in transport from the warehouse storage works to the sites.

The Contractor's responsibility shall also include the construction of an adequate access way, if necessary, for construction and delivery of plant from the public highway to each site.

The Contractor shall ensure that damage to any public or private roads or footpaths used by any vehicles or plant proceeding to or from the site kept to a minimum and shall be responsible for the cost of all repairs necessary to restore such roads or footpaths at least to the condition previously obtaining.

# REDUNDANT EQUIPMENT

The Site is currently vacant and contains no existing equipment or materials requiring removal. Accordingly, this clause is not applicable to the present Project.

# PROGRAMME FOR THE WORKS

The Contractor shall within one (1) week of the “Commencement Date” submit a time-scaled linked bar chart in “Microsoft Projects” for approval by the Addu Equatorial Hospital.

The program shall identify all key activities required to complete the works, show intermediate milestones for the purpose of assessing progress on the works and the proposed timing for all Contract deliverable’s including documentation.

This program shall be maintained by the Contractor throughout the project and shall only be varied with the approval of the Engineer.

# STANDARDIZATION OF CONSTRUCTION WORKS

The works shall be of similar construction to those existing, in order to aid standardization and simplify stock holding and material rationalization.

All or part of such works and variations to this specification may be required due to particular project requirements and the following shall, therefore, be governed by the project requirements as described hereafter.

# STANDARDS

The equipment and works shall be designed and executed in accordance with specified requirements and in accordance with the latest versions of the standards given in the specifications or other recognized engineering standards and codes of practice approved by the Addu Equatorial Hospital. The Contractor shall investigate the existence of any regulations and local by-laws governing the proposed works and shall fully comply with relevant requirements therein.

The following quality and shipping standards should be complied with in design, manufacture, and testing for all equipment and materials supplied by the contractor.

# CONSTRUCTION AND MANUFACTURING STANDARDS

All works, activities, equipment and materials of any type shall be strictly in accordance with the latest technical standards & specifications of the following which serialized according to the following priorities:

- All materials, equipment, construction activities and all works of any type to be implemented under this contract shall fully comply with the “Technical Standards & Technical Specifications” mentioned in the Technical Specifications, Drawings and the Bill of Quantities.

- All materials, equipment, construction activities and all works of any type to be implemented under this contract shall fully comply with the latest “Technical Standards & Technical Specifications” Standards and General Technical Specifications for Building Construction Works” of international standards. Eg;

- British Standard (BS), European Standards (EN) and American Society for Testing and Materials (ASTM)..etc

- International Electro technical Commission (IEC).

- Standards (ANSI), Electromagnetic Compatibility (EMC), Deutsches Institute fur Normay (DIN).

# QUALITY STANDARDS

- ISO 9000: Quality Assurance

- ISO 9001: Quality Systems - Model for quality assurance in design, development, production and servicing.

- ISO 9002: Quality Systems - Model for quality assurance in production, installation and servicing.

- ISO 9004: Quality Management and Quality System Elements.

# CONTRACT MANAGEMENT

    - The Engineer

The Contractor shall comply with all project instructions, management systems, procedures, general and special requirements of the Engineer when carrying out implementation works.

    - Method Statement

Prior to the commencement of the contract, the Contractor shall provide a detailed methodology statement. This shall include full details of both type and quantity of all the plant and equipment he proposes to use and a work program, clearly showing the timing and sequence of all activities.

    - Records

The Contractor shall keep at the site accurate and detailed drawings of the work, including a record of times, dates for site activities, and shall provide the Engineer with copies of these records. At the conclusion of the Project, the Contractor shall supply reproducible copies of all drawings, showing full details of the works implemented.

    - Supervision

The Contractor shall employ at the works at adequate number of engineers and staff during the construction stage to supervise all stages of the work as appropriate.

# QUALITY ASSURANCE REQUIREMENTS

    - Quality Plan

The Contractor shall prepare a job specific Quality Plan for all work performed under the Contract.

This Plan shall include, but not be limited to, the following Contract information and quality system elements:

      - Identify the senior personnel responsible for execution of work and quality for the Contract.

      - Contract procedures, test certificates and manuals.

      - Inspection and Testing including all proposed inspections and testing (ITP's)

      - Inspection, measuring and test equipment.

      - Control of non-conforming product including all applicable records (NCR).

      - Handling, storage, packaging and delivery plan.

      - Quality records.

Should the Contractor fail to execute the work in accordance with the approved Quality Plan, the Contractor shall be deemed to be in default.

    - Submission of HS&E and Quality Plans

The HS&E and Quality Plans shall be submitted to the Engineer for approval within one (1) week of the Commencement Date” and shall contain the approval signature of a person at a suitable level in the Contractor’s organization.

Inspection and Test Plans are required to be submitted for approval. In addition, the engineer will nominate those plans or other documentation referenced in the Quality Plan, that are to be submitted for approval before that portion of the work is commenced.

When changes to the HS&E and Quality Plans are proposed, they shall be submitted to the Engineer for review and acceptance before they are implemented.

    - Audits & Quality System

The Engineer may conduct audits on a daily basis to determine that work is carried out in accordance with the HS&E and Quality Plans.

# TESTING UPON COMPLETION

Prior to taking over of the Works or any section of the Works or to putting any portion of the Works into service, the Contractor shall carry out Tests Upon Completion in accordance with the provisions of the Specification. The tests shall be carried out in the presence of the Engineer and to his satisfaction.

The Contractor shall be responsible for the measurement, recording and reporting of Tests on Completion. As each item is completed, its completion shall be certified by the Contractor and countersigned by the Engineer. Three (3) copies of the certificates shall be submitted to the Engineer.

The Contractor shall provide and bear the cost of competent test personnel, instrumentation and test rigs together with all auxiliary personnel, electric power and other services necessary for the completion of the tests.

The Tests on Completion shall verify the correct functioning of individual parts of the Works and of systems involving more than one item of equipment. The tests shall include tests for dielectric withstand, insulation resistance, earth resistance, correct wiring and connections, correct functions and operating characteristics, and polarities.

If any portion of the Works fails to pass the Tests on Completion, then tests on the said portion shall, if required by the Engineer, be repeated within a reasonable time upon the same terms and conditions, save that all costs and losses incurred by the Engineer in consequence of such failure and/or by such repetition shall be borne by the Contractor.

Proximate notification of each particular test or inspection shall be given to the Engineer on an approved form not later than 24 hours prior to the scheduled commencement of the particular test.

# HEALTH SAFETY AND ENVIRONMENTAL PROVISIONS

    - Protective clothing

Personal safety depends very much on wearing appropriate protective clothing.

    - The head

Safety helmets must be worn at all times and a chin strap used when working at heights.

    - The eyes

Eye protection (approved safety glasses or goggles) must be worn at all times.

    - Mouth and nose

Inhalation of dust and fibrous material can cause irritation of the mouth, nose, throat and lungs. When working in dusty environments or other similar environment, the personnel must wear a mask which covers the nose and mouth.

    - Ears

When working in noisy environments, ear plugs or muffs must be worn.

    - Hands

Safety gloves must be worn during any activity that there is a risk of hand injury (climbing of ladder, cable pulling, hoisting etc.)

    - Feet

Safety boots must be worn at all times.

    - Body

Fire Retardant coveralls must be worn at all times.

    - Work Area

All personnel shall ensure the following:

      - A tidy site must be established and maintained.

      - All accumulated site rubbish must be removed at regular intervals.

      - All statutory warning signs must be installed.

      - Safe access and exit to and from sites must be maintained.

      - All site materials must be stored in an orderly fashion.

      - Contractor management must regularly inspect working site

      - Permit to work must be obtained for the relevant activities, displayed and kept-up to date.

# FIRST AID

- Approved first aid kits shall be available and crew made aware of their location.

- Selected members of the crew must be trained in first aid.

- Supervision to be provided fire and medical emergency response numbers

# FIRE PRECAUTIONS

It is a major requirement to protect against losses due to fire. As a result, adequate measures must be taken to protect individuals as well as the asset for risk due to fire or explosion.

Suitable firefighting equipment shall be provided to ensure adequate protection against these hazards. This equipment, together with fire alarm system and means of escape shall be maintained as far as reasonably practical.

As part of the site induction, all the personnel involved in the execution of the works for this CONTRACT shall receive basic information of the site fire prevention and emergency procedures

Minimum standard is defined as:

- Knowledge and understanding of cause and nature of fire.

- Knowledge and use of fire extinguishers.

- Understanding of evacuation procedure in case of emergency.

- Recognition of calm behavior in order to eliminate panic.

- Recognition of fire extinguishers and types of fires they are most effective against.

# WELFARE FACILITIES

CONTRACTOR shall provide for his employees on site:

- Protection against weather.

- Adequate supplies of drinking water.

# CONTROL OF HAZARDS TO HEALTH

- Material Safety Data Sheets must be made available at the work site for all controlled (hazardous) products.

- A work permit will be required for all work carried out in the vicinity of electrical and process systems.

- A first-aid kit adequate appropriate to number of personnel on site must be provided.

- An emergency list of telephone numbers and location of nearest first aid facility must be posted.

# HS&E INCIDENCE REPORTING

- In the event of any emergency, injury, spill and/or near miss the Project Manager must be informed immediately.

- All unsafe acts and unsafe acts must also be reported to must be reported to the Project Manager in a timely manner.

# INFRASTRUCTURE AND MINIMUM SPACE REQUIREMSNT FOR THE AMBULANCE & TRANSPORT SERVICE COMPLEX

|  | Function | Minimum Area (sqft) | Approx. Size (L × B ft) |
| --- | --- | --- | --- |
|  | GROUND FLOOR |  |  |
| 1 | Covered parking for minimum three (3) ambulances and one (1) transport van. | 850–950 | 38 × 24 ft |
| 2 | Maintenance and washing bay with proper drainage and oil & grease trap connection. | 250–300 | 15 × 18 ft |
| 3 | Minor repair and tyre changing area. | 150–200 | 12 × 15 ft |
| 4 | Tool and consumables store. | 80–120 | 8 × 10 ft |
| 5 | Electrical and service rooms on raised plinth. | 80–120 | 8 × 10 ft |
| 6 | Protected staircase and lift core. | 250–300 | 15 × 18 ft |
|  | Ground Floor Total | 1,750–1,900 |  |
|  | FIRST FLOOR |  |  |
| 1 | Drivers’ lounge. | 200–250 | 14 × 16 ft |
| 2 | Paramedic lounge and resting area with seating. | 250–300 | 15 × 18 ft |
| 3 | Locker facilities for operational staff. | 120–150 | 10 × 12 ft |
| 4 | Male and female toilets with shower and washing facilities. | 80–100 | 8 × 8 ft |
| 5 | Female toilets with shower and washing facilities. | 80–100 | 8 × 8 ft |
| 6 | Small pantry / tea room. | 80–100 | 10 × 10 ft |
| 7 | Meeting / briefing room for operational coordination. | 200–250 | 14 × 16 ft |
| 8 | Storage room for PPE and operational equipment | 100–120 | 10 × 10 ft |
| 9 | Circulation | 250–280 |  |
|  | First Floor Total | 1,450–1,650 |  |
|  | SECOND FLOOR |  |  |
| 1 | Central ambulance control and dispatch room. (Minimum five (5) operator workstations) | 450–550 | 22 × 22 ft |
| 2 | Separate supervisor cabin. | 100–120 | 10 × 10 ft |
| 3 | Meeting room. | 180–220 | 12 × 16 ft |
| 4 | Male toilets. | 50–70 | 6 × 8 ft |
| 5 | Female toilets. | 50–70 | 6 × 8 ft |
| 6 | UPS room (connection to AEH central server) | 100–130 | 10 × 10 ft |
| 7 | Circulation | 250–300 |  |
|  | Second Floor Total | 1,450–1,650 |  |
|  | TERRACE LEVEL |  |  |
| 1 | Staff refreshment terrace (open seating/multipurpose area) | 1,400–1,700 | 38 × 40 ft (approx.) |
| 2 | Refreshment counter & pergola | 120–180 | 10 × 12 ft |
| 3 | Staircase access and landing | 120–150 | 10 × 12 ft |
|  | Total Usable Terrace Area | 1,400–1,700 |  |

Terrace area

The roof level shall function as a staff refreshment terrace.

- Terrace Area (Base Requirement – Mandatory):
The roof level shall be completed as a safe accessible terrace including waterproofing system, finished surface, rainwater drainage, lighting as required, and parapet wall minimum 1.2 m height from finished floor level or as required by applicable building regulations, whichever is higher.

-------------------------------

# APPENDIX A: SITE INFORMATION & EXISTING SITE CONDITIONS

1. Site Information

The proposed Ambulance & Transport Service Complex shall be constructed on the land allocated to Addu Equatorial Hospital (AEH), located along Maarandhoo Magu, Addu City, Republic of Maldives.

The Contractor shall undertake the design and construction of the facility based on the site information provided below. The Contractor shall verify all site dimensions and existing conditions prior to commencement of the detailed design.

| Item | Description |
| --- | --- |
| Project | Ambulance & Transport Service Complex |
| Client | Addu Equatorial Hospital |
| Location | Maarandhoo Magu, Addu City |
| Plot No. | BL353 |
| Approximate Land Area | 1,924 sqft (178.7 m²) |
| Approximate Plot Dimensions | 47'-5" × 41'-3" |
| Road Frontage | Maarandhoo Magu |
| Site Access | Direct vehicular access from Maarandhoo Magu |
| Proposed Development | Three-storey Ambulance & Transport Service Complex with Accessible Roof Terrace |

2. Existing Site Conditions

- The proposed construction site is vacant.

- No permanent buildings currently exist within the allocated plot.

- No demolition works are required under this Contract.

- The site fronts directly onto Maarandhoo Magu, providing suitable vehicular access for ambulance operations.

- Existing utility connection points shall be verified by the Contractor prior to construction.

- The Contractor shall verify all site dimensions, levels and existing conditions before commencing the detailed design.

3. Site Visit

Tenderers shall be deemed to have inspected and examined the Site and satisfied themselves regarding:

- Existing site conditions.

- Site dimensions and levels.

- Ground conditions.

- Access arrangements.

- Existing utilities.

- Drainage conditions.

- Temporary works requirements.

- Material storage areas.

- Construction access.

Failure to inspect the Site shall not relieve the Contractor of any responsibility under the Contract.

4. Contractor's Responsibilities

The Contractor shall:

- Verify all site dimensions prior to commencement of the detailed design.

- Report any discrepancies identified during the site survey to the Employer before proceeding with the design.

- Ensure that the proposed building, ambulance circulation, parking, drainage, utility connections and associated external works are suitable for the available site.

- Comply with all applicable planning regulations, building regulations and relevant statutory requirements of the Republic of Maldives.

5. Site Plan

The Site Plan attached below is provided to indicate the location, approximate plot dimensions, road frontage and orientation of the proposed development site.

The Site Plan is provided for tender reference only. The Contractor shall verify all dimensions, levels and existing site conditions prior to commencement of the detailed design.

Figure A-1: Proposed Site for Ambulance & Transport Service Complex