## Cover
Bill of Quantities
Project :Fuvahmulah City 2 Floor Multi Purpose Laboratory
CLIENT
Ministry Of Fisheries Marine Resources And Agriculture
Republic of Maldives

## Summary of Building
Project :Fuvahmulah City 2 Floor Multi Purpose Laboratory
SUMMARY OF BILL OF QUANTITIES
Bl.no | Item Description | Amount
Note | PREAMBLE TO BILL OF QUANTITY
1 | PRELIMINARIES
2 | GROUND WORKS
3 | CONCRETE WORKS
4 | MASONRY & PLASTERING
5 | FLOORING & TILING
6 | DOORS & WINDOWS
7 | WOOD WORK & CEILING
8 | PAINTING
9 | METAL WORK
10 | HYDRAULICS & DRAINAGE
11 | ELECTRICAL INSTALLATIONS
12 | FIRE FIGHTING SYSTEM
13 | ADDITIONS
14 | OMISSIONS
0
| TOTAL Mvr | 0 | 0
| 6% GST Mvr | 0
| GRAND TOTAL Mvr | 0

## BoQ of Building
Project :Fuvahmulah City 2 Floor Multi Purpose Laboratory
Item | Description | Unit | Qty | Material Rate | Labour Rate | Total
PREAMBLE TO BILL OF QUANTITY
Note | 1. General
a) The nature of this contract is measured unit price contract and the Bill of Quantity (BOQ) shall reflect this fact.
b) BOQ shall be read and construed in conjunction with other Contract Documents
c) The Tenderer is obliged to check the number of the pages of the Bill of Quantity and should any be found missing or duplicated or the figures or writing indistinct, the Tenderer must notify the Employer/Engineer at once and have the matter rectified before the Tender is submitted. No liability whatsoever will be accepted in respect of any claim for errors in the Tenderer’s offer resulting from failure to comply with the foregoing.
d) The Tenderer is deemed to have visited the site/s and fully acquainted himself as to the location of each of the items and works to be carried out and to all conditions which may affect the performance of the works, including but not limited to: -Access to each of the roads where solid waste transfer process will be carried out, and Access for the dump site. -Restrictions applicable to working in Male City area. -All safety regulations and employer site safety procedures. -All Safety regulations.
e) The Tenderer is also deemed to have surveyed the actual condition of the site and buildings and made his own assessment of the type and extent of the works prior to submitting his offer
2. Quantities
Even though that practical care was exercised in preparing the BOQ, but all quantities given herein shall be deemed to be estimated quantities of the work to be done but they are not to be taken as actual and correct quantities of the work to be executed and they are not to absolve the contractor of his obligations under the Contract. They are not to be taken as guarantee that the actual quantities increase or decrease, and any claim whatsoever submitted for cost or extra expenses incurred from such increase or decrease will not be accepted by Employer/Engineer except where else stipulated in the Contract.
3. Materials
All materials used are to be of the best new available and subject to the Employer/Engineer approval, and of durable nature, guaranteed, not liable to any base exchange and manufactured according to applicable BS, ASTM or DIN Standards. Execution also is subject to approval of Employer/Engineer and shall be the best available common practice in engineering codes at the time of execution.
4. Unit Price and Currency
The Unit Prices entered against the various items in the following Bill of Quantities include all operations for execution, completion and maintenance of the various items of the works finished completely in every respect till the final acceptance as specified or described in the Tender Documents, with or without modifications, either by way of additions or deductions, or alterations as may be offered in writing during the progress of the works, and include, without being limited to, all matters and things particularly referred to in the Tender Documents.
The Unit Price shall cover all costs of every kind whatsoever including, without being limited to, all charges for additional site installations, relocation, supervision, labor, transportation and supply of materials; the provision, maintenance, use and efficient repair of all plant, equipment and appliance of every kind, the construction and maintenance of all temporary works, the performance of all services and the fulfillment of all obligations and responsibilities herein defined.
The Tenderer shall be deemed to have fully considered all the conditions, obligations, and requirements of the Tender Documents before entering the respective unit price against the various items of the Bill of Quantities.
The Unit Prices given hereunder the BOQ shall also include erection, installation, fixing, and re-fixing of all elements. These prices shall also include taxes, visa for labor, gate passes, accommodations for the Contractor’s staff and labors, all required insurance and work permits, guarantees, bonds, traffic plan requirements, safety procedures, etc. and all requirements necessary to have the work maintained until its final handing over.
The Unit Prices given hereunder in the Bill of Quantity for this work shall also include overheads, risks, profit etc. and all other financial matters to have all these civil works completed.
PREAMBLE TO BILL OF QUANTITY
BILL No: 01
PRELIMINARIES
1.1.0 | General Notes
1 ) | Abbreviations
m - metre
no - numbers
m³ - cubic metre
m² - square metre
m - metre
t - tonnes
incl - including
mm - millimetre
dia - diameter
SS - Stainless Steel
GI - Galvanised Iron
1.2.0 | Site Management Costs
1 ) | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings, fences, Crane/Concrete pump, Machinaries and similar items | Item | 1
1.3.0 | Sign Board
1 ) | Allow for sign board. | item | 1
1.4.0 | Safety
1 ) | Safety - Providing and fixing scaffolding with G.I. pipes and clamps and pvc netting alaround building during construction | Item | 1
1.5.0 | Clean-up
1 ) | Allow for clean-up of completed works and site upon completion. | Item | 1
1.6.0 | Insurance, Bonds, Guarantees and Warranties
1 ) | Insurance as stated in the General Consditions. | Item | 1
1.7.0 | As-Built Drawings
1 ) | Preparation and submission of "as-built" Drawings. | Item | 1
BILL No: 01 PRELIMINARIES
TOTAL OF BILL No: 01 - Carried over to summary
BILL NO : 02
GROUND WORK
2.1.0 | General
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, consolidating, additional working space and disposing surplus soil.
2.2.0 | Site clearance
| Clearing site - Demolition of Existing building and dispatch all debris, clearing and dispose all unwanted materials away from site and prepare site ready for proposed construction. | m² | 579.82
2.3.0 | Shoring
| Charges for construction of 150mm thick solid block Masonry wall complete including plastering, below existing adjacent building to protect side buildings. | m² | 209
2.4.0 | Excavation
(a) Excavation quantities are measured to the faces of concrete members. Rates shall include for all additional excavation required to place the formwork , back fill , dewatering and others
2.4.1 | Excavation
1 | F1, 1500 x 1500 x 300 | m³ | 13.5
2 | F2, 1300 x 1300 x 300 | m³ | 5.07
3 | F3, 1200 x 1200 x 300 | m³ | 10.08
4 | F4, 1000 x 1000 x 300 | m³ | 8
5 | F5, 800 x 800 x 300 | m³ | 3.84
6 | F6, 550 x 550 x 200 | m³ | 9.9825
7 | TB, 225 x 400 | m³ | 1.4175
8 | WF, 225 x 225 | m³ | 1.4175
2.4.2 | Back filling
(a) Rates shall include for: leveling, grading, trimming and compacting.
(b) Ground need to be compacted to the density required by the consultant
1 ) | 150mm thick highly compacted hard core from Ground floor to below ground floor slab | m² | 579.82
2 ) | 50mm thick Cement/sand blinding layer (1:10 - Cement & Local Sand mix) to receive damp proof membrane below ground floor slab. | m² | 579.82
2.4.3 | Damp Proof Membrane
(a) Rates shall include for: dressing around and sealing to all penetrations, laps and turnups.
2.4.3.1 | Foundation & Beams Below ground
1 ) | Polythene damp proof membrane (2000 gauge) laid on blinding layer. | m² | 54.5225
2.4.3.2 | Ground Slab
1 | Polythene damp proof membrane (2000 gauge) laid on blinding layer. | m² | 54.5225
BILL No: 02 GROUND WORKS
TOTAL OF BILL No: 02 - Carried over to summary
BILL NO : 03
3.0.0 | CONCRETE
(a) Rates shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
(b) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6 by volume.
(c) Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
3.0.1 | FORM WORK
(a) Exposed surface shall have fair finish while remaining may have rough finish.
(b) Timber used for unexposed concrete surface shall sound dressed and seasoned good quality common timber while for exposed concrete surfaces dressedand matched boards uniformly thick and not more than 251mm wide.
c) Plywood used for forms shall be of commercial standard, moisture resistane conrete form plywoodnot lessthan 6mm thick and atleast 12mm thick.
(d) Rates shall include for; all necessary boarding,supports, erecting, framing, temporary cambering cutting, perforations for reinforcing bars, bolts,straps,ties, hangers, pipes and removal of formwork.
3.0.2 | REINFORCEMENT WORK
(a) Main reinforcement steel shall be high tensile steel hot rolled deformed bars complying with BS 1119 or BS 1172 Characteristic strength not less than 160N/mm2.
(b) Stirrups shall be hot rolled mildsteel round bars complying with BS 1119, Characteristic strength not less than 250N/mm2
(c ) Rates shall include for; distribution steel, cleaning, fabrication, placing, the provision for all necessary temporary fixings, and supports including chairs and tie wire , laps and wastage.
3.1.0 | LEAN CONCRETE
3.1.1 | 50mm thick lean concrete below Foundation
1 ) | Foundation Footings & Tie beams | m² | 54.5225
3.2.0 | REINFORCED CONCRETE
3.2.1 | FOUNDATIONS
1 ) | F1, 1500 x 1500 x 300 | m³ | 4.05
| Formwork | m2 | 10.8
| 10 | kg | 110.88
2 ) | F2, 1300 x 1300 x 300 | m³ | 1.521
| Formwork | m2 | 4.68
| 10 | kg | 41.6416
3 ) | F3, 1200 x 1200 x 300 | m³ | 3.024
| Formwork | m2 | 10.08
| 10 | kg | 82.7904
4 ) | F4, 1000 x 1000 x 300 | m³ | 2.4
| Formwork | m2 | 9.6
| 10 | kg | 65.7067
5 | F5, 800 x 800 x 300 | m³ | 1.152
| Formwork | m2 | 5.76
| 10 | kg | 31.5392
6 | F6, 550 x 550 x 200 | m³ | 1.9965
| Formwork | m2 | 14.52
| 10 | kg | 81.9896
7 | TB, 225 x 400 | m³ | 6.03
| Formwork | m2 | 53.6
| 16 | kg | 423.172
| 6 | kg | 185.925
8 | WF, 225 x 225 | m³ | 8.4038
| Formwork | m2 | 74.7
| 16 | kg | 1048.456
| 6 | kg | 331.668
3.2.2 | Column
1 ) | C1, 200 x 200 | m3 | 0.264
| Formwork | m2 | 5.28
| 16 | kg | 41.6856
| 6 | kg | 7.8144
2 | C2, 200 x 200 | m3 | 1.056
| Formwork | m2 | 21.12
| 12 | kg | 93.7728
| 6 | kg | 31.2576
3.3.0 | GROUND FLOOR
3.3.1 | Column
1 ) | C1, 200 x 200 | m3 | 0.72
| Formwork | m2 | 14.4
| 16 | kg | 113.688
| 6 | kg | 21.312
2 | C2, 200 x 200 | m3 | 2.88
| Formwork | m2 | 57.6
| 12 | kg | 255.744
| 6 | kg | 85.248
3.3.3 | Rc Ground Floor Slab
1 ) | 100 | m3 | 57.9
| Formwork, slab including Entrance Steps | m2 | 11
| 10 | kg | 3566.64
3.3.4 | Staircase
1 ) | R.c.c. Staircase -1 | m3 | 1.7673
| Formwork | m2 | 28.5
| 10 | kg | 96.7695
2 | R.c.c. Staircase -2 | m3 | 1.7673
| Formwork | m2 | 28.5
| 10 | kg | 96.7695
3.4.0 | FIRST FLOOR BEAM LEVEL
3.4.1 | Slab Beams
1 ) | B1, 200 x 400 | m3 | 1.6692
| Formwork | m2 | 16.692
| 20 | kg | 474.9516
| 16 | kg | 50.6859
| 12 | kg | 28.5048
| 6 | kg | 85.5144
2 ) | B2, 200 x 400 | m3 | 1.1804
| Formwork | m2 | 11.804
| 20 | kg | 335.8692
| 6 | kg | 60.4728
3 ) | B3, 200 x 400 | m3 | 2.1112
| Formwork | m2 | 21.112
| 20 | kg | 400.4784
| 16 | kg | 128.2148
| 6 | kg | 72.1056
4 | B4, 200 x 400 | m3 | 1.95
| Formwork | m2 | 19.5
| 16 | kg | 236.85
| 12 | kg | 66.6
| 6 | kg | 66.6
5 | B5, 200 x 400 | m3 | 1.3312
| Formwork | m2 | 13.312
| 16 | kg | 161.6896
| 6 | kg | 45.4656
3.4.2 | Slab level -1
1 | 140 | m3 | 35.6272
| Formwork | m2 | 254.48
| 10 | kg | 3656.576
2 | 150 | m3 | 0.51
| Formwork | m2 | 3.4
| 10 | kg | 64.68
3.4.3 | Column
1 ) | C1, 200 x 200 | m3 | 0.84
| Formwork | m2 | 16.8
| 16 | kg | 132.636
| 6 | kg | 24.864
2 | C2, 200 x 200 | m3 | 3.36
| Formwork | m2 | 67.2
| 12 | kg | 298.368
| 6 | kg | 99.456
3.5.0 | ROOF BEAM
3.5.1 | Roof Beams
1 ) | RB1, 200 x 400 | m3 | 3.152
| Formwork | m2 | 31.52
| 16 | kg | 248.8504
| 12 | kg | 69.9744
| 6 | kg | 69.9744
2 | RB2, 200 x 400 | m3 | 10.728
| Formwork | m2 | 107.28
| 12 | kg | 476.3232
| 6 | kg | 238.1616
3.6.0 | OTHER CONCRETE WORKS
3.6.1 | Window Sill & Lintels
| Charges for construction of R.c.c. Sills and Lintels for the windows and doors as per details. Rate shall include for shuttering and Reinforcement works complete. | item | 1
3.6.2 | Rc Ground Water Well (1200mm dia)
| Charges for Construction of 1200mm Diameter R.c.c. Well as per drawing details. Rate shall include for; form work, reinforcement etc complete. | item | 1
3.6.3 | Absorption Trench 1000mm dia 1400 Depth
| Concrete Grate Drain Trench. Charges for Construction of 1000mm Diameter R.c.c. Well as per drawing details. Rate shall include for; form work, reinforcement etc complete. | item | 1
3.6.4 | Rain Water Tank (5000 x 2000 x 1200 Depth) |  |  |  |  | 0
| RC concrete rain water tank | m3 | 6.4 |  |  | 0 | 10 | 1 | 10 | 10 | 100
| Formworks rain water tank | m2 | 64 |  |  | 0 | 10 | 1 | 10 | 10 | 100
| 12mm dia deformed bars - 6m | kg | 759.4667 |  |  | 0
3.6.5 | Waterproofing & Admixtures
(a) | Apply Rubberised bitumin water proofing paint, 2 coats to all exposed concrete and masonry surface below ground level. Consultant to approve | item | 1
(b) | Add approved water proofing admixture as per specification to all concrete below ground level. | item | 1
(c) | Add Plasticiser admixture as per specification to all concrete Substreucture and Super structure. | item | 1
BILL No: 03 - CONCRETE WORKS
TOTAL OF BILL No: 03 - Carried over to summary
BILL No: 04
MASONRY AND PLASTERING
4.1.0 | General
a )Rates shall include for cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs.
b )Cutting or leaving holes and openings as recesses for and building in pipes, conduits , sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joints.
c ) All external wall and all inetrenal walls shall be 100mm thick Solid cement blocks and for masonry mix ratio 1:5 (cement and river sand)
MASONRY
4.1.1 | BELOW GROUND LEVEL
1 ) | 150mm thick Solid block single wall above all Tie beams. | m2 | 104.85
4.1.2 | GROUND FLOOR LEVEL
1 ) | External walls
a ) | 150mm thick Solid block single wall | m2 | 382.4215
2 ) | Interior walls
a ) | 150mm thick Solid block single wall | m2 | 189.033
b ) | 100mm thick Solid block single wall | m2 | 4.26
4.1.3 | FIRST FLOOR LEVEL
1 ) | External walls
a ) | 150mm thick Solid block single wall | m2 | 165.26
2 ) | Interior walls
a ) | 150mm thick Solid block single wall | m2 | 189.996
b ) | 100mm thick Solid block single wall | m2 | 4.26
4.2.1 | PLASTERING
(a) 25mm thick Cement plastering on Exterior surface of External masonry walls and concrete surfaces and 16mm thick plastering on interior walls and concrete surface as specified incl. wire mesh shall be fixed at the joints of concrete surfaces and walls before plastering. Quantity is measured including concrete surfaces - Parapetwalls, Liftwalls, columns & beams.
(b)Rates shall include for External plastering shall 25mm thick (13+12mm) 2 coats in 1:4 cement and river sand mix ratio
c) Rates shall include for approved brand water proofing compound shall be mixed with cement mortar for external wall plastering as per manufacturers specifications.
4.2.2 | BELOW GROUND LEVEL
1 ) | 25mm thick Plastering
a ) | Both surface of below ground level | m2 | 209.7
4.2.3 | GROUND FLOOR LEVEL
1 ) | External Plastering
a ) | External surface of exeterior wall | m2 | 382.4215
2 ) | Internal Plastering
a ) | Internal surface of external wall and both surface of Interior walls | m2 | 760.4875
b ) | Internal surface of 100mm wall | m2 | 4.26
c ) | External surface of RC lift wall | m2 | 27.65
4.2.4 | FIRST FLOOR LEVEL
1 ) | External Plastering
a ) | External surface of exeterior wall | m2 | 165.26
2 ) | Internal Plastering
a ) | Internal surface of external wall and both surface of Interior walls | m2 | 545.252
b ) | Internal surface of 100mm wall | m2 | 4.26
c ) | External surface of RC lift wall | m2 | 27.65
BILL No: 04 - MASONRY AND PLASTERING
TOTAL OF BILL No: 04 - Carried over to summary
BILL N0: 05
FLOORING & TILING
5.1.0 | General
(a) Rates shall include for laying 50mm thick cement mortar in 1 : 5 mix ratio,cleaning down to reveals where necessary and water proofing of Toilet and Balcony floors & Terrace.
FLOORING
50mm thick Floor Screeding
5.1.1 | GROUND FLOOR
1 ) | Ground floor Screed | m2 | 579.82
5.1.2 | FIRST FLOOR
1 ) | First floor Screed | m2 | 255
5.2.1 | FLOOR FINISHES
(a) Rates shall include for: Fixing, bedding, grouting, and pointing materials, making good around pipes, sanitary fixtures, and similar; cleaning & Polishing.
(b) All Tiling work in accordance with specifications and finishes schedule.
(c) Tiles rate shall be given as specified in the drawing.
5.2.2 | GROUND FLOOR
5.2.2.1 | FLOOR TILING (600x600 Homogenous)
1 ) | Floor tiling | m2 | 248
5.2.2.3 | WALL TILING (300x300 Homogenous)
| Toilet walls @ 2.8m height | m2 | 47.6
5.2.3 | FIRST FLOOR
5.2.3.1 | FLOOR TILING (600x600 Homogenous)
1 ) | Floor tiling | m2 | 264
5.2.3.2 | WALL TILING (300x300 Homogenous)
| Toilet walls @ 2.8m height | m2 | 44.8
5.3.1 | WATER PROOFING
Apply 2 coats of Water proofing Compound, on wet surfaces - Toilets, Balcony, Roof slabs
1 ) | Roof slabs | m2 | 13
5.4.1 | TILE ADHESIVE
1 ) | Charges for supplying special tiles grout for fixing tiles to all floors. | m2 | 512
BILL No: 05 -FLOORING AND TILING
TOTAL OF BILL No: 05 - Carried over to summary
BILL N0: 06
DOORS AND WINDOWS
6.1.0 | General
(a) Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
(b) Rates shall include for door frames and window frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings and installation.
(c) All Timber door frames shall be treated timber. Rate shall include for Paint/Varnish finish.
(d) All louvres, windows and sliding doors shall be 30 micron powder coated aluminium as per details given in Door/Window schedule.
(e) All doors and windows shall be accordance with door/window drawing details.
6.2.0 | GROUND FLOOR
DOOR UNITS
External
1 | D1, 2100 x 900, Solid Core Frame, Solid Core Panel/Leaf, (No Glazing) | no | 1
2 | D4, 2100 x 1450, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Partial Glazing) | no | 7
3 | D5, 2700 x 5485, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Reflective Glass) | no | 1
4 | W3, 800 x 1250, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 2
5 | W4, 800 x 1990, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
6 | W6, 1600 x 1850, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
7 | W10, 1100 x 3500, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 2
8 | W13, 1600 x 1285, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 2
9 | W14, 1600 x 3500, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 2
Internal
1 ) | D1, 2100 x 900, Solid Core Frame, Solid Core Panel/Leaf, (No Glazing) | no | 9
2 ) | D2, 2210 x 1200, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Partial Glazing) | no | 6
3 | D4, 2100 x 1450, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Partial Glazing) | no | 1
6.3.0 | FIRST FLOOR
DOOR UNITS
External
1 | D1, 2100 x 900, Solid Core Frame, Solid Core Panel/Leaf, (No Glazing) | no | 1
2 | W1, 800 x 1050, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
3 | W2, 800 x 1050, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
4 | W5, 1100 x 1990, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
5 | W6, 1600 x 1850, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
6 | W7, 1100 x 2400, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
7 | W8, 1100 x 2535, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
8 | W9, 1100 x 2675, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
9 | W10, 1100 x 3500, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 2
10 | W11, 1500 x 1600, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 1
11 | W12, 1500 x 3500, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 3
12 | W14, 1600 x 3500, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Clear Glass) | no | 3
Internal
1 | D1, 2100 x 900, Solid Core Frame, Solid Core Panel/Leaf, (No Glazing) | no | 6
2 | D2, 2210 x 1200, Powder Coated Aluminum Frame, Powder Coated Aluminum Panel/Leaf, (Partial Glazing) | no | 7
BILL N0: 06 - DOORS AND WINDOWS
TOTAL OF BILL No: 06 - Carried over to summary
BILL No: 07
WOOD WORK & CEILING
7.1.0 | General
(a) Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails,bolts & screws.
(b) Rates shall include for applying approved quality wood preservators as per manufactures instructions for all Timber structures.
(c) Rates shall include for 6mm thick Cement board fixed on 35 x 50mm Timber frame,trimming, nails, screws,hooks, hangers, clips and similar.
(d) Rates shall include for 9mm thick Plaster board fixed on 35 x 50mm Timber frame,trimming, nails, screws,hooks, hangers, clips and similar.
7.2.0 | CEILING WORKS
7.2.1 | GROUND FLOOR
Ceiling
1 | 6mm thick Cement Board False Ceiling [200mm below beam bottom] | m2 | 63
7.3.0 | ROOFING WORKS
7.3.1 | ROOF LEVEL-1
1 | 200x50mmTimber Ridge /Hip | m | 77
2 | 150mm x 50mm Timber Rafters @600c/c | m | 625
3 | 50x50mm Timber Purlins @600c/c | m | 665
4 | 150mm x 65mm Wall plate | m | 84
5 | 200mm x 25mm Timber Facia | m | 84
BILL No: 07 - WOOD WORK & CEILING
TOTAL OF BILL No: 07 - Carried over to summary
BILL No: 08
PAINTING
8.1.0 | General
(a) Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window furniture.
(b) All painting work shall be carried in accordance with the Specifications
(c)Rate shall include for weather proof paint finish for exterior surfaces of the wall complete including application of two coats of oil based wall sealer and two coats of weather bond paint
(d)Rate shall include for putty and paint finish for interior surfaces of the wall and ceilings complete including application of two coats of wall sealer, two coats of putty finish and two coats of emulsion paint finish on top for Interior painting.
8.2.0 | GROUND FLOOR
1 ) | Painting exterior surfaces of External Wall, Columns & beams. | m2 | 382.4215
2 ) | Painting interior surfaces Wall, Columns & beams) | m2 | 760.4875
3 ) | Painting Soffit of slab (Ceiling) | m2 | 254
8.3.0 | FIRST FLOOR
1 ) | Painting exterior surfaces of External Wall, Columns & beams. | m2 | 165.26
2 ) | Painting interior surfaces Wall, Columns & beams) | m2 | 545.252
3 ) | Painting Soffit of slab (Ceiling) | m2 | 254
BILL No: 08 - PAINTING
TOTAL OF BILL No: 08 - Carried over to summary
BILL No: 09
METAL WORK
9.1.0 | General
(a) Rates shall include for ; all labour in framing, cutting, welding, cleats, baseplates, flanges,screws, nails, bends, and similar complete with grinding, surface smoothening and polish finishes.
9.2.1 | RAILING
9.3.1 | GROUND FLOOR
1 ) | GI. Railing - Staircase (G-1st) | no
| Supply, Fabrication and Fixing GI Railing as per details | item | 2
9.3.1 | GI COLUMN
9.3.2 | GROUND FLOOR
1 ) | GI.CHS Dia 100 x 2.6mm | no
| Supply, Fabrication and Fixing GI Dia 100 x 2.6mm as per details | item | 33
9.4.0 | ROOF STRUCTURE
9.4.1 | ROOF FRAMING
Roof Truss - Supply, Fabrication and Fixing Roof Trusses complete with Base plates, Bolts, nuts, Washers etc including Paint Finishes. Refer drawing details
1 | TR1 (Refer drawing details) | m | 79
2 | 50mm dia x 2.6mm GI bracing members (Refer drawing details) | m | 73
3 | 100x50x2.5mm GI C purlins @600c/c | m | 278
4 | Roof Covering - Polycarbonate Roofing sheet (LOWER ROOF) | m2 | 263
5 | Roof Covering - Supply and Fixing BHP Lysaght Roofing sheet (UPPER ROOF) | m2 | 980
6 | 50mm mineral wool insulation between purlins | m2 | 980
7 | Capping - Supply and Fixing 600mm wide Lysaght Ridge Capping | m | 77
8 | Gutter - Supply and Fixing 200 x 200mm Lysaght Gutter complete including brackets and clips. | m | 84
BILL No: 09 - METAL WORK
TOTAL OF BILL No: 09 - Carried over to summary
BILL No: 10
HYDRAULICS & DRAINAGE
10.1.0 | General
(a) Design provide and install plumbing network for the entire building complete in accordance to standard set by the local governing body MWSC
(b) The following items and description and the plumbing drawings are given as guidance as to the nature of the information to be returned by the contractor.
(c) Ground water connection shall be made as specified in the drawings.
(d) The cost shall include for; sockets, running joints, connectors, elbows, junctions, reducers, expansion joints, back nuts and similar, incidental fittings, clips, saddles, brackets, straps, hangers, screws, nails , pvc glues, threadseals and fixing complete, including cutting and forming holes, excavating, laying pipes , backfilling trenches.
(e) All pipes shall be High Pressure uPVC "Mutha" or equivalent brand.
10.2.0 | GROUND FLOOR
10.2.1 | Hydraulics
a ) | Charges for Piping for fresh water Pipe work | item | 1
b ) | Charges for Piping for Ground water supply pipe work. | item | 1
c ) | Charges for Providing and Fixing Heavy duty water pump Davey brand for Ground water supply to all floors - ground water net work. | no | 1
d ) | Charges for Providing and Fixing Heavy duty water pump Davey brand for Ground water supply to all floors - Rain water net work. | no | 1
10.2.2 | Drains / Traps & other fixtures
1 ) | Floor Drain | no | 3
2 ) | Floor Gully | no | 4
3 ) | Gully Trap | no | 1
4 ) | Manhole | no | 1
5 ) | 110Ø Rainwater Outlet Perforated Cowl | no | 2
6 ) | Bottle Trap | no | 4
7 ) | Bottle Trap For Sink | no | 4
10.2.3 | Sanitary Fixures & Accessories
1 ) | Basin Faucet | no | 2
2 ) | Bib Tap | no | 2
3 ) | Bidet Shower | no | 2
4 ) | Sink Tap | no | 6
5 ) | Wash Basin | no | 2
6 ) | Water Closet | no | 2
7 ) | Rain Water Bip Tap | no | 2
8 ) | Gate Valve | no | 15
9 ) | Non Return Valve | no | 2
10 ) | MWSC Meter | no | 1
11 ) | Rain Water Pump | no | 1
12 ) | Well Water Pump | no | 1
13 ) | Foot Valve With Strainer | item | 2
10.2.4 | Drainage
10.2.5 | Sewerage & Drainage: Charges for piping for all discharge pipes, sewerage and drainage pipes including connection to Main Sewer network from the Fixtures. | item | 1
10.3.0 | FIRST FLOOR
10.3.1 | Hydraulics
a ) | Charges for Piping for fresh water Pipe work | item | 1
b ) | Charges for Piping for Ground water supply pipe work. | item | 1
10.3.2 | Drains / Traps & other fixtures
1 ) | Floor Drain | no | 4
2 ) | Floor Gully | no | 2
3 ) | Bottle Trap | no | 6
4 ) | Bottle Trap For Sink | no | 3
10.3.3 | Sanitary Fixures & Accessories
1 ) | Basin Faucet | no | 2
2 ) | Bidet Shower | no | 2
3 ) | Sink Tap | no | 7
4 ) | Wash Basin | no | 2
5 ) | Water Closet | no | 2
6 ) | Gate Valve | no | 10
10.3.4 | Drainage
10.3.5 | Sewerage & Drainage: Charges for piping for all discharge pipes, sewerage and drainage pipes including connection to Main Sewer network from the Fixtures. | item | 1
10.3.0 | ROOF LEVEL
10.3.1 | Hydraulics
1 | Rainwater Down Pipes: Charges for piping for all discharge pipes and Drainage pipes including fittings and fixtures from the Gutter to Ground floor. | item | 1
BILL No: 10 - HYDRAULICS AND DRAINAGE
TOTAL OF BILL No: 10 - Carried over to summary
BILL No: 11
ELECTRICAL INSTALLATIONS
11.1.0 | General
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil
(c) Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces and also all elecetrical work shall be carried out according to the Utility Regulation Authority standards and specifications.
(d) Each Light/ light fixture and its switch is measured as one one point; similarly each fan or each socket outlet is measured as one point;
(e) Rates shall include for supply and complete installation of fittings and fixtures.
(f) Rate for all electrical panels shall include for supply and installation of all necessary MCCBs, MCBS, EFRs, ELCBs, auxiliary contacts, Voltmeters, ammeters, Digital analyser,kWh meters, indicator lamps, selector switches, copper bus bars, inter locks, aligning and grounding of the panel, inter connectors, internal wiring connections to switch gear,steel channels and necessary hardware fixing insulating materials,all in fully enclosed metal clad panels and distribution boards completed as shown in drawing. They shall comply with the specifications andI.E.E.regulations and be complete to working order to the approval of local authorities.
(g) Rate shall include for supply, installation, maintaining, testing and commissioning of the system for power and lighting according to drawings and specifications to working order.
(h) All materials, equipment wiring shall confirm to local codes, specifications, standards/latest I.E.E. regulations ( BS 7671 ).
11.2.0 | GROUND FLOOR
11.2.1 | Electric Boards
1 ) | Supply and Installation of Utility Regulatory Authority approved Panel Board with kWh Meter | item | 1
2 ) | Wiring connection to Main Panel Board from Existing Main Distribution Panel network. | item | 1
3 ) | DB, Supply and Installation of Utility Regulation Authority approved brand Distribution board | nos | 6
4 ) | 16mm2 Cabling to DBs Wiring | nos | 6
11.2.2 | Lights/ Switches-Fixtures
1 | Ceiling Down Light (18W) - Weather Proof | nos | 15
2 | Ceiling Light (10W) | nos | 2
3 | Ceiling Light (12W) | nos | 25
4 | Ceiling Light (18W) | nos | 5
5 | Recessed Ceiling Light (12W) | nos | 13
6 | Ceiling Recessed Spot Light (3W) | nos | 1
7 | Indoor Wall Light (18W) | nos | 19
8 | Wall Recessed Light With Motion Sensor (Low Level 8W) | nos | 2
9 | 29 inch To 36 inch Ceiling Fan | nos | 1
10 | Light Switch (1 Gang ) | nos | 4
11 | Light Switch (2 Gang ) | nos | 16
12 | Light Switch (3 Gang ) | nos | 7
13 | Light Switch (4 Gang ) | nos | 7
14 | Ceiling Fan Switch With Controller | nos | 1
11.2.3 | Wiring - Lights/ Switches
1 | 2.5mm2 Wiring to Light Points | points | 118
11.2.4 | Fixtures do not Required Wiring (Plug Top)
1 | Ceiling Mounted Exhaust Fan | nos | 2
2 ) | Emergency Light | nos | 8
11.2.5 | Power Points-Fixtures
1 | 13A Power Socket | points | 5
2 | 13A Power Socket in Weatherproof Polycarbonate Enclosure | points | 7
3 | 13A Twin Socket | points | 21
4 | 13A Twin Socket In Floor Mount Pop-up Box | points | 2
5 | 15A Socket In Polycarbonate Box | points | 2
6 | 15A Switched Socket at High Level | points | 1
7 | 20A TPN Isolator | points | 2
11.2.6 | Wiring -Power Points
1 ) | 2.5mm2 Wiring to Power Points | points | 40
11.2.7 | Telecommunications
a) Provide & install Network and Telephone fittings, wiring equipment inclusive of all necessary connection as per local regulations as described
b) All network ,TV and Telephone socket outlets shall be 'Legrand' brand or equivalent, and PABX Gigabit switch shall be Cisco or equivalent
1 ) | Computer Network Outlet | nos | 4
2 | Twin Computer Network Outlet In Floor Mount Pop-up Box | nos | 2
3 | Internet Switchboard | nos | 1
4 | Wireless Access Point | nos | 2
11.2.9 | Wiring - Telecommunications
a) Wiring connections to main telecommunication switch boards from main telecommunication network
1 ) | Cabling - Data Network points (CAT6) | points | 8
2 | Cabling - Internet | points | 2
11.2.0 | FIRST FLOOR
11.2.1 | Electric Boards
1 | DB, Supply and Installation of Utility Regulation Authority approved brand Distribution board | nos | 4
2 | 16mm2 Cabling to DBs Wiring | nos | 4
11.2.2 | Lights/ Switches-Fixtures
1 | Ceiling Down Light (18W) - Weather Proof | nos | 1
2 | Ceiling Light (10W) | nos | 2
3 | Ceiling Light (12W) | nos | 40
4 | Ceiling Light (18W) | nos | 10
5 | Recessed Ceiling Light (12W) | nos | 3
6 | Ceiling Recessed Spot Light (3W) | nos | 1
7 | 42 inch To 48 inch Ceiling Fan | nos | 1
8 | Light Switch (1 Gang ) | nos | 3
9 | Light Switch (2 Gang ) | nos | 1
10 | Light Switch (3 Gang ) | nos | 10
11 | Light Switch (4 Gang ) | nos | 5
12 | Two Way Light Switches (3 Gang ) | nos | 4
13 | Ceiling Fan Switch With Controller | nos | 1
11.2.3 | Wiring - Lights/ Switches
1 | 2.5mm2 Wiring to Light Points | points | 82
11.2.4 | Fixtures do not Required Wiring (Plug Top)
1 | Ceiling Mounted Exhaust Fan | nos | 2
2 | Emergency Light | nos | 6
11.2.5 | Power Points-Fixtures
1 ) | 13A Power Socket | points | 6
1 ) | 13A Twin Socket | points | 17
1 ) | 15A Switched Socket at High Level | points | 3
1 ) | 20A TPN Isolator | points | 2
11.2.6 | Wiring -Power Points
1 ) | 2.5mm2 Wiring to Power Points | points | 28
11.2.7 | Telecommunications
Provide & install Network and Telephone fittings, wiring equipment inclusive of all necessary connection as per local regulations as described
All network ,TV and Telephone socket outlets shall be 'Legrand' brand or equivalent, and PABX Gigabit switch shall be Cisco or equivalent
1 ) | Computer Network Outlet | nos | 1
2 | Twin Computer Network Outlet | nos | 3
3 | Wireless Access Point | nos | 2
11.2.9 | Wiring - Telecommunications
a) Wiring connections to main telecommunication switch boards from main telecommunication network
1 ) | Cabling - Data Network points (CAT6) | points | 7
2 | Cabling - Public Address System | points | 3
BILL No: 11 - ELECTRICAL INSTALLATIONS
TOTAL OF BILL No: 11 - Carried over to summary
BILL No: 12
FIRE FIGHTING SYSTEM
12.1.0 | GENERAL
a )Rates shall include for: sockets, running joints, connectors, elbows, junctions, reducers, expansion joints, back nuts, and similar incidental fittings, clips, saddles, brackets, straps, hangers screws nails and fixing complete including cutting and forming holes.
b ) Rate shall include for pipe works and inner and outer surface of all pipe work shall be galvanized steel.
c )All wiring and pipe work shall be done as specified in the drawing.
d )Shop drawings of the system shall be prepared to the standard of the government's relevant authority and submitted to the Consultant for approval.
e )Heat Resistant cable shall be laid for connecting the detectors.
12.2.0 | Fire Alarm System
Heat Resistant cable shall be laid for connecting the detectors.
12.3.0 | GROUND FLOOR
12.3.1 | Fire Alarm / Detection System
1 | Manual Call Point | no | 13
2 | Smoke Detector | no | 14
3 | Beacon | no | 1
4 | Sounder Bell | no | 1
5 | Exit Sign | no | 12
6 | Fire Alarm Control Panel | no | 1
12.3.2 | Fire Fighting System
1 | CO2 Extinguisher (load 2kg) In Polycarbonate Enclosure | no | 3
2 | H2O Extinguisher (load 9L) In Polycarbonate Enclosure | no | 2
3 | DCP Extinguisher (load 6kg) In Polycarbonate Enclosure | no | 1
12.3.0 | FIRST FLOOR
12.3.1 | Fire Alarm / Detection System
1 | Manual Call Point | no | 5
2 | Smoke Detector | no | 18
3 | Beacon | no | 2
4 | Exit Sign | no | 7
12.3.2 | Fire Fighting System
1 | CO2 Extinguisher (load 2kg) In Polycarbonate Enclosure | no | 2
2 | H2O Extinguisher (load 9L) In Polycarbonate Enclosure | no | 2
BILL No: 12 - FIRE FIGHTING SYSTEM
TOTAL OF BILL No: 12 - Carried over to summary
BILL No: 13
ADDITIONS
13.1.0 | General
Provision to include quantities as per the drawing which is missed in the bill of quantities.
1 | PRELIMINARIES
2 | GROUND WORKS
3 | CONCRETE WORKS
4 | MASONRY & PLASTERING
5 | FLOORING & TILING
6 | DOORS & WINDOWS
7 | WOOD WORK & CEILING
8 | PAINTING
9 | METAL WORK
10 | HYDRAULICS & DRAINAGE
11 | ELECTRICAL INSTALLATIONS
12 | FIRE FIGHTING SYSTEM
BILL No: 13 - ADDITIONS
TOTAL OF BILL No: 134 - Carried over to summary
BILL No: 14
OMISSIONS
14.1.0 | General
Provision to remove the excess quantity given in the bill quantities if any as per the drawing details
1 | PRELIMINARIES
2 | GROUND WORKS
3 | CONCRETE WORKS
4 | MASONRY & PLASTERING
5 | FLOORING & TILING
6 | DOORS & WINDOWS
7 | WOOD WORK & CEILING
8 | PAINTING
9 | METAL WORK
10 | HYDRAULICS & DRAINAGE
11 | ELECTRICAL INSTALLATIONS
12 | FIRE FIGHTING SYSTEM
BILL No: 14 - OMISSIONS
TOTAL OF BILL No: 15 - Carried over to summary