## COVER PAGE
BILL OF QUANTITIES
PROPOSED THREE STOREY HOSPITAL AT …………..
CLIENT: Ministry of Health
MARCH -2021

## Summary1
SUMMARY OF BILLS OF QUANTITIES
Proposed Three Storey Hospital
Bill No | Description | Amount
1 | PRELIMINARIES
2 | GROUND WORKS
3 | CONCRETE
4 | MASONRY AND PLASTERING
5 | WOODWORK
6 | ROOFING
7 | DOORS AND WINDOWS
8 | CEILINGS
9 | PAINTING
10 | FINISHES
11 | FIRE FIGHTING SYSTEM
12 | HYDRAULICS & DRAINAGE
13 | ELECTRICAL INSTALLATIONS
14 | AIR-CONDITIONING SYSTEM
15 | PAVEMENT
16 | COMMON WORKS
17 | SOLAR PV SYSTEM
18 | TENDERER'S ADJUSTMENTS
| GRAND TOTAL carried to form of bid | 0
Total
Retention
Less Rentention
GST 6%

## BOQ
Item | Description | Unit | Qty | Rate | Amount
BILL No: 01
PRELIMINARIES
1.1 | General Notes
(1) | Abbreviations
m - metre
No - numbers
m³ - cubic metre
m² - square metre
Lm - Linear metre
t - tonnes
incl - including
mm - millimetre
dia - diameter
SS - Stainless Steel
GI - Galvanised Iron
1.2 | Site Management Costs
1 | Allow for all on and off site management cost including costs of foreman and assistants, temporary services, telephone, fax, hoardings and similar. | item | 1
1.3 | Sign Board
1 | Allow for sign board. | no | 1
1.4 | Service and Facilities
1 | Provision and maintenance of service and facilities such as Water, Power supply, lighting and fuel required for the project | item | 1
1.5 | Temporary Fencing and hoarding
1 | Supply, erect and maintenance of a fence through out the construction period and hoarding all along the perimeter of the site. | item | 1
1.6 | Site clearing and Demolition
1 | Demolition of any existing buildings and removal of those material from the site.Removing and clearingany shrubs or trees from the site. Contractor must visit the site and inspect the site before bidding. | item | 1
1.7 | Clean-up
1 | Allow for clean-up of completed works and site upon completion. | item | 1
1.8 | Inspection Trips
1 | Arrange inspection trips to a Client/consultant, each inspection trip takes 2 days, the contractor has to arrange; - 2 air tickets from Male'/ nearby domestic airport of the facility/ Male' by air (normal fair) - Speed boat transport Domestic Airport/ facility Island/ Domestic Airport - Accommodations (2 Air condition rooms) per trip. | no | 15
1.9 | Prepare EIA.
1 | Prepare EIA as per Government regulations, following requirements also include;
| a) Site cleaning, Removal of trees b) Biohazardous chemicals separation, if cleaning is done - biohazard waste disposal using a sewage treatment plant c) Chemical Waste disposal during construction, if applied as well to include in EIA c)Backup Generator - Specification, capacity requirement, fuel storage - day tank size - emissions levels etc. | Item | 1
BILL No: 01 PRELIMINARIES
TOTAL OF BILL No: 01 - Carried over to summary
BILL No: 02
GROUND WORKS
2.1 | General
(a) Rates shall include for: leveling, grading, trimming, compacting to faces of excavation, keep sides plumb, backfilling, dewatering, consolidating and disposing surplus soil.
2.2 | Site Clearing
1 | Clearing site including trees less than 0.5m girth complete with stumps and roots. | m² | 1924
2.3 | Excavation
(a) Excavation quantities are measured to the faces of concrete members. Rates shall include for all additional excavation required to place the formwork.
1 | Excavation for foundation pads ST1 | m³ | 921.024
2 | Excavation for foundation pads ST2 | m³ | 86.346
3 | Excavation for foundation beams TB | m³ | 109.824
4 | Excavation for foundation beams FB | m³ | 78.848
5 | Excavation for boundary | m³ | 26.88
2.4 | Filling
(a) Rates shall include for: leveling, grading, trimming and compacting.
1 | Sand blinding layer to receive damp proof membrane | m³ | 183.42
2 | Earth filling in ground floor (300mm above ground level) | m² | 241.77
3 | 50 mm thick sand blinding layer to recieve damp proof membrane. | m² | 604.42
2.5 | Damp Proof Membrane
(a) Rates shall include for: dressing around and sealing to all penetrations.
1 | Polythene sheet damp proof membrane (500 gauge) laid on blinding layer. | m² | 1028.38
2.6 | BOUNDARY WALL
1 | 2m Height of boundary wall surrounded by the land area with oil based paint system and textured finish Footing: 600 x 600mm (T10 @150 BW) Foundation Beam: 300 x 200mm (4T12, R6@150) Columns (at 3.5M span): 200 x 200mm (4T12, R6@150) Foundation Depth: 750mm Capping Beam: 150 x 150mm (4T10, R6@150) | m | 458
BILL No: 02 - GROUND WORKS
TOTAL OF BILL No: 02 - Carried over to summary
BILL No: 03
CONCRETE
3.1 | General
(a) Rates shall include for: placing in position; making good after removal of formwork and casting in all required items; additional concrete required to conform to structural and excavated tolerances.
(b) Mix ratio for reinforced concrete shall be 1:2:3 and lean concrete shall be 1:2:6 by volume.
(c ) Use plasticiser and admixture checmicals in all concrete works.
3.2 | Lean Concrete
(a) Quantity is measured to the edges of concrete foundation members. Rates shall be inclusive for any additional concrete required to place the formwork.
1 | 50mm thick lean concrete to bottom of Footings and Beams | m² | 953.74
3.3 | Reinforced Concrete
In-situ reinforced concrete to:
3.3.1 | Foundations
1 | Foundation Strip ST1 (5330 x 1600 x 300mm x 5) | m³ | 127.92
2 | Foundation Strip ST2 (53.30m x 900 x 300mm) | m³ | 19.19
3 | Foundation Pad F1 (1950 x 1950 x 350mm x 9) | m³ | 11.98
3.3.2 | Foundation Beams
1 | Foundation Beam ST1 | m³ | 112.6
2 | Foundation Beam ST2 | m³ | 17.32
3 | Tie Beams TB | m³ | 58.5
4 | Foundation Beam FB | m³ | 2.8
5 | Services Building Foundation Beam | m³ | 5.17
6 | Boundary Foundation Beam | m³ | 12.8
3.3.3 | Columns (Foundation to Roof Beams)
1 | Column C1 | m³ | 67.8
2 | Column C2 | m³ | 43.74
3 | Column C3 | m³ | 5.91
4 | Column C4 (Circular) | m³ | 3.82
5 | Column (Boundary) | m³ | 3.14
3.3.5 | RCC Walls
1 | Lift x 2 | m³ | 58.23
2 | X-Ray Room | m³ | 13.48
3.3.6 | First Floor
1 | Beams B1 | m³ | 74.7
2 | Beams B2 | m³ | 22.5
3 | Beams B3 | m³ | 0.9
4 | Beams B4 | m³ | 29.7
5 | Beams B5 | m³ | 13.28
6 | Beams B6 | m³ | 4.5
7 | Beams B7 | m³ | 0.84
3.3.7 | Second Floor
1 | Beams B1 | m³ | 80.1
2 | Beams B2 | m³ | 22.5
3 | Beams B3 | m³ | 0.9
4 | Beams B4 | m³ | 29.7
5 | Beams B5 | m³ | 13.28
6 | Beams B6 | m³ | 4.5
7 | Beams B7 | m³ | 0.84
3.3.8 | Roof Beams
1 | Beams B1 | m³ | 67.5
2 | Beams B2 | m³ | 18.9
3 | Beams B3 | m³ | 0.9
4 | Beams B4 | m³ | 27.9
5 | Beams B5 | m³ | 13.28
6 | Beams B6 (Lift and Stairs) | m³ | 4.2
3.3.9 | Litel Beams
1 | Lintel Beams | m³ | 20.63
3.3.10 | Slabs
1 | First Floor (175mm thickness) | m³ | 94.5
2 | First Floor (150mm thickness) | m³ | 214.2
3 | Second Floor (175mm thickness) | m³ | 1.79
4 | Second Floor (150mm thickness) | m³ | 290.22
5 | Roof Slab (175mm thickness) | m³ | 1.61
6 | Roof Slab (150mm thickness) | m³ | 285.42
7 | Lift and Stair Slab (175mm thickness) | m³ | 1.24
8 | Stairs | m³ | 22.68
3.3.9 | Ramps
1 | Ramps | m³ | 4.29
3.4 | Formwork
(a) Rates shall include for: all necessary boarding, supports, erecting, framing, temporary cambering, cutting, perforations for reinforcing bars, bolts, straps, ties, hangers, pipes and removal of formwork including mould oil.
3.3.1 | Foundations
1 | Foundation Strip ST1 (5330 x 1600 x 300mm x 5) | m² | 652.93
2 | Foundation Strip ST2 (53.30m x 900 x 300mm) | m² | 53.3
3 | Foundation Pad F1 (1950 x 1950 x 350mm x 9) | m² | 46.82
3.3.2 | Foundation Beams
1 | Foundation Beam ST1 | m² | 225.19
2 | Foundation Beam ST2 | m² | 34.65
3 | Tie Beams TB | m² | 117
4 | Foundation Beam FB | m² | 5.6
5 | Services Building Foundation Beam | m² | 10.39
6 | Boundary Foundation Beam | m² | 25.73
3.3.3 | Columns (Foundation to Roof Beams)
1 | Column C1 | m² | 18.9
2 | Column C2 | m² | 583.2
3 | Column C3 | m² | 94.5
4 | Column C4 (Circular metal frame) | m² | 12.72
5 | Column (Boundary) | m² | 66.24
3.3.5 | RCC Walls
1 | Lift x 2 | m² | 507.6
2 | X-Ray Room | m² | 378
3.3.6 | First Floor
1 | Beams B1 | m² | 507.96
2 | Beams B2 | m² | 153
3 | Beams B3 | m² | 6.12
4 | Beams B4 | m² | 201.96
5 | Beams B5 | m² | 90.27
6 | Beams B6 | m² | 41.4
7 | Beams B7 | m² | 7.56
3.3.7 | Second Floor
1 | Beams B1 | m² | 544.68
2 | Beams B2 | m² | 153
3 | Beams B3 | m² | 6.12
4 | Beams B4 | m² | 201.96
5 | Beams B5 | m² | 90.27
6 | Beams B6 | m² | 41.4
7 | Beams B7 | m² | 7.56
3.3.8 | Roof Beams
1 | Beams B1 | m² | 459
2 | Beams B2 | m² | 128.52
3 | Beams B3 | m² | 6.12
4 | Beams B4 | m² | 189.72
5 | Beams B5 | m² | 90.27
6 | Beams B6 (Lift and Stairs) | m² | 38.64
3.3.9 | Litel Beams
1 | Lintel Beams | m² | 223.72
3.3.10 | Slabs
1 | First Floor (175mm thickness) | m² | 486
2 | First Floor (150mm thickness) | m² | 1285.2
3 | Second Floor (175mm thickness) | m² | 9.23
4 | Second Floor (150mm thickness) | m² | 1740.38
5 | Roof Slab (175mm thickness) | m² | 8.28
6 | Roof Slab (150mm thickness) | m² | 1712.52
7 | Lift and Stair Slab (175mm thickness) | m² | 6.39
8 | Stairs | m² | 121.56
3.3.9 | Ramps
1 | Ramps | m² | 29.7
3.5 | Reinforcement
(a) Rates shall include for: cleaning, fabrication, placing, the provision for all necessary temporary fixings, and supports including tie wire (1.6mm dia. X 90mm) and chair supports, laps, distribution bars and wastage.
(b) All reinforcing bars shall be high strength bars.
3.3.1 | Foundations
1 | Foundation Strip ST1 (5330 x 1600 x 300mm x 5)
| 20mm. dia, 6m. high tensile steel bar (15T20) | t | 10.2576
| 16mm. dia, 6m. high tensile steel bar (4T16) | t | 1.6821
| 10mm. dia, 6m. high tensile steel bar (12T10) | t | 1.9732
| 10mm. dia, 6m. Ring bars (3R10@200 with HOOK) | t | 4.4396
| 10mm. dia, 6m. Ring bars (R10@150 with HOOK) | t | 3.5079
| 1.6mm. dia, 90mm Steel ties | t | 0.005292
2 | Foundation Strip ST2 (53.30m x 900 x 300mm)
| 16mm. dia, 6m. high tensile steel bar (4T16) | t | 1.3457
| 10mm. dia, 6m. high tensile steel bar (8T10) | t | 0.32886
| 10mm. dia, 6m. Ring bars (R10@100 with HOOK) | t | 1.5456
| 10mm. dia, 6m. Ring bars (R10@150 with HOOK) | t | 0.39463
| 1.6mm. dia, 90mm Steel ties | t | 0.010716
3 | Foundation Pad F1 (1950 x 1950 x 350mm x 9)
| 12mm. dia, 6m. high tensile steel bar (T12@75) | t | 0.95067
| 1.6mm. dia, 90mm Steel ties | t | 0.00030618
3.3.2 | Foundation Beams
3 | Tie Beams TB
| 16mm. dia, 6m. high tensile steel bar (12T16) | t | 7.385
| 12mm. dia, 6m. high tensile steel bar (2T12) | t | 0.69264
| 6mm. dia, ring bar (2R6@100) | t | 1.2987
| 1.6mm. dia, 90mm Steel ties | t | 0.00384
4 | Foundation Beam FB
| 12mm. dia, 6m. high tensile steel bar (4T12) | t | 0.19891
| 6mm. dia, ring bar (R6@100) | t | 0.055944
| 1.6mm. dia, 90mm Steel ties | t | 0.00108
5 | Services Building Foundation Beam
| 12mm. dia, 6m. high tensile steel bar (4T12) | t | 0.37
| 6mm. dia, ring bar (R6@100) | t | 0.17
| 1.6mm. dia, 90mm Steel ties | t | 0.001
5 | Boundary Foundation Beam
| 12mm. dia, 6m. high tensile steel bar (4T12) | t | 0.90931
| 6mm. dia, ring bar (R6@100) | t | 0.50012
| 1.6mm. dia, 90mm Steel ties | t | 0.00264
3.3.3 | Columns (Foundation to Roof Beams)
1 | Column C1
| 20mm. dia, 6m. high tensile steel bar (4T20) | t | 5.6811
| 12mm. dia, 6m. high tensile steel bar (8T12) | t | 6.9874
| 06mm. dia, 6m. Ring bars (3R6@150 with HOOK) | t | 2.8835
| 1.6mm. dia, 90mm Steel ties | t | 0.029889
2 | Column C2
| 16mm. dia, 6m. high tensile steel bar (8T16) | t | 6.1353
| 6mm. dia, 6m. Ring bars (2R6@150 with HOOK) | t | 1.4745
| 1.6mm. dia, 90mm Steel ties | t | 0.017496
3 | Column C3
| 16mm. dia, 6m. high tensile steel bar (8T16) | t | 1.193
| 6mm. dia, 6m. Ring bars (2R6@150 with HOOK) | t | 0.1958
| 1.6mm. dia, 90mm Steel ties | t | 0.003402
4 | Column C4 (Circular)
| 16mm. dia, 6m. high tensile steel bar (8T16) | t | 0.6817
| 6mm. dia, 6m. Ring bars (2R6@150 with HOOK) | t | 0.11189
| 1.6mm. dia, 90mm Steel ties | t | 0.003402
5 | Column (Boundary)
| 12mm. dia, 6m. high tensile steel bar (4T12) | t | 0.39214
| 10mm. dia, 6m. Ring bars (4R10@200 with HOOK) | t | 0.30156
| 1.6mm. dia, 90mm Steel ties | t | 0.079488
3.3.5 | RCC Walls
1 | Lift x 2
| 12mm. dia, 6m. high tensile steel bar (T12@125 bw) | t | 7.5125
| 1.6mm. dia, 90mm Steel ties | t | 0.009648
2 | X-Ray Room
| 12mm. dia, 6m. high tensile steel bar (T12@125 bw) | t | 5.5944
| 1.6mm. dia, 90mm Steel ties | t | 0.007236
3.3.6 | First Floor
1 | Beams B1
| 20mm. dia, 6m. high tensile steel bar (7T20) | t | 8.9451
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 1.5697
| 6mm. dia, ring bar (R6@125) | t | 1.1498
| 1.6mm. dia, 90mm Steel ties | t | 0.010458
2 | Beams B2
| 25mm. dia, 6m. high tensile steel bar (6T25) | t | 3.2256
| 20mm. dia, 6m. high tensile steel bar (6T20) | t | 2.3094
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.4734
| 6mm. dia, ring bar (2R6@100) | t | 0.8658
| 1.6mm. dia, 90mm Steel ties | t | 0.0063
3 | Beams B3
| 25mm. dia, 6m. high tensile steel bar (8T25) | t | 0.17203
| 20mm. dia, 6m. high tensile steel bar (4T20) | t | 0.061584
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.018936
| 6mm. dia, ring bar (2R6@100) | t | 0.03432
| 1.6mm. dia, 90mm Steel ties | t | 0.000252
4 | Beams B4
| 20mm. dia, 6m. high tensile steel bar (12T20) | t | 6.0968
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.62489
| 6mm. dia, ring bar (2R6@100) | t | 1.1326
| 1.6mm. dia, 90mm Steel ties | t | 0.009504
5 | Beams B5
| 20mm. dia, 6m. high tensile steel bar (4T20) | t | 0.90836
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.27931
| 6mm. dia, ring bar (R6@150) | t | 0.1298
| 1.6mm. dia, 90mm Steel ties | t | 0.001593
6 | Beams B6
| 20mm. dia, 6m. high tensile steel bar (6T20) | t | 0.69282
| 12mm. dia, 6m. high tensile steel bar (2T12) | t | 0.07992
| 6mm. dia, ring bar (R6@150) | t | 0.066
| 1.6mm. dia, 90mm Steel ties | t | 0.00108
7 | Beams B7
| 16mm. dia, 6m. high tensile steel bar (4T16) | t | 0.066276
| 6mm. dia, ring bar (R6@100) | t | 0.0231
| 1.6mm. dia, 90mm Steel ties | t | 0.000126
3.3.7 | Second Floor
1 | Beams B1
| 20mm. dia, 6m. high tensile steel bar (7T20) | t | 9.5917
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 1.6832
| 6mm. dia, ring bar (R6@125) | t | 1.2329
| 1.6mm. dia, 90mm Steel ties | t | 0.011214
2 | Beams B2
| 25mm. dia, 6m. high tensile steel bar (6T25) | t | 3.2256
| 20mm. dia, 6m. high tensile steel bar (6T20) | t | 2.3094
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.4734
| 6mm. dia, ring bar (2R6@100) | t | 0.8658
| 1.6mm. dia, 90mm Steel ties | t | 0.0063
3 | Beams B3
| 25mm. dia, 6m. high tensile steel bar (8T25) | t | 0.17203
| 20mm. dia, 6m. high tensile steel bar (4T20) | t | 0.061584
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.018936
| 6mm. dia, ring bar (2R6@100) | t | 0.03432
| 1.6mm. dia, 90mm Steel ties | t | 0.000252
4 | Beams B4
| 20mm. dia, 6m. high tensile steel bar (12T20) | t | 6.0968
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.62489
| 6mm. dia, ring bar (2R6@100) | t | 1.1326
| 1.6mm. dia, 90mm Steel ties | t | 0.009504
5 | Beams B5
| 20mm. dia, 6m. high tensile steel bar (4T20) | t | 0.90836
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.27931
| 6mm. dia, ring bar (R6@150) | t | 0.1298
| 1.6mm. dia, 90mm Steel ties | t | 0.001593
6 | Beams B6
| 20mm. dia, 6m. high tensile steel bar (6T20) | t | 0.69282
| 12mm. dia, 6m. high tensile steel bar (2T12) | t | 0.07992
| 6mm. dia, ring bar (R6@150) | t | 0.066
| 1.6mm. dia, 90mm Steel ties | t | 0.00108
7 | Beams B7
| 16mm. dia, 6m. high tensile steel bar (4T16) | t | 0.066276
| 6mm. dia, ring bar (R6@100) | t | 0.0231
| 1.6mm. dia, 90mm Steel ties | t | 0.000126
3.3.8 | Roof Beams
1 | Beams B1
| 20mm. dia, 6m. high tensile steel bar (7T20) | t | 8.0829
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 1.4184
| 6mm. dia, ring bar (R6@125) | t | 1.039
| 1.6mm. dia, 90mm Steel ties | t | 0.00945
2 | Beams B2
| 25mm. dia, 6m. high tensile steel bar (6T25) | t | 2.7095
| 20mm. dia, 6m. high tensile steel bar (6T20) | t | 1.9399
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.39766
| 6mm. dia, ring bar (2R6@100) | t | 0.72727
| 1.6mm. dia, 90mm Steel ties | t | 0.005292
3 | Beams B3
| 25mm. dia, 6m. high tensile steel bar (8T25) | t | 0.17203
| 20mm. dia, 6m. high tensile steel bar (4T20) | t | 0.061584
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.018936
| 6mm. dia, ring bar (2R6@100) | t | 0.03432
| 1.6mm. dia, 90mm Steel ties | t | 0.000252
4 | Beams B4
| 20mm. dia, 6m. high tensile steel bar (12T20) | t | 5.7273
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.58702
| 6mm. dia, ring bar (2R6@100) | t | 1.0639
| 1.6mm. dia, 90mm Steel ties | t | 0.008928
5 | Beams B5
| 20mm. dia, 6m. high tensile steel bar (4T20) | t | 0.90836
| 16mm. dia, 6m. high tensile steel bar (2T16) | t | 0.27931
| 6mm. dia, ring bar (R6@150) | t | 0.1298
| 1.6mm. dia, 90mm Steel ties | t | 0.001593
6 | Beams B6 (Lift and Stairs)
| 20mm. dia, 6m. high tensile steel bar (6T20) | t | 0.64663
| 12mm. dia, 6m. high tensile steel bar (2T12) | t | 0.074592
| 6mm. dia, ring bar (R6@150) | t | 0.0616
| 1.6mm. dia, 90mm Steel ties | t | 0.001008
3.3.9 | Litel Beams
1 | Lintel Beams
| 12mm. dia, 6m. high tensile steel bar (8T12) | t | 1.543
| 12mm. dia, 6m. Cross bars (T12@150) | t | 0.77149
| 06mm. dia, 6m. Ring bars (R6@150) | t | 0.22502
| 1.6mm. dia, 90mm Steel ties | t | 0.0078192
3.3.10 | Slabs
1 | First Floor (175mm thickness)
| 12mm. dia, 6m. high tensile steel bar (T12@40) Distribution Steel | t | 1.0789
| 10mm. dia, 6m. high tensile steel bar (T10@150) BW | t | 1.7992
2 | First Floor (150mm thickness)
| 10mm. dia, 6m. high tensile steel bar (T10@150) Top Reinf. | t | 3.1719
3 | Second Floor (175mm thickness)
| 10mm. dia, 6m. high tensile steel bar (T10@150) BW | t | 0.034151
4 | Second Floor (150mm thickness)
| 10mm. dia, 6m. high tensile steel bar (T10@150) Top Reinf. | t | 4.2952
5 | Roof Slab (175mm thickness)
| 10mm. dia, 6m. high tensile steel bar (T10@150) BW | t | 0.030653
6 | Roof Slab (150mm thickness)
| 10mm. dia, 6m. high tensile steel bar (T10@150) Top Reinf. | t | 4.2265
7 | Lift and Stair Slab (175mm thickness)
| 10mm. dia, 6m. high tensile steel bar (T10@150) BW | t | 0.023656
8 | Lift and Stair Slab (175mm thickness)
| 10mm. dia, 6m. high tensile steel bar (T10@100) BW | t | 1.8
3.3.9 | Ramps
1 | Ramps
| 10mm. dia, 6m. high tensile steel bar (T10@250) Bottom Reinf. | t | 1.96
3.5.4 | Water proofing
Rates shall include for: dressing around and sealing to all penetrations
1 | Apply bitumen type waterproofing to all surfaces of concrete below ground level in accordance with manufacturer's instructions. | m² | 1028.43
3.5.5 | Ground water well
1 | Completion of 100mm thic RC concrete well, Rates also includes excavation, concrete works well (top and bottom slab) | Item | 1
BILL No: 03 - CONCRETE WORKS
TOTAL OF BILL No: 03 - Carried over to summary
BILL No: 04
MASONRY AND PLASTERING
4.1 | General
Rates shall include for: cleaning out cavities, forming rebated reveals and pointing and cleaning down to reveals where necessary; fractional size blocks, all necessary machine cutting, cutting or forming chases or edges of floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding frames or plates, building in joists, bearers or similar, temporary supports to openings, templates, reinforcement in walls and for all necessary making good. Bedding mortar (mixing ratio 1:4 i.e. cement: manufactured sand) shall be of OPC & fine aggregate shall be imported river sand shall be approved in grading & clean from any harmful substance. Masonry work shall be done with approved Machine compact cement blocks (300X150X150) with no defects. Lay in line and length as per approved working drawing Block making (mixing ratio 1:4 i.e. cement: Manufactured sand) shall be of OPC & free form salt.
floor slabs, cutting or leaving holes and openings as recesses for and building in pipes, conduits, sleeves and similar as required for all trades; leaving surfaces rough or raking out joints for plastering and flashings, bedding
Rates shall include for: 25mm groove lines on external surfaces as shown on the drawing. Desalinated water shall be used for all purposes, ground water shall not be used.
4.2 | Cement brickwork
Main Building (all floors)
4.2.1 | 150 mm wide solid block masonry wall, laid on and incl. mortar tie rods, compression joint gap filling material such as mastic sealent as specified external walls | m² | 8036.1
Services Building
4.2.2 | 150 mm wide solid block masonry wall, laid on and incl. mortar tie rods, compression joint gap filling material such as mastic sealent as specified external walls | m² | 371.26
4.3 | Plastering
(a) Cement plastering on walls and concrete surfaces as specified incl. wire mesh at the joints of concrete surfaces and walls
4.3.1 | 20mm thick plastering one layer as per specified drawing (external surface ) | m² | 2946.2
4.3.2 | 12mm thick plastering one layer as per specified drawing (internal surface) | m² | 13432.62
4.4 | Cement Screed
| 50 mm thick floor screed on all floors (Main bldg) | m² | 4863
| 50 mm thick floor screed (Services bldg) | m² | 201.4
BILL No: 04 - MASONRY AND PLASTERING
TOTAL OF BILL No: 04 - Carried over to summary
BILL No: 05
WOODWORK
5.1 | General
(a) Rates shall include for: all labour in framing, notching and fitting around projections, pipes, light fittings, hatches, grilles and similar and complete with cleats, packers, wedges and similar and all nails and screws.
5.2 | Skirting
1 | Ground floor (20 x 100 mm timber skirting) | m | 367
2 | First Floor (20 x 100 mm timber skirting) | m | 288
3 | Second Floor (20 x 100 mm timber skirting) | m | 295
5.3 | Accessibility Railing
1 | Accessibility Railing fixed in walkways including fixtures and fastening | m | 284
METAL WORKS
5.4 | General
(a) Rates shall include for: all fabrication work, welding, marking, drilling for bolts including those securing timbers, steel plates, bolts, nuts and any type of washer, riveted work, counter sinking and tapping for bolts or machine screws.
(b) Rates shall include for all painting and finishing as specified
(c) Rates shall include for fabrication and erection and temporary supports and fixing into position
5.5 | Ramp railing
1 | 1100mm high handrail with 3x ø50mm SS pipe horizontally with rounded ends and ø35mm SS balustrades veritically @14m distance with 18mm welded base plates as shown in the drawing | Nos | 2
5.6 | Railing for staircase from Grd flr to Roof level .
1 | 965mm high handrail with 3x ø25mm SS pipe horizontally and ø50mm SS pipes veritically with 18mm welded base plates as shown in the drawing | Nos | 6
5.7 | Canopy roof truss
1 | 20 x 10 x 1.2mm thick SS capping on glass balcony as shown in the drawing | Nos | 1
2 | 6mm thick tempered laminated glass panels x2 with 1.5mm gap | Nos | 1
5.8 | Roof structure
2 | GI Truss battens | m | 460
3 | GI Truss rafters | m | 326
5.9 | Metal signboard
1 | 25mm thick 700mm x 28m Metal signboard fixed in Reception and Exterior. | Nos | 2
BILL No: 05 - WOODWORK AND METALWORK
TOTAL OF BILL No: 05 - Carried over to summary
BILL No: 06
ROOFING
6.1 | General
(a) Rates shall include for: fair edges, dressing over angel fillets, turning into grooves, all other labors, circular edges, nails, screws and other fixings and laps.
(b) Rates shall include to apply Wood preservative to all the surface of timbers (Roof structure).
(b) Rates shall include to remove existing end cap, fascia board and necessary roofing sheets and necessary works to connect new roof to existing roof.
6.2 | Roof Coverings
1 | Roofing sheets: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick - Aqua marine or equivalent, including all fixings, fixed in accordance with manufacturer's instructions. | m² | 604
6.3 | Cappings and Flashings
1 | Ridge Capping and Flashing as per drawing: Blue scope steel international limited MSP, Total coated thickness minimum 0.47mm thick- Aqua marine or equivalent | m | 69
6.4 | Down Pipes
1 | 75 mm dia uPVC down pipes including bends, junctions, straps, brackets, clips, roof drain strainer and all fixings. | m | 100
BILL No: 06 - ROOFING
TOTAL OF BILL No: 06 - Carried over to summary
BILL N0: 07
DOORS AND WINDOWS
7.1 | General
(a) Rates shall include for locks, latches, closers, push plates, pull handles, bolts, kick plates, hinges and all door & window hardware.
(b) Rates shall include for door frames and window frames, mullions, transoms, trims, glazing, tinting, timber panels, boardings, framing, lining, fastenings and all fixings and installation.
(c) All door frames and window frames shall be as specified in the drawing
(d) Rates shall include for all painting and putty as specified.
(Aluminium Profiles to be chosen by client, profile thickness must be minimun 2.5mm thick).
7.2 | Doors
1 | D1 Alum Coated Frame with Tempered Glass Panel (2600 x 2000) Sliding Doors with Mortise Lock x 2 | Nos | 2
2 | D2 Frameless Tempered Glass Panels (2500 x 1600) fixed with Butt Hinge x4 on each flap and Mortose Lock x2 | Nos | 2
3 | D3 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 1600) with Peep through Glass Panels (1300 x 300) Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 15
4 | D4 Powder Coated Aluminum in White with Tempered Glass Panels (2200 x 1100) Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 1
5 | D5 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 1000) Single Flap with Peep through Glass Panel (950 x 300) Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 41
6 | D6 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 800) Single Flap with Peep through Glass Panel (650 x 300) Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 20
7 | D7 Powder Coated Aluminum in White GRP Door Panel with Glazing (2100 x 700) Single Flap with Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 34
8 | D8 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 800) Single Flap with SS Garb Bar and Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 18
9 | D9 Powder Coated Aluminum in White GRP Door Panel with Glazing (2300 x 1000) Single Flap with Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 20
10 | D10 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 1600) with Peep through Glass Panels (1300 x 300) Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 16
11 | D11 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 1200) Single Flap with Peep through Glass Panel (950 x 300) Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 2
12 | D12 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 1200) Single Flap with Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 2
13 | D13 Powder Coated Aluminum in White GRP Door Panel with Glazing (2100 x 700) Single Flap with Silver Butt Hinges x4 per flap and Mortise Lock x2 | Nos | 47
14 | D14 Powder Coated Aluminum in White GRP Door Panel with Glazing (2100 x 900) Single Flap with Silver Butt Hinges x4 per flap and Mortise Lock x3 | Nos | 7
15 | D15 Powder Coated Aluminum in White GRP Door Panel with Glazing (2500 x 1500) Two Flaps (900 + 500) with Silver Butt Hinges x4 per flap | Nos | 4
7.3 | Windows
1 | W1 Power Coated Aluminum Frame with 6mm Float Glass (1400 x 1200) WHITE Finish Sliding Window with Lock x1 | Nos | 46
2 | W2 Power Coated Aluminum Frame with 6mm Float Glass (1200 x 1250) WHITE Finish Sliding Window with Lock x1 | Nos | 25
3 | W3 Power Coated Aluminum Frame with 6mm Clear Glass (1200 x 850) WHITE Finish Window with Brushed Metal (SILVER) Hinges x3 and Lock x1 | Nos | 10
4 | W4 Power Coated Aluminum Frame with 6mm Float Glass (1200 x 1100) WHITE Finish Sliding Window with Lock x1 | Nos | 13
5 | W5 Power Coated Aluminum Frame with 6mm Black Tinted Float Glass (1200 x 1400) WHITE Finish Sliding Window with Lock x1 | Nos | 18
6 | W6 Power Coated Aluminum Frame with 6mm Float Glass (1200 x 2000) WHITE Finish Sliding Window with Lock x1 | Nos | 8
7.4 | Vents
1 | V1 Powder Coated Aluminum Frame (750 x 450) with Louvers WHITE Finish | Nos | 31
7.5 | Fixed glass Units
1 | Fixed glass panels (Main Building) | m² | 951.5
2 | Fixed glass panels (Gift Shop) | m² | 85
7.2 | Services Building
1 | Alum Coated Frame with Aluminium Panels Shutter Door (2600 x 4200) Sliding Doors with Mortise Lock x 2 | Nos | 3
2 | Door Alum Coated Frame with Aluminium Panel (2600 x 950) Single Flap Doors with Mortise Lock x 3 | Nos | 3
3 | Door Alum Coated Frame with Aluminium Panel (2600 x 1700) Double Flap Doors with Mortise Lock x 3 | Nos | 2
4 | W4 Power Coated Aluminum Frame and 2 sliding panels with 6mm Float Glass (1200 x 1100) WHITE Finish Sliding Window with Lock x1 | Nos | 1
5 | W4 Power Coated Aluminum Frame and 3 sliding panels with 6mm Float Glass (1200 x 1100) WHITE Finish Sliding Window with Lock x1 | Nos | 2
7.3 | Hospital Bed Curtains
Supply and complete installation of top quality Hospital grade bed side curtain including Original curved railing/Track. Length of rail/track is 6870mm, and height of curtain would be 2.4 meter.
1 | ER | Item | 7
2 | Treatment room, ER area | Item | 1
3 | Consultation room ( 6 bed) | Item | 6
4 | Pediatric ward | Item | 4
5 | Gynacology ward | Item | 4
6 | Medical ward (Male) | Item | 4
7 | Medical ward (Female) | Item | 4
8 | Surgical ward | Item | 4
9 | Recovery room | Item | 2
10 | Pre Delivery | Item | 2
11 | Private room | Item | 5
BILL N0: 07 - DOORS AND WINDOWS
TOTAL OF BILL No: 07 - Carried over to summary
BILL No: 08
CEILINGS
8.1 | Ground Floor Ceilings
1 | 6 mm thick plywood ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 450
2 | 6 mm thick Gypsum ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 1280
3 | 6 mm thick Gypsum feature ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 182
8.2 | First Floor Ceilings
1 | 6 mm thick plywood ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 45
2 | 6 mm thick Gypsum ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 1157
3 | 6 mm thick Gypsum feature ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 182
8.3 | Second Floor Ceilings
1 | 6 mm thick plywood ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 36
2 | 6 mm thick Gypsum ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 1254
3 | 6 mm thick Gypsum feature ceiling, including timber framing , trimming, nails, screws, 50 x 50 mm timber frame at 600c/c and other fixings as per drawings and renders. | m² | 94
BILL N0: 08 CEILINGS
TOTAL OF BILL No: 08 - Carried over to summary
BILL No: 9
PAINTING
9.1 | General
Exterior wall shall be of 1 coat of oil based textured paint and 2 coats of Kansani weather bond paint ( oil based ) over 1 coat of oil based sealer ( white) or equivalent (according to technical specifications or approved drawings). Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Interior wall shall be of 2-3 coats over 1 coat of water based sealer. Rates includes Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for: the provision, erection and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and/or masking floors, fittings and similar work, removing and replacing door and window and including soffits and sides of beams.
Exterior & Exterior Ceiling (interior and exterior) shall be of 2 coats of (wood paint over 1 coat of wood primer or equivalent. Erection of scaffolding, preparing working platforms, applying sealer and two coats of paint as specified in the working drawings. Removal of scaffolding if any after completion of work. Rates shall include for the provision and removal of scaffolding, preparation, rubbing down between coats and similar work, the protection and or masking floors fittings and similar work removing and replacing door window furniture.
(a) All painting work shall be carried in accordance with the Specifications
(b) Painting system shall be Nippon or Equivalent
9.2.1 | External painting 1 coat of wall sealer, 1 coat tex compound & 2 coats of paints | m² | 6094
9.2.2 | Emulsion paint putty finish system on plastered and concrete surfaces of internal walls. Internal painting 1 coat of wall sealer, 2 coats of paints | m² | 13327.2
9.3 | Ceilings
1 | Emulsion paint finish on ceiling | m² | 3691
Emulsion paint finish after grinding the area and applying putty. Both Slab soffit and false ceiling
BILL No: 09 - PAINTING
TOTAL OF BILL No: 09 - Carried over to summary
BILL N0: 10
FINISHES
10.1 | General
Prepare surface for approved bedding tiles with reach bedding materials as per the technical specifications & approved working drawings, fix tiles with ct grout in a precise manner to maintain correct alignment, applying tile grout and wiping any excess grout to ensure the required standards of finished works. Rates shall include for: fixing, bedding, grouting, and pointing materials; making good around pipes, sanitary fixtures, and similar; cleaning down and polishing any other similar works to ensure the required finish. All tiles shall be Full body homogeneous tiles or equivalent.
10.2 | Ceramic floor tiles
1 | 600 x 600mm Homogeneous floor tiles | m² | 3317
2 | 600 x 600mm Non slip Ceramic floor tiles | m² | 374
3 | 200 x 200mm Stairs non slip ceramic floor tiles | m² | 105
4 | 200 x 50mm Ramps and Stairs non slip edge nosing | m² | 21
5 | Light Grey Linoleum Flooring | m² | 198
6 | Anti Slip Epoxy Rubber Flooring | m² | 1602
7 | Resin Flooring | m² | 59
10.3 | Wall tiles
1 | 150 x 150mm Ceramic wall tiles | m² | 1161
10.4 | Blinds
Supply and complete installation of high quality blinds for following areas.
1 | Ground Floor 1200 x 3900mm Blinds | m² | 292.5
2 | First Floor 1200 x 3900mm Blinds | m² | 339.3
3 | Second Floor 1200 x 3900mm Blinds | m² | 327.6
10.5 | Wall Cladding
Supply and complete installation of high quality wall cladding as per drawings.
1 | 600 x 600mm wall cladding panels | m² | 183
10.6 | Water Feature with Sign and Flagposts
Supplying of Materials and complete works for water Feature with Sign and Flagposts as per drawings.
1 | Signage | Nos | 1
2 | Stepping Stones | m² | 9
3 | Platform for flags and signage | m² | 25
4 | Flagposts, Marine grade SS pipe. | Nos | 3
5 | Water feature and pool | Nos | 1
10.7 | Landscaping
1 | Landscaping and features as per drawings and renders | m² | 630.99
10.8 | Reception Counters and Nurse Stations
1 | Fabrication of Main reception and sub stations | Nos | 12
2 | Built-in storage cabinets/Sink cupboards. All the sink must be Ceramic lab sink, minimum 620x480x255mm, (Cotto or equivalent) with elbow operated taps. | Nos | 23
10.9 | Waiting Areas
1 | completion of Seating in waiting areas as per Drawings, Quality of materials must be top quality. | Nos | 34
10.1 | Interior Works
1 | Interior decorations as per the drawings details as well as renders. Including floor, walls and ceilings. | Item | 1
10.11 | Supplying and installation of Furniture
Supply and Complete installation of Furniture's.
1 | Office Table, 1200mm ( table should be solid wood). Also drawer to be include. | No | 13
2 | Office Table 1500mm for Executives ( table should be solid wood). Also drawer to be include. | No | 2
3 | Office Table with partition, 1200mm ( table should be solid wood). Also drawer to be include. | No | 25
4 | Conference table for 8 Person with Low back chair | No | 3
5 | Secretary chair , high back. | No | 10
6 | Secretary chair , Low back. | No | 70
7 | Dining table for 4 person with chair | No | 15
8 | Sofar set for 3-4 person | No | 10
9 | Sofar set for 2-3 person | No | 11
10 | Auditorium chair | No | 12
11 | Side cupboard lockable. 750X450mm | No | 35
12 | Filling rack, 2000X800mm | No | 25
13 | Meeting room chair Material: Iron/Aluminium Surface treatment: Sprey painting finished. Seat and back: Hight-density sponge, minimum 2.5" thick seat cushion | No | 100
14 | Folding Meeting Table, 1400X600mm, Specifications: Lockabale castorsm Aluminium compolenets Feature: Chrome with polished aluminium feet, Easy tilt machanism for compact storage, Table surface: Scrach resistant, Natural Ash. | No | 20
15 | Supply and installation of 4 seater Airport Bench set, Armrest/Leg/bracket: Die-casting molding of high strength aluminum alloy. Seat: Numerical control hydraulic molding of high quality cold rolling steel plate. Sponge: Cold consolidation and foam-forming of high density and super soft PU. Beam: metal tube with a diamond shape. Coating: Electrostatic coating after Rust-proof treatment, electroplated polishing. | No | 10
BILL No: 10 - FINISHES
TOTAL OF BILL No: 10 - Carried over to summary
BILL N0: 11
FIRE FIGHTING SYSTEM
11.1 | General
(a) Provide and install fire fighting equipment inclusive of all necessary connection as per local requlations as described.
11.1.1 | Ground Floor
1 | Fire extinguisher | Nos | 8
2 | Fire Blanket | Nos | 8
3 | Smoke detector | Nos | 98
4 | Manual call point. | Nos | 15
5 | Alarm Bell | Nos | 14
6 | Fire hose Reel | Nos | 2
11.1.2 | First Floor
1 | Fire extinguisher | Nos | 8
2 | Fire Blanket | Nos | 8
3 | Smoke detector | Nos | 75
4 | Manual call point. | Nos | 10
5 | Alarm Bell | Nos | 10
6 | Fire hose Reel | Nos | 2
11.1.3 | Second Floor
1 | Fire extinguisher | Nos | 8
2 | Fire Blanket | Nos | 8
3 | Smoke detector | Nos | 65
4 | Manual call point. | Nos | 8
5 | Alarm Bell | Nos | 8
6 | Fire hose Reel | Nos | 2
BILL No: 11 - FIRE FIGHTING SYSTEM
TOTAL OF BILL No: 11 - Carried over to summary
BILL No: 12
HYDRAULICS & DRAINAGE
12.1 | Hydraulics
12.1.1 | General
(a) Rates shall include for: sockets, running joints, connectors, elbows, junctions, reducers, expansion joints; backnuts and similar; incidental fittings, clips, saddles, brackets, straps, hangers, screws, nails and
fixing complete, including cutting and forming holes; excavating, laying pipes and backfilling trenches.
(b) All pipework shall be UPVC.
(c) Rate shall include for supply and fixing of all pipes
12.1.2 | Fresh water supply pipe work
1 | Completion of pipe works and Connect ground water supply pipe work to Fresh water network installed at hospital. | Item | 1
12.1.3 | Ground water supply pipe work
1 | Completion of pipe works and Connect ground water supply pipe work. | Item | 1
12.1.4 | Sanitary fixtures & accessories
(a) Sanitary fixtures complete including brackets, flush pipes, overflows, plugs and washers, as specified.
(b) All fixtures shall be Percelain sanitary fixtures and all fittings Chrome plated and shall be Cotto or equivalent.
1 | WC suites incl. Flush tank and fittings with fresh water connection and accessibility railing, Water closet must be (American standard, Neo Modern, Anti bacterial type) or equivalent. | no | 48
3 | Muslim Shower with water connection ( cotto or equivalent) | no | 48
5 | Vanity with counter top | no | 100
6 | Mirror and tower bar | no | 48
7 | Hand shower with hot and cold water ( cotto or equivalent) | no | 17
8 | Head shower with hot and cold water ( cotto or equivalent) | no | 17
9 | Floor drain | no | 48
12.1.5 | Water meter
Supply and installation of appropriate capacity Water pump 'Davey' or equivalent, complete including pump stand, connecting to pipe work and electricity as specified
1 | Water pumps | no | 6
12.1.6 | Water pumps
Supply and installation of water complete including connecting to pipework as specified.
1 | Water meter | no | 6
12.2 | Drainage
12.2.1 | General
(a) Rates shall include for: excavation, maintaining faces of drain pipe trenches and pits, backfilling, disposal of surplus spoil; bends, junctions, reducers, expansion joints and all joints and other incidental materials.
(b) All pipe work shall be UPVC
1 | Constructing Concrete Inspection Chamber of required size with all provisions to connect pipelines as per drawing. | item | 1
12.3 | Pipe work
1 | Completion of pipe works and Connect Waste disposal pipe 75mm dia to Sewer network installed at existing system. | Item | 1
2 | Completion of pipe works and Connect Sewers pipe 100mm dia UPVC to Sewer network installed at existing system. Rates includes to install inspection chamber as per consultants instructions. | Item | 1
3 | Completion of pipe works and Connect Sewers pipe 100mm dia UPVC to Sewer network installed at existing system. Rates includes to install inspection chamber as per consultants instructions. | Item | 1
12.4 | Inspection Chambers,
1 | Inspection chambers complete as shown on the Drawings incl all pipe connections and similar | item | 1
BILL No: 12 - HYDRAULICS & DRAINAGE
TOTAL OF BILL No: 12 - Carried over to summary
BILL No:13
ELECTRICAL INSTALLATIONS
13.1 | General
(a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories
(b) Rates for work in trench shall include for: excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers, warning tape and disposal of surplus spoil
(c) Rates shall include for electrical conduits, fittings, equipment and similar all fixings to various building surfaces
(d) Each Light/ light fixture and its switch is measured as one one point; similarly each fan or each socket outlet is measured as one point;
(e) Rates shall include for supply and complete installation
(f) All main distribution boards distribution boards are 3 phase.
(g) All electrical fittings shall be mid-range Clipsal or equivalent.
13.2 | Mains connection
1 | Main connection: Rates shall include for screws, nails, bolts ,nuts, standard cable, fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories. Rates shall including for electrical conduits, fittings, equipment and similar items. Three - PHASE CABLE WIRING TO D-BOARD: All necessary work in trench shall include for excavation, maintaining faces of excavations, backfilling, compaction, appropriate cable covers warning tape and disposal of surplus soil supply and laying of the cable in according to Maldives electricity bureau. ( 16mm2 4-Core Cable, Approved by respective Authorities, GI pipe, warning tape), contractor has to measure cable length from site. | Item | 1
13.3 | Electrical boards
Complete installation, including for all connections, earthing, painting, testing and similar of:
1 | Main panel board as specified.. (3phase Meter) | no | 2
2 | Sub distribution board | no | 9
3 | Power distribution board | no | 3
13.4 | Electrical wiring
Electrical wiring with copper conductor cable in conduits in walls and in casing on soffits of slab as specified to:
1 | Wiring with 1.5 mm² cable to lighting | points | 568
2 | Wiring with 2.5 mm² cable to power points | points | 643
13.5 | Ceiling fan
1 | 1.2m dia. Ceiling fan, (KDK or equivalent) | no | 108
13.6 | Lighting
1 | Wall Mount Light KTEG LED 597 LED 830 5500lm DMPR 51W RAL9016 DRV | no | 500
2 | Ceiling Mount Light LED Downlight White Square Surface 48W 6500K | no | 119
3 | Ceiling Suspended Light LSP44 - 2x54 - 011 | no | 2
4 | Light Matric 55mm Wall Direct D3 | no | 34
5 | Light DTFN SLITE LED Theatre | no | 10
6 | Light Matric 55mm Wall Direct D3 | no | 33
13.7 | Socket outlets
(a) All socket outlets shall be "Clipsal" or equivalent.
1 | SPN Isolator 20A | no | 6
2 | 2 x13A socket outlet | no | 241
3 | 1 x15A socket outlet | no | 219
13.8 | Light switches
(a) All light switches shall be "Clipsal" or equivalent.
1 | One way switch 2-gang | no | 322
2 | One way switch 1-gang | no | 129
3 | Fan regulators | no | 153
13.9 | Lightening Protection System
1 | Design, supply, and Complete installation of Erco, Eritech or equivalent lightening Protection System to cover the whole building as per local regulations (Rate shall include for all fixing of the system and down conductor to earthing) Coverage of lightning protection should be minimum 100 Meter Radius. | item | 1
13.1 | Internet, Phone and TV
Provide & install Network fittings, wiring(CAT6/RF/coaxial), equipment inclusive of all necessary connection as per drawing
Rates shall include Cable, box,face plate, and fixsing
1 | Network points | nos | 255
2 | Phone points | nos | 95
3 | TV points | nos | 24
4 | Supply and complete installation of PABX, minimum 150 Extensoon and 10 lines, and expandable. With telephones. | Item | 1
13.11 | EQUIPMENTS
Supply and complete installation of following items.
1 | Desktop Computer Systems (Specification attached) | nos | 45
2 | Laser Printers: Paper sizes: Minimum: 76 x 127 mm (3 x 5 inches) Maximum: 216 x 356 mm (8.5 x 14 inches) | nos | 30
3 | Network Server with server rack (Spec Attached) | nos | 1
4 | Manageable Network Port Switch (with spare 24 ports) | nos | 10
5 | Display TV 75" (Spec attached) | nos | 6
6 | Display TV 65" (Spec attached) | nos | 8
7 | Display TV 32" (Spec attached) | nos | 10
8 | Token Printer (Spec attached) | nos | 4
9 | Touch Screen (Spec attached) | nos | 4
10 | 8KVA Smart UPS (Spec attached) | nos | 2
11 | 3KVA Smart UPS (Spec attached) | nos | 25
13.12 | Backup Genset 600KVA
1 | Design, supply and installation of Yanmar or equivalent Genset 600KVA with synchoronize panel board (Approve by Client) | item | 1
13.12 | Oxygen Genarator
1 | Design, supply and complete installation of Oxygen generator with manifold, capacity of Generator must be minimun 40m3 per day.(Approve by Client), also filling component must be installed, | item | 1
13.14 | Oxygen delivery system
Design supply and complete installation of Piped and tested oxygen delivery system from the Oxygen bank as per Specifications and manufactures guidelines, instructions. Oxygen bank, capacity to connect minimum 12 jumbo cylinder. System to be insttaled as per manufactures standards.
GROUND FLOOR
1 | ER | Item | 5
2 | Treatment room | Item | 2
3 | Isolation room 1,2 | Item | 2
FIRST FLOOR
1 | Pediatric Ward | Item | 4
2 | Gynecology Ward | Item | 4
3 | Medical Ward / Men | Item | 4
4 | Medical Ward / Women | Item | 4
5 | surgical Ward | Item | 4
6 | Preparation area of OT | Item | 1
7 | OT | Item | 1
8 | Pre Delivery suite | Item | 2
9 | Delivery suite | Item | 1
10 | NICU | Item | 3
11 | ICU | Item | 4
SECOND FLOOR
1 | Private rooms | Item | 5
13.15 | Medical Air System
Design supply and complete installation of Piped and tested Medical air system from medical air plant as per Specifications and manufactures guidelines, instructions.. Oxygen bank, capacity to connect minimum 12 jumbo cylinder. System to be insttaled as per manufactures standards.
GROUND FLOOR
1 | ER | Item | 5
2 | Treatment room | Item | 2
3 | Isolation room 1,2 | Item | 2
FIRST FLOOR
1 | Pediatric Ward | Item | 4
2 | Gynecology Ward | Item | 4
3 | Medical Ward / Men | Item | 4
4 | Medical Ward / Women | Item | 4
5 | surgical Ward | Item | 4
6 | Preparation area of OT | Item | 1
7 | OT | Item | 1
8 | Pre Delivery suite | Item | 2
9 | Delivery suite | Item | 1
10 | NICU | Item | 3
11 | ICU | Item | 4
SECOND FLOOR
1 | Private rooms | Item | 5
13.16 | Vaccum System
Design supply and complete installation of Piped and tested vacuum system from a central vacuum system as per Specifications and manufactures guidelines, instructions..
GROUND FLOOR
1 | ER | Item | 5
2 | Treatment room | Item | 2
3 | Isolation room 1,2 | Item | 2
FIRST FLOOR
1 | Pediatric Ward | Item | 4
2 | Gynecology Ward | Item | 4
3 | Medical Ward / Men | Item | 4
4 | Medical Ward / Women | Item | 4
5 | surgical Ward | Item | 4
6 | Preparation area of OT | Item | 1
7 | OT | Item | 1
8 | Pre Delivery suite | Item | 2
9 | Delivery suite | Item | 1
10 | NICU | Item | 3
11 | ICU | Item | 4
SECOND FLOOR
1 | Private rooms | Item | 5
13.17 | Bed Head Units
1 | Supply and complete installation of Bed head units, with control panels , each unit must includes 13amp 4 single sockets, 13amp 1 single socket with USB port, 1 network point, Obsevatuion light and necessary accessories. | Item | 46
BILL No:13 - ELECTRICAL INSTALLATIONS
TOTAL OF BILL No:13 - Carried over to summary
BILL No: 14
AIR-CONDITIONING SYSTEM
14.1 | General
(a) Rates shall include for supplying and complete installation of air-conditioning systems; including all pipework, electrical wiring, insulation, stands for outdoor units etc.
(b)All AC Equipments must beVRF or Central systems which have the capacity to control & operate multiple indoor units
(c) The brand of AC Equipment specified or to be proposed should have minimum 2 Fresh air or Hospital Air-condition Projects completed and delivered over the past 5 years in Maldives with proven records of successful Hospital Grade Projects
(d) Contractor shall provide Shop Drawings for Consultants' Approval for all electrical units including lighting, power, ACMV systems.
(e) The Brand of AC Equipment specified or to be proposed should demonstrate that it is adequate to cater for highly corrosive environment of Maldives and should have 5 years of past projects completed
f) Quality of Air condition to be Daikin Inverter VRV IV Q series with 360 Deg. Round flow indoor casette type or Equivalent, Efficiancy of overall system performance must be up to 28 IEER.
(f)The brand or AC Equipment specified should demonstrate all specs below from manufacturers original catalogue
Outdoor Specs
(a)The Outdoor Unit Shall be Factory assembled with Weather Proof casing, constructed from Heavy Gauge Mild Steel Panels and coated with Anti Corrosive Epoxy resin finish. The unit should be completely factory wired and tested and shall be fitted with all necessary controls and switch gear.
(b) All outdoor units need to be VRV or Central systems which have the capacity to control & operate multiple indoor units
(c) The Condensor Coil of the Outdoor must be a black fin Condensor with anti corrosion
(d) The brand of AC Equipment proposed should have an outdoor or outdoor sets with a maximum Energy Efficiency Ratio of (EER) kw/kw 4.5
(e) The brand of AC Equipment proposed should have Outdoor Environment sensor for Compressor Control and adjustment
(f) The Brand of AC Equipment proposed should have an outdoor or outdoor sets of Sound Pressure Level dB (A) below 60
(g)All Outdoor units shall be with inverter compressors and be able to operate even in the event of failure of one compressor
(h) All outdoor units needs to have aluminium fins with 105+2 μm thickness, with special Anti corrosive coating of 1.3 ± 0. 35 μm thickness and an outside Hydrophilic layer coating of 0.35 ± 0. 07 μm thickness.
(j) All outdoor units shall be equipped with high efficiency optimized heat exchangers with variable heat exchanger circuits
(j)The outdoor units shall be provided with its own microprocessor control panels
(k) The manufacturer needs to provide a warranty of 18 months replacement for the outdoor units
Indoor Specs
(a) The address of the indoor unit shall be set automatically in case of individual and group control
(b) In case of centralized control, it shall be set by liquid crystal remote controller
(c) The fan shall be a dual suction, aerodynamically designed turbo, multi blade centrifugal type fan which shall be statically & dynamically balanced to ensure low noise and vibration free operation. The fan shall be direct driven, mounted directly on motor shaft having support from the unit housing.
(d) The cooling coil shall be made out of seamless copper tubes and have continuous aluminum fins. The tubes shall be staggered in the direction of airflow and shall be hydraulically/ mechanically expanded to bond to the fins. Each coil shall be factory tested at 21kg/sqm air pressure under water.
(e) Each unit shall have a cleanable type filter fixed to an integrally moulded plastic frame. The filter shall be a slide out type and shall be neatly inserted.
(f) All AC duct systems must have an H14 Hepa filters attached with 99.99% efficiency on Supply & Return Duct as well
(g) The capacity of Indoor unit have to be calculated as per the volume of the occupied space and should have Air exchange of the Minimum apart from operation theatres i) 9 – 12 air changes per hour from the AC system ii) . 2 -3 air changes per hour of Outside Air (Via Fresh Air System)
(h) For operation Theatres the Air Exchange Guideline should be i) 25 air changes per hour from the AC system ii) 5 air changes per hour from Outside Air (Via Fresh Air System)
(i) Each unit shall be provided with a hand held multi-function remote controller. The controller shall be able to change fan speed and angle of swing, temperature and mode.
(J) Each Unit shall have service Ball valves for After sale service and future Isolation of FCU
AHU General Specs
(a) Panel Specs - Outer Skin : 0.5mm Pre-painted Sheet - Inner Panel-Btm: 0.7mm Galvanized Steel - Inner Panel: 0.5mm Galvanized Steel - Panel Thickness: 50mm - Unit Base H: 100 (GI Plate) mm
(b) Mixing Box - Fresh Type: Aluminium Damper - Control Type: Manual
(c) Pri+Sec Filter - Filter Frame: Frame -Grade: G4 - Dust Filter Type: Bag - Dust Filter Grade: F8
(d) Hepa Filter - Filter Frame: Frame - Grade: H14 (99.99% MPPS) - Frame Material: Galvanized Steel -Type: Box
(e) Cooling Coil -Coil Mode: 3/8", 660.4 x 990 6R 12F 13C - Tube Material: Copper - Hdr Material: Copper - Drain Pan: Stainless Steel - Fin Material: Hydrophilic - Coil Frame: Stainless Steel - Refrigerant: R410A
(f) Electric Heater - Brand: wellen - Current/Stage: 15.8:15.8 A - Stages: 1:1 - Power Supply: 380
(g) Plug Fan Supply - Fan Brand: Nicotra - blade type: plug - Motor Type: TEFC-IP55 - Motor Brand: Alliance - Motor Frequency: Variable Frequency - Power supply: 380V/3Ph/50Hz
Ducting & Ventilation System
(a) All Conceal Duct Indoor System shall be connected to a Duct Ventilation system which shall be designed to provide the most appropriate air flow for designed Air-condition areas
(b) The Duct System shall be made with Pre-Insulated Panels with the below specs - Panel Thickness: 20 – 30mm - Foam Density: 45-48kg/m3 - Aluminium thickness: 80/80m - Alimunium Type: Embossed - The Boards should be Anti-Bacterial, Anti Fungus & Fire Restiant
(c) All supplier & Return Diffusers shall be - The Supply and return air diffusers/grills shall be made of extruded aluminum section with flush fixed pattern - White Powder Coated RAL9010 or 9016 standard - Supply Diffusers shall be with opposed Blade Volume dampers - Thickness of frame should not be less than 1.2mm. The core of the diffuser is 0.9mm thick pressed aluminum.
(d) All ducts shall be installed generally as per the drawings and in strict accordance with approved shop drawings to be prepared by the Contractor.
Refrigerant Piping
(a) All refrigerant piping for the air conditioning system shall be constructed from Hard seamless copper up to outer diameter of 41.3 mm and hard drawn copper above outer diameter of41.3 mm. Fittings shall have silver-soldered joints and connections to equipment shall us compression fittings.
(b) All joints in copper piping shall be swag joints using low temperature brazing and or silver solder. Before joining any copper pipe or fittings, its interiors shall be thoroughly cleaned by passing a clean cloth via wire or cable through its entire length. The piping shall be continuously kept clean of dirt etc. while constructing the joints. Subsequently, it shall be thoroughly blown out using nitrogen.
(c) After the refrigerant piping installation has been completed, the refrigerant piping system shall be pressure tested using nitrogen at pressure of 580 PSIG. Pressure shall be maintained in the system for 24 hours. The system shall then be evacuated to minimum vacuum of 700mm hg and held for 24 hours.
(d) The thickness of copper piping shall as per Standard ASTM B280-03
Refrigerant Pipe Insulation
(a) The whole of the liquid and suction refrigerant lines including all fittings, valves etc. shall be insulated with 25mm thick insulation for all copper sizes. Insulation shall be closed cell elastomeric nitrile rubber.
(b) To protect nitrile rubber of exposed piping from degrading due ultra violet rays & atmospheric conditons, it shall be covered polyshield coating with at least two coats of resin and hardener (Make-Polybond /Paramount Polytreat). Fiberglass tape shall be helically wound & painted with two coats of resin with hardener to give smooth & plain finish.
(c) All insulation has to be wrapped in Aluminium Fiber Foil Tape or sheet
14.2 | Ground Floor Air System
14.2.1 | Laboratory
1 | Design supply and complete installation of AHU unit with VAV and individual remote control for all rooms. 160,000BTU - AHU should be equiped with H14 (99.99%) Efficiency Filters with Precise Temperature & Humidity Control settings - 20mm Thickness PID ducting, Anti Bacterial, One side embossed, One said Plain - Adequate Return & Supply Power Coated Supply Grills | Item | 1
14.2.2 | ER
Design supply and complete installation of following units
1 | 24000BTU 4 Way Casette Indoor for Main ER Lobby | nos | 4
2 | 7000BTU 4 Way Casette Indoor for Equipment Store | nos | 1
3 | 7000BTU 4 Way Casette Indoor for Clean Utility | nos | 1
4 | 7000BTU 4 Way Casette Indoor forDirty Utility | nos | 1
5 | 7000BTU 4 Way Casette Indoor for Medical Store | nos | 1
6 | 7000BTU 4 Way Casette Indoor for Medical Prepration | nos | 1
7 | 96000BTU Duct Fresh Air Indoor for Main ER With 5 Supply Grills and Fresh air Intake from outside | nos | 1
8 | 180,000 VRF Centra Outdoor Top Throw for AHU | nos | 1
9 | 140,000BTU VRF Central Outdoor Top Throw | nos | 1
10 | 100,000BTU VRF Central Outdoor Top Throw for Fresh Air Unit | nos | 1
14.2.3 | Café Zone
1 | 18000BTU 4 Way Casette Indoor for Main Café' | nos | 5
2 | 12000BTU 4 Way casette Indoor for Guest Shop | nos | 1
3 | 9000BTU 4 Way casette Indoor for OPD A | nos | 1
4 | 18000BTU 4 Way casette Indoor for Pharamacy | nos | 1
5 | 140,000BTU VRF Central Outdoor Top Throw | nos | 1
14.2.4 | Walkways
1 | 18000BTU 4 Way Casette Indoor for Walkways and corriddors | nos | 9
2 | 180,000BTU VRF Central Outdoor Top Throw | nos | 1
14.2.5 | Main Reception
1 | 24000BTU 4 Way Casette Indoor for MainReception | nos | 4
2 | 9000BTU 4 Way casette Indoor for Public Relations | nos | 1
3 | 12000BTU 4 Way casette indoor for Meeting room | nos | 2
4 | 12000BTU 4 Way casette indoor for Pantry | nos | 1
5 | 160,000BTU VRF Central Outdoor Top Throw | nos | 1
6 | Air Curtain for Entrance Doors | nos | 4
14.2.6 | Public Health
1 | 18000BTU 4 Way Casette Indoor for MainReception | nos | 3
2 | 12000BTU 4 Way casette indoor for Kids Play zone | nos | 1
3 | 18000BTU 4 Way casette for Vaccination | nos | 1
4 | 9000BTU 4 Way casette Indoor for Reproduction Health | nos | 1
5 | 9000BTU 4 Way casette Indoor for Public Health | nos | 1
6 | 9000BTU 4 Way casette Indoor for Cessation Clinic | nos | 1
7 | 120,000BTU VRF Central Outdoor Top Throw | nos | 1
14.2.7 | Flu Clinic
1 | Design supply and complete installation of 80,000 BTU AHU unit with H14 Hepa Filteration, 10 Air exchange Per Hour and Negative Air pressure Zone for Holding rooms, Isolation Rooms, Dirty Corridor, Staff change, Dirty Utility - 20mm Thickness PID ducting, Anti Bacterial, One side embossed, One said Plain - Adequate Return & Supply Power Coated Supply Grills | Item | 1
2 | 7000BTU 4 Way Casette Indoor for Equipment Store | nos | 1
3 | 7000BTU 4 Way Casette Indoor for Clean utility | nos | 1
4 | 7000BTU 4 Way Casette Indoor for Medical Store | nos | 1
5 | 7000BTU 4 Way Casette Indoor for Medical Preparation | nos | 1
6 | 12000BTU 4 Way Casette Indoor for Walkway and Medical Preparation Lobby | nos | 3
7 | 18000BTU 4 Way Casette Indoor for Flu Clinic Lobby and Reception | nos | 2
8 | 9000BTU 4 Way casette Indoor for Consultation | nos | 1
9 | Air Curtain for Entrance Doors | nos | 4
10 | 100,000 BTU VRF Central Outdoor Top Throw for AHU | nos | 1
11 | 120,000BTU VRF Central Outdoor Top Throw | nos | 1
14.2.8 | OPD, X ray & Scan
1 | 9000BTU 4 Way Casette Indoor for OPD rooms | nos | 6
2 | 18000BTU 4 Way Casette Indoor for Scan room | nos | 1
3 | 24000BTU 4 Way Casette Indoor for X ray room | nos | 1
4 | 9000BTU 4 Way Casette Indoor for X ray control room | nos | 1
5 | 9000BTU 4 Way Casette Indoor for X ray Reception | nos | 1
6 | 7000BTU 4 Way Casette Indoor for Clean Supply | nos | 1
7 | 12000BTU 4 Way Casette Indoor for Sterile Area | nos | 1
8 | 18000BTU 4 Way Casette Indoor for CCSD Clean Room & Packing | nos | 2
9 | 12000BTU 4 Way Casette Indoor for Washing & Disinfector | nos | 1
10 | 200,000BTU VRF Central Outdoor Top Throw | nos | 1
14.3 | First Floor
14.3.1 | Wards
1 | 12000BTU 4 Way Casette Indoor for Surgical ward | Nos | 4
2 | 18000BTU 4 Way Casette Indoor for Female Medical Ward | Nos | 2
3 | 18000BTU 4 Way Casette Indoor for Male Medical Ward | Nos | 4
4 | 12000BTU 4 Way Casette Indoor for Walkway and Nurse Station | Nos | 4
5 | 12000BTU 4 Way Casette Indoor for Gyne Ward | Nos | 6
6 | 9000BTU 4 Way Casette Indoor for Staff room | Nos | 1
7 | 12000BTU 4 Way Casette Indoor for Paedratic Ward | Nos | 4
8 | 12000BTU 4 Way Casette Indoor for Kids Playing room | Nos | 2
9 | 7000BTU 4 Way Casette Indoor forClean rooms | Nos | 2
10 | 96000BTU Duct Fresh Air Indoor for Surgical, Female, Male, Gyne and Paedratic Ward | Nos | 2
11 | 220,000BTU VRF Central Outdoor Top Throw | Nos | 2
12 | 200,000BTU VRF Central Outdoor Top Throw for Fresh Air | Nos | 1
14.3.2 | Operation Theatre
1 | Design supply and complete installation of 240,000 BTU AHU unit with H14 Hepa Filteration, 10 Air exchange Per Hour with Fresh Air Intake and VAV Boxes for Separate Control for all Operation Theatre rooms and areas - 20mm Thickness PID ducting, Anti Bacterial, One side embossed, One said Plain - Adequate Return & Supply Power Coated Supply Grills | Item | 1
2 | 260,000BTU VRF Central Outdoor Top Throw | Nos | 1
3 | Hepa Supply Grill for Air Flow Lamination for OT | Nos | 1
14.3.3 | Birthing Area
1 | 12000BTU 4 Way Casette Indoor for Delivery Suite | Nos | 2
2 | 7000BTU 4 Way Casette Indoor for Sterile Store | Nos | 3
3 | 7000BTU 4 Way Casette Indoor for Changing | Nos | 1
4 | 7000BTU 4 Way Casette Indoor for Dirty Utility | Nos | 1
5 | 7000BTU 4 Way Casette Indoor for Equipment Room | Nos | 1
6 | 12000BTU 4 Way Casette Indoor for Staff Lounge | Nos | 1
7 | 24000BTU 4 Way Casette Indoor for Nurse Statiom | Nos | 2
8 | 7000BTU 4 Way Casette Indoor for Nurse Station Cleaning room | Nos | 2
9 | 12000BTU 4 Way Casette Indoor for Pre Delivery Suite | Nos | 2
10 | 18000BTU 4 Way Casette Indoor for Pre NICU | Nos | 2
11 | 12000BTU 4 Way Casette Indoor for Incubator room | Nos | 1
12 | 7000BTU 4 Way Casette Indoor forMothers feeding, Baby Wash | Nos | 2
13 | 96000BTU Duct Fresh Air Indoor for Delivery Suite & NICU | Nos | 1
14 | 240,000BTU VRF Central Outdoor Top Throw | Nos | 1
15 | 100,000 BTU VRF Central Outdoor Top Throw for Fresh Air | Nos | 1
14.3.4 | ICU
1 | 12000BTU 4 Way Casette Indoor for ICU Unit 1 to 3 & Isolation Unit | Nos | 4
2 | 12000BTU 4 Way Casette Indoor for ICU Unit Lobby & Nurse Station | Nos | 3
3 | 7000BTU 4 Way Casette Indoor for Equipment Room | Nos | 1
4 | 7000BTU 4 Way Casette Indoor for Dirty Utility & clean Utility | Nos | 4
5 | 96000BTU Duct Fresh Air Indoor for ICU | Nos | 1
6 | 140,000BTU VRF Central Outdoor Top Throw | Nos | 1
7 | 100,000 BTU VRF Central Outdoor Top Throw for Fresh Air | Nos | 1
14.3.5 | Walkway & Hangout Space
1 | 24000BTU 4 Way Casette Indoor for Hangout Space | Nos | 6
2 | 18000BTU 4 Way Casette Indoor for walkway | Nos | 4
3 | 220,000BTU VRF Central Outdoor Top Throw | Nos | 1
14.4 | Second Floor
14.4.6 | Private rooms
1 | 18000BTU 4 Way Casette Indoor for Private room 1 to 5 | Nos | 5
2 | 18000BTU 4 Way Casette Indoor for Family room | Nos | 1
3 | 18000BTU 4 Way Casette Indoor for Nurse Station and waiting lounge | Nos | 3
4 | 7000BTU 4 Way Casette Indoor for Dirty Utility | Nos | 1
5 | 7000BTU 4 Way Casette Indoor for Medical Store & Medical Preparaiont | Nos | 2
6 | 12000BTU 4 Way Casette Indoor for Nurse Rest room | Nos | 1
7 | 220,000BTU VRF Central Outdoor Top Throw | Nos | 1
14.4.7 | Hand Therapy
1 | 9000 BTU 4 Way Casette Indoor for Massage room 1 - 3 | Nos | 3
2 | 9000 BTU 4 Way Casette Indoor for Hydro Theraphy | Nos | 1
3 | 9000 BTU 4 Way Casette Indoor for Speech Therapy | Nos | 1
4 | 12000BTU 4 Way Casette Indoor for Supervisors office | Nos | 1
5 | 12000BTU 4 Way Casette Indoor for Pantry | Nos | 1
6 | 24000BTU 4 Way Casette Indoor for exercise room | Nos | 2
7 | 24000BTU 4 Way Casette Indoor for Reception & Main Lobby | Nos | 3
8 | 220,000BTU VRF Central Outdoor Top Throw | Nos | 1
14.4.8 | Canteen & walkway Main lobby
1 | 24000BTU 4 Way Casette Indoor for Cnateen | Nos | 3
2 | 9000 BTU 4 Way Casette Indoor for Male & Female Prayer room | Nos | 2
3 | 12000BTU 4 Way Casette Indoor for Pantry prepration | Nos | 1
4 | 12000BTU 4 Way Casette Indoor for Pantry prepration | Nos | 4
5 | 160,000BTU VRF Central Outdoor Top Throw | Nos | 1
14.4.9 | Multi Purpose Hall
1 | 24000BTU 4 Way Casette Indoor for Hall | Nos | 5
2 | 24000BTU 4 Way Casette Indoor for Training Room | Nos | 1
3 | 7000BTU 4 Way Casette Indoor for Storage | Nos | 1
4 | 180,000BTU VRF Central Outdoor Top Throw | Nos | 1
14.4.10 | Public health unit
1 | 7000BTU 4 Way Casette Indoor for Storage | Nos | 1
2 | 12000BTU 4 Way Casette Indoor for Store room | Nos | 1
3 | 12000BTU 4 Way Casette Indoor for Pantry | Nos | 1
4 | 24000BTU 4 Way Casette Indoor for Main Office | Nos | 3
5 | 7000BTU 4 Way Casette Indoor for Filing Area | Nos | 1
6 | 9000 BTU 4 Way Casette Indoor for Budget | Nos | 1
7 | 12000BTU 4 Way Casette Indoor for Admin | Nos | 1
8 | 18000BTU 4 Way Casette Indoor for Manager room | Nos | 1
9 | 12000BTU 4 Way Casette Indoor for Reception | Nos | 2
10 | 12000BTU 4 Way Casette Indoor for Maintainance Workshop | Nos | 2
11 | 220,000BTU VRF Central Outdoor Top Throw | Nos | 1
14.4.11 | Main office
1 | 7000BTU 4 Way Casette Indoor for Stock & Maintainance | Nos | 2
2 | 9000 BTU 4 Way Casette Indoor for Budget | Nos | 1
3 | 12000BTU 4 Way Casette Indoor for Admin | Nos | 1
4 | 18000BTU 4 Way Casette Indoor for Manager room | Nos | 1
5 | 7000BTU 4 Way Casette Indoor for Filing Area | Nos | 1
6 | 18000BTU 4 Way Casette Indoor for Main office | Nos | 4
7 | 18000BTU 4 Way Casette Indoor for 2 Meeting rooms | Nos | 2
8 | 24000BTU 4 Way Casette Indoor for Server room | Nos | 1
9 | 12000BTU 4 Way Casette Indoor for ZV room | Nos | 1
10 | 12000BTU 4 Way Casette Indoor for waiting & receptionm | Nos | 2
11 | 240,000BTU VRF Central Outdoor Top Throw | Nos | 1
BILL No:14 - AIR-CONDITIONING SYSTEM
TOTAL OF BILL No:14 - Carried over to summary
BILL No: 15
PAVEMENT
15.1 | General
(a) Rates shall include for supplying and complete installation of pavement blocks; including all laying levelling and compacting etc.
15.2 | Pavement blocks, Ambulance Way.
15.2.1 | Pavement blocks 2ft x 2ft x 2in blocks laid with 20mm gaps, Payment blocks must be make with cemenet and course sand.
1 | Pavement bocks | no | 682
BILL No:15 - PAVEMENT
TOTAL OF BILL No:15 - Carried over to summary
BILL No: 16
COMMON WORKS
16.1 | General
a) Rates shall include for: screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rate shall include for electrical conduits, fittings, equipment and similar all fixings
c) Rate shall include for all necessary electrical wiring and accessaries required for completion of lift installation.
16.2 | LIFTS
16.2.1 | Passenger Lift
| Supply and complete installation of lift complete: "Mitsubishi or Equivalent, to lift 6 person capacity, serving all levels as per manufacturer's instructions. Emergency landing device must be installed. | item | 1
16.2.2 | Bed Lift
| Supply and complete installation of lift complete: "Mitsubishi or Equivalent, serving all levels as per manufacturer's instructions. Emergency landing device and acess control system (inside and out side of lift) must be installed. | item | 1
16.3 | Access Constrol system
Access control system as required for all floors (call buttons, monitors etc) design, supply and install according to hospital operators’ demand/specifications.
16.3.1 | Electromagnetic lock with Proximity Card Reader and Push Button | nos | 30
16.3.2 | Door Bell | nos | 25
16.4 | CCTV SYSTEM (SECURITY SYSTEM)
CCTV system full system incluing all hardwear, wiring as required for all floors all inclusive installation and commissioning.design, supply and install according to hospital operators’ demand/specifications.
16.4.1 | Angular Camera | nos | 20
16.4.2 | Ceiling mounted 360 degree camera | nos | 20
16.4.3 | Wall mounted 360 degree camera | nos | 20
16.4.4 | 3KVA Smart UPS APC or equivalent | nos | 1
16.4.5 | Network Video Recorder ( minimum 2 months) and other necessary items required to complete the CCTV system. | nos | 1
16.5 | HUT FOR OXYGEN & AIR DESIGN & BUILD
| a) Rates shall include for: Design & build, supply and Complete installation according to hospital operators’ demand/specifications. screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories. | item | 1
16.5.1 | Hut for Oxygen and Medical Air
16.6 | NURSE CALL SYSTEM & PUBLIC ADDRESS SYSTEM
16.6.1 | Nurse call system and Public address system. incluing all hardwear, wiring as required for all floors all inclusive Design supply, installation and commissioning.design, supply and install according to hospital operators’ demand/specifications. | item | 1
16.7 | QUEUE NUMBER SYSTEM
16.7.1 | Queue Number System. incluing all hardwear, wiring as required for all floors all inclusive Design, supply, installation and commissioning.design, supply and install according to hospital operators’ demand/specifications. | item | 1
16.8 | LIGHTENING PROTECTION SYSTEM
16.8.1 | Design, supply, and Complete installation of Erco, Eritech or equivalent lightening Protection System to cover the whole building as per local regulations (Rate shall include for all fixing of the system and down conductor to earthing) Coverage of lightning protection should be minimum 100 Meter Radius. Pric also include to install Marine grade SS post. | item | 1
16.9 | PUBLIC ADDRESSING (PA) SYSTEM
16.9.11 | Design, supply and complete installation of PA system. incluing all hardwear, wiring as required for all floors all inclusive installation and commissioning.design, supply and install according to hospital operators’ demand/specifications. | item | 1
16.1 | EARTHING.
16.10.1 | Earth pit with resistance must be less than 2 ohms, 3/4 earth rods must be used and must have clamps at the end, Earth pit should be covered junction with cover.
1 | Completion of earth pit with earthing cable and completion of earthing as per the above requirements. | Item | 1
BILL No:16 - COMMON WORKS
TOTAL OF BILL No:16 - Carried over to summary
BILL No: 17
SOLAR PV SYSTEM
17.1 | General
a) Rates shall include for: Design, supply and install according to hospital operators’ demand/specifications. screws, nails, bolts, nuts, standard cable fixing or supporting clips, brackets, straps, rivets, plugs and all incidental accessories.
b) Rate shall include for electrical conduits, fittings, equipment and similar all fixings
c) Rate shall include to complete the system and connect to the grid with net metering as per specification and approval of Consultant/ Client (Junction box specs, solar AC & DC cable specs, solar brackets specs, inverter specs & solar panel specs…etc)
17.1.1 | Design supply and complete installation on 100KW Solar PV system. Rates includes to complete the system and connect to the grid with net metering as per specification. ( junction box specs, Solar AC&DC cable specs, solar bracket specs, inverter specs & solar panel must be same as specification). | item | 1
BILL No:17 - SOLAR PV SYSTEM
TOTAL OF BILL No:17 - Carried over to summary
BILL No: 18
TENDERER'S ADJUSTMENTS
Any adjustments that the contractor may consider necessary should be written below and on similar continuation sheets if required, and the net amount of the adjustments is to be carried to the summary.
(a) Provide detail description of work items under each bill and insert extra pages if required.
16.1 | Additions
1 | Preliminaries - Bill no. 1
2 | Ground works - Bill no. 2
3 | Concrete - Bill no. 3
4 | Masonry and plastering - Bill no. 4
5 | Wood work - Bill no. 5
6 | Roofing - Bill no. 6
7 | Doors and windows - Bill no. 7
8 | Ceiling - Bill no. 8
9 | Painting - Bill no. 9
10 | Finishes - Bill no. 10
11 | Fire fighting system - Bill no. 11
12 | Hydraulics & Drainage - Bill no.12
13 | Electrical Installation - Bill no. 13
14 | Air - condition system - Bill no. 14
15 | Pavement - Bill no. 15
16 | Common Works - Bill no.16
17 | Solar PV System - Bill no.17
ADDITIONS TOTAL
16.2 | Omissions
1 | Preliminaries - Bill no. 1
2 | Ground works - Bill no. 2
3 | Concrete - Bill no. 3
4 | Masonry and plastering - Bill no. 4
5 | Wood work - Bill no. 5
6 | Roofing - Bill no. 6
7 | Doors and windows - Bill no. 7
8 | Ceiling - Bill no. 8
9 | Painting - Bill no. 9
10 | Finishes - Bill no. 10
11 | Fire fighting system - Bill no. 11
12 | Hydraulics & Drainage - Bill no.12
13 | Electrical Installation - Bill no. 13
14 | Air - condition system - Bill no. 14
15 | Pavement - Bill no. 15
16 | Common Works - Bill no.16
17 | Solar PV System - Bill no.17
BILL No: 18- TENDERER'S ADJUSTMENTS
TOTAL OF BILL No: 18 - Carried over to summary