EMPLOYER’S REQUIREMENT

TABLE OF CONTENTS

1.	Project Brief	4

1.1 A summary of key building features are as follows	4

1.2 Design Philosophy	5

1.3 Key Environmental Considerations	5

2.	Scope of works related to Design Stage	6

3.	Scope of works related to Construction Stage	8

4.	Project Management Plan and Work Programme	10

4.1 Project Monitoring Documents	11

4.2 Key Personnel	12

4.3 Work Progress	13

4.4 Project deliverables	13

4.5 General Design Obligations of the Contractor	13

4.6 Price Proposal	14

4.7 Proposed method / material and machinery and equipment	14

4.8 General conditions of contract for the procurement of works	15

5.	Functional Requirement of the Office Building	15

5.1 Ground Floor Facilities	15

5.2 Mezzanine Floor Facilities	15

6.	Building services engineering strategy	16

6.1 Electrical Services	16

6.2 Mechanical services	17

6.3 Fresh Water System	19

6.4 Sanitary System	19

6.5 Fire Fighting System	20

6.3 ICT and Network Infrastructure	20

7.	Technical Specification – General Works	20

7.1 Site Works	21

7.1.2	Site Clearance	21

7.1.3	Excavation	22

7.1.4	De-watering	24

7.1.5	Backfill	24

ANNEX A: CIVIL AND STRUCTURAL DESIGN REQUIREMENTS	26

1.	GENERAL	27

2. LOAD DEFINITION	27

3. STRUCTURAL DESIGN	28

4.	SOIL PROPERTIES	34

5.	ROADS AND PAVED AREAS	34

6.	UNDERGROUND UTILITIES	34

7.	FOUNDATIONS, FOOTINGS AND FLOOR SLABS	34

8.	CONCRETE BLOCKWORK	35

9. DETAILED ENGINEERING DOCUMENTS	35

10. EARTHWORKS	36

ANNEX B: MEP REQUIREMENT	37

1.	GENERAL	37

2. DESIGN CRITERIA	38

3. BUILDING ELEMENTS	39

4. BUILDING LOAD FACTORS	39

5. CODES, STANDARDS AND SPECIFICATIONS	40

ANNEX C: ELV REQUIREMENT	41

1.	Central Lighting Control and Monitoring System	41

2.	Centralized HVAC Control and Monitoring	41

3.	IP-Based Public Announcement	42

4.	Fire Detection and ALARM System	42

5.	Central Access Control	43

6.	IP Based Surveillance System	44

7.	IP Based Telephony	44

8.	IPTV and Digital Signage	44

9.	Managed Meeting Rooms	45

10.	Seminar Halls and Conference Rooms	46

11.	Gigabit network Backbone	46

12.	Central Operations and Control Room	47

13.	Floor MEP and ELV room	47

14.	Metering	48

DEVELOPMENT OF E-SPORTS ARENA AT SULTAN PARK, K. MALE’

# Project Brief

The Government of Maldives proposes the development of a modern E-Sports Arena at Sultan Park, K. Male’, to establish a dedicated venue for digital entertainment, gaming competitions, live broadcasting, and youth engagement activities. The proposed facility will function as a multi-use arena capable of hosting local and international e-sports tournaments, streaming events, VR gaming experiences, community events, and recreational activities.

The project is intended to support the growth of the gaming and digital entertainment industry in the Maldives by creating a technologically advanced, safe, and inclusive venue. The facility shall incorporate dedicated gaming zones, broadcasting rooms, streaming studios, VIP lounges, spectator seating, food and beverage spaces, and operational support areas.

The design shall prioritize operational efficiency, digital connectivity, flexibility of internal spaces, visitor comfort, acoustic performance, and immersive visual experiences. The building shall be developed using durable and sustainable materials suitable for the Maldivian climate, while also supporting long-term operational and maintenance requirements.

## 1.1 A summary of key building features are as follows

- Approximate built-up area: 507.26 sqm

- Ground floor and mezzanine floor arrangement

- Main gaming arena with stepped spectator seating

- Dedicated PC gaming area and VR gaming area

- Broadcasting room and two streaming rooms

- VIP lounge and event viewing area

- Stage and LED display integration for tournaments and events

- Reception and ticketing area

- Kids arcade gaming area

- Food and beverage facilities including kitchen and drinks bar

- Control room and server/network room

- Public toilets and service areas

- Outdoor café and gathering space

- High-speed structured cabling and fiber-ready network infrastructure

- Integrated audio-visual and broadcasting systems

- Accessibility provisions for persons with disabilities

## 1.2 Design Philosophy

The proposed E-Sports Arena shall be designed as a vibrant and immersive digital entertainment environment that encourages social interaction, innovation, and competitive gaming culture. The architectural concept shall combine modern aesthetics with functional flexibility, creating a landmark venue for youth engagement and entertainment within the urban context of Male’.

The facility shall prioritize user experience through carefully designed circulation, visual connectivity, acoustically controlled spaces, ergonomic seating arrangements, and adaptive lighting systems. Interior spaces shall support high occupancy loads during events while also allowing flexible day-to-day operation for casual gaming and training activities.

## 1.3 Key Environmental Considerations

The building shall incorporate energy-efficient systems and environmentally responsible design strategies suitable for tropical climatic conditions. The design shall maximize natural ventilation where practical, while ensuring conditioned indoor environments for gaming and broadcasting areas.

Low-energy LED lighting systems, inverter-based air-conditioning systems, and intelligent controls shall be utilized throughout the facility. Acoustic treatment and thermal insulation shall be integrated to improve energy efficiency and occupant comfort.

Air-Conditioning system is designed as a VRV system, synchronized with an active ventilation system, that will provide the required volume of air-changes within each building space. The system will provide the necessary fresh air supply to the entire building based on an active system. Efficiency of the air-conditioning system depends on how well the building envelope is designed to insulate from solar gain and how well other areas such as the roof provides the necessary thermal insulation. An energy-saving air-conditioning and ventilation system is the intention.

The building’s electrical system is designed to consider a roof-mounted photovoltaic system to harness solar power as a supplement to cut down on fossil fuels, as part of the energy management of the building. The intention is to again reduce energy consumption.

Noise produced within the interiors also accounts for the background noise level. This will be controlled through surface absorption and achieved by specifying appropriate material finishes to the floors, walls, and ceilings.

At this stage, the schematic plans have been addressed according to comments on the evolving concept, and it is understood that due to the nature of building, the actual internal planning can have many variations. Therefore, internal layouts will depend on the tenant’s requirements, the internal circulation governed by means of escape, plus coordination with building services, such as air-conditioning, IT networks etc.

# Scope of works related to Design Stage

The contractor shall carry out and be responsible for the detailed design of the project. The design requirements of the contractor are as follows:

- Detail architectural design based on the architectural floor layouts, elevations and sections and 3D render and architectural finishes provided with the tender document. The winning contractor may propose design changes during the design stage without deviating significantly from the original architectural design intent. These changes shall be accommodated within the contract value.

- Detailed architectural design based on approved schematic layouts and concept drawings.

- Preliminary and detailed structural design as specified.

- All designs must be to BS or equivalent international design standard and comply with the Maldivian laws and regulations.

- Structural design including foundations, framing systems, mezzanine structures, and roof systems.

- Detailed MEP and ELV design for gaming infrastructure and arena operations.

- Interior design including spectator seating, gaming layouts, lighting concepts, and branding integration.

- Acoustic and audio-visual system design.

- Preparation of authority approval drawings and permit documentation.

- Preparation of detailed BOQ, technical specifications, and shop drawings.

- Coordination with utility authorities and relevant government agencies.

It is the responsibility of the winning Contractor to submit the drawings for approval to the relevant authorities to the requirement of local regulations. A site map showing the site boundary will be provided. Any additional surveys or studies required for the submission of the proposal or for any other purpose shall be carried at the expense of the Contractor.

The Contractor shall prepare the detail design as per Employer’s Requirement and obtain approval from the Employer.

The Contractor shall bring in all materials, machinery, equipment, and necessary labour. The Contractor shall provide food and lodging for all management staff and labour. The Contractor shall provide temporary water and electricity and communication connections including cost for connection and monthly charges or alternative solutions at site to ensure the availability of temporary utility services.

The Contractor shall fabricate, supply and execute the installation of buildings, equipment, systems and furniture necessary to complete and make ready for operation as per the approved detail design Drawings, Specifications, Conditions of contract and in compliance with applicable standards & codes and with requirements of relevant authorities.

The Contractor shall execute and complete the design, and construction works within the duration of the project stipulated in the conditions of the contract.

The superstructure of the building is envisaged to be constructed with reinforced concrete. The substructure shall be reinforcement concrete.  The bidder may propose a concrete superstructure provided the materials used for construction shall be of high quality, with a design life of 50 yrs. Operation and maintenance manual with service contracts for lifts, fire-fighting equipment, air-conditioning must be provided in collaboration with the employer before taking over of the building for a period of minimum 2 years. The building shall be design and built, fit for purpose and contractor shall warrant that the structure and it is built shall withstand a minimum design life of 50 years.

All designs shall be completed as per the Detail Project Report and shall consist of all the requirements specified in the documents provided.

The major scope of works related to design stage include (but not limited to):

-	Conducting all necessary surveys, studies and investigations to assess the existing site conditions and prepare reports.

-	Carry out Geotechnical survey and & Soil Investigation report.

-	Load tests (when required).

-	Prepare Environmental Impact Assessment report and obtain approval.

-	Prepare detail design documents in accordance to the requirement of Employer. The documents include:

-	Detail architectural, structural and services drawing

-	Calculations

-	Detail BOQ

-	Specifications

-	Reports

# Scope of works related to Construction Stage

The Contractor shall execute the physical Permanent Works only when the Contractor receives approval from the Employer for all relevant documents under “2.2 Contractor’s Documents related to Design Scope”. However, the Contractor may, subject to obtaining a written approval from the Employer, commence Site (including temporary site) mobilization, Site preparation and ground works, and any other part of Works prior to approval of complete detail design scope.

It is in the Employer’s discretion to instruct the Contractor to commence physical works relating to the Construction Scope, in an event where sufficient documents related to the Design Scope have been approved.

The Contractor shall execute the Works in accordance with the approved Drawings, Specifications, Conditions of Contract and compliance with requirements of relevant authorities (as required). The Contractor shall ensure that all the Works mentioned in the Employer’s Requirement are completed. The Works shall be completed and ready for operation inclusive of establishment of all service connections required as per design.

The work progress and quality of work will be inspected by the Employer throughout the Construction Stage, to check whether the Works confirm with the above-mentioned documents. The Contractor shall facilitate the Employer to carry out these inspections.

All the materials to be used for the Works should be approved by the Employer prior to usage. No work should be executed without prior approval of relevant Method Statements by the Employer. The Contractor shall submit all Method Statements 14 days before a work is planned to commence. Inspections should be requested after making the work ready for inspection.

The Contractor shall submit all the documents stated in Employer’s Requirements, including all documents in 3.1 “Contractor’s Documents related to Construction Works” and Conditions of Contract for Review and approval. The Employer will check/review whether the submitted documents is practical and give approve/comments. The review period by the Employer is 14 calendar days from the submission date of each document.

The Construction Stage will be counted from the 60th day after the Commencement Date, regardless of whether all the drawings and documents under “2.2 Contractor’s Document related to Design Stage” has been approved by then or not.

Notwithstanding the Contractor can only commence the physical works on Site for which he has obtained written approval from the Employer.

The Construction scope is only deemed to be completed when the Employer has issued the “Taking-Over Certificate” in accordance with the Conditions of Contact.

The scope of Works is (but not limited to the following);

- Construction of reinforced concrete and steel structural elements.

- Construction of mezzanine floor and stepped spectator seating.

- Installation of architectural finishes, partitions, doors, glazing, and ceilings.

- Installation of all electrical, mechanical, plumbing, fire protection, and ELV systems.

- Supply and installation of gaming infrastructure and server facilities.

- Installation of LED display systems, audio systems, stage lighting, and broadcasting equipment provisions.

- Testing, commissioning, and operational readiness of all systems.

- External works including paving, landscaping, signage, and outdoor café areas.

- Construction and completion of external facades and all the exterior and interior finishing works, including doors & windows, as per approved detail designs and specifications.

- Interior finishing for all office spaces at the ground, 1st and 2nd floors shall be bare finished which include walls with plastering, screed flooring, and exposed slab soffit with plastering, all surfaces ready to receive paint, tiling or flooring system, and provisions for services. All other spaces at the basement, ground, 1st and 2nd floors shall be fully finished which include all wall, floor and ceiling finishing, as well as doors and windows, and complete services.

- Interior finishing for all spaces shall be bare finished which include walls with plastering, screed flooring, and exposed slab soffit with plastering, all surfaces ready to receive paint, tiling or flooring system, and provisions for services.

- Execution, completion, testing and commissioning of all services up to and including main connections, which includes (but not limited to), HVAC system, electrical system, emergency lighting system, plumbing and drainage system, firefighting fire detection, fire alarm systems, access control system, lightening protection system, telephone and GPON, IT infrastructure and CCTV system, including smart sensors as required to complete as per approved detail design drawings and specifications.

- Supply, installation, testing and commissioning of building management system, vehicular barrier gate system, emergency lighting, and lightening protection and earthing system.

- Supply, installation, testing and commissioning of main panel board, meters, distribution boards, pump systems including all associated charges as per Design and approved specifications.

- Construction and completion of any other works depicted in the approved detail drawings.

All above should be completed, as per approved Detail Drawings, Specifications, Finishing Schedule, Conditions of contract, specifications and compliance with applicable standards & codes and with requirements of relevant authorities. The Contractor shall ensure that all the Works mentioned in the Employer’s Requirement are completed. The Works shall be completed and ready for operation.

Mechanical equipment and systems such as elevators, barrier gates and such, shall be of locally available and a reputed brand with local service experience and spare parts available locally.

All system components shall be installed in accordance with the manufacturer’s recommendations. If installation of a component in accordance with the manufacturer’s recommendations is not possible, advice should be sought from the manufacturer or supplier. The Contractor shall make sure that all the equipment is installed at safe and protected locations.

# Project Management Plan and Work Programme

The Contractor shall submit the followings, as soon as practicable after the contract is signed, but no later than the date stated in Conditions of Contract. These documents should be revised during construction period when required.

a)	Detail work program showing the list of works/tasks in detail with planned start and end dates, durations for each work/task. The programme also shall include the critical path with all relevant predecessors properly linked and identified. The schedule shall also include the timelines when specific areas of the Site would be required to the Contractor.

a.	Manpower schedule showing the number and timing of required personals for Works.

b.	Equipment schedule showing the supplying quantity and timing of major apparatus, machinery, vehicles or any other equipment required for the Works.

b)	Key Personnel specified under 5 “Key Personnel” showing the numbers and qualifications, and timing of required personnel for the Works.

c)	Materials supply schedule showing the supplying quantity and timing of required materials.

d)	Project Management plan which shall include how the project will be carried out, outlining the scope and milestone, health and safety plan, risks and communication management plan.

e)	Work methodology or method statement showing the method each work will be carried out, responsibilities of the Contractor’s personnel, inspections and any testing that needs to be carried out.

f)	Project quality plan showing how the quality of the project is ensured, delineating the procedures, inspection and test carried out.

g)	Project cash flow forecast showing the how the billing will be made for the Works.

The Employer will check whether the submitted programme is practical based on the above information and approve the work programme.

## 4.1 Project Monitoring Documents

The Contractor shall submit the followings, as soon as practicable after the Contract is signed.

a)	Daily progress report should be submitted daily for every day, showing all the activities carried out at site, the number of personnel (both direct and indirect), machinery and plant, major materials used, weather condition and any other important incidents at site.

b)	Weekly progress report should be submitted weekly for every week, showing all the activities carried out at Site, the planned activities for the following week, the number of personnel (both direct and indirect), machinery and plant, major materials used, weather condition and any other important incidents at site.

c)	Monthly progress report should be submitted monthly for every month by the 5th day of each month, showing all the progress at Site (plan versus actual) using a Gantt chart, planned and actual percentages of the Works based on the work programme, the number of personnel (both direct and indirect), machinery and plant, major materials used, weather chart, materials approved, claim notices and claims, variations, financial status, progress photos and any other important incidents at site and off site. Additionally, the report shall include the following minimum requirement:

•	Ongoing works and Upcoming works for the following month

•	Incidents/Accident Report (if any)

•	Issues and challenges on Site

•	List of attended inspections and its reports

•	List of instructions given on-site

•	Documentation of approved methodologies

•	Test & Analysis Report (if any)

Note: Contractor shall arrange periodic sessions where the Employer can carry out a headcount to verify the personnel mentioned in the reports.

## 4.2 Key Personnel

The Contractor must ensure that the required, professional, technical and administrative inputs, required to deliver on the project are considered, costed and made available to the Works as necessary.

The Contractor shall provide sufficient evidence and detail of qualifications, certification, experience and availability for and of personnel, which must be available for the required time to allow the Contractor to deliver on the requirements of the Contract.

The Employer reserves the right to accept or reject based on changes to the Contractor’s personnel.

The Contractor shall make available all the key personnel required for the whole duration that the Works are being executed as per the Conditions of the Contract.

| Position | Qualification |
| --- | --- |
| Project Manager | Degree in Project management or relevant field with 10 years of Project Management experience. |
| Architect | Degree in Architecture with 5 years of experience |
| Civil engineer | Degree in Civil engineering with 5 years of experience |
| Building services engineer | Degree in Building services engineering with 5 years of Building services engineering experience |
| Site engineer | Degree in Civil engineering with 3 years of Site management experience |
| Site supervisor | Diploma in Civil engineering or construction related field with 3 years of experience, or 7 years of experience in Construction field |
| Quantity surveyor | Degree in Quantity Surveying or relevant field with 5 years of Quantity Surveying experience. |
| Project Administrator | Degree in Business Administration with 5 years of experience |

## 4.3 Work Progress

The actual work progress will be determined by the Employer in reference to the submitted Work program.

## 4.4 Project deliverables

In addition to complying with the relevant clauses of the Contract and within the time stipulated

(unless agreed otherwise) the following reports/design documents must be submitted;

- A full schedule of works in Microsoft Project indicating proposed start and end dates and subdivided into major and minor activities and/or durations not exceeding the Time for Completion. In preparation for the schedule, the local climate and other obstacles which may affect delivery must be considered. –

- Schedule of Payments referenced to the actual progress of work achieved ‐

- Preliminary Architectural and Structural design drawings for review and acceptance

- Preliminary MEP design. –

- Preliminary ELV design. –

- Structural and Architectural design drawings and 3D render and other documents as required for the issuance of Construction permit from relevant Maldivian Authorities.

- Complete and detail Architectural, Structural and MEP and ELV design construction drawings of the Project

- Complete Construction Specifications for the project –

The technical documents to be submitted by the contractor for the above and any modification therein shall comprise the Contractor’s Documents forming part of the final agreement.

## 4.5 General Design Obligations of the Contractor

The Contractor shall carry out and be responsible for the design of the Works. These minimum requirements are not an exhaustive list, and contractors shall submit any additional requirements deemed not covered. Contractor shall propose changes to Annex A where practicable to optimize design and cost to the Employer. The Employer’s preliminary design shall be used as a guiding document and shall not be taken as the final quantification for the price proposal.

- Annex A: Proposed Architectural Drawings including finishing Schedule

- Annex B: Civil and Structural Design requirement

- Annex C: MEP requirement

- Annex D: ELV requirement

## 4.6 Price Proposal

The project is a lump sum contract, with schedule of payments for milestones. The Price proposal shall clearly give the cost breakdown of the major activities to be carried out under the project, like;

- Mobilization and project management cost

- Sub and superstructure

- External envelope

- Architectural finishes and internal partitioning

- MEP

- ELV

In addition to price, the contractor must submit a full list of material vendors / supplier / manufacturers upon which the price proposal is based and as per the finishing schedule.

## 4.7 Proposed method / material and machinery and equipment

The contractor shall submit a detailed method statement of proposed works including proposed equipment, procurement timeline of major materials and delivery site. The contractor shall identify its intended uses of areas of the site for materials staging, temporary offices, accommodation, and other activities. The contractor shall identify and propose the type of major material components like superstructure and walls etc. Contractor is encouraged to propose solutions for super structure and enveloping which requires a short construction period. Contractors may be invited during evaluation stage for a presentation of proposed work methodologies and answer any queries.

It is to be noted that the project will not be exempt from local custom duties. The cost proposals shall include for allowance of import duties for both temporary and permanent imported goods. Constructors, at his own discretion are required to inquire with local authorities for rates applicable to construction equipment, machinery, and goods.

## 4.8 General conditions of contract for the procurement of works

The Conditions of Contract comprise the “General Conditions”, which form part of the “Conditions of Contract for EPC/Turnkey Projects” First Edition 1999 published by Fédération Internationale des Ingénieurs-Conseils (FIDIC), and the following “Particular Conditions”, which include amendments and additions to such General Conditions.

Copies of FIDIC Conditions of Contract, referred to above, may be obtained from:

- FIDIC Secretariat

- P.O. Box 86

- CH 1000 Lausanne 12

- Switzerland

- Fax No: +41 21 653 5432

Refer to above FIDIC document which is an integral part of this Contract.

# Functional Requirement of the Office Building

## 5.1 Ground Floor Facilities

Reception and ticketing area

Main gaming arena and stage

VR gaming area

Kids arcade gaming area

Streaming Room 1

Streaming Room 2

Broadcasting room

Control room

Drinks bar and kitchen

Public toilets

Storage and garbage areas

Outdoor café seating

## 5.2 Mezzanine Floor Facilities

PC gaming area

General gaming area

VIP lounge area

Office and administration area

Open viewing pathways overlooking arena

# Building services engineering strategy

Following is the Mechanical, electrical Fire Alarm and Fire Fighting system, building services facilities that are proposed for the development.

## 6.1 Electrical Services

- Electrical Power System

Electrical System shall be designed as per Maldives Energy Authority’s regulations. A high-tension power cable (11KVA) will supply power to the building. A step-down transformer shall be sized and shall be installed on the ground floor of the building that will supply low tension power to the main distribution board. The main distribution board 	will have all the kilo Watt Hour meters and main breakers for all the floor feeders. The proposed schematic design will show the building's power plan for the whole building. This main distribution system shall be designed to accommodate incoming solar power harnessed from the roof top PV Panels.

Emergency generator housed on the ground floor will provide power to all essential power that includes main lobby area, all lift lobbies, lifts, car park ventilation, limited car park ventilation, limited car parking lighting (25% of the car park lighting), limited 	terrace lighting & power for CCTV system and security systems.

Each office space on every floor should have two distribution boards, one for the lighting system and one for the power system (socket outlets). The power distribution boards will 	supply power to all the socket outlets inside the office space via a sub distribution board. Furthermore, all the indoor and outdoor air-conditioning units should be powered from the power distribution board.

The building shall have an emergency generator to cater critical loads such as lifts and public area lighting. The generator should be connected to the main distribution panel via automatic transfer switch. Emergency generator and changeover system shall be designed to power the critical load within 20s of a mains failure

- Electrical Lighting system

All the building lighting systems shall be designed to the specified lighting level as shown 	on the shell and core schedule. The lighting system for each of the office spaces shall be 	controlled by a lighting control system. This lighting controller shall have the capability to have individual lighting controls to be installed in individual office cubical.

- CCTV System

The building shall have a high-quality closed-circuit Television (CCTV) system for surveillance of all public spaces, corridors, and parking areas. The CCTV systems shall have IP cameras and a video management system connected to the building’s data 	network’s security VLAN.

- Lightning Protection System

Lighting protection system shall be designed as per Maldives Energy Authority’s 	regulations. The lightning protection system shall consist of Early Steamer Emission (ESE) air terminal(s) mounted 2m above terrace roof. Down conductor shall run vertically down on a side of the building to a test pit. The down conductor shall be connected to the grounding electrodes via a test clamp.

## 6.2 Mechanical services

The mechanical services in the building shall be designed to follow the industry standards 	as follows:

- Maldives National Building code Handbook 2008

- CIBSE Guide

- NFPA and ASHRAE Standards.

- ANSI / SMACNA Standards

A VRV/VRF air-conditioning system shall be provided to maintain indoor comfort conditions for high-occupancy gaming environments. Mechanical ventilation shall be provided for enclosed spaces, toilets, kitchen, and equipment rooms.

The following will be provided as minimum mechanical systems for the building.

- Air Conditioning & Mechanical Ventilation System

The building will incorporate the following Air-Conditioning and mechanical ventilation systems:

Supply of conditioned or heat reclaimed, or heat reclaimed air into office space as required by ASHRAE 62.1 2007 minimum ventilation requirements for buildings.

Air cooling and conditioning systems to serve comfort cooling as well as functional cooling required for the building.

For operations, monitoring and control, the ACMV system will be divided into roughly four equal zones on each floor of the building. This will help both in power monitoring and operations and in maintenance, because different zones can be isolated and inspected separately.

A centralized but modular VRV system will be used for all cooling purposes of the building. The modular nature of VRV system will enable clustering the system, to dedicate them to different zones of the large floor area of the building. This will enable interchange of systems and use of same and similar spare parts and redundant equipment during maintenance, as priority and use arises.

Zoning of ACMV system also will enable the building owner to meter and monitor the electrical power consumption of the entire system for each zone separately.

Each floor will be served by separate dedicated fresh air processing units and or heat reclaimed ventilation (HRV) units, which will provide the required minimum amount of fresh air to eliminate stuffiness that are normally felt in cooled office spaces without fresh air supply. Supply of fresh air is important because it will reduce sick building syndromes by diluting pollutants generated inside.

Installation of HRV will enable reuse of energy from exhausted air to be used to cool supplied fresh air as part of building ventilation system.

The air conditioning system shall be designed to maintain the office air temperature of 25 degree C & relative humidity to be less than 65 percent. Individual office compartments of every single floor shall have different sets of VRC systems and the power for these units shall be connected for the respected electrical DB.

Ventilation will be provided by Air processing units and or HRV Units dedicated to each air-conditioning zone. Air Grilles shall be sized to minimize static pressure loss across the grille (ideally maintaining below 10Pa) while distributing air at a throw of no less than 4m at an acoustic performance of <30dBA.

Cooling of all areas will be from direct expansion type ceiling mount cassettes easy filter cleaning and easy installation. For ballroom and other grand areas ceiling concealed duct type can be recommended. All the indoor units shall be able to be controlled individually and together from the individual office space. Selection of indoor units will be based on interior requirements with relevance to air through for proper and even distribution of cool air.

All dedicated server rooms or critical electronic equipment rooms requiring rack-wise cooling will be provided with a precision air-conditioning system.

Both indoor and outdoor units’ operations will be monitored by the building Energy Management System which can alarm maintenance personnel in case of breakdowns and service requirements.

All the toilets shall be mechanically ventilated at, and the time shall have minimum of 10ACH. All the four escape staircases shall have roof mounted air supply system to be operated during any fire alarm. The staircase shall be pressurized to 1.2 bars.

Ducts will be insulated to prevent condensation forming within the ceiling void and to minimize noise.

All the lift machine rooms shall be air-conditioned and shall be maintained at 24 deg C.

## 6.3 Fresh Water System

The codes used for the detailed design of the Water Supply System shall be:

- BS EB 806 – 1-5:2010

- BS EN 1717:2000

Main connection to the building will be via MWSC network. The utility provider’s supply pipe will be directly connected to booster pumps via inlet manifold to increase 	pressure of the system. The booster pumps will then directly supply the pressurized water to outlets via individual risers connected to outlet manifold.

It is proposed to use at least two separate potable water risers for each floor when 	considering the large floor area of the office building. Apart from this, a separate line 	will also be provided for each proposed food and beverage space. This will enable separate metering of water supply systems.

A separate pipework, including risers, shall be provided to supply water to all the WC flush tanks. This separation will enable the owner to use recycled or other non-portable water sources such as flushing water. The source of water for flushing is mainly from the harvested rainwater stored in underground water tanks or well embedded underground.

All potable water pipes shall be of PP-R type and all pipes used for non-potable water shall be PVC pipe.

## 6.4 Sanitary System

The codes used for the detail design of all sanitary system shall be BS EN 120562:2000.

All wastewater from the development shall be driven by a gravity drainage system to the 	below ground drainage network. The ground below network will consist of UPVC pipe and shallow ICs for inspection purposes. All liquid waste will eventually be collected to MWS junction located in the plot boundary.

A two-pipe system will be proposed for the building. Separate waste pipes shall be provided for all sanitary fittings within the kitchen, utility room, toilets and shower rooms. Waste branch pipes shall be connected to vertical soil vent pipes (SVP) which will descend directly down to connect either to the below ground drainage system or a sump pump. The heads of the SVPs shall be complete with Air admittance Valves (AAV) to allow air into the system when negative pressure occurs or shall terminate to atmosphere complete with roof cowl. A roof cowl termination shall be incorporated as the preferred option.

All food production area waste connections will be provided with grease traps of adequate capacity to filter out oil and grease before reaching the MWSC main junction.

## 6.5 Fire Fighting System

The codes used for the detailed design of all Fire protecting systems be:

- MNDF local requirements

- NFPA 72 or BS EN 54 for fire detection and Alarm system.

- BS EN 671 for hose reel system

- BS 5041 for wet and dry riser systems

- The fire detection and firefighting systems will be designed to the standard required by MNDF fire department. As such the following systems will be provided.

- A dry riser system consisting of 4 dry risers, each connecting 2 landing valves to each floor.

- A hose reel system consisting of 4 standpipes and 4 hose reels on each floor.

- A fully addressable digital or analogue fire detection and Alam system with 4 dedicated zones on each floor.

## 6.3 ICT and Network Infrastructure

The arena shall include high-speed fiber-ready network infrastructure, dedicated server rooms, gaming-grade networking systems, and low-latency structured cabling to support tournaments, live streaming, and digital broadcasting.

# Technical Specification – General Works

Developers should follow the technical specifications annexed with this document. The developer may also propose to improve upon the specifications provided in its document. In such cases, any improvements to the minimum specifications shall be clearly stated in the proposal. Thus, these technical specifications will form part of the contract document.

These are general technical specifications used for Government Housing Projects. The developer is required to adhere to the specifications applicable for this project. Any further change to these specifications can be brought by mutual agreement between the two parties.

## 7.1 Site Works

7.1.1	Demolition

7.1.1.1	Demolition includes the complete demolition including grubbing up of foundations and the proper termination of all services as required by the Drawings including the removal and disposal of all demolished materials. The demolition work shall be executed in a systematic manner.

7.1.1.2	Demolition operations and the removal of debris shall be carried out to ensure minimum interference with roads, streets, footpaths and other adjacent occupied or used facilities.

7.1.1.3	Damage caused to adjacent facilities by demolition operations shall be repaired by the Contractor at his own expense. The Contractor shall arrange and pay for the disconnecting, removing and capping of utility services, notify the affected utility agency in advance and obtain written approval before commencing work.

7.1.1.4	Before commencement of work, submit a method statement to the Consultant as to the proposed method and sequence of demolition of the building and a safety plan which shall cover the risk assessment and safety measures for such method statement. The Consultant reserves the right to prohibit any method of execution of the Works which he regards as unsafe.

7.1.1.5	Drawing information, particularly for unconventional layouts and special structures, will be made available to the Contractor if possible. The Contractor shall state in his method statement if it is based on such drawings. In the absence of drawings, the Consultant may require a detailed structural survey to be carried out and endorsed by a Registered Structural Engineer (or equivalent) to define the existing structure and the appropriate method and sequence of demolition.

7.1.1.6	No work on site shall be allowed to commence until the proposed method statement has been accepted and all precautionary measures, hoardings, covered walkways, and other requirements are in place.

## 7.1.2	Site Clearance

7.1.2.1	The Site shall be cleared of all vegetation, rock, boulders, etc. and surface soil shall be removed as directed by the Consultant. The trees which are to be retained shall be protected from damage

7.1.2.2	Spreading, leveling and consolidating on site where required, shall be made with suitable surplus excavated material obtained from the Site. Other soils used for filling shall be approved by the Consultant

7.1.2.3	The Contractor shall dispose all unsuitable and surplus excavated material

7.1.2.4	The Contractor shall tidy up and leave the Site in a clean and sanitary condition at all times during the execution of the Works.

## 7.1.3	Excavation

7.1.3.1	Excavation shall be performed to the required depth as shown in the Drawings.

7.1.3.2	A survey of the existing site shall be made and the results of same submitted to the Consultant before commencement of the work

7.1.3.3	Excavation area shall be protected from any water flowing in. Sides of excavations shall be shored or inclined to retain excavation unless otherwise specified

7.1.3.4	Excavation near adjoining structures shall be executed with care so as not to damage those structures.

7.1.3.5	The Contractor shall take all necessary precautions during the excavation for the Works particularly those excavation which are adjoining existing buildings and shall protect such buildings from the damage or collapse by means of temporary or permanent shoring, strutting, sheet piling or underpinning or excavation in short lengths and/or other methods as he deems fit and also he shall properly support all foundations, trenches, walls, floors, etc. affecting the safety of the adjoining existing buildings.

7.1.3.6	The Contractor shall alter, adopt and maintain all such works described above for the whole period of the Contract and shall finally clear away and make good all damages done.

7.1.3.7	The construction and efficiency of the shoring, underpinning, strutting and the like for the purpose for which it is erected shall be the responsibility of the Contractor, should any subsidence or any other damage occur due to the inefficiency of the shoring, underpinning, strutting and the like or any other support provided, the damage shall be made good by the Contractor at his own expense and responsibility.

7.1.3.8	The shoring, strutting, piling and the like, shall be executed in such a manner as to cause as little inconvenience as possible to adjoining owners or the public and the Contractor shall be responsible for negotiating with the adjoining owners the means to safeguard their property and for the use of any portion of their land for the purpose of executing the excavations and no claims submitted on this ground will be entertained.

7.1.3.9	The Contractor shall be held solely responsible for the safety of the adjoining existing buildings, the sufficiency of all temporary or permanent shoring, underpinning, piling, and the like.

7.1.3.10	The Contractor shall keep the Consultant informed as to manner in which he intends to proceed with the execution of the excavations and obtain his approval. Such approval if given shall not absolve the Contractor of his responsibility.

7.1.3.11	Excavation shall extend a sufficient distance from walls, footings, etc. to allow space for placing and removing shoring and formwork, for performing all work in the excavations and for the inspection of same.

7.1.3.12	Excavated material shall be deposited within specified areas as directed unless otherwise specified.

7.1.3.13	The Contractor is deemed to have inspected the site and to leave ascertained for himself as to the nature of the soil, etc. and also the areas where to collect and stack the materials for which necessary site clearance shall have to be made at his own cost.

7.1.3.14	Stacking or excavated materials shall be done at places approved by the Consultant, and he shall have recorded the original ground levels of such places jointly with the Contractor before commencement of stacking operation.

7.1.3.15	Extra excavation and allied lead/lift required specifically for providing working space to workmen or shuttering to walls of basement etc. shall be measured for payment, no extra claim being allowed for such work incidental to development and executions of allied jobs. Only authorized excavation approved by the Consultant shall be paid for

7.1.3.16	Sufficient clear working space shall be left all around excavated area. The disposal of waste/unserviceable materials may be in filling and/or in embankment according to nature of place of disposal. The appropriate specifications for filling and/or embankment shall apply

7.1.3.17	All foundation trenches shall be excavated to the full widths and depths shown on the drawings or to such greater or smaller depths as may be found necessary in the opinion of the Consultant and so instructed by his representative.

7.1.3.18	Should any excavation be taken down below the specified levels, the Contractor shall fill in such excavation at his own cost with cement concrete specified for foundations, well rammed in position until it is brought up to the level.

7.1.3.19	The Contractor shall notify to the Consultant when the excavation is completed, and no concrete or masonry shall be laid until the Consultant has inspected of the soil for each individual footing.

7.1.3.20	All foundation pits shall be refilled to the original surface of the ground with approved materials, which shall be well consolidated as instructed by the Consultant.

7.1.3.21	The Contractor shall erect temporary barricades around the excavations and if necessary, make provisions of red lamps.

7.1.3.22	The Contractor shall remove/maintain/restore all service lines like telephone, water supply, electricity etc. without any extra charges.

## 7.1.4	De-watering

7.1.4.1	Where the excavation level is below the natural water table and it is necessary to pump continuously from the excavation or to install a specialist type of dewatering equipment around the perimeter of the site or excavation, the Contractor will be responsible for ensuring the safety and stability of all adjoining structures and services or utilities above or below ground level.

7.1.4.2	It will also be the responsibility of the Contractor that the equipment installed shall ensure that the excavation and subsequent construction is carried out in dry conditions.

7.1.4.3	Continuous or permanent de-watering of the excavation or Site may not be undertaken without the written approval of the Consultant and the methods to be employed shall also comply with Codes of Practice and Local Authority requirements.

7.1.4.4	The water pumped from the excavations or well points shall be pumped to disposal points or sumps approved by the Consultant and the Local Ward Office and if so required be passed through settling tanks before disposal.

7.1.4.5	Unless prior approval has been obtained no water must be disposed of in the Municipality's sewer systems.

## 7.1.5	Backfill

7.1.5.1	All earth used for filling shall unless otherwise stated, be selected hard dry material from the excavation The maximum dry density of the fill material shall be not less than 1600 kg/m3.

7.1.5.2	The backfill of excavations shall be placed in horizontal layers not exceeding 300mm in thickness. Each layer shall be compacted by hand or other mechanical means to the required density before the next layer is added.

7.1.5.3	Care shall be taken when filling or back-filling to avoid any wedging action or eccentric action upon or against the structure of the work.

7.1.5.4	Before placing of fill, the surface of the sub-grade shall be compacted at optimum water content to the same percentage of maximum dry density required of subsequent lay.

7.1.5.5	The Consultant will inspect all compacting devices that the Contractor proposes and shall have the right to reject any device which he feels is unsuitable for the job.

7.1.5.6	Heavy equipment for spreading and compacting fill and backfill shall not be operated closer to walls than a distance to the difference in height between the top of the footings and the layer being compacted.

7.1.5.7	When back-filling behind retaining walls, basement walls and the like the said structures shall be kept propped during the complete operation. The hydraulic compaction of fill shall not be permitted, and the back filling shall be carried out in layers not exceeding 150mm thick.

7.1.5.8	Each layer shall be compacted to 90% of the modified compaction. No back filling shall be carried out until the wall concrete has achieved its full works cube strength and care shall be exercised so as not to damage the external tanking membrane and its protection.

# ANNEX A: CIVIL AND STRUCTURAL DESIGN REQUIREMENTS

Table of Contents

1.0       General

2.0       Load Definition

3.0       Structural Design

4.0       Soil Properties

5.0       Roads and Paved areas

6.0       Underground Utilities

7.0       Foundations Footings and Floor Slabs

8.0       Concrete Blockwork

9.0       Detailed Engineering Documents

10.0     Earthworks

## GENERAL

This attachment describes the minimum civil and structural requirements to be adopted for the design of new buildings, structures, foundations, and access roads/paved areas.

Structural systems shall be designed in accordance with BS standards or equivalent international codes. The building shall be designed for durability, operational loading, spectator occupancy loads, and environmental exposure conditions applicable to the Maldives.

## 2. LOAD DEFINITION

2.1        Dead Load

Dead loads are vertical loads due to the weights of all permanent building components. Typical components are walls, floors, fixed equipment of all kinds, piping, electrical lighting, suspended ceilings, HVAC components and ductwork. These shall include suitable contingencies for material tolerances.  The unit weights of materials and components shall be as defined in BS 648 “Schedule of Weights for Building Materials” or information from the product supplier giving installed weights of materials or components.

2.2        Live Load

Live loads are all moveable superimposed loads such as furniture, moveable partitions, occupants and moveable equipment, but not including wind, earthquake or equipment dynamic loads.  Live loads shall be as specified in BS 6399, Part 1.  Loads shall be applied as a combined arrangement for the most severe effect.

2.3        Wind Load

The wind pressures shall be calculated in accordance with BS CP3, chapter V, part 2, 1972 “Basic data for Design of Buildings ‐Wind Loads”.  Structures shall be designed for a Basic wind speed of 45 m/sec.

The following wind factors shall be used:

- Topography factor S1=1.0

- Ground Roughness, S2, Building size and Height above ground factor from table 3.

- Statistical factor S3= 1.0

The prevailing wind direction is WSW, but for design purposes wind shall be assumed to come from any direction.

2.4        Load Combinations

Members/elements of buildings/structures as well as their supports and fixing points shall be designed for the following load combinations:

| Load Combinations | Dead | Live | Wind |
| --- | --- | --- | --- |
| D+L | X | X |  |
| D+L+W | X | X | X |
| D+W | X |  | X |

Where "D" is the dead load, "L" is the Live Load, and "W" is the wind load.   Where appropriate, load(s) due to earth pressure and/or water pressure should be included in the load combination(s).

## 3. STRUCTURAL DESIGN

3.1        Reinforced Concrete

3.1.1     General

Design and detailing of structural concrete shall be in accordance with BS 8110 and BS8007.

Earth retaining structures shall be designed to resist the raking active earth pressure based on the soil parameters given in the Soil Investigation report.  For the passive soil pressure neglect the first 300 mm from the finished grade level in the calculations.

All underground structures shall be statically checked for flotation.   In the case of pits, basins, manholes and other soil bearing structures the factor of safety against flotation shall be 1.1 for the empty/construction condition.

The thickness of the blinding layer shall be 75mm minimum.

Types of loads and the load combinations shall be considered as per section 2.4. Load factors shall be applied as per BS 8110 or BS 8007 to obtain the most unfavourable conditions.

In pedestals vertical reinforcing shall be enclosed by complete circumferential ties meeting the size and spacing requirements of BS 8110 for tie reinforcement for compression members.

3.1.2     Material Requirements

3.1.2.1 Cement

Cement for structural reinforced concrete and paving shall be ordinary Portland Cement

(OPC) to BS 12 or equivalent.

3.1.2.2 Concrete Grades

Concrete works shall be designed using the following grades:

| Grade N/mm2 | Applications |
| --- | --- |
| 35 | Structural concrete (Reinforced) |
| 25 | Duct encasement, backing, unreinforced footings |
| 15 | Blinding |

A trial mix shall be conducted and approved by the Employer/Engineer before commencing any concrete works

3.1.2.3 Reinforcing Steel

Reinforcing steel bars shall be uncoated high yield deformed bars of characteristic strength of 460 N/mm² to BS 4449, or equal

Uncoated mild steel plain bars with characteristic strength of 250 N/mm² to BS 4449, or equal

Steel wire fabric shall be of characteristic strength 485 N/mm² in accordance with BS 4483 or equal.

All steel bars shall be bent in accordance with BS 4466:1989.

Mechanical bar couplers, where required, shall be specified as complying with the requirements of BS 8110.

Reinforcement shall be fixed, supported and maintained in position by the adequate use of chairs, spacers and tying wire.

3.1.2.4 Concrete Cover

Concrete cover is the concrete thickness to all steel reinforcement including links:

1)   For all concrete (with protection) in contact with soil cover shall be 70 mm.

2)   For all above grade concrete exposed to weathering cover shall be 50 mm.

3)   For above grade concrete protected from weathering cover shall be:

•   Beams and columns:  40 mm

•   Slabs and walls:     30 mm

4)   Cover to bar couplers shall not be less than the minimum specified for reinforcing bars.

Note: Blinding concrete is not to be considered as cover.

3.1.2.5 Concrete Protection

Appropriate Concrete Protection system shall be designed as per the soil / environmental condition   to   which   the   structural elements are   exposed.  Underground concrete protections system shall be proposed based on the soil report. If the soil condition is very hostile to the concrete structure, then the contractor shall propose a system of concrete protection including the use of appropriate concrete admixtures (micro silica, corrosion inhibitors etc.), as required.  However, the following are the minimum requirement as per QP standards.

Clauses 3.39.1 a), b) and c) of QGPC Standard Specification for Civil Works Volume 1 are replaced by the following.

Concrete in contact with soil in foundations shall be protected using BITUTHENE 3000 HC membrane system or equivalent.

For surfaces not exceeding 45° to the horizontal, the BITUTHENE is to be laid on top of concrete blinding, the top surface of the membrane is to be protected with a cement screed at least 40 mm thick.

At junctions and joints the membrane is to be overlapped by a minimum of 75mm, exposed edges of concrete are to be chamfered, propriety angel beads are to be provided where necessary.

Where rising blockwork walls are supported by concrete foundations, the membrane and protection board shall be applied on each side of the rising wall up to ground level.  Where a floor slab abuts the rising wall, the membrane shall be overlapped by the slab polythene damp proof membrane.

Prior to applying the membrane, the contractor shall ensure that the concrete or blockwork surfaces are finished smooth and that any irregularity which might cause the membrane to be punctured has been removed and all edges shall be chamfered, proprietary corner fillets shall be installed.   The contractor shall adhere strictly to the manufacturers recommendation when applying the protection system.

3.2        Structural Steel

3.2.1     General

The following provisions shall be applicable to steel structures and buildings, stairways, and other miscellaneous steelwork. The design, details, fabrication and erection of structural steel shall be in accordance with BS 5950.  All structural steel shall be Grade 43A to BS 4360: Part 2 or equivalent as a minimum.

Types of loads and the load combinations shall be considered as per section 2.4.   Load factors shall be applied as per BS 5950 to obtain the most unfavourable conditions.

3.2.2     Design Data

Types of loads and load combinations shall be in accordance with section 2.0. The Allowable deflections for some of the members are given below. For other members reference shall be made to BS 5950.

| Category | Member type | Vertical Deflection | Horizontal Deflection |
| --- | --- | --- | --- |
| Steel members | - Purlins Primary floor beams; - With equipment - Without equipment - Cantilever beams | L/200 L/500 L/300 L/400 |  |
| Steel frames | - Without equipment - With equipment; - without wind allowance - with wind allowance |  | H/200 H/300 H/200 |

H is the height of frames, and L is the span of beams

3.2.3     Connections

Standard simple beam connections, unless otherwise noted, shall be designed and detailed by the fabricator as shown in Part 3 of “BCSA Structural Steelwork Handbook”.

Where bolts are permitted in structural connections (beam/column connections, moment connections, bracing connections, etc) they shall be black bolts grade 8.8 conforming to BS

3692 in normal tolerance holes with minimum of two M20 bolts.  Whenever bolted connections are used, the reduced strength due to holes shall be computed.

Connections shall be designed taking into account of the effects of any eccentricity on the component parts of the connection, including welds and bolts.

The minimum leg length of any stressed weld shall be minimum 6mm or in accordance with the following table;

| Thickest part to be connected (mm) | Leg Size (mm) |
| --- | --- |
| Up to and including 20 20 to 35 | 6 8 |

Size of fillet welds shall refer to the leg length.  The effective length of fillet welds shall be the length excluding the first and last 25mm of the weld.

3.2.4     Minimum Material Thickness

Minimum dimensions of load carrying members shall be as follows;

Structural members

Except for the webs of rolled steel sections, steel used for external construction shall not be less than 8mm thick, and in construction not so exposed, not less than 6mm thick.

Gusset plates no thinner than 10mm.

3.2.5     Load on crane beams

The design loads for structures handling moving loads shall include an impact allowance in accordance with BS 5950 as specified below;

| Load Application | Electrical operation | Hand operation |
| --- | --- | --- |
| Vertical loads: increase static wheel loads by | 25% | 10% |
| Horizontal force acting transverse to the rails taken as percentage of lifted load + weight of crab | 10% | 5% |
| Horizontal force along the rails taken as percentage of lifted load + weight of crab | 5% | 5% |

## SOIL PROPERTIES

Where specified, soil characteristics for all the foundations shall be established through appropriate soil investigation carried out in accordance with BS 5930. The scope shall cover the soil bearing capacity considering the strength and settlement, durability and stability of the foundation soils with regard to water erosion, soil corrosion characteristics, and problems with respect to excavation/construction.

## ROADS AND PAVED AREAS

Precast concrete paving blocks, 80mm thick, shall be used or roads and car parking areas. Kerbs shall be provided at the boundaries of all concrete paved areas and at raised islands where these are shown on the drawings.

## UNDERGROUND UTILITIES

All reinforced concrete underground foundations, manholes, and chambers shall be protected externally on horizontal and vertical surfaces, as per Section 3.1.2.5 of this document.

All underground utilities, pipes, structures, culverts and covers shall be designed to accommodate imposed loading from service loading, and construction traffic.

## FOUNDATIONS, FOOTINGS AND FLOOR SLABS

Floor slabs shall be laid flat with no crossfalls. The top level of slab shall not deviate more than ±3mm in 2m when measured in any direction.  All floor joints shall be sealed with an approved two‐part polysulphide sealant or equivalent sealant.

Floor slabs shall be laid on one layer of 1200 gauge polythene sheet lapped minimum 300 mm at each edge on top of 50mm concrete blinding on compacted free draining imported granular material.

In stability analysis calculations the foundation shall be designed to have a minimum factor of safety of 2.0 against overturning and 1.5 against sliding.  The weight of soil overburden may be taken into account when calculating factor of safety. The minimum factor of safety against floatation shall be 1.1.   In determining the factor of safety against floatation allowance shall be made for removal of soil overburden and possible loss of skin friction from the sides.

## CONCRETE BLOCKWORK

Blockwork shall be designed to BS 5628.  External walls shall be cavity type comprising 100mm solid concrete externally, a 50mm insulated cavity and 150mm hollow concrete Block internal skin.

Walls dividing storage areas from office areas, walls surrounding electrical rooms shall be minimum 200mm hollow concrete block. Other internal blockwork walls shall be minimum 150mm hollow concrete block.

Blockwork walls shall be tied to structural columns and beams using a proprietary stainless-steel system that complies with the requirements of BS 5628.  Cavity wall ties shall also be stainless steel.

Where joints are required, stainless steel plaster stops shall be used either side of each joint for all external wall joints.  Internal wall joints in office areas shall be finished flush with plaster on stainless steel expanded metal. Wall joints formed using plaster stops shall be filled using an approved two‐part polysulphide sealant.

All blockwork up to the ground level shall be of solid blocks and of sulphate resistant cement and shall have a minimum compressive strength of 15N/mm2.

## 9. DETAILED ENGINEERING DOCUMENTS

1)	Detail of design and calculations shall be shown on sketches showing structural arrangements, loads, member sizes, etc. Computer printout of input data files shall be supplemented with analysis model plots, illustrating node/element numbers, support type (fixed, pinned, spring), member property/size, member orientation, member length, and member loading. Computer model plots shall not be altered by hand.

2)	For Structural analysis, a structural analysis software such as STAAD or similar software shall be used and the input file, shall be submitted for design approval.

3) 	All calculations shall be in SI units. The calculation report and the drawings shall be in English.

## 10. EARTHWORKS

10.1      Fill

The controlled earth filling shall be done using ‘selected fill’ material imported from an approved area.

Any fill shall be spread in layers of maximum 250 mm compacted thickness and with a minimum density equal to 95% of the maximum dry density (MDD) as determined by BS1377 Test 13.

The first layer of fill shall be limited to 200 mm loose thickness. After placement but prior to compaction the area shall be scarified to a depth of 300 mm (100 mm into the natural soil) to break up any weathered crust and mixed with the new fill.

10.2      Excavation

The contractor shall obtain the relevant excavation permits as required to commence work.  Materials to be excavated are not specifically classified and the work shall include excavation of all types of soil and rock, whether water bearing or not.

Excavated materials suitable for fill shall be transported to and replaced in fill areas within the limits of workspace.  The gradation limit shall be within the gradation limits specified below.

Excavated material unsuitable for fill shall be disposed off in spoil approved areas. Unsuitable material for fill includes organic clay or silt, wood or other material subject to decomposition, dune sand or desert fill not conforming to the gradation curve or to maximum allowed salt content, materials obtained during site clearance, e.g. concrete, steel, etc.,

The contractor shall liaise with the Employer with respect to the work near utility services and shall establish safety procedures and clearance requirements at the start of the excavation work.

Finished excavation slopes in the permanent works shall be free from debris and loose material.

The contractor shall pay special care to ensure no damage occurs to the any existing pipes/ducts or culverts during the excavation. Should The contractor in the course of excavation or subsequently, uncover any previously uncovered services, He shall notify the Employer in writing, description, dimensions and level above datum and other appropriate details on an appropriate drawing.

The contractor shall be responsible for all damage, which may arise from the entry of water into the excavations and shall provide all necessary labour and equipment to bale, de‐water, or drain as required keeping the excavations clear of water arising from whatever source.

# ANNEX B: MEP REQUIREMENT

MINIMUM REQUIREMENTS FOR MEP (MECHANICAL ELECTRICAL AND PLUMBING)

Building Services

## GENERAL

Mechanical, electrical, and plumbing systems shall support continuous operation of gaming equipment, broadcasting systems, and event functions. Energy-efficient systems and maintainability shall be prioritized.Architect shall be summarized, but not be limited to the following:

•   Air conditioning and Ventilation

•   Lighting and Emergency Lighting

•   Lightning protection

•   Electrical and Power

•   Plumbing

•   Drainage

•   Infrastructure Connections (Electricity, Water, and Drainage)

For the minimum requirements associated with the Building Services see the appropriate attachment.

Building Services design shall be carried out by a SUBCONTRACTORS who are approved by Engineer the SUBCONTRACTORS shall have qualified and experienced personnel and appropriate facilities for carrying out the design works required.

## 2. DESIGN CRITERIA

2.1   External Ambient Conditions

The Building Services elements shall be designed based on using the following external environmental conditions;

Max temp: 320 C and Min Temp:  230C

It should be noted that equipment shall perform to their design parameters based on the above ambient condition, but it will not be expected to safety fail in conditions of 500 C db (dry bulb).

2.2   Internal Design Conditions

The Building Services elements shall be designed based on using the following internal environmental conditions;

Storage Areas                               -    24.50 C db (dry bulb)

- 50% rh (relative humidity)

Equipment rooms                          -    24.50 C db (dry bulb)

- 50% rh (relative humidity)

Battery rooms                                -    300 C db (dry bulb)

- 50% rh (relative humidity)

Offices/occupied Areas                 -    22.50 C db (dry bulb)

- 50% rh (relative humidity)

Locker/Storage                              -    24.50 C db (dry bulb)

- 50% rh (relative humidity)

Toilets/Pantry (indirect A/C)          -    24.50 C db (dry humidity)

- 50% rh (relative humidity)

Humidity shall vary between 40% to 60% but not beyond the comfort zone as set by ASHRAE Standards.

2.3   Lighting/Emergency Lighting & Small Power Installation

Lighting/Emergency lighting and Small Power Installation shall be designed to match the building and equipment layouts.

Lighting/Emergency lighting system shall be designed to provide uniform intensities according to current C.I.B.S.E lighting code requirements for buildings.

## 3. BUILDING ELEMENTS

3.1   Roof

The Heat Transmission (‘U’) value for the Roof shall not exceed 0.57 watts/m2 0C (0.1 Btu/f t2. hr. 0F)

3.2   Walls

The Heat Transmission (‘U’) value for the External walls shall not exceed

0.741 watts/m2 0C (0.13 Btu/f t2 . hr. 0F).

3.3   Windows

All windows shall be single glazed and/or shall be fitted with solar reflecting glass.

## 4. BUILDING LOAD FACTORS

4.1   Equipment

The actual heat gains from all the equipment, which shall be installed in different areas, shall be allowed when calculating the air conditioning load.

4.2   Occupancy

The occupancy levels shall suit the project/building layout.

4.3   Ventilation

Ventilation rates shall be per the C.I.B.S.E Guidebook (1970) recommendation.

Extract rates for the battery rooms shall be 10 air changes per hour minimum i.e. to ensure that correct temperature and safe toxic levels are maintained.

Extract rates for the toilets, locker rooms and pantries shall be 10 air changes per hour minimum drawing air from a conditioned space if possible.

4.4   Infiltration

The design shall take into account infiltration due to windows and door frames taking into consideration the regional.

## 5. CODES, STANDARDS AND SPECIFICATIONS

All designs shall be carried out in accordance with good engineering practices and the latest revisions of National and International Codes of Practice and Standards

# ANNEX C: ELV REQUIREMENT

MINIMUM REQUIREMENT FOR ELV (ELECTRIC LOW VOLTAGE SYSTEM)

Structured cabling system

CCTV surveillance system

Access control system

Public announcement system

IPTV and digital signage

Centralized control room integration

High-speed Wi-Fi coverage

## Central Lighting Control and Monitoring System

- Dimmable Lighting: All the lighting fixture used should be dimmable and have a flicker free operation with the lighting control system

- Addressable Drivers: Drivers for lighting fixture should be either DALI or equivalent addressable to save cost of wiring for lighting control

- Sensor Based Common Areas: All common areas should be equipped with sensors and should control the lights based on the occupancy of those areas

- Central Monitoring and Control: The lighting control system should be centrally controlled and monitored by the engineering team housed in control room

- Reports: System should be capable of generating reports for power consumption analysis for cost efficiency

- Scenes Based Ambience: All the lights in the areas should be controlled as part of scenes instead of independent switching like Day Scene, Night Scene, Meeting Scene etc.

- Architectural Keypads: Keypads used should be aesthetically good and blend in with the architecture and design of building

## Centralized HVAC Control and Monitoring

- VRF: Centralized VRF or equivalent type HVAC should be used with dedicated units per floor

- Control & Monitor: This air conditioner system should be controlled and monitored centrally by the engineering team housed in control room.

- Occupancy Based Operation: HVAC system should be smart enough to be integrated with the occupancy status provided by the lighting control system and should be able to automatically adjust according to the status of the room

## IP-Based Public Announcement

- Public Announcement: The building should be equipped with an intelligent De-Centralized Public announcement system that can integrate with Fire Detection and Alarm System

- EN-54 Complaint: All the components used in this system should be EN-54 complaint i.e. approved for use with fire alarm systems

- Redundant Operation: The system should be equipped with back-up power in case of power outage. Auto Failover amplifier capability allows an un-interrupted operation

- Multi-Zone Paging: The system should be capable enough to page any specific zone or multiple zones or all zones.

- No Single Point of Failure: The system should be De-Centralized and there should be no single point of failure for the whole system and reliable enough to run in an emergency condition

- Audio over IP: Communication of Audio over IP (CobraNet or AVB) allows the system to be scalable and support multiple audio channel running on IEEE approved standards

- BGM: Sources for BGM might include a local audio player, PC, AM/FM Tuner, Internet Radio and online streaming services like Deezer etc that can provide curated background playlists for workplace environment

## Fire Detection and ALARM System

- Smart Fire Alarm System: Intelligent Addressable Fire Alarm Shall be designed to cover the entire building in order to provide complete end to end Life Safety Strategy in case of fire.

- Integrate-able: The system should be managed from the same software as cameras and access control operated by IT team housed in Control Room. The system should be smart enough to integrate with the other services of the building including following

- Public Announcement System

- Lighting Control System

- HVAC System

- Redundant: All used components should have a redundant power supply in case of power failure

- EN-54 Compliant: All the components used in this system should be EN-54 Compliant

## Central Access Control

- Access Control: Access Control of the building should be managed centrally with all the main door of every floor equipped with access control panel

- Access Method: Access Method should be RFID based. All the databases should be maintained centrally by the security team housed in control room

- Turnstile Gate: Main Access to building should be through a turnstile gate connected to the access control system to maintain the flow of people in and out of the building

- Boom Barrier: Flow of vehicles in parking area should be maintained by boom barrier installed at Entrance and Exit of the building

- Guest Access: Main reception should have card cutting machine to give access to any guest to a specific area depending on the clearance level

- Elevator Access: All the Main and Service elevators should be accessible through RFID based on the allowed floor level

- Critical Rooms: All the MEP, ELV, Control, Server or any other room with highly sensitive level should be equipped with access control panel

- Service Entry: All the Service entry doors should be equipped with access control and only accessible to service people.

- Integrate-able: The system should be managed from the same software as cameras and Fire Detection system operated by IT team housed in Control Room. The access control system should be integrate-able with Fire Alarm and detection system and should unlock all main and service doors in case of fire.

## IP Based Surveillance System

- Cameras: The building should be equipped with cameras covering all the entrances, exits, common areas, lifts, offices and service rooms.

- IP-Based: All the cameras should be IP based and sit on a separate Network to avoid any kind of interruption from the other systems.

- Night Mood: All the cameras should be equipped with IR and should be operate-able in night mood

- Outdoor Cameras: All the cameras used for outdoor should be weather and vandal proof

- Back Up: All the cameras should be able to record locally in case of disconnection from the network. The backend should have enough storage to store video up to 45 days for all the cameras with smart recording based on motion detection. All cameras should support H.265 compression.

- Monitoring: All the cameras should be monitored by the security team housed in control room.

- Integrate-able: The system should be managed from the same software as Fire Detection and access control operated by IT team housed in Control Room.

## IP Based Telephony

- IP Based: All the telephony inside the building should be IP based and should sit on a separate network.

- End point: Each room should be equipped with UC system or IP Phone for communication through the building

- IP PBX: An IP PBX should be installed to manage the telephony and should be maintained by IT Team housed in the control room.

## IPTV and Digital Signage

- IP Encoder: All the TV Channels should either come in as IP streams encoded in H.264/H.265 or an IP Head-End (Modular) should be installed to transmit all the channels over the existing network to each TV.

- STB: A Set-top Box should be installed behind each TV with customized GUI for the workplace TVs

- IPTV Server: There should be one server to maintain and program all the STBs of the building

- Digital Signage: Main reception should have an ultra-narrow bezel 2x2 video wall (55” displays) and every floor should have wall mounted 32” digital signage display in front of every lift. All the digital signage displays should be 24/7 operations and IPS displays. These displays should be manageable by the IT team housed in Control Room

- Wireless Presentation for Minister’s Office: All Minster Rooms should have a 55” UHD IPS display equipped with wireless presentation feature.

## Managed Meeting Rooms

- Wireless Presentation: Every Meeting Room should have wireless presentation feature with low latency for Windows/iOS/Mac OS/ Android

- Camera: Every meeting room should be equipped with an HD camera for video conferencing with a PC for Soft Codec

- Display: The meeting room should be equipped with 65” UHD IPS display that should integrate with existing system in the room with the feature of auto turning on when someone enters the room.

- Speaker Phone: There should be an integrated speaker phone in the system that can connect via Bluetooth to make calls.

- SIP Phone: The system should also be capable of connecting to the existing IP Telephony system to make local calls in the building

- Touchscreen: A 7” touch screen should be installed outside the meeting room to show the room status like schedule or running meeting

- Scheduling: All the meeting rooms should be bookable through the touchscreen and should be manageable throughout the building by IT Team housed in Control Room

## Seminar Halls and Conference Rooms

- Seminar Halls and Conference Rooms: All Seminar Halls should be equipped with Hi-Fi Audio/Video Equipment designed as per the dimensions and layout of the room.

- Displays: The room should be equipped with fixed 98” UHD IPS display (Integrate-able).

- Wireless Presentation: The room should be equipped with wireless presentation feature as well as multiple HDMI Input for local input

- Audio System: The installed audio system for Seminar Hall should be able to do echo cancellation natively with advanced Digital Signal Processor

- Speakers: All the speakers installed should be passive surface mounted with appropriate amplifiers to match the impedance and power accordingly.

- Provisions: There should be XLR input/output provisions for installing external audio setup

- Touchscreen: A 10” touch screen should be installed in the room for controlling the AV equipment of the room.

- Wireless Microphones: There should be at least one wireless microphones of each of the following type

  - Hand-Held

  - Lavaliere

  - Headmic

  - Table Top

## Gigabit network Backbone

- Network Backbone: This is the most important part of all the mentioned services. There should be a well-designed network that caters needs for today and future provisions as well. All the edge switches should be Layer 3 switches

- Structured Cabling: All the copper cables used for Local Area Network should be Category 6A whereas the uplink from Server Room to Floor ELV rooms should be optical fibre based. All the cabling should be properly documented and tagged.

- Services: All the services should ideally sit on separate network or separate VLAN.

- Core Switch: The core switch should be capable enough to handle the existing services and should have extra provisions for future expansions

- Passive Optical fibre: Each floor should have a passive optical fiber patched between floor and the server room to enable that floor to utilize any external service provider of choice and to make sure that it does not combine with the existing building network

- Wireless Access Point: The whole building should have a complete and secure Wi-Fi (2.4GHz and 5GHz) coverage through-out the building. The Wireless Access Points should be managed by the same software as the network backbone

## Central Operations and Control Room

- Central Control Room: There should be one control room for the whole building to house Security, IT and Engineering team to help them coordinate together and run the daily operations. It should be large enough so that multiple teams can be accommodated in it along with all the services equipment being installed there.

- Video Wall: The room should be equipped with a high-end video wall for monitoring of the whole building including Lighting, Metering, HVAC, Blinds, Network, PA, Fire Detection, Meeting rooms, Multipurpose Hall, Access Control, Telephony and Surveillance

- Security: The room should be highly restricted area with strict access to authorized personnel only.

- Control Equipment and Servers:  This room should also separate area to house all the equipment for all the services.

- Maintained Temperature: As highly sensitive electronic equipment is to be installed here so the temperature of the room should be maintained.

## Floor MEP and ELV room

- MEP Room: Every floor should have a separate room to house the MEP equipment of that floor

- ELV Room: Each floor should have a separate room to house all the Extra Low voltage equipment

- Security: These two rooms should have highly restrictive access control

## Metering

- Electrical and Water Supply: Electricity should be metered separately for the four tenants that may or may not change. All the electrical distribution should be designed accordingly to standards approved by Maldives Energy Authority and STELCO.  Main water supply system should be design to standards approved by MWSC.

- Services and Public Area: Power supply for Fire Detection and Alarm, Access control System, Surveillance System, Public Announcement System, Network Backbone, other ELV services along with Electricity for Public Areas should be metered separately. All the electrical distribution should be designed accordingly.