## Summary_BOQ_WSP
Water Supply Facilities in Hdh. Finey, Maldives
SUMMARY OF BOQ
Bill No. | INDEX | AMOUNT | REMARKS
I | GENERAL AND PRELIMINARIES | 0
II | WATER SUPPLY CONVEYANCE SYSTEM; LENGTH: 639.00M | 0
III | WATER SUPPLY NETWORK; 868.00 M | 0
IV | ULTRAFILTER; FILTRATION CAPACITY- 2 CUM/HOUR/UNIT | 0
V | RAIN WATER COLLECTION / LIFT WELL; CAPACITY - 6 CUM; SIZE: 3.00m Dia x 2.50m Depth | 0
VI | RECHARGE STRUCTURES - PERCOLATION PITS - OVERFLOW CHAMBERS | 0
VII | RAW WATER TANK CAPACITY-100 CUM | 0
VIII | CLEAR WATER TANK; CAPACITY - 50 CUM. | 0
IX | MECHANICAL WORK | 0
X | ELECTRICAL WORKS | 0
XI | GATE | 0
XII | FENCING ARRANGEMENT | 0
XIII | HOUSING ARRANGEMENT FOR TREATMENT SYSTEM, PUMPS, ETC | 0
XIV | SUPPLY OF O&M EQUIPMENT AND SPARES | 0
XV | TESTING AND COMMISSIONING | 0
XVI | PROVISIONAL SUM FOR WATER TAPPING | 0
| TOTAL MVR | 0

## 1.1-Valve Specials (hidden)
Water Supply Facilities in Ha. Kelaa, Maldives
Details of All Valves with Dia, Nos., K12 Specials, DI Pipe Length
Sr. No. | Discription | Data | [14 empty] | Remarks
1 | SLUICE VALVE | [15 empty] | #REF!
| Valve Dia (mm) | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | #REF! | #REF! | #REF! | #REF! | #REF!
| K-12 (2 nos. Reducer) Specials Required for fixing the valve (QTL) | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wt. of 2 nos. Reducer Taken from Jindal Brousher-Engineering Data-Pipe Fittings
| Length of D/F DI Pipes (K-9) (m) | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Butterfly Valve | [15 empty] | 0
| Valve Dia (mm) | - | - | - | - | - | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| K-12 (2 nos. Reducer) Specials Required for fixing the valve (QTL) | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wt. of 2 nos. Reducer Taken from Jindal Brousher-Engineering Data-Pipe Fittings
| Length of D/F DI Pipes (K-9) (m) | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | SCOUR VALVE
| Valve Dia (mm) | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | 0 | 0 | 0 | 0 | 0
| K-12 (01 no.Tee+2 no. Tail Piece+01 no. Reducer) Specials Required for fixing the valve (QTL) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Length of D/F DI Pipes (K-9) (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | AIR VALVE | [15 empty] | #REF!
| Valve Dia (mm) | 50 | 50 | 80 | 100 | 150 | 200
| Main /Pipe Diameter (mm) | 63-100 | 110-150 | 160-200 | 225-250 | 280-300 | 350 | 400 | 450 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
| No. of Valve | #REF! | #REF! | #REF! | #REF! | #REF! | 0
| K-12 (01 no.Tee+2 no. Tail Piece+01 no. Reducer) Specials Required for fixing the valve (QTL) | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | [9 empty] | Wt. of (01 no.Tee+2 no. Tail Piece+01 no. Reducer) Taken from Jindal Brousher-Engineering Data-Pipe Fittings
| Length of D/F DI Pipes (K-9) (m) | #REF! | #REF! | #REF! | #REF! | #REF! | 0
SUMMARY OF SPECIALS & PIPE/TAIL PIECE
Sr. No. | Discription |  |  | Dia | Unit | Qty.
A | Specials K - 12
1 | Specials K - 12 |  |  | Upto 300 mm | Qtl | #REF!
2 | Specials K - 12 |  |  | Above 300 mm | Qtl | 0
B | Double Flanged DI Pipe K-9
1 | DI Pipe K - 9 |  |  | 50 | m
2 | DI Pipe K - 9 |  |  | 80 | m
3 | DI Pipe K - 9 |  |  | 100 | m | #REF!
4 | DI Pipe K - 9 |  |  | 150 | m | #REF!
5 | DI Pipe K - 9 |  |  | 200 | m | #REF!
6 | DI Pipe K - 9 |  |  | 250 | m | #REF!
7 | DI Pipe K - 9 |  |  | 300 | m | #REF!
8 | DI Pipe K - 9 |  |  | 350 | m | 0
9 | DI Pipe K - 9 |  |  | 400 | m | 0
10 | DI Pipe K - 9 |  |  | 450 | m | 0
11 | DI Pipe K - 9 |  |  | 500 | m | 0
12 | DI Pipe K - 9 |  |  | 600 | m | 0
13 | DI Pipe K - 9 |  |  | 700 | m | 0
14 | DI Pipe K - 9 |  |  | 750 | m | 0
15 | DI Pipe K - 9 |  |  | 800 | m | 0
16 | DI Pipe K - 9 |  |  | 900 | m | 0
17 | DI Pipe K - 9 |  |  | 1000 | m | 0

## BOQ.-WSP
Water Supply Facilities in Hdh. Finey, Maldives
BILL OF QUANTITIES
Item No. | Description | Unit | Quantity | Material Rate | Labor Rate | Amount
I | GENERAL AND PRELIMINARIES | LS | 1
1.1 | Contractual Requirements
1.1.1 | Provide & Maintain all necessary Insurances, Guarantees and Securities. | Item | LS.
1.2 | SPECIFIED REQUIREMENTS
1.2.1 | Provision of Contractor's Office | Item | LS
1.2.2 | Provision of Contractor's Staff Accommodation | Item | LS
1.2.3 | Maintaining Contractor's Office | Month | 10
1.2.4 | Maintaining Contractor's Staff Accommodation | Month | 10
1.2.5 | Provision of adequately equipped Laboratory services as required for site control on the quality of materials and the works as per special specification. | Item | LS
1.2.6 | Maintaining the Laboratory services as required for site control of materials and works as per specification including all costs | Month | 10
1.2.7 | Provision and Erection of Notice Boards 3m x 4m size as per drawing and specification, including complete cost and conveyance of materials, labour charges, & etc. | No. | LS
1.2.8 | Provision of photographs and video graph of important activities of the work during the progress of work as directed by the Engineer, including all costs, etc. Provision of media to client / engineer on a weekly basis. | No. | LS
1.2.9 | Training of employer's nominees in operation and maintenance as per Employer's Requirement. | Item | LS
1.3 | TEMPORARY WORKS
1.3.1 | Dewatering as per local regulations | Item | LS
1.4 | SITE PREPARATION
1.4.1 | Clearing grass, bushes, shrubs, saplings, uprooting rank vegetation all along the pipeline route and removal & disposal of rubbish to approved tips anywhere in the island as directed by the Engineer-in-charge. Cutting of trees, including trunks, branching and removal of stumps, roots, stacking of serviceable materials with all lifts and up to all lead within project area and earth filling in the depression/pit, including excavation & backfilling. | Item | LS
II | WATER SUPPLY CONVEYANCE SYSTEM; LENGTH: 639.00M | M | 639
A | For Civil Works
1 | PIPE WORKS: SUPPLY & LAYING OF PIPES
Pipe laying works shall includes clearing vegetation, earth works (excavation, bed preparation, backfilling and compacting), shoring, strutting, as per specification and drawing, for pipeline trenches. In all kinds of soil including material, labour, testing cleaning, disinfection and commissioning as per Technical Specifications and as directed by the Engineer in Charge. Safe storage and proper handling of pipe and fitting material in accordance with the instruction of the manufacturer is included in the pipe works.
Backfilling includes sand filling for the sides of the pipe line and up to 100mm above the crown of the pipe including 150 mm bedding below the pipe as per Specification & drawings and as directed by the Engineer.
Providing, lowering, laying, aligning, fixing in position at and jointing at all level/ depths ISI marked HDPE pipes of PE-100 grade & PN-6 for potable water as per IS 4984 (amended up to date) in trenches in complete including all material, labour, testing and commissioning as per Technical Specifications and as directed by the Engineer in Charge; including jointing at all level/ depths HDPE pipe accessories/ fittings of PE-100 grade & PN-6 for potable water as per IS 8360 for fabricated (amended up to date) within pipe line including Disinfecting C.I. water mains by flushing with water containing bleaching powder @ 0.5 gms per litre of water and cleaning the same with fresh water, operation to be repeated three times including getting the sample of water from the disinfected main tested in the municipal laboratory.
1.1.1 | 90 mm | m | 91
1.1.2 | 110 mm | m | 234
1.1.3 | 125 mm | m | 21
1.1.4 | 140 mm | m | 63
1.1.5 | 160 mm | m | 142
1.1.6 | 200 mm | m | 88
1.1.7 | 225 mm | m | 230
1.1.8 | 250 mm | m | 40
2 | VALVES AND APPURTENANCES
2.1 | Supplying, delivering fixing and jointing at site Sluice / Gate valves as per Specification & drawings.
2.1.1 | 90 mm | No. | 2
2.1.2 | 110 mm | No. | 3
2.1.3 | 125 mm | No. | 1
2.1.4 | 140 mm | No. | 0
2.1.5 | 160 mm | No. | 1
2.1.6 | 200 mm | No. | 0
2.1.7 | 225 mm | No. | 0
2.1.8 | 250 mm - Inlet of Lift Well | No. | 1
2.2 | Providing, lowering, laying, aligning, fixing in position and jointing in pipe line, dual plate Non Return / check valves of following dia (including jointing and jointing material), including all material, labour, testing and commissioning as per Technical Specifications and as per direction of Engineer.
2.2.1 | 90 mm | No. | 2
2.2.2 | 110 mm | No. | 3
2.2.3 | 125 mm | No. | 1
2.2.4 | 140 mm | No. | 0
2.2.5 | 160 mm | No. | 1
2.2.6 | 200 mm | No. | 0
2.2.7 | 225 mm | No. | 0
2.2.8 | 250 mm - Inlet of Lift Well | No. | 0
2.3 | Supply and Installing Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
2.3.1 | 90 mm | No. | 4
2.3.2 | 110 mm | No. | 6
2.3.3 | 125 mm | No. | 2
2.3.4 | 140 mm | No. | 0
2.3.5 | 160 mm | No. | 2
2.3.6 | 200 mm | No. | 0
2.3.7 | 225 mm | No. | 0
2.3.8 | 250 mm - Inlet of Lift Well | No. | 1
3 | CONSTRUCTION OF CHAMBER FOR VALVES
3.1 | Construction of Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum , including chamber cover & Frame
3.1.1 | Sluice Valve, Non Return Valve and Washout Valve Chamber
3.1.1.1 | 90 mm | No. | 2
3.1.1.2 | 110 mm | No. | 3
3.1.1.3 | 125 mm | No. | 1
3.1.1.4 | 140 mm | No. | 0
3.1.1.5 | 160 mm | No. | 1
3.1.1.6 | 200 mm | No. | 0
3.1.1.7 | 225 mm | No. | 0
3.1.1.8 | 250 mm - Inlet of Lift Well | No. | 1
4 | ROOF WATER HARVEST GUTTERS
4.1 | Providing and fixing on wall face un-plasticized-PVC (working pressure 4 kgf per sqm) rain water Gutters shape will be semi-circular or rectangular, V-shaped gutters as per specification including jointing with seal ring, leaving 10 mm gap for thermal expansion and as per direction of engineer in charge.
4.1.1 | width 150 mm | m | 225
5 | ROOF WATER HARVEST DOWN PIPES
5.1 | Providing and fixing on wall face un-plasticized-PVC (working pressure 4 kgf per sqm) rain water pipes conforming to specification including jointing with seal ring, leaving 10 mm gap for thermal expansion and as per direction of engineer in charge.
5.1.1 | 63 mm | m | 12
5.1.2 | 75 mm | m | 24
5.1.3 | 90 mm | m | 48
5.1.4 | 110 mm | m | 0
5.1.5 | 125 mm | m | 24
5.1.6 | 140 mm | m | 0
5.1.7 | 160 mm | m | 0
5.1.8 | 200 mm | m | 0
5.1.9 | 225 mm | m | 0
5.2 | Automated first flush mechanism as per the detailed drawings. Including drainage and soil absorption or recharge pit / well recharge. - 2 Nos. for Each Community Centre | No. | 18
5.3 | Providing and fixing valve for First Flush Diversion at each roof top on each down pipe as per specification and drawing.
5.3.1 | 63 mm | No. | 2
5.3.2 | 75 mm | No. | 4
5.3.3 | 90 mm | No. | 8
5.3.4 | 110 mm | No. | 0
5.3.5 | 125 mm | No. | 4
5.3.6 | 140 mm | No. | 0
5.3.7 | 160 mm | No. | 0
5.3.8 | 200 mm | No. | 0
5.3.9 | 225 mm | No. | 0
5.4 | Supplying, delivering fixing and jointing Gate valves at eah down pipe.
5.4.1 | 63 mm | No. | 6
5.4.2 | 75 mm | No. | 12
5.4.3 | 90 mm | No. | 24
5.4.4 | 110 mm | No. | 0
5.4.5 | 125 mm | No. | 12
5.4.6 | 140 mm | No. | 0
5.4.7 | 160 mm | No. | 0
5.4.8 | 200 mm | No. | 0
5.4.9 | 225 mm | No. | 0
III | WATER SUPPLY NETWORK; 868.00 M | M | 868
A | For Civil Works
1 | PIPE WORKS: SUPPLY & LAYING OF PIPE LINE |  |  |  |  | 0
| Pipe laying works shall includes clearing vegetation, earth works (excavation, bed preparation, backfilling and compacting), shoring, strutting, as per specification and drawing, for pipeline trenches. In all kinds of soil including material, labour, testing cleaning, disinfection and commissioning as per Technical Specifications and as directed by the Engineer in Charge. Safe storage and proper handling of pipe and fitting material in accordance with the instruction of the manufacturer is included in the pipe works. |  |  |  |  | 0
| Backfilling includes sand filling for the sides of the pipe line and up to 150mm above the crown of the pipe including 150 mm bedding below the pipe as per Specification & drawings and as directed by the Engineer. |  |  |  |  | 0
| Providing, lowering, laying, aligning, fixing in position at and jointing at all level/ depths ISI marked HDPE pipes of PE-100 grade & PN-6 for potable water as per IS 4984 (amended up to date) in trenches in complete including all material, labour, testing and commissioning as per Technical Specifications and as directed by the Engineer in Charge; including jointing at all level/ depths HDPE pipe accessories/ fittings of PE-100 grade & PN-6 for potable water as per IS 8360 for fabricated (amended up to date) within pipe line including Disinfecting C.I. water mains by flushing with water containing bleaching powder @ 0.5 gms per litre of water and cleaning the same with fresh water, operation to be repeated three times including getting the sample of water from the disinfected main tested in the municipal laboratory. |  |  |  |  | 0
| 63mm | m | 868
2 | VALVES AND APPURTENANCES
2.1 | Supply, delivery and fixing of brand new Tamper proof Kinetic Air Valves with dimensions as per Specification & drawing conforming to BS 2494 and BS 4865 part I, as per Specification, drawings and as directed by the Engineer.
2.1.1 | 25 mm | No. | 2
2.2 | Supplying, delivering fixing and jointing at site Sluice/Gate valves as per Specification & drawings.
2.2.1 | 63 mm - No of Tap Bay points | No. | 4
2.3 | Supplying, delivering fixing and jointing at site Wash out valve as per Specification & drawings.
2.3.1 | 50 mm - at dead ends | No. | 3
2.4 | Supply and Installing PE Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
2.4.1 | 50 mm | No. | 2
2.4.2 | 63 mm | No. | 4
2.5 | Providing, laying in position, jointing, hydraulic testing and commissioning of specials suitable for push on jointing including flanged special such as tees, bends, collars, tapers and caps etc. including cost of water required for testing etc. complete and as directed by the Engineer in Charge. | LS | 1
3 | CONSTRUCTION OF CHAMBER FOR VALVES
3.1 | Construction of Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum
3.1.1 | Sluice valve and Washout Valve chamber
3.1.1.1 | 50 mm | No. | 2
3.1.1.2 | 63 mm | No. | 4
IV | ULTRAFILTER; FILTRATION CAPACITY- 2 CUM/HOUR/UNIT
| Supply, Transportation to site, lifting, installation, Testing, Commissioning of Ultrafiltration unit as per all relevant Codes, international practices and As per the Specification etc. complete and as per direction of Engineer In Charge. | No. | 1
V | RAIN WATER COLLECTION / LIFT WELL; CAPACITY - 6 CUM; SIZE: 3.00m Dia x 2.50m Depth | No. | 1
Civil Works for Foundation
| Foundation of Tank, PCC | cum | 1.6128
REINFORCED CEMENT CONCRETE
Providing and laying RCC of grade C35 including fabrication of high yield steel (fy = 415 MPa), as per Specification & drawing and as directed by the Engineer
| Top Slab of Tank | cum | 1.4967
| Bottom Slab of Tank | cum | 2.8863
| Vertical Wall | cum | 4.2634
Thermo-Mechanically Treated bars (FE-500)
| Foundation of Tank | MT | 0.86464
| Accessories like Manhole Cover (Checquered plate), Lifting arrangement for Pumps, Steps inside the well, screen at the inlet of Lift well, etc | LS | 1
1 | PUMPING MAIN from Collection well to RWT
Providing, lowering, laying & jointing of H.D.P.E. PIPES PE-100 GRADE; PN-6 pipes including fixing of complete components, such as bends, tees, tail pieces, reducers. Suitable for the pipeline etc., by fusion welding and giving satisfactory hydraulic test as per specification including Excavation, Refilling, Sand bedding etc. all complete.
The cost should include the cost of All earth works, including Barricading, Excavation, Bed Preparation, Pipe Welding, Back Filling, Disposal of Surplus Earth, Shoring & Strutting wherever necessary, Testing & Disinfection. Overflow drainage and recharge system Etc. all complete
| 180mm dia | RM | 25
VI | RECHARGE STRUCTURES - PERCOLATION PITS - OVERFLOW CHAMBERS | Nos. | 2
| Circular Pits filled with coral stone, filler material, interconnection Piping, etc | LS | 1
CEMENT CONCRETE
| Providing and laying Cement Concrete of required grade as per Specification & drawing and as directed by the Engineer | cum | 0.11781
MANHOLES
Supply and installation of Corrugated Manholes without Base of diameter and depth as follows:
| 1000mm dia and Depth - 2000mm | Nos | 2
VII | RAW WATER TANK CAPACITY-100 CUM
1 | Geotechnical Investigation, Providing, Transportation to site, lifting, installation and fixing to allocated places; Closed Top Vertical Flat Bottom Water Storage Tank; made of RTP (Rolled, Tapered Panel), LIQ Fusion 7000 FBE™ powder coated, bolted tank as manufactured by Tank Connection Affiliate Group. A) The cost shall be all inclusive of supply, erection and construction, all testing, disinfecting and commissioning of tank, Providing ladders with cage (Outside & Inside, as applicable), 600mm man way frame with cover, handrail, providing a mechanical float type water level indicator, Lift Lugs, Circular Cleanout, Skylight, Ventilation, Railings, Rungs etc. complete as per specification and relevant code and as per direction of engineer in charge. B) The Manufacturer shall follow all relevant Code and Specification etc. complete and produce all relevant information about the products before supply & Installation.
1.1 | 100,000 litres Capacity - 5.5m Dia & 4.60m height | No. | 1
A | Civil Works for Foundation
2 | REINFORCED CEMENT CONCRETE
2.1 | Providing and laying RCC of grade C35 including fabrication of high yield steel (fy = 415 MPa), as per Specification & drawing and as directed by the Engineer
| Bottom Slab for the Tank | cum | 19.9093
| Foundation of Tank | cum | 5.5133
3 | Thermo-Mechanically Treated bars (FE-500)
3.1 | Foundation of Tank | MT | 2.5423
4 | VALVES AND APPURTENANCES
4.1 | Supplying, delivering fixing and jointing at site Wash out valve as per Specification & drawings.
| 50 mm | No. | 1
4.2 | Supplying, delivering fixing and jointing at site Sluice/Gate valves with flanged ends as per Specification & drawings.
| 180mm - Inlet | No. | 1
| 63 mm - Oulet | No. | 1
4.3 | Supply and Installing PE Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
| 50 mm | No. | 1
| 63 mm - Oulet | No. | 1
4.4 | Providing, lowering, laying & jointing of H.D.P.E. PIPES PE-100 GRADE; PN-6 pipes including fixing of complete components, such as bends, tees, tail pieces, reducers. Suitable for the pipeline etc., by fusion welding and giving satisfactory hydraulic test as per specification and drawing.
The cost should include the cost of All earth works, including Barricading, Excavation, Bed Preparation, Pipe Welding, Back Filling, Disposal of Surplus Earth, Shoring & Strutting wherever necessary, Testing & Disinfection. Etc. all complete
4.4.1 | 50 mm (Washout Pipe) | m | 30
4.4.2 | 75 mm (Overflow Pipe) | m | 30
4.5 | CONSTRUCTION OF CHAMBER
Construction of Valve chamber C30 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum, Cover and frame.
| 63 mm | No. | 1
5 | FLOW MEASUREMENT
5.1 | Flow Meter
Supply, installation, testing and commissioning of Flow Meter etc. including all materials (excluding fittings) and making connection with existing pipeline required for Flow Meter including cutting the existing pipe line etc. complete in all respect as per technical specification and as per direction of Engineer.
| 63 mm | No. | 1
| 180 mm - Inlet | No. | 1
5.2 | Ultrasonic level measuring sensor
| Providing, installing, testing and commission of Ultrasonic Level sensor with level window in the electrical panel for showing water level. | No. | 2
VIII | CLEAR WATER TANK; CAPACITY - 50 CUM.
1 | Geotechnical Investigation, Providing, Transportation to site, lifting, installation and fixing to allocated places; Closed Top Vertical Flat Bottom Water Storage Tank; made of RTP (Rolled, Tapered Panel), LIQ Fusion 7000 FBE™ powder coated, bolted tank as manufactured by Tank Connection Affiliate Group. A) The cost shall be all inclusive of supply, erection and construction, all testing, disinfecting and commissioning of tank, Providing ladders with cage (Outside & Inside, as applicable), 600mm man way frame with cover, handrail, providing a mechanical float type water level indicator, Lift Lugs, Circular Cleanout, Skylight, Ventilation, Railings, Rungs etc. complete as per specification and relevant code and as per direction of engineer in charge. B) The Manufacturer shall follow all relevant Code and Specification etc. complete and produce all relevant information about the products before supply & Installation.
1.1 | 50,000 litres Capacity - 4.15m dia & 4m height | No | 1
A | Civil Works for Tank Foundation
2 | REINFORCED CEMENT CONCRETE
2.1 | Providing and laying RCC of grade C 35/20 including fabrication of high yield steel (fy = 415 MPa), as per Specification & drawing and as directed by the Engineer
2.1.1 | Bottom Slab for the Tank | cum | 12.9881
| Foundation of Tank | cum | 4.4531
3 | THERMO-MECHANICALLY TREATED BARS (FE-500)
Reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete.
| Foundation of tank | MT | 1.7441
4 | VALVES AND APPURTENANCES
4.1 | Supplying, delivering fixing and jointing at site Wash out valve as per Specification & drawings.
| 50 mm Washout | No. | 1
4.2 | Supplying, delivering fixing and jointing at site Sluice/Gate valves with flanged ends as per Specification & drawings.
| 63mm - Inlet | No. | 1
| 63 mm (Pipe outlet) | No. | 1
4.3 | Supply and Installing PE Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
4.3.1 | 50 mm (Washout Pipe) | Nos. | 1
4.3.2 | 63 mm (Pipe outlet) | Nos. | 1
4.4 | Providing, lowering, laying & jointing of H.D.P.E. PIPES PE-100 GRADE; PN-6 pipes including fixing of complete components, such as bends, tees, tail pieces, reducers. Suitable for the pipeline etc., by fusion welding and giving satisfactory hydraulic test as per specification and drawing. |  | 0
The cost should include the cost of All earth works, including Barricading, Excavation, Bed Preparation, Pipe Welding, Back Filling, Disposal of Surplus Earth, Shoring & Strutting wherever necessary, Testing & Disinfection. Etc. all complete
4.4.1 | 50 mm (Washout Pipe) | m | 30
4.4.2 | 63 mm (Overflow Pipe) | m | 30
4.5 | Construction of Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum
4.5.2 | 63 mm | Nos. | 1
5 | FLOW MEASUREMENT
5.1 | Flow Meter
Supply, installation, testing and commissioning of Flow Meter etc. including all materials (excluding CI/fittings) and making connection with existing pipeline required for Flow Meter including cutting the existing pipe line etc. complete in all respect as per technical specification and as per direction of Engineer.
5.1.1 | 63 mm (Inlet) | No. | 1
5.1.2 | 63 mm (Outlet) | No. | 1
5.2 | ULTRASONIC LEVEL SENSOR
5.2.1 | Providing, installing, testing and commission of Ultrasonic Level sensor with level window in the electrical panel for showing water level. | No. | 1
IX | MECHANICAL WORK
1 | CENTRIFUGAL SPLIT CASTING PUMP SETS WITH MOTOR
1.1 | Supply, delivery at site with necessary packing, receiving, unloading, shifting, storing, installation, testing and commissioning of Horizontal Centrifugal Split Casting pumps with motor, casing and delivery pipes and casing ring, SS 316 impeller, SS 410 Shaft and shaft sleeve, coupling guard, common base plate, foundation bolts etc. complete with all respect as per the specification.
1.1.2 | For RWT to Ultra Filter: 6 cum/day, 10m Head; (1W +1 S) =2 Nos. | Nos. | 2
1.1.3 | Ultra Filter to Treated water Tank: 6 cum/day, 10m Head; (1W +1 S) =2 Nos. | Nos. | 2
1.1.4 | Water Supply Pumps: 48 cum/day, 10M Head; (1W +1 S) =2 Nos. | Nos. | 2
1A | SUBMERSIBLE PUMP SETS WITH MOTOR
Supply, delivery at site with necessary packing, receiving, unloading, shifting, storing, installation, testing and commissioning of submersible pumps with motor, casing and delivery pipes and casing ring, SS 316 impeller, SS 410 Shaft and shaft sleeve, coupling guard, common base plate, foundation bolts etc. complete with all respect as per the specification.
1.1.4 | Rain water Lifting Pumps 110 cum/hr, 15 m Head; (1W +1 S) = 2 Nos. | Nos. | 2
2.0 | Supplying, delivering fixing and jointing at site Sluice valve as per Specification & drawings.
2.2 | 180 mm - Delivery of Lifting Pumps | Nos. | 1
2.2.1 | 180 mm - Individual Delivery | Nos. | 2
2.3 | 63 mm - Suction & Delivery of Raw water Pumps | Nos. | 4
2.4 | 63 mm - Suction & Delivery of Treated water Pumps | Nos. | 4
2.5 | 63 mm - Suction of water Supply pumps | Nos. | 2
2.6 | 63 mm - Delivery of water Supply pumps | Nos. | 2
3 | Providing, lowering, laying, aligning, fixing in position and jointing in pipe line, dual plate Non Return/check valves of following dia (including jointing and jointing material), including all material, labour, testing and commissioning as per Technical Specifications and as per direction of Engineer - Delivery of Pumps
3.1.1 | 180 mm - Individual Delivery | Nos. | 2
3.2 | 63 mm | Nos. | 2
3.3 | 63 mm | Nos. | 2
3.4 | 63 mm - Delivery of Tap Bay Supply pumps | Nos. | 2
4.0 | Supply and Installing PE Dismantling joints for isolating valves and suitable for angular deflections without leakage and protected outside by epoxy coating, with required flanges of suitable size including cost of all other joints, bolts, nuts and labor charges.
4.1 | 180 mm - Delivery of Lifting Pumps | Nos. | 1
4.2 | 180 mm - Individual Delivery | Nos. | 4
4.3 | 63 mm | Nos. | 6
4.4 | 63 mm | Nos. | 6
4.5 | 63 mm - Suction of water Supply pumps | Nos. | 6
5.0 | Construction of Valve chamber C30/20 grade for the valves as specified below including earth wok to the required depth as per the Drawing. Back filling and disposal of the surplus soil after back filling including special required for fixing of valves as specified in the drawing inclusive of reinforced steel @ 115 kgs/cum including chamber cover & Frame
5.1 | 180mm | Nos. | 1
5.2 | 180 mm - Individual Delivery | Nos. | 4
5.3 | 63 mm | Nos. | 6
5.4 | 63 mm | Nos. | 6
5.5 | 63 mm - Suction of water Supply pumps | Nos. | 6
6 | Providing, installation, testing and commissioning of glycerin filled Pressure gauge (0-10 kg/cm2) of following ranges with isolation valve and tap off pipe complete in all respect as per technical specification and as per direction of Engineer. | Nos. | 10 |  |  | 0
7 | Providing, installing, testing and commissioning of Pressure transmitters (0 - 10 bar) in delivery pipes and as per direction of Engineer. | Nos. | 4 |  |  | 0
8 | Pump Foundation - below the pumps for installation and placing | Cu.m | 1.2
X | ELECTRICAL WORKS
Soil excavation/foundation/cable trench for cable laying, street light poles, panels or any other civil works related to electrical works shall be considered.
1 | Supply, Installation, Testing and Commissioning of 400V LV Panel with Starters as per SLD, specifications and relavent BS/IEC/IEEE or International Standards | No. | 1
2 | Supply, Installation, Testing and Commissioning of power and control cables as per SLD, specifications and relavent BS/IEC/IEEE or International Standards
2.1 | 1.1KV, 4C x 35SQMM Al Arm XLPE (from nearest distribution box to Main Switch board - approx. 100 mtr for each location) | Mtr. (approx.) (for each location) | 100
2.2 | 1.1KV, 3C x 6Sqmm Flat Submersible Cu Cable | Mtr. | Lot
2.3 | 1.1KV, 3C x 4Sqmm Flat Submersible Cu Cable | Mtr. | Lot
2.4 | 1.1KV, 3C x 6Sqmm XLPE Al Arm Cable | Mtr. | Lot
2.5 | 1.1KV, 3C x 4Sqmm XLPE Al Arm Cable | Mtr. | Lot
2.6 | 1.1KV, 4C x 4Sqmm XLPE Al Arm Cable | Mtr. | Lot
2.7 | Any other power and control cables, if required | Mtr. | Lot
3 | Supply, Installation, Testing and Commissioning of cable termination kits, glands, lugs etc. for all above power and control cables as per specifications and relavent BS/IEC/IEEE or International Standards | Lot | 1
4 | Supply, Installation, Testing and Commissioning of 1x36W Industrial Tube Light with required nos. of switches, plug points etc and all necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | Nos. | 2
5 | Supply, Installation, Testing and Commissioning of 1x150W HPSV Street Light Fixtures with all necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | Nos. | 6
6 | Supply, Installation, Testing and Commissioning of 1x36W Tube Light Street Light Fixtures with all necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | Nos. | 4
7 | Supply, Installation, Testing and Commissioning of 9Mtr steel tubular street light pole with necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | Nos. | 5
8 | Supply, Installation, Testing and Commissioning of 5Mtr steel tubular street light pole with necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | Nos. | 4
9 | Supply, Installation, Testing and Commissioning of Earthing System for all electrical equipments, metallic bodies etc. | Lot | 1
10 | Supply, Installation, Testing and Commissioning of Start/stop buttons with control panel for submersible motors as per specifications and relavent BS/IEC/IEEE or International Standards | Nos. | 2
11 | Supply, Installation, Testing and Commissioning of Outdoor type local push button stations near all motors. as per specifications and relavent BS/IEC/IEEE or International Standards | Nos. | 6
12 | All other electrical works which are not specified / mentioned in BOQ as per relavent BS/IEC/IEEE or International Standards | Lot | 1
13 | Preparation and approval of all required electrical drawings based on the power layouts provided. Also control panel electrical shop draings from manufacturers should also get approval. | Lot | 1
XI | GATE
1 | Providing and fixing Gate made of PVC coated chain link fencing net, mesh size 50mm x 50mm, 20 gauge or equivalent - Plate Size 1.5m x 2.1m | Nos. | 2
2 | 38mm GI Pipe 2.1m height, | Nos. | 4
3 | Foundation Block, 450mm x 450mm blocks | Nos. | 2
XII | FENCING ARRANGEMENT
1 | Providing and fixingboundary wall made of PVC coated chain link fencing net, mesh size 50mm x 50mm, 20 gauge or equivalent, 2.1m height | m | 92
2 | 38mm GI Pipe 2.1m height, | Nos. | 23
3 | Foundation Block, 450mm x 450mm blocks | Nos. | 23
4 | Constructing brick wall 0.3m height below the boundary wall all along the boundary including exacavtion & back filling, plastering, painting, all complete. | Cu.m | 12.42
XIII | HOUSING ARRANGEMENT FOR TREATMENT SYSTEM, PUMPS, ETC
1 | CONCRETE WORKS
| Foundation | Nos. | 6
| Concrete (1:2:3) | cu.m | 6.075
| Excavation | cu.m
| Lean concrete (1:2:6) | cu.m | 1.024
| Steel deformed bars, 10mm dia x6m | kg | 141.98
2 | Columns | Nos. | 6
| 100mm diameter G I Pipe for columns | m | 27
3 | Beams
| Plinth Beams - Lateral |  | 3
| Reinforced Cement Concrete | cu.m | 0.966
| Excavation | cu.m | LS
| Steel deformed bars, 10mm dia x6m | kg | 19.32
| Plinth Beams - Longitudinal |  | 4
| Reinforced Cement Concrete | cu.m | 0.805
| Excavation | cu.m | LS
| Steel deformed bars, 10mm dia x6m | kg | 16.1
Roof Beams
| 100mm x 150mm RHS beams - 12mm thick - 7 numbers | m | 18
4 | Miscellaneous
4.1 | Concrete flooring - PCC flooring inside the plant room - Providing and laying PCC of grade C 35/30 | Cu.m | 2
4.2 | Supply and installation, of Lysaght Wall Cladding both internally and externally around the GI Pping | Sq.m | 730
4.3 | Spinning Turbo Ventilator | Nos. | 1
4.4 | Gutters & Downtake Pipes | LS | 1
5 | CEILING, ceiling system - 50mm THICK ROCK WOOL (BOTTOM SIDE Aluminium Foiled ON PLASTIC COATED WIRE MESH (25mm) | sq.m | 35.75
6 | Supporting arrangment for the roof as required, Timber battens, rafters, G. I Purlins, etc | LS | 1 |  |  | 0
7 | Supply and Providing the Weather protection Pump Cover of material Aluminium, Size as required for the site conditions | No | 4
XIV | SUPPLY OF O&M EQUIPMENT AND SPARES | Item | LS
Spares for all pump stations:
1 | Safety Tools
1.1 | Supply and Delivery of the following safety equipments and tools:
1.1.1 | 5 kg capacity dry chemical powder type Fire Extinguisher. | Nos | 2
1.1.2 | Fire Safety Rules chart. | Nos | 2
1.1.3 | Shock Treatment Chart | Nos | 2
1.1.4 | Smoke Detector | Nos | 2
2 | Maintenance Tools
2.1 | Supply and Delivery of the following maintenance tools / equipments.
2.1.1 | Adjustable wrench made up of carbon steel with standard pattern of size 200mm. | Nos | 2
2.1.2 | Double ended open jaw spanner set of sizes (mm): 6x7, 8x9, 10x11, 12x13, 14x15, 16x17, 18x19, 20x21, 22x23, 24x25, 26x27, 28x29, 30x31, 32x33. | Nos | 2
2.1.3 | Screw driver set consisting of various sizes (6", 8", 12"). | Nos | 2
2.1.4 | Cutting Pliers 12" | Nos | 2
2.1.5 | Hacksaw frame with blade | Nos | 2
3 | Manuals and Catalogues.
3.1 | Supply of Three complete sets of pump catalogues, installation manuals, mentenance manual & training manual | Nos | 2
3.1.1 | Set of Pump Spare Parts of each pump recommended by manufacturer. | Nos | 2
3.1.2 | All other items not covered above, including all materials, equipments and labour, for installation of equipment, drives, wiring, leakage, dewatering sump pump conduits, wire trays, lighting, breakers, switchgear, fixtures, access ladders, metal works, etc. |  | LS
4 | Operation and Maintenance Equipments
4.1 | Provision of all operations and maintenance equipments as recommended by manufacturer.
| Set of cleaning rods. | Nos | 1
XV | TESTING AND COMMISSIONING
| Testing and Commissioning of the overall water supply system | Item | LS
XVI | PROVISIONAL SUM FOR WATER TAPPING
1 | Flow Meter
| Supply, installation, testing and commissioning of Flow Meter etc. including all materials (excluding fittings) and making connection with existing pipeline required for Flow Meter including cutting the existing pipe line etc. complete in all respect as per technical specification and as per direction of Engineer. | No. | 4
63 mm
2 | Stand posts
2.1 | Construction of Stand post, a brick wall of height 1m above ground for supporting the piping, foundation concrete for the same, taps for dleivery of water, making platform and draining arrangment, along with three taps of diameter 15mm - 3 taps. at each Tapping Point | No. | 4
2.2 | Supply and fixing of Water supply tap as per the direction of Engineer in charge at the tap bay points
2.3 | 15mm dia |  | 12
4.3 | Providing, lowering, laying, aligning, fixing in position at and jointing at all level/ depths ISI marked MDPE pipes of PE-80 grade & PN-6 for potable water as per IS 4984 (amended up to date) in trenches in complete including all material, labour, testing and commissioning as per Technical Specifications and as directed by the Engineer in Charge
| 18mm dia |  | 18

## Electrical BOQ (hidden)
Sr. No. | Description | Qty. | Unit | Unit Rate | Total Rate
1 | Supply, Installation, Testing and Commissioning of 400V LV Panels (Outdoor type) with Starters as per SLD, specifications and relavent BS/IEC/IEEE or International Standards | 1 | No.
2 | Supply, Installation, Testing and Commissioning of power and control cables as per SLD, specifications and relavent BS/IEC/IEEE or International Standards
2.1 | 1.1KV, 3.5C x 35SQMM Al Arm XLPE | Lot | Mtr.
2.2 | 1.1KV, 3.5C x 25SQMM Al Arm XLPE | Lot | Mtr.
2.3 | 1.1KV, 3C x 6Sqmm Flat Submersible Cu Cable | Lot | Mtr.
2.4 | 1.1KV, 3C x 4Sqmm Flat Submersible Cu Cable | Lot | Mtr.
2.5 | 1.1KV, 3C x 6Sqmm XLPE Al Arm Cable | Lot | Mtr.
2.6 | 1.1KV, 3C x 4Sqmm XLPE Al Arm Cable | Lot | Mtr.
2.7 | 1.1KV, 4C x 4Sqmm XLPE Al Arm Cable | Lot | Mtr.
2.8 | Any other power and control cables, if required | Lot | Mtr.
3 | Supply, Installation, Testing and Commissioning of cable termination kits, glands, lugs etc. for all above power and control cables as per specifications and relavent BS/IEC/IEEE or International Standards | 1 | Lot
4 | Supply, Installation, Testing and Commissioning of 1x150W HPSV Street Light Fixtures with all necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | 6 | Nos.
5 | Supply, Installation, Testing and Commissioning of 1x36W Tube Light Street Light Fixtures with all necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | 4 | Nos.
6 | Supply, Installation, Testing and Commissioning of 9Mtr steel tubular street light pole with necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | 5 | Nos.
7 | Supply, Installation, Testing and Commissioning of 5Mtr steel tubular street light pole with necessary accessories/equipments etc. as per specifications and relavent BS/IEC/IEEE or International Standards | 4 | Nos.
8 | Supply, Installation, Testing and Commissioning of Earthing System for all electrical equipments, metallic bodies etc. | 1 | Lot
9 | Supply, Installation, Testing and Commissioning of Start/stop buttons with control panel for submersible motors as per specifications and relavent BS/IEC/IEEE or International Standards | 2 | Nos.
10 | Supply, Installation, Testing and Commissioning of Outdoor type local push button stations near all motors. as per specifications and relavent BS/IEC/IEEE or International Standards | 6 | Nos.
11 | All other electrical works which are not specified / mentioned in BOQ as per relavent BS/IEC/IEEE or International Standards | 1 | Lot
Note | Soil excavation/foundation/cable trench for cable laying, street light poles, panels or any other civil works related to electrical works shall be consider in Civil BOQ/Items
Canopy or Shed for outdoor motors/local control stations shall be consider in Civil BOQ/Items

## 4.2-Abst.-RWR (hidden)
Water Supply Facilities in Ha. Kelaa, Maldives
RAW WATER RESERVOIR
ABSTRACT OF QUANTITY
S. No. | Particulars | Unit | Quantity | Reference
1 | EARTHWORK IN EXCAVATION
1.1 | Excavation in Coral/Ordinary Soil
Earthwork excavation including clearing vegetation, shoring, strutting, and ramming with selected earth for preparing the bed level, as per the specification and drawing, for Pipeline trenches.
| 0 to 0.50 m | cum | #REF!
| From 0.50 m to 1.00 m | cum
| From 1.00 m to 1.50 m | cum
1.2 | FILLING OF SOIL WITH APPROVED EXCAVATED SOIL
| Refilling pipeline trenches with selected available earth from trench excavation using mechanical vibration including watering, compaction of layers of 30cms, With all leads and lifts as per Specification & drawing and as directed by the Engineer. | cum | #REF!
1.3 | DISPOSAL OF SURPLUS EARTH
| Disposal of the remaining soil after the back filling from the available soil to the general garbage yard as approved by the engineer. | cum | #REF!
2 | PLANE CEMENT CCONCRETE; M-15
2.1 | Providing and laying of PCC 20/20 (20 N/mm2) grade using sulphate resistant cement for foundation as per Specification & drawing and as directed by the Engineer | cum | #REF!
3 | REINFORCED CEMENT CONCRETE- M30
Providing and laying RCC of grade C 35/20 including fabrication of high yield steel (fy = 415 MPa), as per Specification & drawing and as directed by the Engineer
3.1 | All work up to plinth level | cum | #REF!
3.2 | All works above plinth level upto floor fifth level. | cum | #REF!
4 | Thermo-Mechanically Treated bars (FE-500)
4.1 | All work up to plinth level | MT | #REF! | 2% taken for overall
4.2 | All works above plinth level upto floor fifth level. | MT | #REF!
5 | FORM WORK (CENTERING, SHUTTERING & SCAFFOLDING SYSTEM)
5.1 | Foundations, footings, bases of columns, etc. for mass concrete | sqm | #REF!
5.2 | Walls (any thickness) including attached plasters Butteresses, plinth and string courses etc. | sqm | #REF!
5.3 | Columns, Pillars, Piers, Abutments, Posts and Struts | sqm | #REF!
5.4 | Lintels, beams, plinth beams, girders, bressumers and cantilevers | sqm | #REF!
5.5 | Suspended floors, roofs, landings, balconies and access platform | sqm | #REF!
5.6 | Small surfaces such as cantilever ends, brackets and ends of steps, caps and bases to pilasters and columns. | sqm | #REF!
5.8 | SCAFFOLDING SYSTEM | sqm | #REF!
6 | CEMENT PLASTER
6.1 | Inner Side | sqm | #REF!
7 | PAINTING WORKS
7.1 | EPOXY PAINT
| Inner Side (Qty. taken as inner cement plaster) |  | #REF!
7.2 | EXTERIOR PAINTING OF REQUIRED SHADE
| Outer Side walls | sqm | #REF!
7 | DOUBLE FLANGED DI PIPES & SPECIALS
7.1 | DOUBLE FLANGED DI PIPES
7.1.1 | 200 mm (Washout Pipe) | m | #REF!
7.1.2 | 350 mm (Overflow Pipe+Inlet Pipe+Bypass Arrangement) | m | #REF!
7.1.3 | 500 mm (Pipe outlet) | m | #REF!
7.2 | DOUBLE FLANGED SPECIALS
7.2.1 | 350 mm (Overflow + Inlet + Bypass)
| Duckfoot bend | each | #REF!
| D/F Bend -90 degree | each | #REF!
| Tee 350x350 mm | each | #REF!
7.2.2 | 500 mm (Outlet)
| Duckfoot bend inlet | each | #REF!
| D/F Bend for over flow-90 degree | each | #REF!
| Tee 500x500 mm | each | #REF!
8 | VALVES AND APPURTENANCES
8.1 | SLUICE VALVES
| 200 mm | each | #REF!
8.2 | BUTTERFLY VALVES
| 350 mm dia | each | #REF!
| 500 mm dia | each | #REF!
8.3 | DOUBLE FLANGED DI PIPES
| 200 mm dia | m | #REF!
| 350 mm dia | m | #REF!
| 500 mm dia | m | #REF!
8.4 | DISMANTLING JOINTS
| 200 mm | each | #REF!
| 350 mm | each | #REF!
| 500 mm | each | #REF!
8.5 | CONSTRUCTION OF MASONRY CHAMBER
| 900x1000x1400 | each | #REF!
| 1550x1500x1750 | each | #REF!
| 1650x1700x1900 | each | #REF!
9 | FLOW MEASUREMENT
9.1 | Electromagnetic Flow Meter
| 500 mm | each | #REF!
9.2 | Ultrasonic level measuring sensor | each | #REF!
10 | Miscellaneous Works
10.1 | Weathering Protection for Roof Slab | Sqm | #REF!
10.2 | Cement Concrete tiles for plinth Protection | Sqm | #REF!
10.3 | Ventilation Pipe 100mm dia | each | #REF!
10.4 | CI Manhole Cover MH1 600x600mm | each | #REF!
10.5 | Sky Light 6mm glass; Rectangular shape 0.60*0.60 mm | each | #REF!
10.6 | Cage Ladder Stainess Steel (Ladder Type I) | m | #REF!
10.7 | Ladder Type II-1.00M Width | m | #REF!
10.8 | G.I. Steel Pipe Railing (RWR+Stair) | m | #REF!
10.9 | Lightening Arrester | set | #REF!
10.10 | Water Tightness Test | Job | #REF!
10.11 | Disinfection & washing | Job | #REF!