Section 6 - Employer’s Requirements

Table of Contents

1	Scope of Supply of Plant and Services	3

1.1	Background	3

1.2	Scope of work	18

1.3	Scope of Supply	21

1.4	Erection / Installation, Testing and Commissioning	24

1.5	Spare parts	28

1.6	Training	29

1.7	Change Orders	29

1.8	Defect Liability	29

1.9	Time Schedule	29

1.10	Documentation upon completion	30

1.11	Project Management System (PMS)	30

1.12	Project Personnel:	32

1.13	Equipment:	32

1.14	Environmental and Social Safeguards	32

1.15	Environmental, Health and Safety Management	32

2	Specifications	34

3	Environmental, Health and Safety Management Requirement	35

4	Drawings	36

5	Certificates	37

5.1	Form of Completion Certificate	37

5.2	Form of Operational Acceptance Certificate	38

6	Change Orders	39

6.1	Change order procedure	39

6.2	Change Order Forms	40

7	Personnel Requirements	49

8	Equipment Requirements	50

ABBREVIATIONS

| AC BESS | - - | Alternate Current Battery Energy Storage System |
| --- | --- | --- |
| CAPEX DC | - - | Capital Expenditure. Direct Current |
| FENAKA | - | The Utility responsible for electricity, water and sanitation |
| PMU | - | Project Management Unit |
| GUI MPP PCMS PV | - - - | Graphical User Interface Maximum Power Point PV-Diesel Hybrid Plant Control and Monitoring System Photovoltaic |
| RE | - | Renewable Energy. |
| SCADA SOC SWA SS THD | - - - - - | Supervisory control and data acquisition State Of Charge Steel wire armoured Substation Total Harmonics Distortion |

WEIGHTS AND MEASURES

| kW | – | Kilowatt |
| --- | --- | --- |
| kWh | – | Kilowatt-hour |
| MW | – | Megawatt |

# Scope of Supply of Plant and Services

## Background

The objective of this bid is to carry out necessary modifications and expansions to microgrid systems for Integration of proposed Solar Photovoltaic Systems in 20 Islands in Maldives. These 20 Islands are the participating Islands of the ASSURE project (Accelerating Sustainable System Development Using Renewable Energy Project) provided in Table 6.1.

### Existing Power Supply System:

Power supply to above Islands are presently provided through Diesel Generator (DG) Supply via Low Voltage networks whereas in some Islands both Low Voltage (0.415 kV) and Medium Voltage (11 kV) networks are used. The ‘Power House’ in respective Islands is the heart of the power supply system where DGs, Switchgear Panels and Transformers are installed and system control operations are carried out. DGs are connected to busbars in LV Switchgear Panel (LVDB) in the powerhouse and operated in parallel in synchronized, load sharing mode. LVDB is connected to LV distribution networks via MCCB panels in LVDB whereas in case of Islands having MV networks, supply voltage is stepped-up using step-up transformers located in the Powerhouse. Both LV and MV networks comprise of underground cable networks. LV networks are connected to final consumer supply connections via LV Distribution Boxes (feeder pillars) for downstream control and protection. MV networks are generally connected to LV networks via MV/LV Packaged Substations (PSS). The power networks in all these Islands are operated as microgrids in Islanding mode. Some details of existing power infrastructure in respective Islands are provided in Table 6.1.

Fenaka Corporation Limited (Fenaka) is the sole authority and utility providing electricity, water and sanitation services to these Islands. The electricity supply plants and networks in these Islands are owned and operated by Fenaka.

### Proposed Developments under ASSURE Project

ASSURE Project targets Accelerating Sustainable System Development Using Renewable Energy in these 20 Islands. Following key developments are planned to be implemented under the ASSURE project in these Islands;

- Promote solar energy generation upto 21 MWp capacity in 108 Nos identified PV/FPV sites through private sector investments.

- Provide Battery Storage (BESS) Capacity and Power Plant Control and Monitoring System (PCMS) / Energy Management System (EMS) for efficient management and utilisation of renewable energy.

– This scope will be implemented under separate Contract to add 37 MWh of BESS storage capacity and 20 EMS in respective Islands.

- Modify and expand microgrid systems in respective Islands to integrate solar energy generation from proposed 108 Nos PV/FPV sites, battery storage and EMS. This scope is covered in this bid.

Table 6.1 ASSURE Project Participating Islands and Key Information

| Island Info. |  |  |  |  | Existing Electricity Infrastructure |  |  | Proposed Developments |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Island No | Island Name | Coordinates | Habitants (Appox) | Harbour type / size | Peak Demand (kW) | Existing DGs | Existing Networks | Proposed PV/FPV | BESS (Proposed) | EMS (Proposed) |
| Haa Alifu Atoll |  |  |  |  |  |  |  |  |  |  |
| A04 | Dhidhdhoo | 6°53'16.60" N 73°06'49.55" E | 4,186 | 395x75x5m | 1200 kW | 04 Nos (1x600, 2x800, 1x1000 kW) | MV / LV | 2299 kWp (11 PV Sites) |  | Yes |
| Haa Dhaalu Atoll |  |  |  |  |  |  |  |  |  |  |
| B01 | Hanimaadhoo | 06°45′57″N 73°10′33″E | 1,951 | 350x90x5m | 1160 kW | 04 Nos (1x250, 1x800, 2x1000 kW) | MV / LV | 1300 kWp ( 3 PV sites) | 2000 kW / 2000 kWh | Yes |
| Shaviyani Atoll |  |  |  |  |  |  |  |  |  |  |
| C02 | Milandhoo | 06°17′05″N 73°14′36″E | 2,529 | 230x90x5m | 950 kW | 03 Nos (1x400, 1x500, 1x800 kW) | MV / LV | 594 kWP (9 PV Sites) | 2500 kW / 2500 kWh | Yes |
| Noonu Atoll |  |  |  |  |  |  |  |  |  |  |
| D02 | Manadhoo | 05°45′46″N 73°24′38″E | 2,041 | 380x120x5m | 840 kW | 03 Nos (1x320, 1x520, 1x600 kW) | MV / LV | 1400 kWp (15 PV sites) | 3000kW / 3000 kWh | Yes |
| D03 | Velidhoo | 05°39′45″N 73°16′24″E | 2,682 | 300x120x5m | 825 kW | 4 Nos (1x250, 1x400, 1x648+1x800 kW) | LV (Planned for upgrading to MV) | 1300 kWp (8 PV sites) | 3000kW / 3000 kWh | Yes |
| D04 | Hulhudhoo | 05°45′18″N 73°15′47″E | 1,638 | 280x65x5m | 580kW | 3 Nos (1x400, 1x520, 1x600 kW) | LV | 410 kWp (6 PV sites) | 1200 kW / 1200 kWh | Yes |
| Raa Atoll |  |  |  |  |  |  |  |  |  |  |
| E01 | ALIFUSHI | 5°58′00″N 72°57′15″E | 2,700 | 230x90x5m | 726kW | 3 Nos (1x480, 2x600 kW) | LV (Planned for upgrading to MV) | 1000 kWp (1 FPV sites) | 1850 kW / 1850 kWh | Yes |
| E02 | Hulhudhuffaaru | 05°45′50″N 73°00′45″E | 1,131 | 225x80x5m | 430kW | 3 Nos (1x250, 2x400 kW) | LV | 600 kWp (5 PV sites) | 1500 kW / 1500 kWh | Yes |
| Baa atoll |  |  |  |  |  |  |  |  |  |  |
| F01 | Thulhaadhoo | 05°1′23″N 72°50′23″E | 1,506 | 365x165x5m | 780kW | 2 Nos (1x600, 1x800 kW) | LV | 2225 kWp (23 PV sites) | 3000kW / 3000 kWh | Yes |
| F03 | Dharavandhoo | 05°09′30″N 73°07′50″E | 857 | 210m x 95 x 5 m | 470kW | 3 Nos (1x400, 1x600, 1x800 kW) | LV (Planned for upgrading to MV) | 1000 kWp (8 PV sites) | 2250 kW / 2250 kWh | Yes |
| Meemu Atoll |  |  |  |  |  |  |  |  |  |  |
| K01 | RAIYMANDHOO | 03°05′20″N 73°38′20″E | 112 | Natural Harbour | 64kW | 3 Nos (1x64, 1x150, 1x160 kW) | LV | 175 kWp (1 FPV site) | 500 kW / 500 kWh | Yes |
| K02 | MULAH | 02°56′50″N 73°35′05″E | 3,975 | 230x90x5m | 545kW | 3 Nos (1x250, 1x360, 1x600 kW) | LV | 1000 kWp (1 FPV site) | 2000 kW / 2000 kWh | Yes |
| K03 | VEYVAH | 02°57′20″N 73°36′00″E | 263 | 75x50x5m | 112kW | 3 Nos (1x128, 2x160) | LV | 250 kWp (1 FPV site) | 500 kW / 500 kWh | Yes |
| K05 | MULI | 2°55′18.84″N 73°34′52.9″E | 1,013 | 280x80x5m | 485kW | 3 Nos (1x250, 1x400, 1x500 kW) | LV (Planned for upgrading to MV) | 1200 kWp (1 FPV site) | 2000 kW /2000 kWh | Yes |
| Faafu Atoll |  |  |  |  |  |  |  |  |  |  |
| L02 | NILANDHOO | 03°03′20″N 72°53′28″E | 1,663 | 185x100x5m | 830kW | 4 Nos (1x400, 1x600, 1x800, 1x1000 kW) | LV (Planned for upgrading to MV) | 1200 kWp (1 FPV site) |  | Yes |
| Thaa Atoll |  |  |  |  |  |  |  |  |  |  |
| N02 | THIMARAFUSHI | 2°12′23.51″N 73°8′37.21″E | 1,190 | 210x90x5m | 600kW | 3 Nos (1x400, 1x500, 1x800 kW) | LV (Planned for upgrading to MV) | 1199 kWp (7 PV sites) | 3000kW / 3000 kWh | Yes |
| N04 | Guraidhoo | 02°19′25″N 73°19′00″E | 2,010 | 250x90x5m | 722kW | 3 Nos (1x400, 1x600, 1x800 kW) | LV (Planned for upgrading to MV) | 1000 kWp (8 PV sites) | 2500 kW / 2500 kWh | Yes |
| Gaafu Alifu Atoll |  |  |  |  |  |  |  |  |  |  |
| P02 | MAAMENDHOO | 00°43′05″N 73°26′25″E | 1,137 | 270x100x5m | 422kW | 3 Nos (1x200, 2x400 kW) | LV | 600 kWp (1 FPV site) | 1000 kW / 1000 kWh | Yes |
| Gaafu Dhaalu Atoll |  |  |  |  |  |  |  |  |  |  |
| Q04 | FARESMAATHODA | 0°11′55″N 73°11′25″E | 1,104 | 296x100x5m | 428kW | 3 Nos (1x250, 1x400, 1x640 kW) | LV (Planned for upgrading to MV) | 1000 kWp (1 FPV site) | 3000kW / 3000 kWh | Yes |
| Q05 | GADHDHOO | 00°17′25″N 73°27′25″E | 4,052 | 400x100x5m | 655kW | 4 Nos (1x400, 1x500, 1x600 kW) | LV (Planned for upgrading to MV) | 1250 kWp (1 FPV site) | 2500 kW / 2500 kWh | Yes |

Fig 6.1 Island Maps with key sites

Source of all satellite pictures shown in the maps is Google Earth.

Map of Island B01 - Hanimaadhoo

Map of Island A04 - Dhidhdhoo

Map of Island D02 - Manadhoo

Map of Island C02 - Milandhoo

Map of Island D03- Velidhoo

Map of Island D04- Hulhudhoo

Map of Island E02-Hulhudhuffaaru

Map of Island E01- ALIFUSHI

Map of Island F01- Thulhaadhoo

Map of Island  F03 - Dharavandhoo

Map of Island K02-MULAH

Map of Island K01 - RAIYMANDHOO

Map of Island K03 - VEYVAH

Map of Island K05- MULI

Map of Island N02- THIMARAFUSHI

Map of Island L02- NILANDHOO

Map of Island  N04-Guraidhoo

Map of Island P04 - MAAMENDHOO

Map of Island  Q04-FARESMAATHODA

Map of Island Q05 - GADHDHOO

### Engagement of a Turnkey Contractors

The Employer intends to engage a suitably qualified and experienced Contractors with expertise and capacity for implementation of required microgrid modifications and expansions in respective Islands on turnkey basis, through a process of competitive bidding.

The Turnkey Contractor shall be fully responsible for design, engineering, supply, installation, testing and commissioning of required microgrid modifications and expansions, to integrate solar energy generation from proposed PV/FPV sites, battery storage and EMS systems for its intended functionality in a reliable manner. Further the Contractor shall be responsible for provision of training and documentation to Fenaka to ensure satisfactory operation and maintenance of the microgrid systems in respective Islands.

The Bidder/s should provide credentials and references to demonstrate expertise in successful implementation of similar projects of similar or higher scale. The bidder/s should meet qualification criteria provided in section 3 of this Volume.

## Scope of work

### Summary Scope of Work

The scope of This bid primarily covers modifications and expansion of the microgrid systems in respective Islands to integrate (a) solar energy generation from proposed PV/FPV sites, and (b) proposed battery storage and EMS systems.

The implementation work will be carried out separately in three Lots (Contracts) covering different Islands as follows;

LOT 1:

A04   DHIDHDHOO ISLAND

B01 	HANIMAADHOO ISLAND

C02 	MILANDHOO ISLAND

D02   MANADHOO ISLAND

D04   HOLHUDHOO ISLAND

LOT 2:

D03   VELIDHOO ISLAND

E01 	ALIFUSHI ISLAND (FPV)

E02 	HULHUDHUFFARU ISLAND

F01 	THULHAADHOO ISLAND

F03 	DHARAVANDHOO ISLAND

LOT 3:

K01 	RAIYMANDHOO ISLAND (FPV)

K02 	MULAH ISLAND (FPV)

K03 	VEYVAH ISLAND (FPV)

K05 	MULI ISLAND (FPV)

L02 	NILANDHOO ISLAND (FPV)

N02 	THIMARAFUSHI ISLAND

N04 	GURAIDHOO ISLAND

P02 	MAAMENDHOO ISLAND (FPV)

Q04 	FARESMAATHODA ISLAND (FPV)

Q05 	GADHDHOO ISLAND (FPV)

The bidders may submit prices using the Price Schedules for one or more lots. Evaluation of the bids shall be subject to multiple contracts criteria as given in clause 1.4 of Section 3.

The related scope of work and services in each Lot include but not limited to the following works;

Survey of the sites, existing equipment and networks and preparing detailed design and engineering for proposed microgrid modifications and expansions in respective Islands.

Design, engineering, manufacture, factory testing, inspection and supply of proposed equipment and mandatory spare parts which include but not limited to the following;

  - Low Voltage Switchgear Panels (LVDB) – Extension panels and works

  - Medium Voltage Switchgear Panels (MVDB) and Ring Main Units (RMU)

  - Step-up Transformers

  - LV Underground Cables and Accessories

  - MV Underground Cables and Accessories

  - Packaged Substations (PSS)

  - LV Distribution Boxes (Feeder Pillars)

- In addition to the above, the Contractor is required to supply other miscellaneous items required for installation of the above equipment. *

Coordinate design and construction activities with other contractors / subcontractors

Installation / construction, testing and commissioning of all equipment as per approved designs.

Integration of equipment with automated control systems such as Battery Management System (BMS), PCMS / EMS systems for proper and coordinated operation.

Providing training according to Employer´s Requirements including on the job training for nominated personnel in respective Islands.

Providing complete documentations including specifications, test reports, O&M manuals, as built drawings and maps.

*  Note: Supply of any miscellaneous items required for installation of specified equipment is deemed to be Bidders responsibility and this should be included in bidders rates for installation/ erection. Further, Bidders shall note that in respect of the civil works for powerhouse building modifications, provisional sums will be allocated in the Contract as per bid document and will be paid according to civil works rates approved by Fenaka.

### Detailed Scope of Work

The bidders shall note that scope of work vary for respective Islands / Lots.

The detailed scope of work in respective Islands are provided in the following documents in Volume II ;

- Design Diagrams

- Equipment Schedules

In addition to above Technical Specifications applicable for supply equipment are provided in Volume II. Bidders shall comply with the requirements specified therein and any deviations shall be indicated in schedule of deviations.

### Site Survey

Upon provision of site access, the contractor shall carry out detailed survey in each Island which should include, but not limited to the following.

- Collection of details of existing equipment in the Powerhouse such as MVDB, LVDB, DGs, Transformers including ratings, configurations, designs etc.

- Layout of the Powerhouse building

- Location of proposed PV / FPV sites

- Existing MV / LV cable routes and location of existing and proposed substations (PSS), RMUs, Distribution Boxes etc.

- Proposed LV / MV Cable Routes and equipment locations for network expansions.

The Contractor shall ensure allocation of necessary resources and logistics for carrying out site surveys. Fenaka staffs in respective Islands will assist the Contractor in carrying out site surveys.

Upon completion of the site survey the Contractor shall submit survey information to the Employer including details of equipment and powerhouse layout drawings, maps of proposed locations for facilities and cable routes etc for review and approval. The drawings shall be provided in AutoCAD and maps shall be georeferenced maps based on GPS coordinates. Both hard copy and electronic copies of survey data shall be provided.

### Design and Engineering

Upon completion of site surveys, the Contractor shall carry out design and engineering to develop proposed solutions and details of work. This should include but not limited to the following;

- Detailed design / specifications for proposed equipment including LVDB extensions, MVDB, Step-up transformers, RMU, PSS, LV Distribution Boxes etc. This should cover details such as dimensions, configurations, ratings, electrical protection and control schemes, protection settings and secondary circuits etc.

- Maps of proposed line routes for LV and MV underground cables, updated cable lengths, construction details for laying of underground cables, joint pits etc.

- Proposed modifications to powerhouse buildings and layout diagrams

- Proposed equipment foundation details for Step-up transformers, RMUs, PSS and LV Distribution Boxes.

- Details of proposed features for integration of equipment with BMS and EMS.

- Calculations with respect to equipment and cable ratings etc.

Upon completion of design and engineering stage the Contractor shall provide proposed design details, schedules, technical particulars, specifications, drawings and maps for approval of the Employer. The drawings shall be provided in AutoCAD and maps shall be georeferenced maps based on GPS coordinates. Both hard copy and electronic copies of survey data shall be provided.

The Contractor is also required to prepare and submit updated equipment schedules and quantities and final cost estimates (based on bid rates) for respective Islands for the approval of the Employer.

No work shall commence until approval of the designs by the Employer. The Employer shall not be responsible for any material ordered or works implemented without approval of the designs.

It should be noted that approval of the Employer for proposed designs, schedules, technical particulars, specifications, drawings and maps will be provisional and does not relieve the Contractor of his overall responsibility for ensuring proper design for development of the entire microgrid system for safe, efficient and coordinated operation.

## Scope of Supply

All plant / equipment and materials to be supplied by the Contractor shall fully comply with technical specifications and applicable standards provided in Volume II. The Contactor shall follow due procedure as specified in the bid document for approval of sub-contractors / manufacturers for supply of major items as required.

In addition to above, requirements indicated in following sub-clauses shall apply for supply, of plant, equipment and materials.

### Guaranteed Technical Particulars (GTPs)

The Bidder shall furnish Guaranteed Technical Particulars (GTP) as per GTP Schedules provided in the Technical Specifications (Volume II) together with other technical information such as catalogues, engineering data, technical information, design documents, drawings etc for all major items in the scope of supply.

The bidder shall provide key technical parameters in the GTPs during bidding stage for verification of general technical compliance of the items offered, for the purpose of technical evaluation of the bids. These should include manufacturer details, compliance standards, equipment model numbers, capacity and ratings, accessories, guaranteed performance details including guaranteed losses (if applicable).

During execution of works, the Contractor is required to provide complete and detailed technical parameters in GTPs together with other technical information and samples (if required) for the purpose of details review and approval.

### Schedule of Deviations

The bidder shall submit Schedule of Deviations for all key items under the scope of supply clearly indicating any deviations from technical specifications and standards. Any discrepancy between the specification and the catalogues or the bid, if not clearly indicated in the schedule of deviations, will not be considered as valid deviation.

Manufacturers may have standardized on the use of certain components, materials, processes or procedures different from those specified in technical specifications. Alternate proposals offering similar equipment based on the manufacturer’s standard practice will also be considered provided such proposals meet the basic design, standard and performance requirements and are acceptable to the Employer.

### Type Tests

Contractor shall supply equipment / materials of type & design which has already been Type Tested in accordance with applicable standards. Bidder / Contractor shall provide certified copies of such type test reports for all mandatory type tests specified in relevant technical specifications / standards for each item in the scope of supply. No extra payment or time shall be granted for type testing of equipment / materials.

Type test reports should have been issued during period not exceeding 5 years from the bid opening date. In case the type test reports are of the test conducted earlier than 5 (five) years prior to the date of bid opening, the contractor shall repeat these test(s) at no extra cost to the Employer.

Type tests reports shall be from reputed independent accredited testing laboratories accredited to ISO/IEC 17025:2005 for carrying out specified type tests. The test laboratories should be acceptable to the Employer.

In case the Contractor opts to supply any item from more than one manufacturer, certified copies of type tests reports shall be submitted for each manufacturer / product.

In the event of any discrepancy in the type test reports i.e. any test report not acceptable due to any model /design/manufacturing changes (including substitution of components) or due to non-compliance with the requirements stipulated in the Technical Specification required type tests shall be repeated without any additional cost implication to the Employer.

If Employer requires any additional type tests to be carried out or any mandatory type test to be repeated on the offered equipment in accordance with applicable standards, Contractor shall arrange such tests to be conducted as required. Reasonable costs incurred by the Contractor in this respect shall be reimbursed by the Employer as per invoice from the test laboratory and reasonable shipping and overhead costs.

### Routine and Acceptance Tests

Acceptance Tests shall mean those tests which are to be carried out on samples taken from each lot offered for pre-dispatch inspection, for the purposes of acceptance of that lot.

Routine Tests shall mean those tests, which are to be carried out on the material / equipment to check requirements which are likely to vary during production.

The Employer may nominate his representative and / or third-party inspection company to witness the acceptance tests to verify compliance to the specified technical requirements.

The Contractor shall facilitate such inspections in coordination with the manufacturer. The manufacturer shall afford the inspector all reasonable facilities, without charge, to satisfy him that the material is being furnished in accordance with the specifications. The Contractor shall submit notice of acceptance tests to be carried out by the manufacturer for each batch of supply at least two weeks in advance. Generally, acceptance tests shall be arranged together with pre-dispatch inspections.

### Inspections

The Employer, his duly authorized representative and/or third-party inspection agency acting on behalf of the Employer shall have free access at all reasonable times to the Contractor’s/sub-vendors premises of Works and shall have the power at all reasonable times to inspect and examine the materials and workmanship of the Works during its manufacture. Inspections may be made at any stage of manufacture, dispatch or at site at the discretion of the Employer and the equipment if found unsatisfactory due to bad workmanship or quality, are liable to be rejected.

The Contractor shall submit schedule of dispatch by the manufacturer for each batch of supply and Employer may nominate his representative and / or third-party inspection company to inspect the items prior to dispatch. The Employer may also make similar arrangements to inspect items at Contractor’s stores upon delivery. The Contractor in coordination with the manufacturer shall afford the inspector all reasonable facilities, without charge, to carry out such inspections.

### Packing, Marking and Transportation

Packing and markings shall be provided for all supply items shall be as specified in technical specifications.

All the items shall be suitably protected, sealed, coated, covered or boxed and crated to prevent damage or deterioration during transit, handling and storage. This includes any special arrangements required for transportation of larger equipment such as panels, transformers, RMUs and PSS.

The Contractor shall be responsible for any loss or damage during transportation, handling and storage due to improper packing.

### Handling and storage

The Contractor shall be responsible for examining all shipments and notify the Employer immediately of any damage, shortage, discrepancy etc. for the purpose of information only.

The Contractor shall be solely responsible for any shortages or damages in transit, handling and/or in storage and erection of the equipment at site. Any demurrage, wharfage and other such charges claimed by the transporters shall be the responsibility of the Contractor.

The Contractor shall be responsible for making suitable indoor/ outdoor storage facilities, to store equipment and materials until installation. Fenaka may assist the Contractor in securing such facilities or allow usage of its storage facilities in respective Islands, subject to availability.

The Contractor shall be fully responsible for the equipment / material until the same is handed over to the Employer in an operating condition after commissioning.

## Erection / Installation, Testing and Commissioning

All Installations shall be carried out by qualified and skilled staffs following proper technical procedures and using proper equipment and tools. The staff assigned to carry out erection work that require special skills / training such as installation of panels, transformers, PSS, underground cables and commissioning tests must have proper trade certificates for performing such specialized jobs. Workmanship of installations shall be of acceptable quality.

### Installation of Panels and Equipment

Installation of panels and equipment, transformers, PSS etc in the powerhouse as well as in field shall be carried out in full complacence with the applicable standards, local codes, and specifications following international best practices.

The Contractor must ensure availability of adequate space between equipment and building walls etc. to ensure safety of operators and to facilitate operation and maintenance activities. Heavy equipment such as transformers, PSS, RMUs shall be mounted in proper foundations / stands as per approved designs. In case of PSS and Distribution Boxes elevate foundation shall be used to ensure bottom levels are above the established flood levels.

Contractor must properly secure panels and equipment to ensure adequate mechanical strength against forces acting in all situations like fault currents. Cable terminations in panels and equipment shall be carried out using approved termination kits and cable entry properly secured using brass cable glands. Cable entry into panels and equipment must be properly sealed to block ingress of moisture and entry of rodents, termites etc. Required labelling including mimic diagrams, operating instructions, danger signs, permit to work boards shall be provided for panels and equipment as required.

Earthing shall be carried out as per applicable local codes, international standards and best practices. Earth cables shall be insulated type and proper accessories shall be used for earthing connections including earth rods, clamps etc. Earth resistance provided at earth pits shall be maintained below 1 Ohm. Where necessary chemical earthing compounds and other earth enhancing material shall be used in respective sites to obtain specified minimum earth resistance.

### Installation of underground cables

The Contractor is responsible to carryout LV and 11 kV underground cable installations complying with the standard practice by Fenaka. Upon completion of survey, the Contractor shall prepare and submit drawings of proposed cable routes including location of joints, road crossings and equipment and construction drawings for underground cable installations. These should be approved by the Employer prior to commencement of works. The rates submitted by the Bidders for installation of underground cables shall include all works and installation material, covering following requirements for underground cable installations;

Trench Design: The armoured MV and LV cables shall be installed direct buried in open cut trenches upto 1.2 m depth. Multiple cable circuits of MV and LV cables may be installed in the same trench to minimize excavation of roads and foot paths. The contractor shall submit trench plans for proposed cable lines, based on the proposed grouping and spacing of cable circuits with thermal capacity derating calculations for approval of the Employer. The cables shall be placed at specified depth in the trench on a fine sand bed of minimum 75 mm. Top fine stand layer shall also be provided so that total sand cushioning shall be at least 250 mm. Warning tape and protective tiles / bricks shall be provided at suitable depths for protection of cables.  Suitable cable route markers approved by the Employer shall be provided along the runs of cables at intervals not exceeding 100 m. The contractor shall be responsible to reinstate road / footpath surfaces as per original condition upon installation of cables.

Cable Joints and Termination: The heat shrink type jointing / termination kits approved by Employer shall be used for cable joints and terminations. Cable jointing / terminations shall be carried out by qualified and experienced jointers with proper trade certifications and experience whose CVs are approved by the Employer. Manufacturers’ instructions shall be strictly followed for carrying out cable joints and terminations. Accurate measuring, cutting, stripping and torque settings and workmanship shall be in accordance with the manufacturer’s instructions.

Joint Pits: For 11 kV cable lines cable pits shall be provided for cable joints. Joint pits shall be designed and construed by the Contractor as per Fenaka standard practice.

Road Crossings: For road crossings, cables shall be installed inside GI pipes / conduits of appropriate size as approved by the Employer. The total length of road crossings are expected to be less than 5% of the total length of LV and MV cables to be installed as indicated in the BOQs.

Cable Pulling: Stocking pulling, pulling eye or bond pulling methods may be used to pull the cables through conduits or in trenches. Armour pulling is not permitted for XLPE cables. Cables shall be pulled on appropriately placed rollers to avoid and damage to over sheath.

Cable pulling tensions shall not exceed the manufacturer’s recommendations. Winch used to pull cables shall have either a facility to automatically limit the pulling tension applied to a cable (a tension fuse) or a continuous reading dynamometer incorporated in the pulling arrangement to enable the actual pulling tension to be monitored.

End caps: Where MV or LV cables are to be placed without terminations such as at the vicinity of PV / FPV sites for future connections, cable ends shall be sealed using heat shrinkable end caps.

Testing and Commissioning:  The MV cables shall be tested during installation. The following tests shall be performed as per applicable standards;

- Insulation Resistance Test before installation of cable (in drums) and after laying but before jointing and terminations.

- Conductor Resistance tests after cable laying, jointing and terminations.

- Phase identification test

- High Voltage tests after laying of cable, jointing and terminations (If approved by the Employer)

Following successfully performing the tests indicated above and complete installation, the cables shall be energized at system voltage without load current for five minutes prior to application of load.

### Civil Works

All civil works shall be carried out in compliance with applicable local codes and in accordance with existing practice of Fenaka.

### Statutory Clearances and Approvals

The Contractor shall be responsible for obtaining statutory clearances, permits and approvals from the concerned authorities for execution of works. Employer shall provide necessary assistance and authorization for obtaining such clearances.  Applicable fees for obtaining such clearances shall be reimbursed by the Employer.

### Right of Way

Contractor is required to ensure approvals for right of way for cable lines and legal ownership / permits for use of proposed land for installation of field equipment are provided by the Employer. During pre-construction stage lines and facilities shall be planned to be installed in suitable areas avoiding any environmentally, ecologically and culturally sensitives areas. The guidelines provided in the Environmental Management Plan shall be followed in this respect. Contractor shall ensure any compensation required to be paid for right of way / land compensation (if any) are arranged by the Employer.

### Safety and Quality Assurance during Erection

The Contractor is required to submit Safety Plan and Quality Management Plan for execution of works for the approval of the Employer.

The Contractor shall ensure all approved safety and quality assurance measures and procedures are followed when carrying out erection works. Adherence to specified requirements shall be monitored by the Employer.

Employer shall to carry out inspections through his nominated staffs, consultants or third party inspectors, during execution to verify works are carried out in compliance to technical specifications, standards, safety procedures and are of acceptable quality of workmanship.

Employer has the right to issue notices of site observations / noncompliances against quality and safety of any works that are not satisfactory. The contractor shall follow-up such issues any implement necessary remedial actions. Any of the works with improper installation or poor workmanship are liable to be rejected the Employer.

### Supply Interruptions for Erection / Testing and Commissioning

Contractor shall be responsible for obtaining prior approval for required electricity supply interruptions for carrying out erection, testing and commissioning work. The contractor shall notify intended interruption schedules to the Fenaka authorities in respective Islands to process necessary approvals. The Contractor shall make all efforts to minimize supply interruptions by proper planning and scheduling of the works.

Electricity supply is an essential service in the Islands to ensure availability of other critical services such as water supply, health etc. Therefore, prolonged supply interruptions may not be permitted. Where prolonged supply interruptions are required due to nature of works, Contractor shall make alternate / temporary arrangements to ensure continued supply of electricity, particularly for critical services.

### Testing and Commissioning

The Contractor to submit detailed test plan and commissioning schedule for approval. The test plan shall comply with the requirements indicated in technical specifications and standards provided in Volume II.

Any special equipment and tools required for carrying out commissioning tests shall be provided by the contractor.

Pre-Commissioning: On completion of erection of the equipment and before charging, equipment and lines shall be inspected for correctness and completeness of installation. All equipment installation records shall also be verified and approved. Pre-commissioning tests shall be carried out as per approved test plan and results shall be recorded.

Commissioning of equipment and lines shall be carried out ensuring all components are operational and provide required functionality individually and collectively under energized condition. Required functional testing shall be carried out as per approved commissioning procedure and test plan.

### Completion and Operational Acceptance

Scope of works in each Island shall be considered as a sub-project for project management, certification and payment purposes.

Upon completion of supply of materials, installation and testing of the facilities at each designated Island (sub-project) the Contractor shall notify the Employer in writing. Upon such notification, the Employer/ Employer’s representative shall carry out the joint inspection along with the Contractor to verify the quantities and quality of material /work as per the employer’s requirement in section 6, technical specifications.

Subsequent to the joint inspection, joint inspection report will be issued with certified quantities of materials and works, and list of any defects and /or deficiencies (snag / defects list), jointly signed by Employer/ Employer’s representative and Contractor.

The delivery & installation status for payments is presumed to be completed at this stage provided there are no major defects listed. Pursuant to GCC clause 24, Employer will issue completion certificate in respect of the facilities at each designated site (sub-project).

Pursuant to GCC clause 25, the Contractor shall complete commissioning including pre- commissioning tests and notify the Employer in writing.

Pursuant GCC clause 25, Employer will issue operational acceptance in respect of the facilities for each designated site (sub-project). All defect / punch lists issued by the Employer with respect to works implemented by the Contractor shall be cleared prior to issuance of operational acceptance certificate.

## Spare parts

The Contractor is required to supply mandatory spare parts as indicated in technical specifications for respective items.

In addition, the bidder is required to provide schedule of recommended spare parts and tools (Schedule 6) based on life cycle requirements of the facilities as per on OEM recommendations.

Bidders shall note that the prices of recommended spare parts quoted in Price Schedule No. 6 will not be considered in the price bid evaluation. However the Employer may opt to include any of the recommended spare parts (deemed to be required in addition to mandatory spare parts) during bid award.

The Contractor shall ensure availability of spare parts required for the operation and maintenance of the installed facilities for a minimum period of 10 years from completion of defects liability period.

## Training

The Contractor shall arrange necessary training to nominated Fenaka staffs in each Island on operation and maintenance of following equipment;

- Low Voltage Distribution Board (LVDB)

- Medium Voltage Distribution Board (MVDB)

- Step-up Transformers,

- Underground Cables, and

- Package Substations

- LV Distribution Boxes (Feeder Pillars)

Training shall cover both theoretical and practical aspects of design, operation and maintenance of the equipment. In addition, training should include overall control, operation and management of the microgrid system, which should be provided as an on-the-job training of duration as recommended by the Contractor.

Bidder is required to submit a tentative Training Plan in accordance with the above requirements indicating scope and duration of each training module. The tentative training plan shall be finalized during execution of the Contract which should be implemented by the Contractor.

If any part of training is considered not satisfactory based on Fenaka evaluation, the Contractor may be required to repeat such training.

## Change Orders

If any variation is required in design or approved schedule of quantities and cost estimates, during implementation of works due to site conditions or technical requirements, the Contractor shall submit Request for Change Proposal with necessary justifications to the Employer and follow stipulated procedures as provided in this section. No changes shall be permitted by the Employer in the Contract without following applicable process for Change Orders.

The Bidders shall note that scope of works specified in the schedules and BOQs are subject to Change in the Facilities provisions as per clause 39 of GCC (Section 7) and any corresponding clause included in SCC (Section 7).

## Defect Liability

The Contractor is required to rectify, repair, replace, troubleshoot and remedy any defect/s in the design, engineering, materials, workmanship, software and in integration of equipment with specified systems, found and notified during the defect liability period as specified in the bid document.

## Time Schedule

The Contractor shall comply with the time schedule for completion as indicated in Appendix 4 (Section 9) of the bid document.

## Documentation upon completion

The Contractor is required to finalize and submit all documentation including as built drawings, georeferenced maps, wiring diagrams, settings, operation and maintenance manuals, safety instructions, licenses, clearances and guarantees prior to issuance of completion / substantial completion certificates.

## Project Management System (PMS)

### Employer will designate a Project Manager to coordinate and manage all project related activities who will act as the overall in-charge of the Project, whose decisions are binding on the implementation of the project. The successful bidder (Contractor) shall assign a Team Leader with the authority to make commitments and decisions. All communications between Employer and the Contractor shall be coordinated through the Project Manager.

In addition to above, the Employer shall appoint a Focal Point for each Island for coordination of all activities between the Project Manager and Team Leader of the Contractor who will also monitor and report contract activities in the Island.

### The Contractor shall comply with all requirements specified in the bid document including communications, submittals, approvals, documentation, progress monitoring, quality Assurance, occupational health & safety management system to ensure smooth functioning of the PMS. Any non-compliances with respect to the above will be dealt with in accordance with the terms and conditions of the Contract.

### In the event computerized / web-based tools are introduced by the Project Manager for effective functioning of PMS, the Contractor is required provide necessary facilities, data and inputs in a timely manner for functioning of such system.

### The Project Manager / ADB may appoint Consultants / third party inspectors to handle various technical and management aspects of the Project on their behalf. The Contractor is required to cooperate with such Consultants including provision of information and facilitating inspection of work.

### Organization Chart: The Bidder shall provide to the Employer an organization chart showing the proposed organization to be established for implementation of project activities if Contract is awarded to him.

### Project Implementation Program

The bidder shall submit proposed mobilization, construction plans, method statements and other information as provided in section 4, along with the bid for implementation of the scope of work.

The successful bidder (Contractor) shall submit detailed implementation program for review and approval of the Employer showing the sequence in which proposed implementation activities to be carried out with time periods in the form of “BAR CHART” and “SUB BAR CHARTS” within 28 days after effective date. Also, Contractor shall indicate the dates by which the Contractor reasonably requires that the Employer shall have fulfilled its obligations under the Contract so as to enable the Contractor to execute the contract in accordance with the program and to achieve completion, commissioning and acceptance in accordance with the Contract. The program so submitted by the Contractor shall accord with the dates and periods specified in the Contract.

The Contractor shall update, revise, and submit the program as and when appropriate.

### Communication Plan

The Project Manager will establish a communication plan with necessary time frames for supply of information and submittals etc. for effective management of the Project. The bidder shall provide his inputs / submittals according to such Plan.

### Document Control

The Contractor shall submit to the Employer all documents in accordance with the contract. The Contractor shall also submit any further information (in the form of drawings, documents, manuals, literature, reports etc.) when asked by the Employer.

The Contractor shall supply 3 hard copies and soft copy of all drawings and documents. The Contractor shall maintain a correspondence index and assign transmittal numbers for all Contractor documents. Employer shall also maintain a similar numbering scheme identifying documents and correspondence that Employer initiates.

The Contractor and Employer shall agree to establish a proper document control and identification system with necessary stamping and / or colour coding. This should include standard requirements with respect to document number, date, title, revision number etc. and document status stamps such as ‘For Approval’, ‘For Information’ ‘Approved’ ‘,Approved with comments’ , ‘Returned for Corrections’ etc

### Meetings

Scheduled project meetings shall be conducted each month attended by the Contractor, Employer and Consultants in order to review the progress and to discuss and resolve any implementation issues. Minutes of the meetings shall be maintained.

### Progress Reports

The Contractor shall monitor progress of all the activities specified in the project implementation program and supply a progress report to the Project Manager every month. The progress report shall be in a form acceptable to the Project Manager and shall indicate: (a) progress of physical completion for each activity; and (b) where any activity is behind the program, giving comments and likely consequences and stating the corrective action being taken.

Employer shall maintain an overall progress chart with respect to activities in all Islands, closely monitor progress of implementation works, review any activity falling behind the schedule for necessary corrective actions.

## Project Personnel:

The Bidder must demonstrate that it has the suitably qualified and experienced personnel  to manage and carry out project implementation works as per requirements indicated in Clause 8 of this section.

## Equipment:

The Bidder must demonstrate that they possess the required equipment for construction works as per requirements specified in clause 8.

The use of appropriate equipment and tools provided for work at site, may verified by the Employer during implementation activities.

## Environmental and Social Safeguards

The Contractor shall comply with all the applicable environment and social regulations in the country and shall obtain necessary permits, clearances and approvals prior to commencement of work. The Contractor shall comply with ADB environmental safeguard requirements [ADB’s Safeguard Policy Statement (2009)], the International Finance Corporation’s Environmental Health and Safety General Guidelines and the guidelines.

The Environmental Management Plan (EMP) applicable to this Project is provided in Appendix AA of Volume I. The contractor will be required to comply with the EMP requirements during all relevant phases, which will be closely supervised and monitored by the Employer and ADB. The contractor will be delegated, through the contract, the requirement to undertake relevant mitigation and monitoring actions as set out in the EMP. The contractor is required to engage suitably qualified and experienced environmental safeguards team as per EMP to monitor and supervise the contractor’s EMP implementation on a day-to-day basis. They will be responsible for reporting environmental safeguards progress and performance in accordance with the EMP.

## Environmental, Health and Safety Management

The Contractor is required to comply with all applicable labour, health and safety regulations of Maldives and shall obtain all necessary permits and clearances prior to commencement of the work.

Pursuant to requirements specified in Section 3, Bidder is required submit an outline Environmental Health and Safety Management Plan (EHSMP) commensurate with the risks and impacts of the proposed works and activities. The Contractor shall submit detailed EHSMP during execution stage for approval of the Employer which shall be followed and closely monitored during implementation.

Also, the Contractor shall comply with the EHS requirements specified in the EMP. Accordingly the contractor is required to employ suitably qualified and experienced EHS staffs to monitor and supervise implementation activities on a day-to-day basis and to report EHS assessments and progress.

# Specifications

2.1 	Technical specifications provided in Volume – II shall be applicable for supply of plant / equipment and materials and execution of works. The Design Diagrams and Equipment Schedules provided therein shall also be applicable for supply and works as well as for identification of scope of works for respective Islands.

2.2	All equipment, material and works shall comply with the standards provided in technical specifications. Other alternative standards which ensure equal or better quality than the standard mentioned above, will also be considered for acceptance. In such case bidder shall submit copies of the alternate standards together with comparison of requirements as per applicable standards. Decision of the Employer regarding acceptance of alternate standards shall be final.

2.3	In case technical specifications does not cover details of certain items, bidder shall offer suitable product and specifications as per item description in the Schedules and intended application, which is subject to approval of the Employer during contract execution stage.

2.4	Order of precedence for technical specifications:

Bidders shall note that the following order of precedence shall apply with respect to technical requirements.

- Price Schedules (BOQs) provided in Section 4.

- Volume I – All Sections Including Section 6

- Design Diagrams and Equipment Schedules, Volume – II

- Technical Specifications, Volume II

In the event of any ambiguity or uncertainty with respect to interpretation of the technical requirements provided in bid document, the above order of precedence shall apply, unless otherwise advised by the Employer during execution of the Contract.

# Environmental, Health and Safety Management Requirement

The bidder will not take access of the powerhouse site from the Employer until they have satisfied themselves that FENEKA has complied with the corrective action plan for existing facilities.

The bidder will implement all actions and responsibilities allocated to the contractors under the EMP (Appendix AA of Volume I) for the full duration of the contractor’s involvement in the project, ensuring adherence to all applicable national environment, health, safety, and labor laws and regulations in force at the time and ensuring adherence to ADB’s Safeguard Policy Statement (2009) and the related IFC Environment, Health and Safety (EHS) guidelines.

The bidder will ensure the feasibility studies and detailed designs reflect the EMP requirements; seeking to ensure the same or no worse impact than the design assessed in the IEE available at https://www.adb.org/projects/documents/mld-55191-001-iee.

The bidder will ensure adequate budget and staff resources are allocated to comply with and implement the contractor’s responsibilities under the EMP and to supervise and monitor the active construction site to protect the environment and ensure the health and safety of all workers and affected communities. They will ensure a suitably qualified and experienced safeguards team has been appointed to undertake regular on-site supervision and monitoring activities before the commencement of works. Each island and active construction site is to have adequate health and safety supervision to ensure the health and safety of all workers and local communities; the environment officer and health and safety officer will be supported by full-time on-site EHS supervisors with at least one supervisor per island, and full-time on-site Health and Safety stewards with at least one steward at each active construction site

The bidder will undertake and document a facilitated health and safety risk assessment considering all stages of the project, not just those stages the contractor is responsible for. The bidder will prepare a Construction Environment Management Plan (CEMP) and a Construction Health and Safety Management Plan (CHSMP) both with sub-plans as specified in the EMP for review and approval by the Employer prior to the commencement of works – these documents will comprise the contractor’s Environmental, Health, and Safety Management Plan (EHSMP). The Environmental, Health, and Safety Management Plan (EHSMP) shall cover, but not limited to the following:

Standards and Guidelines to be followed:

- National environment, health and safety (labor) laws and regulations as detailed in the IEE, Chapter II

- IFC EHS General Guidelines (https://www.ifc.org/en/insights-reports/2000/general-environmental-health-and-safety-guidelines)

- ILO Safety and Health in Construction (https://www.ilo.org/global/topics/safety-and-health-at-work/normative-instruments/code-of-practice/WCMS_107826/lang--en/index.htm)

- ILO worker accommodation standards (https://www.ilo.org/wcmsp5/groups/public/---ed_emp/---emp_ent/---multi/documents/publication/wcms_116344.pdf)

- World Health Organization Community Noise Guidelines and Ambient Air Quality Guidelines.

- World Health Organization Drinking Water Standards where more stringent than national standards

The bidder will ensure no site establishment or construction activity is to take place before the Employer has received and approved the detailed design and requisite contractor’s EHSMP (CEMP and CHSMP including all sub-plans).

The bidder will ensure that all construction workers including all formal and informal employees and subcontractors understand their responsibilities to implement the EMP and mitigate environmental impacts associated with pre-construction and construction activities. They will ensure attendance at EHS training provided by the Employer. They will provide and ensure attendance at EHS training for formal and informal construction workers and other personnel as required.

The bidder will adopt a zero-tolerance approach to OHS on the project, enforce all workers to comply with the OHS requirements of the EMP including the wearing of appropriate PPE on the construction site.

The bidder will support the Employer in undertaking ongoing public consultations and implementing the site-level GRM; in particular, the contractor’s GRM focals (safeguards team) shall thoroughly document details of complaints and make its best efforts to resolve the complaints at project site level; all this information is to be included in monthly reports to be submitted by the contractor to the Employer.

The bidder will undertake environmental monitoring as set out in the EMOP (Appendix AA of Volume I) for the duration of their involvement in the project and documenting qualitative and quantitative monitoring results.

The bidder will establish their own internal systems for monitoring and reporting their EMP implementation.

The bidder will attend monthly EHS meetings and submit monthly and quarterly environmental management reports per an agreed template to the Employer (these reports will be included as part of the contractor’s monthly progress reports), relating the work undertaken over the reporting period and documenting the environmental measures including monitoring activities that have been carried out, problems encountered, record data including near misses and incidents, grievances received, and follow-up actions that were taken (or will be taken) to correct the problems.

The bidder will inform the Employer immediately in case of any approved detailed design changes or unanticipated environmental impacts occurring during the project implementation stage, and as required, provide any information needed to the Employer to enable them to promptly update the IEE/EMP for clearance by ADB before any changes are implemented.

The bidder will inform the Employer within 24 hours in case of chance find or incident on site and providing within 48 hours an incident report with corrective action detailing how reoccurrence will be prevented.

The bidder will inform the Employer immediately in case of any non-compliance and help them to prepare as necessary a corrective action plan for clearance by the financier, the contractor is required to implement all necessary corrective action requested by the Employer to ensure the project remains in compliance with national regulatory requirements, ADB’s Safeguard Policy Statement (2009), the project’s loan covenants and EMP requirements.

Some of the environmental concerns envisaged for the project and its mitigation measures are mentioned in the IEE available at https://www.adb.org/projects/documents/mld-55191-001-iee:

- Grid upgrades work shall only be carried along existing roads and no vegetation will be cleared or trees removed for cable laying.

- Cable routes should avoid the area beneath tree crowns (zone for root protection) especially for mature trees.

- Contractors should provide an inventory of physical cultural resources e.g., mosques adjacent to the grid cable works to inform the construction workers of the need to avoid damage to them.

- Inform the timing of noisy construction works to residents and if existing services will be disrupted, affected communities must be informed well in advance of any power outages.

- For private property or public utilities/street furniture that may be damaged during construction, including from potential breaking/drilling vibration damage (buildings, roads, drains etc.) photographic and/or structural pre-condition surveys are to be completed and agreed with MOECCT prior to any works, including site establishment. To be documented in a pre-project condition report, which will serve as baseline in case any inadvertent damage or vibration impact to property occurs. If risk of structural damage to adjacent properties from vibration identified due to current condition, consider alternative construction methods or temporary relocation of occupants during works if at risk.

- Check with public service providers (electric, water, telecoms) whether there are known pipes, cables, or other utility lines and carry out a scan using cable avoidance tool to identify any unknown underground utilities prior to excavation. Contractors to identify in consultation with service providers appropriate measures to minimize period of disruption to utilities and reduce health and safety risks during installation.

- Trenching and cable laying work will be carried out as fast as possible; the trenches will only be left open for a single day. Whole roads will not be blocked with temporary diversion plans following the traffic management sub-plan as needed

- Work will be barricaded with solid moveable fences/barriers, warning signs, lights, and flag persons provided to control pedestrian and traffic movement

Impact on workers:

- Workers may be put at physical risk from electrical shocks, dust, handling heavy materials and equipment, falls and falling objects, work on slippery surfaces, fire hazards, and chemical hazards such as toxic fumes and vapours from batteries which cause significant damage; all of which will be present throughout the project construction period. Workers may come into contact with high-voltage power lines/equipment during operation, maintenance and repair. Other hazards include accidents, flammable gas, carbon monoxide, and fire. These impacts can be mitigated by undertaking a risk assessment, and management planning following the mitigation hierarchy including the use of Personal Protective Equipment (PPE) as the last resort and Emergency Response Procedures (ERP), developed in compliance with relevant safety regulations and guidelines.

- Project construction has the potential to cause disturbances in the community, such as public safety risks from construction activities, spills of materials, and risks associated with unauthorized entry into work areas. These potential impacts can be mitigated by implementing good community health and safety practices, installation of site safety fencing and warning signs and, employing on-site supervision personnel (including night guards) as determined by the risk, to prevent unauthorized access to construction areas.

In addition to the above, the contractor should follow the requirements of the Environmental Management Plan provided in Appendix AA of Volume I.

Schedule for monitoring and supervision:

The contractor shall undertake periodic monitoring as per an agreed schedule to ensure that management measures are being fulfilled to mitigate environmental and social impacts.

Monitoring will focus on the two key areas discussed below as well as those required under the Environmental Monitoring Plan attached in Appendix AA of Volume I:

Compliance Monitoring

- During the project preparation phase, compliance monitoring activities will focus on ensuring the effective implementation of the EMP and contractor’s Environmental, Health, and Safety Management Plan.

- The environmental officer and health and safety officer of the Contractor agency will ensure proper and timely implementation of environment, health and safety measures in compliance with the EMP and contractor’s Environmental, Health, and Safety Management Plan.

- During the implementation phase, compliance monitoring by the Employer will include inspections during the construction of the project’s components to verify the extent to which environmental authorization conditions and the EMP and contractor’s EHSMP are being adhered to.

Impact monitoring:

- The EMP and contractor’s Environmental, Health, and Safety Management Plan (EHSMP) will form the basis for contractor activities at the project site to ensure that works proceed in accordance with required mitigation and management measures.

Arrangement for Reporting:

Monthly and quarterly project environmental and social progress reports will be compiled as part of project performance reporting. Such environmental and social reporting would be integrated with overall project status and performance reporting. The reporting should include parameters required to be monitored by the Contractor as outlined in the Environmental Monitoring Plan in Appendix AA of Volume I.

Requirement for training and capacity building:

The implementing agency will provide training to all the staff working on-site. This training program will focus on environmental, health and safety laws, regulations and policies, for the proposed grid upgrade work.

# Drawings

  - The Design Diagrams provided for respective Islands in Volume II shall be applicable. Bidders shall note that the design diagrams provided are indicative. Detailed designs shall be prepared and finalized by the successful Bidder upon site survey.

  - The Contractor during implementation phase is required prepare required construction drawings in accordance with the designs, BOQs, characteristics of the equipment offered and as per applicable specifications, standards & statutory requirements and submit them for approval of the Employer.

  - All drawings submitted by the Contractor shall be in sufficient detail to indicate the type, size, arrangement, material description, BOQs, weights, dimensions, internal & external connections, fixing arrangements and any other information specifically requested in the specifications.

  - Each drawing submitted by the Contractor shall be clearly marked with the drawings and revision numbers, name of the Employer & Contractor, title, reference number and the name of the Project. If standard catalogue pages are submitted, the applicable items shall be indicated therein. All titles, noting, markings and writings on the drawing shall be in English. All the dimensions should be in metric units.

Further, work carried out by the Contractor shall be in strict accordance with the approved drawings and any deviation if so required, shall be permitted with the written approval of the Employer.

  - The review of these drawings by the Employer will cover only general conformance of the data to the specifications and documents interfaces with the equipment provided under the specifications. This review by the Employer may not indicate a thorough review of all dimensions, quantities and details of the equipment, materials, any devices or items indicated or the accuracy of the information submitted. This review and/or approval by the Employer shall not be considered by the Contractor as limiting any of his responsibilities and liabilities for mistakes and deviations from the requirements, specified under these specifications and documents.

  - All manufacturing and fabrication work in connection with the equipment prior to the approval of the drawings shall be at the Contractor’s risk. The Contractor may make any changes in the design which are necessary to make the equipment conform to the provisions and intent of the Contract and such changes will again be subject to approval by the Employer. Approval of Contractor’s drawing or work by the Employer shall not relieve the contractor of any of his responsibilities and liabilities under the Contract.

  - All drawings and engineering data submitted by the Contractor after final process including review and approval by the Employer shall form part of the Contract Document and the entire works performed shall be performed in strict conformity with the specifications, unless otherwise expressly requested by the Employer in Writing.

# Certificates

## Form of Completion Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Dear Ladies and/or Gentlemen,

Pursuant to GCC Clause 24 (Completion of the Facilities) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . . . .insert date. . . . . ], relating to the [. . . .brief description of the Facilities . . . .], we hereby notify you that the following part(s) of the Facilities was (were) complete on the date specified below, and that, in accordance with the terms of the Contract, the Employer hereby takes over the said part(s) of the Facilities, together with the responsibility for care and custody and the risk of loss thereof on the date mentioned below.

1.	Description of the Facilities or part thereof:  [. . . .description . . . .]

2.	Date of Completion:  [. . . .date . . . .]

However, you are required to complete the outstanding items listed in the attachment hereto as soon as practicable.

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

## Form of Operational Acceptance Certificate

Contract: [. . . . .insert name of contract and contract identification details.  . . . . ]

Date:

Certificate No.:

To:  [. . . . .insert name and address of contractor.  . . . . ]

Pursuant to GCC Subclause 25.3 (Operational Acceptance) of the General Conditions of the Contract entered into between yourselves and the Employer dated [. . .date. . .], relating to the [. . .brief description of the facilities. . .], we hereby notify you that the Functional Guarantees of the following part(s) of the Facilities were satisfactorily attained on the date specified below.

1.	Description of the Facilities or part thereof:  [. . . description . . .]

2.	Date of Operational Acceptance:  [. . . date . . .]

This letter does not relieve you of your obligation to complete the execution of the Facilities in accordance with the Contract nor of your obligations during the Defect Liability Period.

Very truly yours,

[. . . .Signature . . . .]

Project Manager

# Change Orders

## Change order procedure

### General

This section provides samples of procedures and forms for implementing changes in the Facilities during the performance of the Contract in accordance with GCC Clause 39 (Change in the Facilities) of the General Conditions.

### Change Order Log

The Contractor shall keep an up-to-date Change Order Log to show the current status of Requests for Change and Changes authorized or pending. Entries of the Changes in the Change Order Log shall be made to ensure that the log is up-to-date. The Contractor shall attach a copy of the current Change Order Log in the monthly progress report to be submitted to the Employer.

### References for Changes

(1) Request for Change as referred to in GCC Clause 39 shall be serially numbered CR-X-nnn.

(2) Estimate for Change Proposal as referred to in GCC Clause 39 shall be serially numbered CN-X-nnn.

(3) Acceptance of Estimate as referred to in GCC Clause 39 shall be serially numbered CA-X-nnn.

(4) Change Proposal as referred to in GCC Clause 39 shall be serially numbered CP-X-nnn.

(5) Change Order as referred to in GCC Clause 39 shall be serially numbered CO-X-nnn.

Note:

(a)	Requests for Change issued from the Employer’s Home Office and the Site representatives of the Employer shall have the following respective references:

Home Office	CR-H-nnn

Site	CR-S-nnn

(b)	The above number “nnn” is the same for Request for Change, Estimate for Change Proposal, Acceptance of Estimate, Change Proposal and Change Order.

## Change Order Forms

### Request for Change Proposal Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to the captioned Contract, you are requested to prepare and submit a Change Proposal for the Change noted below in accordance with the following instructions within [  number  ] days of the date of this letter [or on or before (  date  )].

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Originator of Change:

Employer:  [Name]

Contractor (by Application for Change Proposal No. [Number Refer to Annex 6.2.7])

4.	Brief Description of Change:  [  Description  ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [  Description  ]

6.	Reference drawings and/or technical documents for the request of Change:

Drawing No./Document No.		Description

7.	Detailed conditions or special requirements on the requested Change:  [  Description  ]

8.	General Terms and Conditions:

(a)	Please submit your estimate showing what effect the requested Change will have on the Contract Price.

(b)	Your estimate shall include your claim for the additional time, if any, for completing the requested Change.

(c)	If you have any opinion that is critical to the adoption of the requested Change in connection with the conformability to the other provisions of the Contract or the safety of the Plant or Facilities, please inform us in your proposal of revised provisions.

(d)	Any increase or decrease in the work of the Contractor relating to the services of its personnel shall be calculated.

(e)	You shall not proceed with the execution of the work for the requested Change until we have accepted and confirmed the amount and nature in writing.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Estimate for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

With reference to your Request for Change Proposal, we are pleased to notify you of the approximate cost to prepare the below-referenced Change Proposal in accordance with GCC Subclause 39.2.1 of the General Conditions.  We acknowledge that your agreement to the cost of preparing the Change Proposal, in accordance with GCC Subclause 39.2.2, is required before estimating the cost for change work.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Number  ]

3.	Brief Description of Change:  [  Description  ]

4.	Scheduled Impact of Change:  [  Description  ]

5.	Cost for Preparation of Change Proposal:  [  insert costs, which shall be in the currencies of the contract  ]

(a)	Engineering	(Amount)

(i)	Engineer		 hours (hrs) x 	 rate/hr =

(ii)	Draftsperson		 hrs x 	 rate/hr =

Sub-total		 hrs

Total Engineering Cost

(b)	Other Cost

Total Cost (a) + (b)

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Acceptance of Estimate Form

[ Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [ Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby accept your Estimate for Change Proposal and agree that you should proceed with the preparation of the Change Proposal.

1.	Title of Change:  [  Title  ]

2.	Change Request No./Rev.:  [  Request number/revision  ]

3.	Estimate for Change Proposal No./Rev.:  [  Proposal number/revision  ]

4.	Acceptance of Estimate No./Rev.:  [  Estimate number/revision  ]

5.	Brief Description of Change:  [  Description  ]

6.	Other Terms and Conditions:  In the event that we decide not to order the Change accepted, you shall be entitled to compensation for the cost of preparing the Change Proposal described in your Estimate for Change Proposal mentioned in para. 3 above in accordance with GCC Clause 39 of the General Conditions.

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

In response to your Request for Change Proposal No. [Number], we hereby submit our proposal as follows:

1.	Title of Change:  [  Name  ]

2.	Change Proposal No./Rev.:  [  Proposal number / revision ]

3.	Originator of Change:	Employer:  [ Name  ] / Contractor:  [  Name  ]

4.	Brief Description of Change:  [  Description  ]

5.	Reasons for Change:  [  Reason  ]

6.	Facilities and/or Item No. of Equipment related to the requested Change:  [  Facilities  ]

7.	Reference drawings and/or technical documents for the requested Change:

[  Drawing/Document No./Description  ]

8.	Estimate of increase/decrease to the Contract Price resulting from the Change Proposal:

Amount

[ insert  amounts in the currencies of the Contract ]

(a)	Direct material

(b)	Major construction equipment

(c)	Direct field labor (Total 	 hrs)

(d)	Subcontracts

(e)	Indirect material and labor

(f)	Site supervision

(g)	Head office technical staff salaries

Process engineer		 hrs @ 	 rate/hr

Project engineer		 hrs @ 	 rate/hr

Equipment engineer		 hrs @ 	 rate/hr

Procurement		 hrs @ 	 rate/hr

Draftsperson		 hrs @ 	  rate/hr

Total			hrs

(h)	Extraordinary costs (computer, travel, etc.)

(i)	Fee for general administration, 	 % of Items

(j)	Taxes and customs duties

Total lump sum cost of Change Proposal		[  Sum of items (a) to (j)  ]

Cost to prepare Estimate for Change Proposal	 [  Amount payable if Change is not accepted  ]

9.	Additional time for Completion required due to Change Proposal

10.	Effect on the Functional Guarantees

11.	Effect on the other terms and conditions of the Contract

12.	Validity of this Proposal:  within [Number] days after receipt of this Proposal by the Employer

13.	Other terms and conditions of this Change Proposal:

(a)	You are requested to notify us of your acceptance, comments or rejection of this detailed Change Proposal within [Number] days from your receipt of this Proposal.

(b)	The amount of any increase and/or decrease shall be taken into account in the adjustment of the Contract Price.

(c)	Contractor’s cost for preparation of this Change Proposal: [ . . . .insert amount. This cost shall be reimbursed by the employer in case of employer’s withdrawal or rejection of this Change Proposal without default of the contractor in accordance with GCC Clause 39 of the General Conditions . . . . ]

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We approve the Change Order for the work specified in the Change Proposal (No. [  number  ]), and agree to adjust the Contract Price, Time for Completion, and/or other conditions of the Contract in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Change Request No./Rev.:  [  Request number / revision  ]

3.	Change Order No./Rev.:  [  Order number / revision  ]

4.	Originator of Change:	Employer:  [Name] / Contractor:  [  Name  ]

5.	Authorized Price:

Ref. No.:  [  Number  ]	Date:  [  Date  ]

Foreign currency portion [  Amount  ]  plus Local currency portion [  Amount  ]

6.	Adjustment of Time for Completion

None		Increase [  Number  ] days	 	Decrease [  Number  ] days

7.	Other effects, if any

Authorized by:  		Date:

Employer

Accepted by:  		Date:

Contractor

### Pending Agreement Change Order Form

[  Employer’s letterhead  ]

To:  [  Contractor’s name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We instruct you to carry out the work in the Change Order detailed below in accordance with GCC Clause 39 of the General Conditions.

1.	Title of Change:  [  Name  ]

2.	Employer’s Request for Change Proposal No./Rev.:  [  number/revision  ]	dated:  [ date  ]

3.	Contractor’s Change Proposal No./Rev.:  [  number / revision  ]	dated:  [ date ]

4.	Brief Description of Change:  [ Description ]

5.	Facilities and/or Item No. of equipment related to the requested Change:  [ Facilities ]

6.	Reference Drawings and/or technical documents for the requested Change:

[  Drawing / Document No. / Description  ]

7.	Adjustment of Time for Completion:

8.	Other change in the Contract terms:

9.	Other terms and conditions:

[  Employer’s name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

### Application for Change Proposal Form

[  Contractor’s letterhead  ]

To:  [  Employer's  name and address  ]	Date:

Attention:  [  Name and title  ]

Contract Name:  [  Contract name  ]

Contract Number:  [  Contract number  ]

Dear Ladies and/or Gentlemen:

We hereby propose that the work mentioned below be treated as a Change in the Facilities.

1.	Title of Change:  [  Name  ]

2.	Application for Change Proposal No./Rev.:  [  Number / revision  ]	dated:  [  Date  ]

3.	Brief Description of Change:  [  Description  ]

4.	Reasons for Change:

5.	Order of Magnitude Estimation (amount in the currencies of the Contract): [  Amount  ]

6.	Scheduled Impact of Change:

7.	Effect on Functional Guarantees, if any:

8.	Appendix:

[  Contractor's name  ]

[  Signature  ]

[  Name of signatory  ]

[  Title of signatory  ]

# Personnel Requirements

Using Form PER-1 and PER-2 in Section 4 (Bidding Forms), the Bidder must demonstrate that it has personnel who meet the following requirements, for each Lot:

| No | Position | Total Work Experience [years] | Experience in Similar Work [years] |
| --- | --- | --- | --- |
| 1 | Team Leader | 8 | 5 |
| 2 | Site Manager / Electrical Engineer (Assigned to one or group of Islands) | 5 | 5 |
| 3 | Electrical Engineers experienced in design, engineering, construction, testing and commissioning Switchgear Panels, Transformers, PSS, Underground Cabling | 5 | 3 |
| 4 | Specialist Engineer for integration of panels and equipment with automated control systems (BMS/EMS) | 5 | 3 |
| 4 | Construction Supervisors experienced in erection and commissioning of design, engineering, construction, testing and commissioning Switchgear Panels, Transformers, PSS and Underground Cabling | 5 | 3 |
| 5 | Civil Engineer with experience in powerhouse or substation building construction. | 5 | 3 |
| 6 | Skilled manpower (specialized) with requisite tradesmen/ license/certifications in following fields; * Cable Jointers and Underground Cabling Technician * Technicians for Switchgear Panel Installation * Technicians for electrical equipment installation | 5 | 3 |
| 7 | Survey and mapping staff | 2 | 2 |

* No of personnel and period of engagement shall be as determined by the Contractor, to ensure timely completion of works. Team Leader and Site Manager shall be available on full time basis during construction phase.

Using Form EXP-6 in Section 4 (Bidding Forms), the Bidder must demonstrate that it has EHS personnel who meet the following requirements:

Key Personnel as determined by the EMP and other safeguard management plans

| No. | Position/specialization | Relevant academic qualifications | Minimum years of relevant work experience | Minimum time on-site (%FTE) |
| --- | --- | --- | --- | --- |
| 1 | Environment and social officer | As per EMP with Degree in environmental management |  | Full-time |
| 2 | Health and Safety Officer | As per EMP with NEBOSH/IOSH certification or equivalent |  | Full-time |

# Equipment Requirements

Using Form EQU in Section 4 (Bidding Forms), the Bidder must demonstrate that it has the key equipment listed below:

| No | Equipment Type and Characteristics* | Minimum Number Required |
| --- | --- | --- |
| 1 | Insulation Tester | Quantities to be determined by the bidder suit implementation the scope of works in Respective Islands |
| 2 | Earth Resistance Tester |  |
| 3 | Secondary Injection Test Set |  |
| 4 | Digital Clamp Meter |  |
| 5 | Phase Sequence Indicator |  |
| 6 | Tools & Tackles (complete set) |  |
| 7 | Drill machine with bits |  |
| 8 | Oil Testing Equipment |  |
| 9 | Crimping Machine |  |
| 10 | GPS Receivers |  |
| 11 | Cable pulling winch machine |  |
| 12 | Cable Drum Trailer / Drum Jacks / Stands |  |
| 13 | Cable rollers |  |
| 14 | Cable rollers |  |
| 15 | Cable testing equipment |  |
| 16 | Personal protective equipment (PPE) including helmets, safety glasses, gloves, and appropriate clothing |  |
| 17 | Portable fire extinguisher |  |
| 18 | Truck mounted crane for lifting and transporting heavy equipment |  |
| 19 | Chain hoist / Pallet jacks or forklift |  |
| 20 | Concrete Mixer |  |
| 21 | Excavation equipment |  |
| 22 | Construction Vehicles |  |

* Bidder may propose alternate equipment based on the site conditions.